## Overview
Initiating Events Coding Guidance Document. (double-click icon to open) | IPF Code | IPF ShortDesc | IPFDesc
| A1 | Station Blackout | Station blackout. Loss of offsite power and the loss of emergency power to all ac busses.
| B1 | Loss of Offsite Power (LOSP) | A simultaneous loss of electrical power to all safety-related buses that causes emergency power generators to start and supply power to the safety-related buses. The offsite power boundary extends from the offsite electrical power grid to the output breaker (inclusive) of the step-down transformer that feeds the first safety-related bus with an emergency power generator. The plant switchyard and service-type transformers are included within the offsite power boundary. This category includes the momentary or prolonged degradation of grid voltage that causes all emergency power generators to start (if operable) and load onto its associated safety-related buses (if available). This category does not include an LOSP event that occurs while the plant is shutdown. In addition, it does not include any momentary undervoltage event that results in the automatic start of all emergency power generators, but in which the generators do not tie on to their respective buses due to the short duration of the undervoltage. Loss of Offsite Power – Note that this event does not include events involving a momentary undervoltage that causes the EDGs to auto start but not load.
| C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) | Loss of Safety-Related Buses – Excluded are events involving momentary de-energization of buses caused by slow auto bus transfer. Also excluded are events where a bus is de-energized by spurious circuit breaker actuation or personnel error. Generally, there must be damage or some reason of unavailability besides an open circuit breaker (e.g., cable ground, transformer fault, etc.) Loss of a safety related electrical bus is any sustained de-energization of a safety-related bus due to the inability to connect to any of the normal or alternative electrical power supplies. The bus must be damaged or its power source unavailable for reasons beyond an open, remotely operated feeder breaker from a live power source. Examples include: supply cable grounds; failed insulators; damaged disconnects; transformer deluge actuations; or improper uses of grounding devices. This category does not include a momentary de-energization of a bus caused by a slow automatic transfer to an available power source. Losses of all lower voltage buses caused by the loss of the medium voltage feeder bus are not classified under this category unless a lower voltage bus was damaged beyond use. A loss of power to a single component in another system because of a failed or mis-positioned breaker that does not affect the entire bus is not included in this category, but is instead classified as a failure of the system that the single breaker serves. For example: a circuit breaker failure that causes a loss of power to a condensate pump that results in inadequate condensate flow, would be classified as a Partial Loss of Condensate (QP4).
| C2 | Loss of Vital Low Voltage ac Bus (<600 V) | Loss of Safety-Related Buses – Excluded are events involving momentary de-energization of buses caused by slow auto bus transfer. Also excluded are events where a bus is de-energized by spurious circuit breaker actuation or personnel error. Generally, there must be damage or some reason of unavailability besides an open circuit breaker (e.g., cable ground, transformer fault, etc.) Loss of a safety related electrical bus is any sustained de-energization of a safety-related bus due to the inability to connect to any of the normal or alternative electrical power supplies. The bus must be damaged or its power source unavailable for reasons beyond an open, remotely operated feeder breaker from a live power source. Examples include: supply cable grounds; failed insulators; damaged disconnects; transformer deluge actuations; or improper uses of grounding devices. This category does not include a momentary de-energization of a bus caused by a slow automatic transfer to an available power source. Losses of all lower voltage buses caused by the loss of the medium voltage feeder bus are not classified under this category unless a lower voltage bus was damaged beyond use. A loss of power to a single component in another system because of a failed or mis-positioned breaker that does not affect the entire bus is not included in this category, but is instead classified as a failure of the system that the single breaker serves. For example: a circuit breaker failure that causes a loss of power to a condensate pump that results in inadequate condensate flow, would be classified as a Partial Loss of Condensate (QP4).
| C3 | Loss of Vital dc Bus | Loss of Safety-Related Buses – Excluded are events involving momentary de-energization of buses caused by slow auto bus transfer. Also excluded are events where a bus is de-energized by spurious circuit breaker actuation or personnel error. Generally, there must be damage or some reason of unavailability besides an open circuit breaker (e.g., cable ground, transformer fault, etc.) Loss of a safety related electrical bus is any sustained de-energization of a safety-related bus due to the inability to connect to any of the normal or alternative electrical power supplies. The bus must be damaged or its power source unavailable for reasons beyond an open, remotely operated feeder breaker from a live power source. Examples include: supply cable grounds; failed insulators; damaged disconnects; transformer deluge actuations; or improper uses of grounding devices. This category does not include a momentary de-energization of a bus caused by a slow automatic transfer to an available power source. Losses of all lower voltage buses caused by the loss of the medium voltage feeder bus are not classified under this category unless a lower voltage bus was damaged beyond use. A loss of power to a single component in another system because of a failed or mis-positioned breaker that does not affect the entire bus is not included in this category, but is instead classified as a failure of the system that the single breaker serves. For example: a circuit breaker failure that causes a loss of power to a condensate pump that results in inadequate condensate flow, would be classified as a Partial Loss of Condensate (QP4).
| D1 | Loss of Instrument or Control Air System | A total or partial loss of an instrument or control air system that leads to a reactor trip or occurs shortly after the reactor trip. Examples include: ruptured air headers; damaged air compressors with insufficient backup capability; losses of power to air compressors; line fitting failures; improper system line ups; and undesired operations of pneumatic devices in other systems caused by low air header pressure. This category does not include a loss of air to a single component in another system because of a blockage or incorrect line up that does not affect the header pressure, but is instead classified as a failure of the system that the single component serves. For example: a solenoid valve malfunction that causes a loss of plant air to a single feedwater valve and causes the feedwater valve to shut, would be classified as a Partial Loss of Feedwater (QP2). A loss of a redundant component in the air system is not classified as a partial loss of the air system as long as the remaining, similar components provide the required level of performance. Loss of Instrument or Control Air – A loss of a redundant component is the air system is not classified as a partial loss of instrument air as long as the similar component is available and does not fail.
| E1 | Total Loss of Service Water | Loss of Safety-Related Cooling Water – This category includes a loss of non-safety-related cooling water involving facilities where it provides cooling to safety-related components during normal plant operations (safety-related cooling water pumps auto start on loss of pressure). A service water system (SWS) can be an open-cycle or a closed-cycle cooling water system. An open-cycle SWS takes suction from the plant’s ultimate heat sink (e.g., the ocean, bay, lake, pond or cooling towers), removes heat from safety-related systems and components, and discharges the water back to the ultimate heat sink. A closed-cycle or intermediate SWS removes heat from safety related equipment and discharges the heat through a heat exchanger to an open-cycle service water system. These categories include the total or partial loss of a safety-related SWS, or a non-safety-related SWS that provides cooling to safety-related components during normal plant operations. For the latter case, a standby safety-related service water system automatically starts upon the loss of the non-safety-related system or during an accident sequence initiation.
| E2 | Partial Loss of Service Water | Loss of Safety-Related Cooling Water – This category includes a loss of non-safety-related cooling water involving facilities where it provides cooling to safety-related components during normal plant operations (safety-related cooling water pumps auto start on loss of pressure). A service water system (SWS) can be an open-cycle or a closed-cycle cooling water system. An open-cycle SWS takes suction from the plant’s ultimate heat sink (e.g., the ocean, bay, lake, pond or cooling towers), removes heat from safety-related systems and components, and discharges the water back to the ultimate heat sink. A closed-cycle or intermediate SWS removes heat from safety related equipment and discharges the heat through a heat exchanger to an open-cycle service water system. These categories include the total or partial loss of a safety-related SWS, or a non-safety-related SWS that provides cooling to safety-related components during normal plant operations. For the latter case, a standby safety-related service water system automatically starts upon the loss of the non-safety-related system or during an accident sequence initiation. Partial Loss of Service Water is a loss of one train of a multiple train system or partial loss of a single train system that impairs the ability of the system to perform its function. Examples include pump cavitation; strainer fouling; and piping rupture. These categories do not include a loss of a redundant component in a SWS as long as the remaining, similar components provide the required level of performance. For example, a loss of a single SWS pump is not classified as a partial loss of a SWS as long as the remaining operating or standby pumps can provide the required level of performance. A loss of service water to a single component in another system because of a blockage or incorrect line up that does not affect the cooling to other components serviced by the train is not included under this category, but is instead classified as a failure of the system that the single component serves.
| E3 | Loss component cooling water | Loss of Safety-Related Cooling Water – This category includes a loss of non-safety-related cooling water involving facilities where it provides cooling to safety-related components during normal plant operations (safety-related cooling water pumps auto start on loss of pressure). A component cooling water system (CCW) is a closed-cycle cooling water system. A closed-cycle removes heat from safety related equipment and discharges the heat through a heat exchanger to an open-cycle service water system. These categories include the total or partial loss of a safety-related CCW, or a non-safety-related CCW that provides cooling to safety-related components during normal plant operations. For the latter case, a standby safety-related service water system automatically starts upon the loss of the non-safety-related system or during an accident sequence initiation.
| E4 | Partial loss component cooling water | Loss of Safety-Related Cooling Water – This category includes a loss of non-safety-related cooling water involving facilities where it provides cooling to safety-related components during normal plant operations (safety-related cooling water pumps auto start on loss of pressure). A component cooling water system (CCW) is a closed-cycle cooling water system. A closed-cycle removes heat from safety related equipment and discharges the heat through a heat exchanger to an open-cycle service water system. These categories include the total or partial loss of a safety-related CCW, or a non-safety-related CCW that provides cooling to safety-related components during normal plant operations. For the latter case, a standby safety-related service water system automatically starts upon the loss of the non-safety-related system or during an accident sequence initiation. Partial Loss of CCW is a loss of one train of a multiple train system or partial loss of a single train system that impairs the ability of the system to perform its function. Examples include pump cavitation; strainer fouling; and piping rupture. These categories do not include a loss of a redundant component in a CCW as long as the remaining, similar components provide the required level of performance. For example, a loss of a single CCW pump is not classified as a partial loss of a CCW as long as the remaining operating or standby pumps can provide the required level of performance. A loss of CCW to a single component in another system because of a blockage or incorrect line up that does not affect the cooling to other components serviced by the train is not included under this category, but is instead classified as a failure of the system that the single component serves.
| F1 | Steam Generator Tube Rupture PWR (SGTR) | Only include events where the coolant lost to leaking or ruptured tubes exceeds 100 gpm. A rupture of one or more steam generator tubes that result in a loss of primary coolant to the secondary side of the steam generator at a rate greater than or equal to 100 gpm. A SGTR can occur as the initial plant fault, such as a tube rupture caused by high cycle fatigue or loose parts, or as a consequence of another initiating event. The latter case would be classified as a functional impact. This category applies to PWRs only. This category includes excessive leakage caused by the failure of a previous SGTR repair (i.e., leakage past a plug).
| G1 | Very Small LOCA or Leak | A pipe break or component failure that results in a loss of primary coolant between 10 to 100 gpm, but does not require the automatic or manual actuation of high-pressure injection systems. Examples include: reactor coolant pump (PWR) or recirculating pump (BWR) seal failures; valve packing failures; steam generator tube leaks; and instrument line fitting failures. Note: Leakage from a pressurizer code safety valve (PWR), main steam line safety valve (BWR), or Automatic Depressurization System relief valve (BWR) are classified under category G2 or G5. Leakage from a pressurizer power operated relief valve is classified under category G4. A steam generator tube rupture (PWR) is classified under category F1. A small primary system leak (less than 10 gpm) that results in a manual reactor trip is classified under category Primary System Leak (QG9). Category QG9 only applies to the initial plant fault group, however.
| G2 | Stuck Open (1 Safety Relief Valve) | A failure of one primary system safety and/or relief valve (SRV) to fully close that results in the loss of primary coolant. The valves included in this category are pressurizer code safety valves (PWR), main steam line safety valves (BWR), and Automatic Depressurization System relief valves (BWR). The stuck open SRV may or may not cause the automatic or manual actuation of high-pressure injection systems. This category includes a stuck open valve that cannot be subsequently closed upon manual demand (BWRs) or does not subsequently close on its own immediately after the reactor trip (BWRs). The mechanism that opens the valve is not a defining factor. The different mechanisms than can open an SRV are transient-induced opening, manual opening during valve testing (BWRs), and spurious opening. In BWRs, only a stuck open SRV event initiated by routine surveillance testing of the valve during power operations would be classified as an initial plant fault under this category since no other initial plant fault category applies. All stuck open single SRV events in BWRs and PWRs are classified as a functional impact under this category. An inadvertent open SRV event during power operations which closes on its own after the reactor trip and before the manual or automatic actuation of a high pressure injection system are classified under category QG10, Inadvertent Open/Close: 1 Safety/Relief Valve. Category QG10 only applies to the initial plant fault group, however. This category does not include a weeping safety valve. Note: A stuck open pressurizer power-operated relief valve (PWR) is classified under category G4.
| G3 | Small Pipe Break LOCA | For a BWR, a pipe in the primary system boundary with a break size less than 0.004 ft2 (or a 1 inch inside diameter pipe equivalent) for liquid and less than 0.05 ft2 (or an approximately 4 inch inside diameter pipe equivalent) for steam. For a PWR, a pipe break in the primary system boundary with an inside diameter between ½ to 2 inches. The above break size ranges were used in the NUREG-1150 analyses of a selected group of plants. The plant-specific range of LOCA sizes should be divided into groups for which plant response, in terms of required system operability, is the same or very similar. The following generic definition was used in NUREG-1150: a small break LOCA is a break that does not depressurize the reactor quickly enough for the low pressure systems to automatically inject and provide sufficient core cooling to prevent core damage. However, low capability systems (i.e., 100 to 1500 gpm) are sufficient to make up the inventory completion. Note: A steam generator tube rupture is classified under category F1. A steam generator tube leak is classified under category G1 or QG9. A stuck open safety or relief valve is classified under category G2, G4, or G5.
| G4 | Stuck Open: Pressurizer PORV | A pressurizer power-operated relief valve (PORV) that fails to close. This category applies to PWRs only.
| G5 | Stuck Open (2 or More Safety Relief Valves) | Two or more primary system safety and/or relief valves that fails to close. The valves included in this category are pressurizer code safety valves (PWR), main steam line safety valves (BWR), and Automatic Depressurization System relief valves (BWR). This category does not include a weeping safety valve. Note: A stuck open pressurizer power-operated relief valve (PWR) is classified under category G4, Stuck Open PORV.
| G6 | Medium Pipe Break LOCA | For a BWR, a pipe in the primary system boundary with a break size between 0.004 to 0.1 ft2 (or an approximately 1 to 5 inches inside diameter pipe equivalent) for liquid and between 0.05 to 0.1 ft2 (or an approximately 4 to 5 inches inside diameter pipe equivalent) for steam. For a PWR, a pipe break in the primary system boundary with an inside diameter between 2 to 6 inches. The above break size ranges were used in the NUREG-1150 analyses of a selected group of plants. The plant-specific range of LOCA sizes should be divided into groups for which plant response, in terms of required system operability, is the same or very similar. The following generic definition was used in NUREG-1150: a medium break LOCA is a break that does not depressurize the reactor quickly enough for the low pressure systems to automatically inject and provide sufficient core cooling to prevent core damage. However, the loss from the break is such that high capacity systems (i.e., 1500 to 5000 gpm) are needed to makeup the inventory depletion.
| G7 | Large Pipe Break LOCA | For a BWR, a pipe in the primary system boundary with a break size greater than 0.1 ft2 (or an approximately 5 inches inside diameter pipe equivalent) for liquid and steam. For a PWR, a pipe break in the primary system boundary with an inside diameter greater than 6 inches. The above break size ranges were used in the NUREG-1150 analyses of a selected group of plants. The plant-specific range of LOCA sizes should be divided into groups for which plant response, in terms of required system operability, is the same or very similar. The following generic definition was used in NUREG-1150: a large break LOCA is a break that depressurizes the reactor to the point where the low pressure systems can injection automatically providing sufficient core cooling to prevent core damage
| G8 | Reactor Coolant Pump Seal LOCA (PWR) | A catastrophic failure the reactor coolant pump seal assembly that results in a primary coolant leak into the primary containment at a rate greater than 100 gpm. This category applies to PWRs only. A reactor coolant pump seal leak with a leak rate less than 100 gpm is classified under category G1 or QG9.
| H1 | Fire | Fire – To be coded as a fire, the smoke or flames must result in damage to equipment (safety-related or not). Something like a smoked relay or a trash can fire does not qualify. Smoke or flames inside the plant or site boundary that results in damage to safety- or non-safety-related equipment. Examples include: fires located in the plant switchyard (e.g., transformers, switchgear); burning thermal or electrical insulation; transformer, circuit breaker, and power supply fires; rags ignited by hot relief valve tailpipes; burning lube oil; and offsite brush fires that caused a loss of an electrical power transmission line. Fire-related events classified under this category typically require a response by plant personnel, however, damage to plant equipment determined in the post event evaluation to be caused by a fire that went undetected is also included in this category. This category does not include a smoldering lightning arrestor caused by a lightning strike; the “smoking” of a set of breaker auxiliary contacts or a small relay coil; a simple fire in a trash can or ash tray; or a fire to an administrative support building (e.g., trailer) that does not effect plant structures, equipment or components required to maintain the plant in a safe condition.
| J1 | Flood | A major on-site pipe break other than a high energy line break (as defined by heading K) that causes damage to structures, equipment, or components. An example of this is leakage from condensate or feedwater lines (as defined under category QK4) as long as the leakage resulted in damage to structures, equipment or components. This category does not include an activation of a transformer deluge system or natural flooding (e.g., river overflowing, heavy rains, etc.).
| K1 | Steam Line Break Outside Containment | High Energy Line Breaks – This category includes breaks of steam and feedwater lines greater than one inch in diameter. It does not have to be a complete break. Included are actuation or failure of rupture disks, splits, cracks, and failed welds. A break of one inch equivalent diameter or more in a steam line located outside the primary containment that contains main turbine working fluid at or above atmospheric saturation conditions. Examples include: operation of rupture disks; and breeches of a pipe caused by a split, crack, weld failure, or circumferential break.
| K2 | Feedwater Line Break | High Energy Line Breaks – This category includes breaks of steam and feedwater lines greater than one inch in diameter. It does not have to be a complete break. Included are actuation or failure of rupture disks, splits, cracks, and failed welds. A break of one inch equivalent diameter or more in a feedwater or condensate line that contains main turbine working fluid at or above atmospheric saturation conditions. Examples include: breeches of a pipe caused by a split, crack, weld failure, or circumferential break.
| K3 | Steam Line Break Inside Containment (PWR) | High Energy Line Breaks – This category includes breaks of steam and feedwater lines greater than one inch in diameter. It does not have to be a complete break. Included are actuation or failure of rupture disks, splits, cracks, and failed welds. A break of one inch equivalent diameter or more in a steam line located inside the primary containment that contains main turbine working fluid at or above atmospheric saturation conditions. This category applies to PWRs only. Examples include: breeches of a pipe caused by a split, crack, weld failure, or circumferential break.
| L1 | Inadvertent Closure of All MSIVs | Inadvertent Closure of All MSIVs – This includes automatic closure of at least one MSIV in each steam line, and manual closure of the MSIVs due to a fault (such as to isolate a steam leak) where the condenser heat sink is not available. This does not include events where the MSIVs are manually closed solely to limit primary cooldown. A complete closure of at least one MSIV in each main steam line. An example includes the automatic closure of all MSIVs as part of an engineered safety feature actuation. This category does not include a manual closure of all MSIVs to limit cooldown rate after a reactor trip, as long as the MSIVs are capable of being reopened by operator demand.
| L2 | Loss of Condenser Vacuum | Loss f Condenser Vacuum – This category includes loss of condenser vacuum events in which a complete loss of condenser vacuum prevents the condenser from removing decay heat after a reactor trip. This category does not include loss of condenser vacuum due to a loss of offsite power and does not include condenser vacuum lost after a reactor trip due to another cause (trip not directly related to low vacuum). The main condenser boundary includes the condenser air ejectors and condenser vacuum pumps. Ths category does not include events in which a degraded condenser vacuum causes a reactor trip, but the condenser is still available for removing decay heat after the reactor trip. These events should be coded as QL7, Degraded condenser vacuum. Note: In BWRs, a low condenser vacuum signal will generate a reactor trip. In PWRs, a low vacuum signal will cause turbine-driven main feedwater pumps to trip, which will result in a reactor trip on low steam generator level.
| L3 | Turbine Bypass Unavailable | Turbine Bypass Unavailable – This category does not include turbine bypass valve closures due to a loss of offsite power. The failure of one or more turbine bypass valves (TBVs) to maintain the reactor pressure and temperature at the desired operating condition. Turbine bypass failures included in this category may result in an automatic or manual reactor trip during an unsuccessful turbine run back; and the sustained use of one or more atmospheric dump valves (PWR) or safety relief valves to the suppression pool (BWR) after the reactor trip. This category does not include turbine bypass valve closures caused by the loss of offsite power.
| N1 | Interfacing system loss of coolant (ISLOCA) | Interfacing system loss-of-coolant accidents (ISLOCAs) are a class of accidents that can result in the over-pressurization and rupture of systems that interface with the reactor coolant system outside containment. A backflow of high pressure coolant from the primary system through low pressure system piping which results in the breach of the pipe or component.
| P1 | Total Loss of Feedwater Flow | Total Loss of Feedwater – A main feedwater isolation caused by a valid automatic system response after a reactor trip is not coded as a total loss of feedwater. A complete loss of all main feedwater flow. Examples include: the trip of the only operating feedwater pump while operating at reduced power; the loss of a startup or an auxiliary feedwater pump normally used during plant startup; the loss of all operating feed pumps due to trips caused by low suction pressure, loss of seal water, or high water level (BWR reactor level or PWR steam generator level); anticipatory reactor trip due to loss of all operating feed pumps; and manual reactor trip in response to feed problems characteristic of a total loss of feedwater flow, but prior to automatic Reactor Protection System signals. This category also includes the inadvertent isolation or closure of all feedwater control valves prior to the reactor trip, however, a main feedwater isolation caused by valid automatic system response after a reactor trip is not included. This category does not include the total loss of feedwater caused by the loss of offsite power.
| QC4 | Loss of ac Instrumentation and Control Bus. | Like loss of a safety-related bus, events involving momentary de-energization of buses caused by slow auto bus transfer are excluded. Also excluded are events where a bus is de-energized by spurious circuit breaker actuation or personnel error. Generally, there must be damage or some reason of unavailability besides an open circuit breaker (e.g., cable ground, transformer fault, etc.). A sustained de-energization of an ac instrumentation and control bus due to the inability to connect to any of the normal or alternative electrical power supplies. An event classified in this category is normally associated with damage to the bus itself, or damage to its uninterruptable power supply or supply breaker. The bus had to be damaged or its power source unavailable for reasons other than a remotely operated feeder breaker being open. This category includes only those failures of safety- and non-safety-related ac instrumentation and control buses that lead to an automatic or manual reactor trip. This category does not include a momentary undervoltage of a bus caused by a slow automatic transfer, or a loss of one output from the bus (e.g., failure of one output breaker), but is instead classified as a loss of the affected system.
| QC5 | Loss of Non-safety-Related Bus | A sustained deenergization of a non-safety-related bus other than an ac instrumentation and control bus due to the inability to connect to any of the normal or alternative electrical power supplies. This category is normally associated with damage to the bus itself, or damage to its feeder transformer or supply breaker. The bus had to be damaged or its power source unavailable for reasons other than a remotely operated feeder breaker being open. This category includes faults to high (>10kV), medium (>600V, <10KV), and low (>120V, <600V) non-safety-related ac buses that lead to an automatic or manual reactor trip. This category does not include a momentary undervoltage of a bus caused by a slow automatic transfer, or a loss of one output from the bus (e.g., failure of one output breaker), but is instead classified as a failure of the affected system.
| QG10 | Inadvertent Open/Close: 1 Safety/Relief Valve | One or more primary system safety and/or relief valves that inadvertently opens during normal power operations and then closes on its own prior to the manual or automatic actuation of a high pressure injection system. The valves included in this category are pressurizer code safety valves (PWR), pressurizer power-operated relief valves (PWR), main steam line safety valves (BWR), and Automatic Depressurization System relief valve (BWR). This category only applies to the initial plant fault group.
| QG9 | Primary System Leak | A small leak of primary coolant, inside the primary containment, at a rate less than 10 gpm and results in an automatic or manual reactor trip. A crack in one or more steam generator tubes that result in a loss of primary coolant to the secondary side of the steam generator at a rate less than 10 gpm. A plant shutdown is required for primary leak rates that exceeds technical specification limits. Most shutdown events of this nature do not result in a reactor trip. Manual reactor trips are sometimes initiated to expedite the controlled shutdown to avoid violating technical specification requirements. Automatic reactor trips may occur during the controlled shutdown caused by problems not related to the leak itself. Examples include feedwater flow problems at low power or operator errors. This category includes those primary leak events that prompt a controlled reactor shutdown and somehow result in an automatic or manual reactor trip.
| QK4 | Steam or Feed Leakage | A loss of the main turbine working fluid at or above atmospheric saturation conditions from the steam or main feedwater system up to and including a pipe break less than one-inch equivalent diameter. This category includes a small steam or feedwater leak that leads to an automatic or manual reactor trip. Examples include: flange leaks, packing leaks, blown fittings and leaks through other system connections. Note: Pipe breaks one-inch equivalent diameter or more are classified under heading K, High Energy Line Breaks.
| QL4 | Loss of Non-safety-Related Cooling Water | A total or partial loss of a non-safety-related cooling water system that leads to an automatic or manual reactor trip. This category includes the loss of non-safety-related cooling water systems that provide cooling to non-safety-related balance-of-plant components. Examples of cooling water systems include turbine building service water systems, non-safety-related mechanical draft cooling towers, and condenser circulating water systems. This category does not include partial or total loss of a safety-related cooling water system (e.g., service water, component cooling water) that results in a reactor trip due to the loss of non-safety-related balance-of-plant equipment in which it serves during normal plant operations. This event is classified under the appropriate category under heading E, Loss of Safety-Related Cooling Water.
| QL5 | Partial Closure of MSIVs | Any combination of partial or full closure of one or more main steam isolation valves (MSIVs) with at least one main steam line open to pass steam to the main condenser. This category includes partial MSIV closures that leads to an automatic or manual reactor trip. Examples include: full closure of one MSIV and partial closure of one MSIV. Note: In BWRs, a reactor trip signal will be generated by the closure of any single MSIV.
| QL6 | Condenser Leakage | Faults in the condenser shell, tubing, or connective components that result in leakage (fluid or gas) to or from the condenser. Example include condenser expansion joint ruptures or leaks, tube leaks/ruptures that require shutdown for conductivity/chemistry although condenser vacuum is normal, and breaks in piping attached to the condenser.
| QL7 | Degraded condenser vacuum | An automatic turbine trip leading to an automatic scram or manual reactor scram caused by lowering condenser vacuum. This category includes events for which degraded conditions in the main condenser require a plant trip, but the condenser is still available for decay heat removal after the trip. Events in which the condenser is not available after the trip should be coded under heading L, Loss of Condenser Heat Sink.
| QP2 | Partial Loss of Feedwater Flow | This category does not include a protective trip of a single main feedwater pump due to inadequate suction pressure caused by a partial loss of condensate flow. In this case the event would be coded QP4, Partial Loss of Condensate Flow. A reduction in main feedwater flow that leads to an automatic or manual reactor trip. All main feedwater system component malfunctions in conjunction with a steam generator low level alarm were considered to be at least a partial loss of feedwater (if not a total loss of feedwater as defined by category P1). Examples include the partial or full closure of a feedwater regulation valve, and a trip of one feedwater pump. This category does not include steam generator level shrinkage events due to the injection of colder water (usually during low power operations). In addition, protective trip of a single main feedwater pump due to inadequate suction pressure caused by a partial loss of condensate flow is classified under QP4, Partial Loss of Condensate Flow.
| QP3 | Loss of Condensate Flow | A complete loss of condensate flow that leads to an automatic or manual reactor trip. Examples include: the failure of all condensate pumps or booster pumps; and a malfunction that causes a loss of all condensate flow to the main feedwater system. Note: An event that results in a total loss of condensate flow as the initial plant fault will result in the total loss of feedwater flow, therefore, this event will also be classified under function impact category P1, Total Loss of Feedwater Flow.
| QP4 | Partial Loss of Condensate Flow | A reduction in condensate flow that leads to an automatic or manual reactor trip. Examples include: the failure of less than all condensate pumps; and a fault in the feed heater or condensate path that causes a reduction of condensate flow.
| QP5 | Excessive Feedwater Flow | An inadvertent increase in feedwater flow that leads to an automatic or manual reactor trip. Excessive feedwater transients as the initiating event can generate various reactor protection system (RPS) trip signals. Examples of events caused by excessive feedwater as the transient initiator include: an automatic reactor trip on high rate of power change caused by moderator temperature effects (BWR); a turbine trip/reactor trip due to high reactor water (BWR) or high steam generator (PWR) level; a reactor water (BWR) or steam generator (PWR) low-level reactor trip that follow the tripping of feedwater pumps caused by high levels due to excessive feedwater flow; and a manual reactor trip in response to improper feedwater regulation valve operation. This category does not include a transient that results in a swell (increased level) in the reactor vessel or steam generator caused by other than excessive feedwater flow (usually depressurization of steam).
| QR0 | RCS High Pressure (RPS Trip) | A transient not classified under any other category that causes reactor pressure to increase to the high pressure RPS trip setpoint.
| QR1 | RCS Low Pressure (RPS Trip) PWR | A transient not classified under any other category that causes primary pressure to decrease to the low pressure RPS trip setpoint. This category only applies to PWRs.
| QR2 | Loss of Primary Flow (RPS Trip) PWR | A total loss or reduction in reactor coolant system flow that results in a RPS trip. This category only applies to PWRs. Examples of events that may cause a reactor coolant pump (RCP) trip include momentary undervoltage transients and RCP faults. This category does include RCP trips caused by a damaged RCP electrical bus as a result of Fire (H1).
| QR3 | Reactivity Control Imbalance | This category does not include reactivity anomalies that result in a high reactor power trip (these would be coded as QR4, Core Power Excursion). Included are high and low neutron flux rate trips, dropped rods, rod control malfunction, and inadvertent rod withdrawal that does not cause a high reactor power trip. A reactivity anomaly that leads to an automatic or manual reactor trip. Examples include: high negative or positive neutron flux rate RPS trip (PWR); and automatic and manual reactor trips caused by a dropped control rod, an inadvertent rod withdrawal, a rod control system malfunction, a neutron flux imbalance, or an indication of core instability. This category does not include a reactivity anomaly that results in a high reactor power RPS trip (classified under category QR4, Core Power Excursion.)
| QR4 | Core Power Excursion (RPS Trip) | Inadvertent rod withdrawal events that result in a high power trip would be coded under this category instead of QR3, Reactivity Control Imbalance. A reactivity anomaly that causes reactor power exceeding the high reactor power RPS trip setpoint. Examples of events that typically cause a high reactor power RPS trip include: an inadvertent rod withdrawal that do not cause a high neutron flux rate RPS trip; improper operation of the mode selector switch during startup or shutdown that enables a power level trip lower than the present power level (BWR); a neutron flux spike due to pressure changes or recirculation flow changes (BWR); steam pressure oscillations caused by a turbine control system malfunction (BWR); neutron flux exceeding the flow biased average power range monitor (APRM) scram setpoint (BWR); and a power increase caused by overfeeding cold feedwater (BWR).
| QR5 | Turbine Trip | Turbine Trip. An inadvertent trip of the main turbine that results in a cessation of steam flow to the turbine, and leads to an automatic or manual reactor trip. Manual turbine trips performed to cause a reactor trip were never an initiating event. Events of this type were considered as special interest group. The main turbine as defined in this category includes the main turbine and its auxiliaries; the electro-hydraulic control system; turbine throttle valves; main generator and its auxiliaries; and the main generator output breakers. This category includes: inadvertent closure of all turbine throttle valves; EHC fault; main generator trip due to a switchyard equipment fault (e.g., output breaker, main transformer, switchyard breaker, offsite transmission line); response to electrical grid undervoltage voltage or frequency anomaly; inadequate plant response to an electric load rejection; unplanned manual turbine trip; and a spurious turbine trip.
| QR6 | Manual Reactor Trip | A manual initiation of a reactor trip, either purposely or by human error. This category does not include: the improper operation of the mode selector switch during startup or shutdown that enables a power level trip lower than the present power level (classified under category QR4, Core Power Excursion).
| QR7 | Other Reactor Trip (Valid RPS Trip) | All other reactor trips (other than those listed above) that result when an actual plant condition reaches the RPS trip setpoint for that condition.
| QR8 | Spurious Reactor Trip | An automatic reactor trip caused by hardware failure or human error in a RPS instrumentation or logic channel, or a reactor trip breaker. Examples include: incorrect venting of an instrument line during maintenance that causes false signal being sent to the RPS; and any other RPS system fault or human error that generates a reactor trip signal that does not reflect actual plant conditions.
| QR9 | Spurious Engineered Safety Feature Actuation | A spurious actuation of the Engineering Safety Features (ESF) system caused by hardware failure or human error in an ESF instrumentation or logic channel that results in a reactor trip.

## 2021 IE Events
Docket | LERNuma | EventDt | IPFCode | IPFShortDesc | A_Blackout | B_LOOP | C_Bus | D_Pneumatic | E_CoolingWater | F_SGTR | G_LOCA | H_Fire | J_Flood | K_HELB | L_Heatsink | M_ATWS | N_ISLOCA | P_LOF_C | AX_Blackout | BX_LOOP | CX_4X6VAC | C2_48VAC | C3_DC | DX_PlantAir | EX_ServiceWater | E2_PartialServWater | E3_CCW | E4_PartialCCW | FX_SGTR | GX_SLOCAVerySmall | G2_OpenXSRV | G3_SLOCA | G4_OpenPORV | G5_Open_GE_2SRV | G6_MLOCA | G7_LLOCA | G8_SealLOCA | HX_Fire | H2_F_internal | JX_Flood | KX_StmLineBrk_ext | K2_FeedBrk | K3_StmLineBrk_int | LX_MSIVClosure | L2_CondenserVacuum | L3_BypUnavailable | MX_ATWS | NX_ISLOCA | PX_LossOfFeed | RptName | PLANT_TYPE | VENDOR | UnitMode | PowerLevel | Abstract
29 | 291987003 | 1987-02-18 | QR3 | Reactivity Control Imbalance | [45 empty] | Yankee-Rowe | P | WE | PO | 100 | On 2/18/87, at 0001 hours, during normal steady state operation, (Mode 1, at 100 percent power) and no rod motion in progress, the Control Room operators observed a decrease in reactor power and that No. 2 control rod's position lights indicated that it had dropped. The operators immediately began to reduce generator load to restore the main coolant system Tave per plant procedure. At 0003 hours the reactor protection system initiated an automatic scram as the result of a high main coolant pressure condition. The high main coolant pressure occurred because the load reduction by the operator overcompensated for the power reduction from the dropped rod. The NRC was notified via the ENS at 0101 hours February 18, 1987. <br /><br />The root cause of this event was determined to be a procedure inadequacy. An engineering evaluation following the event concluded that a manual load reduction was inappropriate and could result in a high pressure trip from overcompensation, as was experienced. The manual load reduction requirement was subsequently removed from the immediate action of the procedure. The stationary gripper coil which had an open circuit was replaced in kind. <br /><br /> All systems performed as intended during this occurrence. There was no adverse effect to the public health or safety as a result of this event.
29 | 291987012 | 1987-07-06 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Yankee-Rowe | P | WE | SU | 1 | On July 6, 1987, with the plant in Mode 2 at 5 E-6 amps reactor power, a reactor scram on high main coolant pressure occurred during a main turbine overspeed trip test. The primary cause of this event has been attributed to personnel error. The turbine operator (at the turbine pedestal) used an excessive amount of steam to increase turbine speed which initiated a steam flow, reactor power mismatch. A second factor was the lack of communication between the turbine operator and the reactor operator which delayed timely compensatory actions. <br /><br /> Plant response was normal following the scram. Corrective actions were taken to reinstruct personnel and establish a direct communications link between the turbine operator and reactor operator. <br /><br />There was no adverse effect to the public health or safety as a result of this event.
29 | 291988002 | 1988-03-22 | QR8 | Spurious Reactor Trip | [45 empty] | Yankee-Rowe | P | WE | PO | 100 | On 3/22/88, at 0042, with the Plant operating in Mode 1 at 100% power, an automatic reactor scram occurred when power to the scram amplifiers in the Nuclear Instrument (NI) cabinet "A" was lost. The loss of power to NI Cabinet "A" was a result of a failed Sola Transformer (Type CV) within the NI Cabinet. The loss of power produces a loss of indication of NI channels 1, 3 & 6. An ENS phone call was made at 0141 on 3/22/88. The plant Emergency Diesel Generator No.2 started as required with the expected loss of power to the #1-2400 volt and #4-480 volt busses following the turbine generator trip.<br /><br /> The root cause of this event is the failure of one of two capacitors in the Sola Transformer. Both capacitors were replaced with direct replacements (in kind) which were dedicated in accordance with the plant Quality Assurance program. The NI channels were satisfactorily tested to the approved plant surveillance procedure. There was no adverse affect on the health or safety of the public as a result of this event. Similarly, but not reportable, a capacitor in the Sola transformer failed in 1985 and subsequently was replaced during testing in 1985. The replacement capacitors were of a different manufacturer, since the original capacitor is no longer produced. This is the first reported event of this nature. No other corrective actions are deemed necessary at this time.
29 | 291988003 | 1988-03-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Yankee-Rowe | P | WE | PO | 85 | On March 26, 1988, while at 85% power and returning to normal full power operation, there was an alarm for SG high-low level, immediately followed by an automatic reactor scram and turbine trip on low SG levels. Just prior to this event, loop No. 2 feedwater flow began oscillating and loop No. 4 feedwater flow started decreasing. As a result, the levels in No. 2 and 4 steam generators were decreasing rapidly towards the trip setpoint. The reactor scram and turbine trip occurred at 0529 hours. The NRC was notified via ENS at 0603 hours.<br /><br /> As part of the emergency procedures, the operators restarted the feedwater pumps. All automatic safety systems functioned as designed and the plant responded as expected. <br /><br /> The root cause of this event is the failure of the power supply for SG level control channels on No. 2 and 4 steam generators. Corrective action involved the replacement of the failed equipment. No other action is deemed necessary at this time. As a result of this event, there was no adverse effect to the public health or safety. This is the first occurrence of this nature at this facility.
29 | 291988008 | 1988-05-17 | QR5 | Turbine Trip | [45 empty] | Yankee-Rowe | P | WE | PO | 100 | At 2323 hours, 17 May 1988, in Mode 1 at full power operation (100%), a loss of generator field excitation resulted in automatic turbine governor response and subsequent relay action which tripped BK-1 and BK-2 (reactor trip breakers). The loss of generator field excitation resulted from automatic tripping of the AC feed to the static exciter. The Harriman (Z-126) transmission line also deenergized during this event. Loss of both generator excitation and one of two transmission lines resulted in a loss of flow from three of four main coolant pumps (MCPs). The operators secured MCP #1 approximately two minutes after plant trip and established natural circulation. By 2330 hours the Z-126 line had been re-energized. By 2345 hours the electrical busses had been cross-tied and restart of the MCPs had commenced. At 0005 hours, 18 May 1988, all four MCPs were operating. All automatic safety systems functioned as designed: the plant emergency diesel generators No 2 and 3 started as required. <br /><br /> The root cause of this event was a failure of the Field Overvoltage Protection unit circuit board. Corrective action involves implementing a plant design change that will modify the static exciter's internal control and 2400V feeder circuit breaker control. There was no adverse effect to the public health or safety. This is the first occurrence of this nature at this facility.
29 | 291989005 | 1989-04-06 | QL5 | Partial Closure of MSIVs | [45 empty] | Yankee-Rowe | P | WE | PO | 100 | On April 6, 1989 at 1123 hours with the plant at 100% power, the reactor was manually tripped when Number 1 Main Steam Line Isolation Valve (MSLIV) was inadvertently closed during a routine surveillance test of the MSLIV automatic control system. The manual trip was initiated, as required by procedure, to prevent a possible challenge to the Main Steam Line Safety Valves on Number 1 Steam Line. Full closure of the valve occurred when Instrumentation and Control personnel performing the control system functional test missed a procedure step. The missed step requires the insertion and removal of a test plug into a test jack terminal to block a trip signal prior to operating the valve control switch. If this step had been completed prior to operating the control switch, the valve would not have closed. After the plant trip, all plant systems functioned as designed. <br /><br /> The root cause of the event has been attributed to personnel error in that the technician performing the procedure missed a step. Corrective actions included counseling the technicians on the importance of following procedure steps as written, and understanding the expected results of each step prior to its' performance. All special surveillance procedures of this type will be reviewed for human factors considerations and revised as necessary to improve usability. <br /><br /> This is the first event of this nature. There was no adverse effect on the, health and safety of the public as a result of this event.
29 | 291989007 | 1989-04-23 | QR3 | Reactivity Control Imbalance | [45 empty] | Yankee-Rowe | P | WE | PO | 100 | On 4/23/89 at 1830 hours, during normal steady state operation, (Mode 1, at 100 percent power) the Control Room Operator observed that Group C control rods could not be moved. The operating crew determined that the control rods' cam motor was inoperable. An electrician was called in. The electrician performing troubleshooting requested the control room operator withdraw the group one step for troubleshooting purposes. The cam motor and control rods appeared to operate properly while being pulled one step. Almost immediately the control room received indication of dropped rods. Within five to ten seconds after the rods dropped an automatic scram occurred as a result of low main coolant pressure. An Unusual Event was declared at 1910 hours and terminated at 1915 hours. NRC notification was made at 1938 hours. <br /><br /> A thorough investigation was conducted determine the cause of the dropped rods. The cause of the inoperable cam motor was attributed to a broken compression connector found on the motor's brake solenoid circuit. The connector was replaced in kind. No abnormalities were found during the inspection or testing of the control rods' circuits and components. Control rod exercising was performed without abnormal indications. A root cause for this event could not be positively determined. <br /><br /> There was no adverse effect to the public health or safety as a result of this event.
29 | 291989013 | 1989-08-29 | QR8 | Spurious Reactor Trip | [45 empty] | Yankee-Rowe | P | WE | SU | 1 | On August 29, 1989, at 1738 hours, following a maintenance outage, while in Mode 2 at approximately 1% power with Main Coolant System pressure at 2000 psig, a Reactor Scram resulted when the Train B Nonreturn Valve (NRV) Trip switch was inadvertently placed in the Trip position. Plant response following receipt of the trip signal was normal. <br /><br /> The root cause of this event is attributed to personnel error. A contributing cause was a procedural deficiency. The control room operator inadvertently turned the Train B NRV Trip switch to the trip position while performing procedure steps that were not required for the plant operating conditions. The procedure has been revised to eliminate the switch operation and a caution sign affixed to the control switch cabinet. An evaluation of the control panel switch design will be initiated to determine if human factors engineering is appropriate. <br /><br /> This is the second event of this nature. A previous reactor scram due to inadvertent mispositioning of the NRV Trip switch was reported as LER 86-13. There was ne adverse effect on the health and safety of the public as a result of this event.
29 | 291990011 | 1990-12-05 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Yankee-Rowe | P | WE | PO | 100 | On 12/5/90, at 0702 hours, with the plant in Mode 1 at 100% power, following performance of valving to support repair of a control air leak, an automatic reactor scram occurred. Closure of a control air isolation valve (CA-V-1239) resulted in an unanticipated loss of air to the Heater Drain Tank High Level Dump Valve causing it to open. This resulted in sequential automatic tripping of the Heater Drain Pump on low Heater Drain Tank level and the Boiler Feed Pumps (BFPs) on low suction pressure. The loss of feedwater flow from the BFPs resulted in a low level condition in the steam generat rs which initiated the automatic reactor scram. <br /><br /> The root cause of this event has been-attributed to personnel error. An incomplete notation on a plant drawing and the valve identification tag contributed to the error. As corrective actions the drawing and valve tag have been corrected and a walkdown of the control air system drawings is in progress.<br /><br /> All plant systems functioned as designed during the event. There was no adverse effect on the health or safety of the public as a result of this event.
29 | 291991002 | 1991-06-15 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Yankee-Rowe | P | WE | PO | 88 | On June 15, 1991, at 2350 hours, while in Mode 1 at 88% reactor power, a lightning strike resulted in destruction of a lightning arrestor on the No. 3 Station Service Transformer (SST) and flashover of an insulator on the Z-126 115 kV transmission line disconnect switch. As a result, all offsite AC power was lost, an automatic reactor scra and turbine trip occurred, and all three EDGs operated as designed. On June 16, 1991, at 0010 hours, an UNUSUAL EVENT (UE) was declared based on the loss of offsite power and a fire emergency (smoldering arrestor). At 0014 hours, one source of offsite power was restored. At 0130 hours, an ALERT was declared at the discretion of the Shift Supervisor. While attempting to normalize the emergency busses, an inadvertent SI actuation signal was initiated at 0155 hours. Following restoration of essential communication systems and plant equipment, the ALERT was de-escalated to an UE at 0450 hours. On June 17, 1991, the plant attained a cold shutdown condition at 0755 hours and the UE was terminated at 0925 hours. <br /><br /> The root cause of this event has been attributed to lightning-induced transients. Immediate corrective actions involved repairing and testing of affected electrical and mechanical equipment and plant instrumentation, and returning normal and emergency communication equipment back to service. A Yankee Investigation Team was assembled to evaluate the event and develop immediate and long-term corrective actions. There was no adverse effect to the public health or safety.
29 | 291991004 | 1991-08-03 | QR5 | Turbine Trip | [45 empty] | Yankee-Rowe | P | WE | PO | 88 | On August 3, 1991, at 1647 hours, with the plant in Mode 1 at 78% power, the turbine generator static exciter input breaker opened, causing a loss of generator field with resultant turbine trip and reactor scram. There were no inoperable structures, components or systems that contributed to the event. <br /><br /> The root cause of the event is still under investigation. The plant is operating on the rotating exciter. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv) which identifies actuation of a Reactor Protection System as a reportable event. At no time during the event was the plant in an unanalyzed condition or in a condition outside the plant design basis. All Engineered Safety Feature systems and equipment operated as designed. Therefore, the health and safety of the public was not adversely effected by this event.
155 | 1551988002 | 1988-02-05 | QR6 | Manual Reactor Trip | [45 empty] | Big Rock Point | B | GE | SU | 10 | Big Rock Point Technical Specifications require that during power operation a minimum of one recirculation loop be in service (Technical Specification 4.1.2(a)) at a flow of 6E6 pounds per hour (Technical Specification 5.2.1).<br /><br /> On February 5, 1988 at 0816 hours, both (2) recirculation pumps tripped as designed, during a momentary loss of station power (three seconds). Per procedure, plant operators tripped the reactor manually in response to the loss of recirculation flow and all control rods withdrawn successfully inserted. No other engineered safety features were challenged by the event. Reactor power was approximately 10 percent at the time of the trip. <br /><br /> The momentary loss of station power occurred when the 138kV transmission tie breaker tripped during main generator synchronization. The breaker trip was caused when the plant operator attempted to close the main generator breaker slightly out of phase with the load. <br /><br /> Following check-out of all associated equipment (relays, breakers, transformer), no equipment problems were identified and restart commenced on February 7, 1988.<br /><br /> To prevent recurrence a training memo was developed to discuss the event, system operation, and proper method of synchronization with all plant operators.
155 | 1551988008 | 1988-10-28 | QR5 | Turbine Trip | [45 empty] | Big Rock Point | B | GE | PO | 95 | On October 28, 1988 at 1630 hours, control room alarms indicated that a load rejection occurred due to loss of the transmission line. The turbine bypass valve opened to control reactor pressure and the turbine runback feature actuated, however, within 10 seconds a reactor and turbine trip occurred on low condenser vacuum due to large amount of steam flow into the condenser from the bypass valve. All control rods inserted following trip initiation. The turbine trip resulted in a momentary loss of station power for less than 5 seconds until automatic transfer to the backup offsite power source was completed. During this transition the Control Rod Drive M/G set failed to transfer causing a loss of position indication until operators reclosed the normal supply breaker. All other systems functioned properly. <br /><br /> Subsequent investigation showed the cause of the load rejection was a lightning rod which broke off during high winds and caused a fault on the transmission line approximately 10 miles from the plant site. Following check-out of the transmission line, repair of the M/G set, and testing the plant was returned to service on October 29, 1988.
155 | 1551988009 | 1988-11-21 | QR5 | Turbine Trip | [45 empty] | Big Rock Point | B | GE | PO | 93 | On November 21, 1988 the plant was in steady-state operation at 93% power. At 2022 hours, control room operators heard a loud noise from the turbine building and immediately thereafter a reactor trip occurred on high power. All control rods inserted and plant cooldown commenced using the main condenser. No other safety systems were challenged during the trip. Subsequent investigation determined that a connecting rod on the turbine control valves failed causing valve closure (the loud noise). Loss of the turbine resulted in reactor pressure increase and reduction in void content causing reactor power increase to the trip setpoint. <br /><br /> Following replacement of the connecting rod and testing, the plant was returned to service on November 24, 1988.
155 | 1551989008 | 1989-08-22 | QR5 | Turbine Trip | [45 empty] | Big Rock Point | B | GE | PO | 74 | On August 22, 1989 the unit was operating at approximately 74 percent power following start-up from the Refueling Outage a week earlier. At 0635 hours, Operators noticed a slow reactor pressure increase and adjusted the Initial Pressure Regulator to restore pressure to normal. At 0645 hours, reactor pressure increased rapidly causing a reactor trip on High Neutron Flux. All control rods inserted and plant cooling was maintained with the main condenser. No Engineered Safety Systems other than the Reactor Protection System were actuated during the event. <br /><br /> Cause of the trip was a rapid closure of the turbine admission valves due to gross leakage in the Turbine Initial Pressure Regulator bellows assembly. After repair of the bellows assembly and successful testing, the plant was restarted on August 22, 1989 at 2211 hours.
155 | 1551992009 | 1992-05-13 | QR3 | Reactivity Control Imbalance | [45 empty] | Big Rock Point | B | GE | SU | 2 | On May 13, 1992, the plant was starting up after a refueling outage. At 1224 the operators were testing the Turbine Stop Valve, and experienced difficulty in getting the valve to open fully. The turbine bypass valve was placed in manual and opened at 1353, reducing the delta P across the turbine stop valve. At 1401 the turbine stop valve opened. The turbine bypass valve was then given a partial close signal as the turbine stop valve opened, and at 1401 the reactor scrammed on short reactor period detected by two out of three wide range neutron monitors.<br /><br /> The cause of the event has been attributed to opening the turbine bypass valve to reduce reactor pressure at low power levels. This action lowered reactor power from roughly 1.5% to a level just below 1% power which enabled short period scram protection. The root causes that led to operating the valve in this range can be attributed to not recognizing the sensitivity of the nuclear instrumentation below 1% power, lack of written precautions or warnings operating the bypass valve in this power range and undersized steam flow pilot holes internal to the turbine stop valve. <br /><br /> The pilot holes' size was increased, the turbine stop valve was reassembled, and successfully tested at 2329 on May 16 during a subsequent plant startup.<br /><br /> Operator training and appropriate procedure revisions will be completed.
155 | 1551992010 | 1992-06-03 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Big Rock Point | B | GE | PO | 77 | On June 3, 1992 plant operations were normal. At 0533, the reactor scrammed on high flux due to a sudden spike in reactor pressure from 1335 psig to 1360 psig. All control rods inserted fully and no other engineered safeguards equipment was challenged, however contrary to design, the turbine did not trip and the Generator Output Breaker did not open. <br /><br /> The root cause of the reactor scram has been determined to be an IPR bellows failure due to a weld defect combined with normal operating mechanical, cyclic stresses. <br /><br /> Hand Trip Solenoid Binding is the most likely root cause of the failure of the turbine to trip. <br /><br /> The facility was returned to operation on June 7, 1992. The IPR bellows was replaced with a spare, and the H nd Trip Solenoid was disassembled, inspected and tested successfully before re-installation. Long term evaluations will be performed to address upgrading the current IPR and Hand Trip Solenoid designs.
155 | 1551992014 | 1992-10-29 | QR5 | Turbine Trip | [45 empty] | Big Rock Point | B | GE | PO | 98 | On October 29, 1992 at 1111, the facility experienced a momentary interuption of station power. The main transformer protective relay operated, tripping the 138 kV tie breaker and the generator output breaker. Station Power was automatically transfered from the 138 kV line to the 46 kV line. Consequently the turbine was automatically tripped. The reactor was also manually scrammed at 1112. An Unusual Event (UE) was conservatively declared at 1135. The UE was exited at 1426.<br /><br /> Upon investigation, a loose connection was discovered in the current transformer terminal block of the 138 kV tie breaker. This resulted in thermal damage and separation of one of the inputs to the protective relays causing a false differential condition. <br /><br /> The terminal block was repaired and tested. The normal lineup for station power was restored on October 30, 1992. Containment pipeway coolers that exhibited leakage during the event were repaired and returned to service. Following an evaluation of a high differential temperature condition on the reactor vessel, the Plant was returned to power operation on November 2, 1992.
155 | 1551994007 | 1994-09-30 | QR6 | Manual Reactor Trip | [45 empty] | Big Rock Point | B | GE | PO | 69 | On September 30, 1994, the reactor was manually scrammed at 2146 from 69% power during a planned facility shutdown for the 1994 Refueling Outage. Cooldown rate and temperature spreads between primary system equipment were maintained in accordance with Technical Specifications. <br /><br /> The turbine generator (T/G) controls were not operating smoothly, causing uncontrolled variances in reactor pressure control. (These oscillations had been experienced late in the operating cycle, and were exacerbated during the shutdown). Plant management deliberated for several hours on how to lower power with erratic T/G controls, and decided that a manual scram would be the preferred method. Following the manual scram, the plant equipment operated as expected. <br /><br /> The root cause of the erratic T/G controls was the binding of the admission valve operating piston pilot valve extension rod in its guide bushing. The extension rod and the guide bushing were cleaned and dimensional checks performed to obtain clearance information. Prior to returning to service, the system will be tested-to ensure performance.
155 | 1551994010 | 1994-11-29 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Big Rock Point | B | GE | PO | 54 | On November 29, 1994, reactor power escalation following a refueling outage was in progress. In addition, the second condensate pump was being returned to service following the replacement of a mechanical seal. <br /><br /> At 1530, the reactor was manually scrammed from about 54% power due to loss of suction pressure to the only operating feedwater pump. While filling and venting the condensate pump prior to operating, air was drawn through the common vent line to the operating condensate pump and discharged to the operating feedwater pump. All of the rods inserted and the plant functioned as designed. An Administrative cooldown limit for the Steam Drum was briefly exceeded, however an evaluation confirmed that engineering design limits were well within the specified parameters. <br /><br /> The loss of feedwater was caused by a procedure that had never been validated for the rare operating condition of returning a condensate pump to service during power operation after it had been drained for maintenance. Corrective actions include procedure revision and validation for this operating condition.
155 | 1551995007 | 1995-11-16 | QP5 | Excessive Feedwater Flow | [45 empty] | Big Rock Point | B | GE | PO | 22 | On November 16, 1995, the facility was being returned to service following a short maintenance outage taken to repair leaking main condenser tubes. With the reactor power at approximately 22%, an automatic reactor scram occurred at 0315. The scram was automatically initiated (by the reactor protection system) due to a high rate of power change caused by excessive feedwater flow shortly after the controller had been switched from manual to automatic operation. The operators completed all scram actions, and established a primary system cooldown rate less than the 100 degrees F per hour required by Technical Specifications. <br /><br /> The root cause of this event was failure to place the feedwater regulating valve in automatic using a bumpless transfer. Performance of multiple activities during plant startup contributed to the unsuccessful feedwater control transfer. Prior to restarting the facility, Operations' procedures O-TGS-1, Master Checklist, and Standard Operating Procedure 16, Feedwater System were revised to offer more guidance during this segment of plant startup. <br /><br /> The facility was returned to service on November 17, 1995.
155 | 1551996010 | 1996-09-16 | QK4 | Steam or Feed Leakage | [45 empty] | Big Rock Point | B | GE | PO | 56 | On September 16, 1996, @ 0251, Big Rock Point experienced an automatic reactor scram due to high reactor pressure. All systems operated as expected. The unit was in the process of being returned to service following a short forced outage prompted by a packing leak on a Reactor Depressurization System isolation valve. <br /><br /> The initiator of this event has been attributed to the failure of the turbine Initial Pressure Regulator (IPR) bellows (the IPR maintains an essentially constant steam line pressure without regard to the generator or the transmission line system load). A crack had developed in the bellows, causing a loss of steam pressure and resulting closure of the turbine admission valves, causing the reactor pressure to increase beyond the high pressure scram setpoint. The root cause of the bellows failure was determined to be a lack of fusion defect on an inside weld bead.<br /><br /> An IPR bellows with one operating cycle (about 12 months) of satisfactory performance has been installed in lieu of a new bellows, which would not be available for at least 10 weeks. The unit was then returned to service on September 17, 1996. <br /><br /> To prevent future bellows failures, deficiencies in the vendor's fabrication process will be evaluated and corrected.
155 | 1551996013 | 1996-12-07 | QR5 | Turbine Trip | [45 empty] | Big Rock Point | B | GE | PO | 98 | On December 7, 1996, @ 1210, Big Rock Point experienced an automatic reactor scram initiated by a turbine/generator trip. The trip was caused by the inability of the Amplidyne voltage regulator to provide the necessary feedback control for the plant generator excitation circuitry. A resistor failed within the associated logic circuit. When the turbine tripped, the turbine stop valve closed, causing reactor power to increase beyond the high power scram setpoint, resulting in an automatic reactor scram. All systems operated as expected. <br /><br /> The damaged Amplidyne voltage regulator resistor was replaced. The resistor failure was attributed to age degradation coupled with the effects of constant energizing and deenergizing of the unit (thermal expansion) of the wire wound wrap. Similar resistors associated with the Amplidyne voltage regulator will be replaced during the next refueling outage.
206 | 2061987003 | 1987-03-10 | QR5 | Turbine Trip | [45 empty] | San Onofre 1 | P | WE | PO | 92 | At 1024 on March 10, 1987, with the Unit at 92% power, a trip signal initiated in response to a loss of generator field, resulted in a turbine trip and subsequent reactor trip. The Auxiliary Feedwater System automatically actuated on low steam generator level as expected from a trip at this power level. <br /><br />During the trip recovery, equipment deficiencies were noted which included: failure of two rod bottom indicating lights to illuminate; one of two intermediate range nuclear instrumentation channels failed off-scale low; eight Moisture Separator Reheater steam dump valves and their associated motor operated isolation valves failed to close, which in turn caused perforations in one of the Low Pressure turbine casing rupture discs; and, the main feedwater block valve to "A" Steam Generator failed to fully close upon demand. <br /><br />The loss of generator field was due to an electrical short resulting from a brush being inadvertently dropped into the main exciter commutator assembly during performance of routine brush replacement on the commutator and brush assemblies. Inadequate lighting within the commutator enclosure was a contributing factor since the electrician held a flashlight in one hand while replacing the brush with the other, thereby limiting his dexterity. Enhancements to the available lighting within the commutator enclosure have been completed. Additionally, this incident has been discussed with all electricians who may be involved in similar work. <br /><br />Since none of the equipment failures resulted in a loss of safety function, there were no safety consequences to this event.
206 | 2061989019 | 1989-07-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | San Onofre 1 | P | WE | PO | 76 | On July 24, 1989, at 1216 while at 76% power, Unit 1 was manually tripped due to a loss of feedwater flow to Steam Generator (SG) "A" and resultant low level. The loss of feedwater flow occurred during performance of a test of the SG "A" high level alarm. At 1215, operators authorized maintenance technicians to perform testing of the SG "A" high level alarm and Steam Flow/Feed Flow Mismatch Reactor Trip alarm. During the high level alarm portion of the test, the SG "A" high level alarm annunciated as anticipated. The high level alarm was promptly followed by the SG "A" Steam/Feed Mismatch alarm, which was not anticipated at this point in the test sequence. After observing that SG "A" levels were rapidly decreasing and the SG "A" main feedwater Flow Control Valve (FCV) had tripped closed, operators unsuccessfully attempted to open the FCV and, in accordance with procedures, manually tripped the reactor. SG "A" may have dried out for a brief period shortly after the reactor had been tripped until the auxiliary feedwater system actuated at 1217. All required systems functioned normally. <br /><br /> The effects of a recent design change on the FCV circuitry were not recognized to result in a loss of feedwater flow and were, therefore, not transferred into station procedures or operator training. The root cause is attributed to weaknesses in SCE's processes for ensuring that design change information is adequately incorporated into procedures.<br /><br /> The methods by which design change information is prepared and reviewed for incorporation into Station Procedures will be reviewed by a multi-disciplinary group to determine appropriate enhancements and corrective actions necessary to assure recognition of impacts. The SG high level alarm test will be performed only while the unit is shutdown. Other recent design changes were reviewed for similar discrepancies with none being found.
206 | 2061989021 | 1989-08-03 | QR8 | Spurious Reactor Trip | [45 empty] | San Onofre 1 | P | WE | PO | 91 | At 1800 on 8/3/89, with Unit 1 at 91% power, a reactor trip occurred due to actuation of the Reactor Protection System (RPS) on low Reactor Coolant System (RCS) flow in one loop. All systems responded normally to the trip and the operators (utility, licensed) stabilized the plant in Mode 3. The RPS operated in accordance with design, with no malfunctions noted. <br /><br /> The brief low RCS flow signal occurred in Loop C and was caused by a loss of insulation resistance of the flow transmitter cable. The loss of insulation resistance resulted from time-temperature-radiation exposure degradation of the polyethylene insulation which has occurred since installation of the cable during original construction (i.e., prior to 1968).<br /><br /> As corrective action, the cable was replaced and the RCS Loop C flow instrument was verified to be operating properly. The remaining two RCS loop flow instrumentation cables were tested and were found to be satisfactory. The RCS loop flow instrumentation cabling and the remaining cabling having the same insulation, which remain in service in important-to-safety applications, are not required to be Environmentally Qualified (EQ). The remaining cables having similiar insulation will be periodically tested for insulation degradation. A sample of these cables will be removed from service during the next refueling outage and replaced. The cables in the sample will be examined for indication of insulation degradation. Appropriate corrective actions will be developed based on the examination results.
206 | 2061989023 | 1989-09-18 | QR3 | Reactivity Control Imbalance | [45 empty] | San Onofre 1 | P | WE | PO | 91 | At 1921 on 9/18/89, with Unit 1 in Mode 1 at 91% power, 4 Control Rods (CRs) from Shutdown Bank 2 dropped into the core. Approximately 23 seconds later, the remaining 12 Shutdown Bank CRs (4 from Shutdown Bank 2 and 8 from Shutdown Bank 1) dropped into the core. Operations personnel promptly responded by manually tripping the reactor, verifying that all systems responded normally to the trip, and completing the requirements of the Reactor Trip Response procedure. At 1942, the plant was stabilized in Mode 3 (Hot Standby) and the Reactor Trip Response procedure was exited. <br /><br /> Investigation into the cause of the dropped CRs revealed that: 1) Shutdown Bank 2 contactor coil 2MS1 failed, resulting in the de-energization of 4 moveable gripper coils and subsequent drop of the initial 4 CRs; and 2) as the fault from 2MS1 progressed, current passing through the (+) 125 VDC fuse to both Shutdown Bank 1 and 2 contactor coils increased to the point at which the fuse blew, thus de-energizing the moveable gripper coils for the remaining 12 CRs and causing the CRs to drop into the core.<br /><br /> The failed contactor coil and fuse were replaced with in-kind parts. The insulation resistance of all Shutdown Bank and Control Bank contactor coils was checked and determined to be satisfactory. A thermographic inspection was also performed and no anomalous conditions were identified. <br /><br /> The root cause of the contactor coil 2MS1 failure is unknown at this time. The coil has been sent to an offsite independent laboratory for failure mode analysis. Additional long term corrective action, if required, will be determined based on the results of the failure mode analysis. Upon completion of this analysis, a supplemental LER will be submitted.
206 | 2061990007 | 1990-04-30 | QR8 | Spurious Reactor Trip | [45 empty] | San Onofre 1 | P | WE | PO | 91 | At 2202 on 4/30/90, with Unit 1 at 91% power, a reactor trip occurred due to actuation of the Reactor Protection System (RPS) on a spurious low Reactor Coolant System (RCS) flow signal in loop B. All systems responded normally to the trip and the operators stabilized the plant in Mode 3. The RPS operated in accordance with design with no malfunctions noted; therefore there was no safety significance to this event.<br /><br /> The root cause of this event is believed to be the existence of voids in the loop B RCS flow transmitter coil insulation, which caused a ground in the coil. It has been determined that the voids were due to an isolated manufacturing defect. <br /><br /> SCE believes that the ground in the flow transmitter coil caused the instrument loop to be sensitive to the presence of magnetic fields adjacent to the instrument loop cables. The occurrence of a magnetic field, which could be caused by the normal operation of plant equipment, near the flow transmitter signal cable (or a steady magnetic field if the ground was intermittent) could have produced a noise pulse large enough and of sufficient duration to cause an induced current in the flow instrumentation circuit sufficient t actuate the low flow trip signal, thereby causing the reactor trip. <br /><br /> Corrective actions included replacement of the defective transmitter and verifying that all RCS loop flow instruments were operating properly.
206 | 2061990011 | 1990-05-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | San Onofre 1 | P | WE | PO | 92 | On May 15, 1990, at 0243 with Unit 1 at 91.5% power, the reactor was manually tripped due to a low and decreasing level in Steam Generator (SG) C resulting from a loss of feedwater flow. The loss of feedwater flow occurred during maintenance on an Auxiliary Feedwater (AFW) pump while de-terminating a valve control circuit which resulted in an inadvertent short circuit to ground. The short circuit initiated automatic transfer of a vital bus and a momentary power interruption to the SG C high level actuation which, in turn, initiated closure of SG C main feedwater control valve (FCV). The high level actuation circuitry reset when it was re-energized at the completion of the transfer. The control room operator then reset the FCV controls in order to gain manual control of the FCV in accordance with procedures. However, the control operator was unable to re-establish feedwater flow before SG C reached the level at which procedures require the reactor to be tripped. <br /><br /> Closure of the FCV resulted from a relay/bistable race which occurred when the SG C high level FCV closure circuitry was re-energized. The potential for this interaction was not previously recognized. Corrective actions include: 1) temporarily disabling the SG high level closure of the FCV, 2) testing of the vital buses which are susceptible to brief power interruptions revealed no other unacceptable interactions, and 3) performance of a human performance enhancement system investigation into the cause of the short circuit is in progress.
206 | 2061991010 | 1991-05-28 | QR3 | Reactivity Control Imbalance | [45 empty] | San Onofre 1 | P | WE | PO | 91 | At 2343 on 5/28/91, with Unit 1 in Mode 1 at 91% power, two of the 12 Control Bank 1 control rods (CRs) (H-6 and H-10) dropped into the core. Appropriate control room alarms were received and operators confirmed negative reactivity insertion per procedures. Operators properly responded (within 20 seconds) by manually tripping the reactor. At 2344, the auxiliary feedwater (AFW) system actuated on low steam generator (SG) water level which occurred due to expected SG water level shrinkage. At 0044 on 5/29/91, the reactor trip response procedure was exited with the plant stabilized in Mode 3. <br /><br /> The CRs dropped as a result of an open connection in the "half-voltage" resistor network associated with this rod subgroup. The open connection de-energized the moveable gripper coils associated with the affected rods, thus permitting them to drop into the core. The open connection was caused by a conductor/lug (jumper) connection failure at one termination point. Destructive physical analysis has revealed that the open connection resulted from long-term localized heating resulting in oxidation of the copper wire in the vicinity of the failure site. Continued heating led to arcing, melting, and eventual failure.<br /><br /> The failed jumper was replaced with in-kind parts. In addition, other jumper wires/lugs within the CR "half power" resistor bank were replaced in-kind. A continuity check and thermographic inspection were performed and no anomalous conditions were identified. Rod position indication and control rod drive operability tests were completed satisfactorily prior to startup.
206 | 2061991017 | 1991-10-17 | QR8 | Spurious Reactor Trip | [45 empty] | San Onofre 1 | P | WE | PO | 91 | At 1314 on 10/17/91, during the performance of corrective maintenance on an alarm module powered from Vital Bus No. 1 (VB1), and with a pre-existing failure of the high startup rate (SUR) block relay (AP4D), Unit 1 automatically tripped from 91% power on a spurious high SUR signal. The spurious SUR signal was generated when a momentary power interruption to VB1 occurred during an automatic transfer of VB1 to its alternate power source, which was initiated due to a momentary ground fault on the bus. As a taped alarm module power lead was being routed through a grooming hole in the module chassis, the lead arced apparently through the tape to the module chassis, causing the ground. The reactor protection system (RPS) and automatic control systems functioned as designed, and the plant was stabilized in Mode 3 at 1342. An auxiliary feedwater (AFW) actuation occurred due to the expected decrease in steam generator levels following the trip. All AFW components responded in accordance with design, and the AFW actuation was reset at 1401. <br /><br /> Laboratory analysis of the taped lead revealed that the insulating capability of the tape had apparently been degraded during handling. This is postulated to have occurred when the taped lead contacted a sharp edge of the grooming hole on the alarm module chassis when the lead was inserted through the hole. <br /><br /> The methodology used to route insulated live leads will be reviewed. Any methodology enhancements identified by this review will be implemented as appropriate. <br /><br /> There is no safety significance to this event since all RPS and AFW components actuated in accordance with design.
213 | 2131987005 | 1987-04-16 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Haddam Neck | P | WE | PO | 100 | On April 16, 1987 with the plant operating at 100 percent power in mode 1, a turbine control system malfunction caused a high steam flow condition which resulted in a reactor trip. Subsequent troubleshooting revealed that impurities were present in the turbine control oil system. These impurities had clogged an orifice in the control oil system which in turn caused erratic operation of turbine control valve number 4 and the high steam flow condition. The cause of the event has been determined to be contamination of the control oil system with water. These water sources have been identified and eliminated. This event is reportable under 10CFR50.73(a)(2)(iv) since it involved automatic actuation of the Reactor Protection System. <br /><br /> This revision is submitted to provide information on the source of the oil contamination and long-term corrective action not available at the time of the initial report.
213 | 2131988012 | 1988-04-30 | QR8 | Spurious Reactor Trip | [45 empty] | Haddam Neck | P | WE | PO | 60 | At approximately 1130 on April 30, 1988, with the plant at 60% power, an automatic reactor trip occurred while returning an idled reactor coolant system loop to service. The most probable cause of the trip was determined to be a false trip signal indicating that both turbine stop valves had closed. The cause of the signal was due to improper installation of the turbine stop valve cam switches. The operators performed the immediate actions as specified by the emergency operating procedures and the plant responded as expected. The switches were repaired and tested. A maintenance procedure will be developed to ensure proper installation and testing of the turbine stop valve cam switches.<br /><br /> This event is reportable under 10CFR50.73(a)(2)(iv) since it involved automatic actuation of the reactor protection system.
213 | 2131990018 | 1990-09-03 | QP5 | Excessive Feedwater Flow | [45 empty] | Haddam Neck | P | WE | PO | 80 | On September 3, 1990, at 0457 hours, with the plant in Mode 1 at 80 percent power, the main feedwater regulating valve for the No. 1 steam generator failed open. Immediate operator action consisted of manually tripping the plant, closing the main steam trip valve and isolating feedwater to the No. 1 steam generator. This event also resulted in automatic actuation of the auxiliary feedwater system. Subsequent disassembly and inspection of the valve revealed that the plug had separated from the valve stem. It was also noted that fragments of the valve stem were carried downstream in the feedwater system. An engineering evaluation determined that the loose parts were not a concern for one operating cycle. The root cause was improper part fabrication at the factory. Corrective action consisted of modifying the stem plug assemblies on all four feedwater regulating valves with a welded joint where the plug attaches to the stem. This event is reportable under 10CFR50.73(a)(2)(iv) since it resulted in manual actuation of the Reactor Protection System and automatic actuation of an Engineered Safety Feature.
213 | 2131990020 | 1990-09-20 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Haddam Neck | P | WE | PO | 50 | On September 20, 1990, at 0715 hours, with the plant in Mode 1 at 50 percent power the B condensate pump was shut down for troubleshooting. The A condensate pump was unable to provide sufficient pressure to the suction of the main feed pump requiring control room operators to manually trip the plant. The root causes of the event consisted of the degradation of the rubber flexible couplings in the condensate pump suction piping to the point that flow was restricted and personnel error since the pump was shut down at a higher power level than that required by procedure. Corrective action included replacing the flexible rubber couplings with stainless steel couplings and re-emphasizing the importance of procedural compliance to all operators. This event is reportable under 10CFR50.73(a) (2) (iv) since it resulted in manual actuation of the Reactor Protection System.
213 | 2131992009 | 1992-03-12 | QR5 | Turbine Trip | [45 empty] | Haddam Neck | P | WE | SU | 2 | On March 12, 1992, at 1618 hours, with the plant in Mode 2 and reactor power approximately 2 percent of rated thermal power, an automatic reactor trip occurred when indicated reactor power exceeded the P-7 permissive enable setpoint and plant conditions were such that the reactor protection system trip logic was satisfied. The root cause of this event was procedural inadequacy. Corrective action consisted of procedure revisions to require adjustment of indicated reactor power gains and clearly identify the P-7 enable setpoint. This event is reportable under 10CFR50.73(a)(2)(iv) since it resulted in an automatic actuation of the Reactor Protection System.
213 | 2131993002 | 1993-03-23 | QR3 | Reactivity Control Imbalance | [45 empty] | Haddam Neck | P | WE | PO | 100 | On March 23, 1993, at 0844 hours, with the plant at 100 percent power, operators attempted to insert control Bank B. When rods were inserted one step, control rods 31 and 32 from Bank B dropped approximately 50 steps. A decision was made to recover the misaligned rods. Rods 31 and 32 were placed in disconnect to prevent further insertion. When the remaining rods in Bank B were inserted one step, control rods 31 and 32 dropped approximately another 100 steps. Immediate operator action was to initiate a manual trip of the reactor. Subsequent investigation revealed that a faulty contactor allowed the control rods to drop during a demand for rod insertion. The root cause was inadequate procedural verification on the maintenance of control rod contactors. Corrective action will be implemented through procedural enhancement. This event is reportable under 10CFR50.73 (a)(2)(iv) since it resulted in manual actuation of the Reactor Protection System.
213 | 2131994009 | 1994-03-28 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Haddam Neck | P | WE | PO | 7 | On March 28, 1994 at 2227 hours with the plant in mode 1 and reactor power approximately 7 percent of rated thermal power, an automatic reactor trip occurred while performing Normal Operating Procedure (NOP) 2.1-6, 'Reactor Just Critical to Minimum Load.' When the operators transferred the 4160 volt electrical power supply to reactor coolant pump bus 1-1A from offsite power to the main generator, circuit breaker 3T-1A opened however 309-1A failed to close. Subsequently, indicated reactor power exceeded the P-7 permissive enable setpoint while reactor coolant pumps 1 & 2 were de-energized. Before breaker 3T-1A could be reclosed, the 2 out of 4 reactor coolant low flow trip logic was satisfied and the reactor tripped. The cause of this event was equipment failure and a procedure deficiency. Immediate corrective actions consisted of a procedure revision to NOP 2.1-6 and the repair/reinstallment of breaker 309-1A. This event is reportable under 10CFR50.73 (a) (2) (iv) since it resulted in an automatic actuation of the Reactor Protection System.
213 | 2131994018 | 1994-07-11 | QR6 | Manual Reactor Trip | [7 empty] | X | [25 empty] | X | X | [10 empty] | Haddam Neck | P | WE | PO | 100 | On July 11, 1994, at approximately 0745 hours, with the plant in Mode 1 at 100 percent power, control room operators received a low oil level alarm for No.3 reactor coolant pump (RCP) motor accompanied by increased bearing temperatures. A load reduction was commenced at 0833 however, at 0907, at approximately 50 percent power, a manual reactor trip was initiated, with subsequent shutdown of the RCP, when bearing temperatures reached 200 degrees F. Immediately following the trip the No.1 feedwater regulating valve failed to close resulting in actuation of the steam generator overfill protection system which closed the feedwater regulating valve and its associated motor operated isolation valve. In addition, one of the main steam safety pilot valves appeared to be simmering. At 0956 a heat detector near #3 RCP alarmed. At 1004 a fire was observed on the pump's insulation. The fire brigade entered the containment and at 1010 the fire was extinguished. cracked PVC coupling on the line leading from the #3 RCP motor upper bearing oil reservoir to its lift oil pump. Corrective action consisted of redesigning the coupling and shimming the supports to eliminate stress. This supplemental report provides the results of the failure cause of the feedwater solenoid valves.
213 | 2131995016 | 1995-07-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Haddam Neck | P | WE | PO | 100 | On July 27, 1995, at approximately 0155 hours, with the plant in Mode 1 at 100 percent power, control room operators received a 4160 volt ground alarm. At 0156 the 'B' main feed pump motor breaker tripped resulting in steam flow/feed flow mismatch alarms on all four steam generators. At 0157 the operators manually tripped the reactor and turbine. Automatic initiation of the auxiliary feedwater system and the subsequent cooldown caused pressurizer level to decrease to less than 13 percent and safety injection was manually initiated. After restoring pressurizer level, safety injection was terminated at 0230 hours and the plant was stabilized in Mode 3 (hot standby). The cause of the event was degraded insulation in the main feed pump motor stator believed to be due to heat and the age and design of the motor. Corrective action consisted of installing a spare stator. In addition the 'A' main feed pump was tested and found satisfactory. At 0510, with the plant in Mode 3, operators failed to obtain a loop boron sample before restarting the No. 1 reactor coolant pump and opening the affected loop cold leg isolation valve which constituted a violation of the Technical Specifications. The cause was operator error. Corrective action consisted of discussing with the crew the need to follow the Technical Specification requirements for sampling.
219 | 2191987005 | 1987-01-16 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Oyster Creek | B | GE | PO | 84 | On January 16, 1987, at 2018 hours, a high flux reactor scram occurred due to increased recirculation flow. At the time, "E" recirculation pump was undergoing testing which required starting the pump. The pump discharge valve had been closed, however, as the pump was started, recirculation flow increased resulting in an APRM high flux scram. The cause of this event is attributed to a partially open discharge valve. The root cause of the event was a low torque switch setting which controls the closing thrust of the discharge valve. Following the APRM high flux scram, a second scram occurred due to the slow response of the mechanical pressure regulator (MPR) which the operators were using to control reactor pressure following the first scram. The slow response of the MPR is attributed to a calibration error since the MPR rate adjustment had been set with the turbine cold. As operating temperature increased the MPR response rate decreased resulting in excessive opening of the turbine bypass valves. When the valves were closed, a reactor low water level scram occurred. The closing thrust of the "E" recirculation pump discharge valve was measured and the torque switch setting was raised to its proper value. Torque switch settings for the remaining four discharge valves will be similarly reset. In the interim, future valve closure will be verified by monitoring motor current, as a minimum, and valve closure time when possible. With regard to the MPR, future calibrations will include adjustments to account for the effects of operating temperature. A similar occurrence is described in LER 85-026.
219 | 2191987011 | 1987-02-14 | QP5 | Excessive Feedwater Flow | [45 empty] | Oyster Creek | B | GE | PO | 98 | On February 14, 1987, at approximately 1301 hours a reactor scram occurred as a result of a high reactor water level turbine trip. The high reactor water level was caused when a technician moved a control room panel wire harness which inadvertently disconnected the "A" feedwater flow signal wire. The Feedwater Level Control System responded to the apparent loss of "A" feedwater flow by automatically opening the Feedwater Regulating Valves (FRV). This raised reactor water level until the turbine tripped and the scram occurred. The root cause of this event was insufficient procedural controls over wire termination practices. On February 26, 1987, at 1200 hours, while conducting an inspection of wire terminations as a corrective action for the above event, a technician disturbed a loose wire de-energizing relays which were bypassing a protective function by design. This resulted in an automatic closure of the main steam isolation valves. The reactor was in the SHUTDOWN mode with reactor coolant temperature less than 212 degrees Fahrenheit. The root cause of this event was faulty wire installation either during plant construction or subsequent maintenance. Terminations in the control room, and others vital to safety and operation were inspected and tightened where necessary. Procedures will be revised to control future termination practices.
219 | 2191987029 | 1987-07-30 | QL5 | Partial Closure of MSIVs | [45 empty] | Oyster Creek | B | GE | PO | 97 | On July 30, 1987 at 0500 hours a high reactor pressure scram occurred when an air leak caused a Main Steam Isolation Valve (MSIV) to close with reactor power greater than the level where one main steam line alone is sufficient to maintain reactor pressure below the scram setpoint. The plant was operating at approximately 97% rated power prior to this event with reactor pressure at 1020 psig and reactor temperature at 524 degrees F. During a 5% closure test of MSIV NS04A, the air test pilot valve partially dislodged from its mounting causing the MSIV to close beyond 5% and stabilize at an intermediate position. This produced a low control air pressure alarm. The operators quickly diagnosed the problem and began reducing power and started two additional air compressors. Fifteen minutes had elapsed and reactor power had been reduced to approximately 70% when the air test pilot valve dislodged completely closing the MSIV. <br /><br /> This caused a high reactor pressure scram. The cause of this event is the air test pilot valve mounting cap screws were 1/4 inch shorter than vendor specifications. The dislodged air test pilot valve and all other MSIV air pilot valves were reinstalled with proper length cap screws. The MSIV air pilot valve installation procedure will be revised to identify the proper length screws for future maintenance.
219 | 2191989011 | 1989-04-22 | QL7 | Degraded condenser vacuum | [45 empty] | Oyster Creek | B | GE | SU | 2 | On April 22, 1989 at 1850 hours, the mechanical vacuum pump was placed into service in order to maintain condenser vacuum during a planned shutdown evolution. The equipment operator who placed the vacuum pump into service failed to properly align the seal water makeup supply. At 1935 hours a gradual decrease in the main condenser vacuum was noted. The rate of decrease in condenser vacuum prevented any significant attempts to correct the problem so the Group Shift Supervisor directed. the operators to manually scram the reactor at 1945 hours. The cause of this occurrence is attributed to operator error. The operator failed to establish a complete valve lineup to the seal water makeup supply in accordance with the operating procedure. Starting the mechanical vacuum pump is a simple evolution but infrequently performed by individual operators. Operators are not required to have a procedure in hand when performing a simple or routine evolution. This contributed to the oversight by the operator. Without seal water makeup the mechanical vacuum pump operated properly until the seal water tank emptied which then caused a significant air leak to the main condensers. This caused the decrease in condenser vacuum which resulted in the reactor scram. The safety significance of this event is minimal because the reactor was at low power (approximately 2%) when the event occurred. To prevent a similar occurrence in the future, other infrequently performed evolutions that currently do not require a procedure in hand will be reviewed to determine if further guidance is warranted.
219 | 2191989015 | 1989-05-18 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Oyster Creek | B | GE | PO | 100 | On May 18, 1989 at 1103 hours the reactor automatically shut down due to a trip of the main turbine generator. An instrument technician had been assigned the task of calibrating the plant megavar recorder. He discussed the activity with shift management but did not mention that input leads to the recorder would be disconnected. The technician started the evolution an hour and a half later without informing the Control Room. Upon disconnecting the input leads to the recorder, a Hi/Low VAR alarm was received. The operators did not realize that the alarm was the result of the technician's work and attempted to manually restore the VAR loading. The operator did not realize that he was actually increasing megavars because he was not observing bus voltages, which were increasing. A generator overexcitation condition resulted which tripped the main generator, caused a reactor scram, and resulted in a fast start of both diesel generators. The operators proceeded to cooldown the plant with the Isolation Condensers until the Shutdown Cooling System was placed into service at 1523 hours. The plant reached cold shutdown conditions at approximately 1700 hours. The root cause of this event was personnel error on the part of both operations and maintenance personnel. To prevent a recurrence of a similar event, administrative controls have been implemented and increased emphasis has been placed on communications between the work group and the control room. Operators will be briefed on the need to use all available indications during a response to an abnormal condition to avoid a recurrence of this event.
219 | 2191989016 | 1989-06-25 | QR5 | Turbine Trip | [45 empty] | Oyster Creek | B | GE | PO | 97 | On June 25, 1989 at 0008 hours, the main generator tripped due to a phase differential condition caused by a fault in one of the main output transformers. When the generator tripped a turbine trip signal was generated which resulted in an anticipatory reactor scram. The plant was cooled down with the main condensers and the shutdown cooling system and reached a cold shutdown condition at 1100 hours. The cause of this event was equipment failure. Examination of the transformer determined that an internal winding had failed thereby causing the phase differential condition which caused the generator trip. This transient was within the design basis of the plant and had no safety significance. Preparations have been made to remove the failed transformer and install a spare. Until the spare is installed the plant will be operated at half load. No other corrective action was determined necessary.
219 | 2191989017 | 1989-07-11 | QR5 | Turbine Trip | [45 empty] | Oyster Creek | B | GE | PO | 100 | On July 11, 1989 at 0055 hours, the Main Generator tripped due to a phase differential condition caused by a fault in the operating main output transformer (the other main transformer failed on June 25, 1989). When the generator tripped, a turbine trip signal was generated which resulted in an anticipatory reactor scram. The plant was cooled down utilizing the main condenser and the Shutdown Cooling System and reached the cold shutdown condition at 0950 hours. The cause of this event was equipment failure. Examination of the transformer determined that an internal winding had failed, causing the phase differential condition which caused the generator trip. The plant responded as designed and operator action was prompt and appropriate. This transient was within the design basis of the plant and had no safety significance. The entire Electrical system was evaluated for adverse effects due to the fault, and an evaluation was completed to determine if a generic problem existed between the two failed transformers and the other power transformers at the station. As a result, it was determined the failure was confined to the two main output transformers and did not involve any other transformers. The plant was returned to power operation on July 19, 1989 using the spare transformer installed due to the previous failure of the other Main Output Transformer.
219 | 2191989021 | 1989-09-22 | QR5 | Turbine Trip | [45 empty] | Oyster Creek | B | GE | PO | 100 | On September 22, 1989, at approximately 1418 hours, mechanical test equipment was inadvertently left connected to one of the reactor pressure vessel (RPV) water level instruments after testing was complete. While being placed back in service, the reference leg of the instrument was vented to the test equipment causing a false high RPV water level signal to be generated in all five level instruments attached to that common reference leg. The false high RPV water level caused a trip of the turbine generator which resulted in a reactor scram. The technician performing the valve manipulation recognized the problem and closed the root valve. The cause of this event was personnel error since the test equipment was not removed as required by the surveillance procedure. This event had minimal safety significance because the Reactor Protection System is designed to protect the reactor from any turbine trip condition, and the excess flow check valves in the instrument line would have prevented any significant loss of coolant. All engineered safety features would have functioned normally due to redundant RPV level instrumentation. All instruments involved in this event were calibration checked to ensure no problems had resulted from the momentary depressurization. The technicians involved in this event were counseled.
219 | 2191990004 | 1990-02-20 | QR8 | Spurious Reactor Trip | [45 empty] | Oyster Creek | B | GE | PO | 100 | On February 20, 1990, while performing a surveillance on a reactor vessel level instrument, an Instrument & Controls (I&C) technician keyed a hand-held radio near the analog trip units for the Alternate Rod Injection (ARI) System causing the system to actuate due to radio frequency interference (RFI). Control room operators noted that air operated valves supplied from the Scram Air System were repositioning and that control rods were drifting into the core. The operators initiated a manual reactor scram as required by procedure due to the drifting control rods. The cause of this occurrence has been attributed to personnel error by the technician performing the surveillance procedure. The access door to the area where the ARI System components are located is well marked with reference to the restriction on the use of radios in the area. This event is determined to have minimal safety significance because a manual scram was initiated by the operators within 5 seconds of rod movement. Chemistry samples indicate that no fuel damage resulted from this event. The use of radios by I&C technicians must now be approved by the technician's supervisor. Appropriate site personnel will receive training on this event and an investigation will be conducted into minimizing the ARI System's sensitivity to RFI.
219 | 2191990005 | 1990-04-21 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Oyster Creek | B | GE | PO | 80 | On April 21, 1990 at 0955 hours, power was lost to Unit Substation (USS) 1B2 when a power supply cable shorted to ground. Several safety related components were affected by the loss of power. and drywell unidentified leak rate increased to greater than 5 gpm due to loss of power to the Drywell Equipment Drain Tank Pump Control Circuit. The plant was shutdown due to loss-of-power to required electrical busses, and on April 22nd at 1005 hours, the reactor reached cold shutdown. USS 1B2 was isolated from the failed supply cable and reenergized from USS 1A2 via the crossconnect breaker. During the cooldown, the A isolation condenser was declared inoperable due to the inability to electrically cycle a DC isolation valve because of thermal binding. This thermal binding problem was corrected by modifications completed during the 13R refueling outage.<br /><br /> The cause of the cable failure was determined to be a 'void' in the insulation of the cable. A new supply cable was installed and the USS was repowered from it's normal source. A representative sample of other cables supplying safety related components were tested, and no generic concerns were found. On March 22, 1991, the 1A2 cable failed during the 13R outage. There appears to be no connection between the failures of these two cables.
219 | 2191990008 | 1990-06-25 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Oyster Creek | B | GE | PO | 100 | On June 25, 1990, at approximately 6:18 AM, a reactor scram occurred on low condenser vacuum. The scram occurred during initiation of backwashing of the A north main condenser. The scram was caused by the failure of the backwash outlet valve to open, causing a loss of circulating water to the A condenser. The backwash outlet valve failed to open due to a breaker trip of the motor operator. The plant was stabilized in a hot standby condition and subsequently taken to cold shutdown. The motor operator, the breaker and the valve were all inspected and tested satisfactorily. The auxiliary contacts on the motor close coil were replaced and auxiliary contacts on the motor open coil were realigned. The remaining 20 circulating water valves manipulated during backwashing evolutions were tested and verified to be operating properly.
219 | 2191991005 | 1991-08-22 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Oyster Creek | B | GE | PO | 100 | On August 22, 1991, at 0306 hours, a reactor scram occurred due to low reactor water level. The cause of the low reactor water level was a loss of feedwater flow due to a main feed pump trip on low suction pressure. The root cause of this event was a grounded condensate pump motor which led to a condensate pump trip while the plant was operating above 80% power. The motor was replaced. <br /><br /> The shrink in reactor water level caused by the scram and the reduction in feedwater flow caused reactor water level to reach the double low Reactor Protection System (RPS) setpoint which actuated appropriate Engineered Safety Features. <br /><br /> A second event being reported is a procedure violation which occurred at 1012 hours. While plant cooldown to cold shutdown conditions was in progress, all five reactor recirculation discharge valves were shut simultaneously with reactor temperature above 212 degrees F. The plant achieved cold shutdown at approximately 1800 hours.
219 | 2191992005 | 1992-05-03 | B1 | Loss of Offsite Power (LOOP) |  | X | [5 empty] | X | [7 empty] | X | [17 empty] | X | [11 empty] | Oyster Creek | B | GE | PO | 100 | A reactor scram and subsequent Engineered Safety Features systems actuations were caused by a turbine load rejection due to faults on off-site 230kV transmission lines caused by a forest fire. The scram occurred at 1326 hours on May 3, 1992 and the event concluded at 0635 hours on May 4, 1992. The reactor was operating at approximately 100% power before the scram. Numerous other engineered safety features actuated including Isolation Condensers, Containment Isolation, Diesel Generator fast start, Core Spray and Standby Gas Treatment. Several additional scram signals occurred in the process of bringing the plant to cold shutdown and returning power supplies to off-site sources. An Unusual Event was declared based on high drywell temperature, and an Alert was declared based on the potential of the forest fire to further affect the plant. The plant was brought to cold shutdown at 2234 hours on May 3, and the emergency condition was terminated at 0635 hours on May 4, after off-site power was restored to vital electrical buses. Off-site power had been available since 1331 hours on May 3, but plant management decided not to place the vital buses on off-site power until reliability could be assured. No plant structures or equipment were damaged by the fire. The forest fire which caused the loss of off-site power was the root cause of the event, and the safety significance was minimal because all systems functioned as required. Corrective actions include a revision to the Diesel Generator operating procedure to prevent an avoidable scram when securing diesel generator operation. Utility personnel inspected off-site power lines and found no damage. High resistance contacts on the control rod drive pump time delay relay were replaced due to the pump's failure to start on a diesel generator load sequence.
219 | 2191992009 | 1992-08-22 | QP2 | Partial Loss of Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Oyster Creek | B | GE | PO | 100 | A reactor low water level scram from full power occurred on August 22, 1992, at 1255 hours. A low-low water level condition occurred immediately after the scram, which resulted in the actuation of several engineered safety features: Core Spray system initiation, Diesel Generator start, primary containment isolation, main steam isolation, Isolation Condenser initiation, and Standby Gas Treatment system initiation. Once the Main Steam Isolation Valves were closed, reactor water level was restored using the Feedwater system. The reactor was cooled using the Isolation Condensers. The cause of the event was a failed proportional amplifier in the Feedwater Control system, which caused the system to sense a large decrease in steam removed from the reactor vessel. The system compensated for the apparent steam flow decrease by rapidly reducing Feedwater flow, which caused the low water level and scram. The safety significance of the event is considered minimal. The failed proportional amplifier was replaced and the plant was restarted. The Feedwater Control system is scheduled to be replaced in the upcoming refueling outage.
219 | 2191994003 | 1994-04-05 | QP5 | Excessive Feedwater Flow | [45 empty] | Oyster Creek | B | GE | PO | 100 | On 04/05/94 at 1550 hours a turbine trip and reactor scram occurred due to high reactor water level. Cause of the event was the failure of a proportional amplifier which provides a density correction signal to both A & B steam flow signals. This resulted in a false high steam flow signal which resulted in the feedwater control system increasing feedwater flow to the reactor which caused reactor water level to increase. When water level reached the high level turbine trip setpoint of 175', the turbine tripped and a reactor scram occurred as designed. The faulty electronic module was replaced and the feedwater flow control system was returned to operational status.
219 | 2191994007 | 1994-05-31 | QR5 | Turbine Trip | [45 empty] | Oyster Creek | B | GE | PO | 100 | A reactor scram occurred due to modification work in the switchyard on May 31, 1994 at 1332 hours. While loosening a wire connected to an auxiliary relay of the 230 KV bus section differential relay, to install a Digital Fault Recorder, the relay actuated causing a generator and turbine trip resulting in a reactor scram. All five Recirculation Pumps tripped, two Electromatic Relief Valves opened and both Isolation Condensers initiated. All systems responded to the scram as expected and therefore, there was no safety significance to this event. The plant was placed in cold shutdown at 2210 hours on May 31. Corrective actions included placing the modification on hold pending engineering review and strengthening procedural controls over switchyard work.
219 | 2191995008 | 1995-12-18 | QR5 | Turbine Trip | [45 empty] | Oyster Creek | B | GE | PO | 100 | On 12/18/95 at 0437 hours a reactor scram and turbine trip occurred due to high reactor pressure. The cause of the event was a generator runback due to high stator cooling water temperature. The elevated cooling water temperature was caused by the failure of the system temperature control valve to properly regulate cooling water temperature. When cooling water temperature reached the high temperature setpoint of 89 Degrees C, the generator protection system initiated a turbine generator runback. The closing of the turbine control valves beyond the limit of the bypass valves reduced the mass flow capability of the turbine control system and reactor pressure increased. When reactor pressure reached the high pressure scram setpoint of 1045 psig, a reactor scram occurred as designed. Reactor power peaked at 108.5 % power during the pressure transient. After the scram, reactor water level dropped below the low level scram setpoint (139.48 in. TAF) to a level of 97 in. TAF and then was recovered in accordance with plant procedures. The faulty temperature control valve was repaired and the stator cooling system was returned to operational status.
219 | 2191996005 | 1996-04-30 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Oyster Creek | B | GE | SU | 10 | On April 30, 1996, with a reactor startup in progress, a reactor scram occurred at 0256 hours. When reactor level decreased to 139 inches above Top of Active Fuel (TAF), a Low Level reactor scram occurred as designed. Following the scram, water level further decreased to approximately 120 inches TAF before being restored to normal. The cause of the event was a failure on the part of the operator to properly control reactor water level, aggressively take action to restore level, and use the most conservative reactor water level indicator. A contributory cause was ineffective supervisory oversight in that two SRO licensed supervisors did not take positive action to halt startup activities until normal level control could be reestablished.<br /><br /> The safety significance of this event was minimal. Adequate core cooling was maintained. <br /><br /> Immediate corrective action was taken to recover water level and place the reactor in a shutdown condition. A discussion of the event was issued to the operators. Guidance was issued to the operators on reactor water level control, and use of the most conservative level indicator during a reactor startup. <br /><br /> Additional long term corrective action will be taken to evaluate the transition point for feedwater control during a reactor start up.
219 | 2191996007 | 1996-09-04 | QL7 | Degraded condenser vacuum | [45 empty] | Oyster Creek | B | GE | PO | 100 | On September 4, 1996, the A North Main Condenser was being placed into backwash mode for routine cleaning. The A North inlet valve did not close resulting in a decrease in condenser vacuum. A low vacuum reactor scram occurred as designed. A pressure increase occurred as expected and two of the five Electromatic Relief valves actuated to relieve pressure until the condenser bypass valves opened. controller which did not close the valve on demand. <br /><br /> The safety significance of this event has been determined to be minimal as all safety systems functioned as designed. <br /><br /> Immediate corrective action was taken to stabilize the plant and subsequently place the reactor in the cold shutdown mode. Prior to restart from the current 16R refueling outage, corrective actions will be taken to repair the controller and evaluate the deficiency for potential generic concerns.
219 | 2191996008 | 1996-10-25 | QR6 | Manual Reactor Trip | [45 empty] | Oyster Creek | B | GE | PO | 100 | On October 25, 1996 at approximately 1159 hours a manual scram of the reactor was initiated in accordance with plant procedures due to a confirmed Main Generator Runback, Plant response to the generator runback and manual scram was normal. All control rods inserted fully, and plant response was as designed. Initial troubleshooting did not identify the initiating component. However, subsequent monitoring identified an invalid temperature switch actuation, which were then disconnected pending further analysis. Corrective actions include continued fault analysis on the existing temperature sensing switches. New temperature sensing devices will be evaluated and tested prior to returning the temperature portion of the main generator runback circuit to service.
219 | 2191997010 | 1997-08-01 | H1 | Fire |  | X | [5 empty] | X | [7 empty] | X | [17 empty] | X | [11 empty] | Oyster Creek | B | GE | PO | 100 | A manual scram was initiated in response to sparking in the main generator exciter commutator. The sparking was caused by a brush failure due to the use of incorrect parts. As a result of a low voltage condition, the emergency buses separated from off-site power and were subsequently energized by the emergency diesel generators. Several engineered safety features actuated. The two control rod drive pumps failed to start as designed. During a review of the transient, it was identified that the startup transformer voltage regulators were set to regulate voltage outside the plant's design basis as described in the degraded grid voltage study. A design defect in the control rod drive pump breaker control logic was also identified. Corrective actions include repair of the exciter, resetting the transformer voltage regulators and adding a time delay to the control rod drive pump start sequence.
219 | 2191998004 | 1998-03-20 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Oyster Creek | B | GE | PO | 71 | On March 20, 1998, the steam supply valve to the Steam Jet Air Ejectors (SJAE) failed closed. Due to the loss of the SJAEs, main condenser vacuum decreased. With vacuum decreasing rapidly and approaching the low vacuum scram setpoint, the operators manually scrammed the reactor in accordance with station procedures. Plant response to the scram was normal and there were no unexpected activations of or challenges to engineered safety features. The cause was failure of the solenoid operated valves (SOVs) associated with the SJAE steam supply valves. The SOVs failed because they were not temperature rated for the environment in which they were located. The root cause was inappropriate replacement of direct acting solenoid valves with pilot operated valves with elastomer material not rated for the environmental conditions. Immediate corrective action was taken to stabilize the plant and subsequently place the reactor in cold shutdown mode. A detailed root cause and extent review was conducted by engineering. Prior to restart, the SOVs were replaced with valves rated for the environment. Additional guidance will be developed for the design, procurement and installation of SOVs.
219 | 2192000001 | 2000-01-21 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Oyster Creek | B | GE | PO | 65 | On January 21, 2000, at approximately 1049 hours, control room operators manually scrammed the reactor in response to a multiple reactor recirculation pump trip. Human error caused the multiple pump trip during performance of an isolation condenser actuation system surveillance. The isolation condenser actuation system also inserts trip signals into the reactor recirculation pump trip system. After testing the first instrument, the recirculation pump trip system was not properly reset before proceeding to the second instrument. When a test signal was introduced to the second instrument, the pumps tripped as designed. Plant response to the manual scram was normal. A human performance assessment has been completed and corrective actions to reinforce management expectations will be completed.
219 | 2192000003 | 2000-03-01 | QC5 | Loss of Non-safety-Related Bus | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Oyster Creek | B | GE | PO | 25 | NULL
219 | 2192000011 | 2000-11-15 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Oyster Creek | B | GE | SU | 5 | On November 15, 2000, during reactor startup from the 18 R outage, turbine pre-warming had been completed and Operators were transitioning to steam chest warming in accordance with procedures. Reactor Pressure was approximately 460 psig. Due to a misinterpretation of the procedure, the operators did not close the Bypass Valve Opening Jack prior to closing the Load Limiter. This resulted in several Turbine Bypass Valves (BPVs) rapidly opening and a subsequent reactor level increase. Immediate response to the high level condition was to reduce feedwater flow and increase letdown. This action combined with the inventory loss through the BPVs resulted in overcompensating and the level decreased to the low-level scram setpoint. A full reactor scram was received. All control rods inserted. Reactor level was stabilized. Reactor pressure continued to decrease until the bypass valves were shut (approximately 17 minutes into the transient). The main consequence of this transient was the scram, which resulted in the excessive cooldown rate, and exceeded the 100 degrees F per hour Technical Specification limit. The root cause of this event was personnel error. Operators demonstrated a lack of fundamental knowledge with respect to system operations in that they did not fully comprehend the consequences of not closing the bypass valve opening jack prior to closing the limit load and failed to close the BPVs. Corrective actions included revising the procedure to clarify the misinterpreted step. An evaluation of the effects of excessive cool down rate was also conducted.
219 | 2192003002 | 2003-05-20 | C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) |  |  | X | [13 empty] | X | [28 empty] | Oyster Creek | B | GE | PO | 100 | On May 20, 2003, at 0030 hours, 4160 VAC bus 1 C locked out due to a ground fault. The plant continued operating at full power. Due to the equipment made inoperable by the loss of power to bus 1 C, Technical Specifications required the reactor to be placed In the COLD SHUTDOWN CONDITION. The reactor was manually scrammed at 0943 hours. The COLD SHUTDOWN CONDITION was reached at 1913 hours. The safety significance of this event is considered minimal. The redundant 4160 VAC bus remained in service and redundant safety-related equipment remained operable. The plant remained within Technical Specification limits and achieved SHUTDOWN and COLD SHUTDOWN within the allowed time limits. Previous experience has shown this type of cable is subject to accelerated degradation from water at the site of any defects In the insulation. All cables in this run were replaced with cables of a different manufacture. Corrective action included confirming that all buried cable powering safety-related equipment was not of the type that failed.
219 | 2192003003 | 2003-08-14 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Oyster Creek | B | GE | PO | 100 | On August 14, 2003, an electrical disturbance in the off-site electrical power grid caused an overexcitation condition in the main generator. This resulted in a main generator lockout, turbine trip, and reactor scram from 100% power. The reactor shut down as designed. Plant cooldown to cold shutdown was required due to the trip of all five recirculation pumps (three auto trip and two manual trip). Off-site power was available throughout the event. The safety significance of this event is considered minimal. The plant responded as designed for this type of event. Technical Specification limits were maintained. There was no radioactive release. Off-site power was not lost Operator response was appropriate.
219 | 2192003004 | 2003-08-22 | QR5 | Turbine Trip | [45 empty] | Oyster Creek | B | GE | PO | 100 | On August 22, 2003, a Turbine Trip was caused by a spurious actuation of Moisture Separator Hi-Hi Level switch, LS-4-691. This resulted in a Reactor Scram from 100% power. The reactor shut down as designed. Plant cooldown to cold shutdown was required due to the trip of all five recirculation pumps. The safety significance of this event is considered minimal. The plant responded as designed for this type of event. Technical Specification limits were maintained. There was no radioactive release . All safety systems were fully operable. Off-site power was available. Operator performance was satisfactory. All four level switches were replaced and a root cause is in progress.
219 | 2192004003 | 2004-05-27 | QR8 | Spurious Reactor Trip | [45 empty] | Oyster Creek | B | GE | SU | 2 | On May 27, 2004, at 00:31 hours, with the Reactor Mode switch in the Startup position, a reactor scram from approximately 2% power was caused by a spurious actuation of Nuclear Instrumentation (NI) Intermediate Range Monitor (IRM) (EIIS-IG) channels 13, 14, and 18. The spurious actuation was caused by electromagnetic interference (EMI). The reactor shut down as designed. The safety significance of this event is considered minimal. The plant responded as designed for this type of event. Technical Specification limits were maintained. There was no radioactive release. All safety systems were fully operable. Off-site power was available. Operator performance was satisfactory. A Root Cause Analysis has been completed identifying the root cause of the EMI induced spiking of the IRM channels. IRM-13 & 14 were found to have loose cable connections at the drawer and nicks in the outer surface of the cable. This has been traced as the entry point of the noise intrusion and the reason the channels spiked. A coated surface on the circuit preamplifier box, on IRM-1 8, caused a poor connection to a common ground point and provided another entry point for noise intrusion. Connections were tightened, damaged cabling was repaired, and one IRM pre-amplifier was replaced.
219 | 2192005002 | 2005-06-01 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Oyster Creek | B | GE | PO | 100 | On June 1, 2005, at 21:09, with Oyster Creek at 100% power, an Anticipatory Generator Load Reject scram occurred. During restoration of a transformer by the transmission utility at their substation, a failure of lightning arrestors resulted in a phase-to-phase-to-ground short circuit. This resulted in a grid transient of sufficient magnitude that the Oyster Creek Turbine-Generator sensed a load rejection condition, which resulted in a reactor scram signal. The reactor scrammed and the turbine-generator tripped as expected for this condition. All safety systems performed as expected. The plant was stabilized in the hot shutdown mode. Corrective actions included completing restart required evaluations, testing and confirmation from the involved transmission utility that conditions in the substation would not result in recurrence of the grid disturbance. The apparent cause of this event was equipment failure of the lightning arrestors in the transmission utility substation that created a grid disturbance. There have been several grid disturbances over the life of the plant, including two LERs: LER 2003-003, Actuation of Reactor Protection System Due to a Grid Transient (August 14, 2003). LER 1994-007 was a reactor scram caused by a 230 KV bus section differential relay trip while a switchyard worker was installing a Digital Fault Recorder.
219 | 2192007001 | 2007-07-17 | QP2 | Partial Loss of Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Oyster Creek | B | GE | PO | 100 | On July 17, 2007 at 05:21 while operating at 100% power, an automatic reactor scram occurred due to low reactor water level following a trip of the "C" Reactor Feed Pump (RFP). The cause of the "C" RFP trip is attributed to an electrical fault internal to the motor. This transient led to an automatic scram on low reactor water level and subsequent reactor isolation on a low-low reactor level. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to the automatic reactor protection system and subsequent ECCS actuations.
219 | 2192007003 | 2007-12-19 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Oyster Creek | B | GE | PO | 55 | At 1145 on 12/19/2007, an Unplanned Manual Reactor Scram occurred due to critical omission of technical information regarding the minimum Circulating Water (CW) system configuration necessary to maintain the Main Condenser water boxes filled. At the time of the event, the station CW system was being operated in accordance with procedural guidance and available design basis information. Based upon a review of historical documents since 1968, a critical omission of technical information existed regarding the minimum CW system configuration necessary to maintain the Main Condenser water boxes filled. Two corrective actions to prevent recurrence were developed; (1) revise the CW operating procedure to provide minimum system configuration and pressure to maintain the Main Condenser water boxes filled, and (2) revise design basis documentation to provide minimum system configuration and pressure to maintain the Main Condenser water boxes filled. Additional corrective actions were developed including a Technical Human Performance case study to reinforce failed or ineffective barriers.
219 | 2192008001 | 2008-11-28 | QR5 | Turbine Trip | [45 empty] | Oyster Creek | B | GE | PO | 98 | On November 28, 2008 at 2101 while operating at 98% power, a generator trip occurred due to a transformer differential relay actuation. The cause of the differential relay actuation is attributed to an electrical fault internal to the M1A Main Power Transformer. This transient led to a reactor automatic shutdown due to a load reject SCRAM. All safety systems operated as expected following the SCRAM. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to the automatic reactor protection system actuation.
219 | 2192009001 | 2009-02-01 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | Oyster Creek | B | GE | PO | 100 | On February 1, 2009 the Oyster Creek Generating Station was operating at 100% reactor power, 661 Megawatts Electric (MWE). Oyster Creek had been online for 56 days following the 1F17 Forced Outage due to the MIA transformer failure on November 28, 2008. At 2156 hours, Oyster Creek's main generator tripped due to the actuation of the 230kV bus section differential relay due to the failure of the MIA main power transformer. This caused a load reject SCRAM that automatically shut down the reactor. The transformer failure led to the declaration of an Unusual Event at 2211 hours, based on a fire lasting greater than 15 minutes affecting the M1A transformer. The fire was extinguished at 2227 hours and the Unusual Event was terminated at 2337 hours on February 1, 2009. There were no nuclear safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to the automatic reactor protection system actuation.
219 | 2192009003 | 2009-04-25 | QR6 | Manual Reactor Trip | [45 empty] | Oyster Creek | B | GE | PO | 100 | On April 25, 2009, with the unit at 100% power, loss of cooling to the Main Power Transformer M1A resulted in a manual plant scram. The loss of cooling was caused by a faulted cooling bank motor starter, resulting in the failure of the MIA auxiliary control power transformer and subsequent loss of control power for the remaining cooling bank motor starters. A reactor load reduction was commenced in accordance with the alarm response procedure to maintain MIA temperatures below the alarm set points. While reactor power was being reduced, transformer operation was limited to 30 minutes without forced cooling. Operations secured the power reduction and manually scrammed the reactor from 74% power in accordance with plant procedures. The post scram response was normal and the required notifications were made. All safety systems operated as expected following the reactor scram. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to manual actuation of the reactor protection system.
219 | 2192009005 | 2009-07-12 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Oyster Creek | B | GE | PO | 100 | On July 12, 2009 with the Unit at 100% power in the "Power Operation" mode, a severe electrical storm resulted in multiple lightning strikes on an interconnected 34.5 kV offsite transmission line. These lightning strikes in conjunction with a failure of a line breaker to open caused grid disturbances, a main generator trip on over-excitation, an automatic reactor scram due to the load rejection, and a loss of offsite power to the Startup Transformers. When the plant experienced the loss of offsite power to the Startup Transformers, both Emergency Diesel Generators (EDGs) started and energized their associated safety related buses. During the event, EDG #1 was slow to tie onto its safety-related bus and the erratic "B" Isolation Condenser (IC) level indication resulted in operators declaring the IC inoperable. An Unusual Event was declared for the loss of power to the Startup Transformers for greater than 15 minutes. All declarations and notifications were made correctly and in a timely manner. This event is being reported pursuant to: 10CFR50.73(a)(2)(iv)(A) due to automatic actuation of the reactor protection system, isolation condensers, and emergency diesel generators; and 10CFR50.73(a)(2)(v)(D) due to loss of offsite power to the Startup Transformers.
219 | 2192010002 | 2010-12-23 | QL7 | Degraded condenser vacuum | [45 empty] | Oyster Creek | B | GE | SU | 1 | On December 23, 2010, with the reactor critical high in the Intermediate Range in the "Startup" mode, the reactor automatically scrammed on low main condenser vacuum. The cause was due to exceeding the 600 psig bypass reset enabling the low condenser vacuum trip prior to establishing the required vacuum. This bypass allows operation at reduced power below 600 psig during startup until adequate vacuum can be established in the main condenser. The main condenser low vacuum reactor protection scram signal processed when reactor pressure was raised above the 600 psig bypass function during reactor startup. A procedure requirement for confirming all main condenser low vacuum alarms and trips are reset prior to exceeding 500 psig ensures that a scram signal is not present. The direct cause of the event was determined to be inadequate procedure compliance by the Unit Reactor Operator (URO) in not verifying that all requirements were met prior to proceeding above 500 psig reactor pressure. Corrective actions include enhancement of operating procedures to clearly define key milestones requiring supervisor concurrence prior to continuing with reactor startup or shutdown. This event is being reported pursuant to: 10CFR50.73(a)(2)(iv)(A) due to an automatic actuation of the Reactor Protection System (RPS).
219 | 2192012001 | 2012-07-23 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Oyster Creek | B | GE | PO | 100 | On July 23, 2012, a turbine-generator trip occurred when all three 230 kV transmission paths from the station tripped unexpectedly following a single phase to ground fault on one of the three lines. There are three 230 kV lines leaving the Oyster Creek switchyard, N-1028, O-1029, and S-2045. The initial fault occurred on the S-2045 line. Subsequent to the initial fault, an over tripping event occurred as a result of the actuation of the directional overcurrent ground (KRD) relays associated with the N-1028 and O-1029 lines. These relays actuated when the current polarized directional signal caused the directional contact to close and complete the trip circuit. <br /><br /> As a result of the turbine-generator trip, the reactor automatically shutdown from 100% reactor power with all control rods fully inserting and all safety systems functioning as required. Concurrent with the turbine-generator trip and the tripping of the three 230kV transmission lines, the Q121 Oyster Creek-Whitings 34.5kV sub-transmission line opened up at the Oyster Creek switchyard causing an interruption of off-site power. Due to the interruption of off-site power, both Emergency Diesel Generators automatically started and carried loads on the safety buses (1C and 1D buses). Oyster Creek declared an Unusual Event based on a loss of all off-site AC power to 4160V Buses 1C and 1D for greater than 15 minutes. All declarations and notifications were made correctly and in a timely manner. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to automatic actuation of the reactor protection system. <br /><br /> A Root Cause Investigation was performed and determined that the current transformer input that is used to provide a polarized directional signal for fault indication was landed incorrectly at the KRD relay. The leads were found to be reversed when compared to the required configuration. In this reversed configuration, the relay provided a trip signal for faults in the non-trip direction and failed to provide a trip signal for faults in the trip direction. The Root Cause of this event was determined to be a failure to adequately maintain configuration and validate the proper functionality of transmission system protective relays, following Oyster Creek transformer replacement activities in 2010.
219 | 2192013002 | 2013-10-06 | QL7 | Degraded condenser vacuum | [45 empty] | Oyster Creek | B | GE | PO | 20 | On October 6, 2013 at approximately 1040 EDT, during a planned reactor power ascension with reactor power at approximately 20% of rated thermal power, main condenser vacuum began to lower. In accordance with the abnormal operating procedure for degrading vacuum, Operators inserted a manual scram of the reactor at 1130 EDT.<br /><br /> Following the reactor SCRAM, operations and maintenance personnel identified an approximate 1" hole on Y-1-26, 'B' Condenser Steam Inlet Expansion Joint on the south side of 'B' Condenser. It was confirmed to be an active leak and subsequently the source of condenser vacuum degradation. A temporary leak repair was performed.<br /><br /> All control rods fully inserted and plant response was as expected. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to an actuation of the Reactor Protection System (RPS).
219 | 2192013004 | 2013-12-14 | QR6 | Manual Reactor Trip | [45 empty] | Oyster Creek | B | GE | PO | 95 | On 12/14/13 at approximately 0336 EST, during quarterly turbine valve testing with reactor power at 95% of rated thermal power, the plant experienced reactor pressure control abnormalities. Turbine Control Valves 2 and 3 failed closed due to the Servo Motor Feedback Support Bracket bolts backing out and falling out thereby requiring a scram. Operators initiated a manual reactor scram due to reactor pressure rising to 1042 psig which approached the scram set point.<br /><br /> These conditions were corrected during 1F33. These were determined during complex troubleshooting as the failures that drove the event. The root cause determined that the manufacturer failed to assemble the Control Valve Hydraulic Enclosure per their design.<br /><br /> There were no safety consequences impacting the plant or public safety as a result of this event. All control rods fully inserted and plant response was as expected. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to an actuation of the Reactor Protection System (RPS).
219 | 2192014001 | 2014-07-11 | QL7 | Degraded condenser vacuum | [45 empty] | Oyster Creek | B | GE | PO | 56 | On July 11, 2014 at approximately 0312 EDT, during planned reactor power ascension with reactor power at approximately 56% of rated thermal power, main condenser vacuum began to degrade. In accordance with the abnormal operating procedure for degrading vacuum, Operators inserted a manual scram of the reactor at 0314 EDT.<br /><br /> Following the reactor scram, operations and maintenance personnel identified an approximate 2"x6" hole and an approximate 2”x3” hole on the last convolute of the downstream side of Y-1-26 ('B' Condenser Steam Inlet Expansion Joint). It was confirmed to be an active leak and subsequently the source of condenser vacuum degradation. As a corrective action to this event, the expansion joint was replaced.<br /><br /> All control rods fully inserted and plant response was as expected. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to an actuation of the Reactor Protection System (RPS).
219 | 2192014006 | 2014-10-12 | QR8 | Spurious Reactor Trip | [45 empty] | Oyster Creek | B | GE | SU | 1 | On October 12, 2014, an automatic SCRAM occurred during the reactor startup evolution following the 1R25 refueling outage. The SCRAM occurred when a station electrician, in conjunction with a General Electric technician and a site engineer, secured power to the Main Generator Automatic Voltage Regulator (AVR) controllers while the Main Turbine warming evolution was in progress. The individuals were not authorized to perform this action nor did they have procedures in the field to operate the equipment. Their actions resulted in an automatic reactor SCRAM on low water level. <br /><br /> ENS 50524 was submitted on October 12, 2014, and updated on October 17, 2014. This issue is reportable under 10 CFR 50.73(a)(2)(iv)(A), because it involved an event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).<br /><br /> The Root Cause Analysis was completed on January 30, 2015. The cause of this event was determined to be that Station Leadership has inconsistently reinforced Human Performance Error Reduction Tool Use and Procedure Use and Adherence. This resulted in the breakdown of multiple fundamental practices and standards that led to the event.
219 | 2192015001 | 2015-03-22 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Oyster Creek | B | GE | SU | 1 | On March 22, 2015 at 1414, an automatic SCRAM from full power operation occurred at Oyster Creek due to a valid RPS actuation on APRM Hi-Hi flux. The APRM Hi-Hi flux was caused by a rise in reactor pressure due to the failure of the Electric Pressure Regulator (EPR). The backup Mechanical Pressure Regulator (MPR) did not limit reactor pressure. <br /><br /> The scram occurred due to inadvertent contact with degraded wiring during troubleshooting to isolate a DC ground identified within the turbine control indication circuitry. The contact caused a loss of signal from the EPR to its controlling Programmable Logic Controller (PLC) resulting in a loss of the EPR. This loss of signal, concurrent with the MPR being out of position, resulted in the subsequent rise of both reactor pressure and APRM flux that caused the SCRAM.<br /><br /> ENS 50916 was submitted on March 22, 2015 as required by 10 CFR 50.72 (b)(2)(iv)(B). This issue is reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).
219 | 2192015002 | 2015-05-07 | QR5 | Turbine Trip | [45 empty] | Oyster Creek | B | GE | PO | 100 | On May 7, 2015 at 1727 hours, a Main Turbine Trip and subsequent Reactor Scram occurred from a trip of the Main Transformer Differential Lockout Relay, 86T. The Main Transformer Differential Lockout Relay, 86T is a protection function provided by Digital Protection Relay System "B" (DPRS B). The 86T trip signal was sensed arnd cleared, without operator action, in 17 milliseconds (ms) or 1 cycle prior to the 230KV output breakers opening. The results of extensive troubleshooting ruled out an actual fault in the Main Transformers or lso-phase Bus, and determined that the Main Transformer Differential Relay actuation was a spurious trip, and not due to an actual degraded equipment condition. <br /><br /> ENS 51055 was submitted on May 7, 2015 as required by 10 CFR 50.72 (b)(2)(iv)(B). This issue is reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B).
219 | 2192016003 | 2016-04-30 | QR6 | Manual Reactor Trip | [45 empty] | Oyster Creek | B | GE | SU | 1 | On April 30, 2016, at 1804 hours, during the plant startup following the 1M38 maintenance outage, a reactor SCRAM was manually inserted by the Control Room Operators during post maintenance testing following work on the 'D' Reactor Recirculation Pump (RRP) mechanical seal. The SCRAM was initiated since leakage was discovered by a rising trend in drywell unidentified leakage during plant startup. The seal had been replaced during the maintenance outage. The SCRAM was selected as the preferred method of shutting down the reactor due to low decay heat conditions following the outage. <br /><br /> ENS 51895 was submitted on April 30, 2016, as required by 10 CFR 50.72 (b)(2)(iv)(B). This issue is reportable under 10 CFR 50.73(a)(2)(iv)(A), for any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B).
219 | 2192017001 | 2016-11-20 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Oyster Creek | B | GE | PO | 92 | On 11/20/2016 at approximately 0342 EST, an automatic reactor SCRAM occurred at 92% power due to Average Power Range Monitor (APRM) high flux. Oscillations of the turbine control valves and bypass valves were experienced during planned testing of the Turbine Master Trip Solenoid Valve at 95% power. Power was reduced from 95% to 92% by the Main Control Room Operators in an effort to stop the observed oscillations. The control valves did not respond properly during the power reduction, leading to an unexpected rise in reactor pressure and the subsequent scram on high flux. <br /><br /> There were no safety consequences impacting the plant or public safety as a result of this event. All control rods fully inserted and the plant response was as expected. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to an actuation of the Reactor Protection System (RPS).
219 | 2192017002 | 2017-07-03 | QL7 | Degraded condenser vacuum | [45 empty] | Oyster Creek | B | GE | PO | 100 | On July 3, 2017, at approximately 10:15 AM following a grid disturbance, a manual scram was inserted due to degrading main condenser vacuum because of an improper configuration of the Augmented Off-gas (AOG) System. <br /><br /> The loss of main condenser vacuum resulted when Operations personnel failed to execute procedural requirement to align the AOG system into a shutdown lineup. The loss of vacuum was caused by degraded Steam Jet Air Ejectors (SJAE) performance due to a blocked discharge path. <br /><br /> The AOG system tripped 11 hours earlier following a grid disturbance. During the trip, operations personnel failed to re-align the AOG treatment system to a shutdown lineup resulting in the AOG Flame Arrestor siphoning into the inlet piping which filled the lower section of the off-gas hold up line with water.
220 | 2201987014 | 1987-10-16 | QR4 | Core Power Excursion (RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Nine Mile Pt. 1 | B | GE | PO | 89 | During normal operation on October 16, 1987, a malfunction of the turbine control system caused steam pressure oscillations, resulting in a reactor scram from a power excursion to the Average Power Range Monitor high neutron flux scram setpoint. The High Pressure Coolant Injection mode of feedwater initiated due to the momentary low reactor water level, which was the result of the reactor scram. The turbine control system malfunction also caused reactor pressure to decrease such that closure of the Main Steam Isolation Valves occurred as a protective action. The turbine control system failure has been attributed to a stuck servo-valve in the Electrical Pressure Regulator hydraulic actuator. An immediate corrective action included replacement of the servo-valve. Increased preventive maintenance of the Electrical Pressure Regulator will also be scheduled. Alternative designs will be evaluated. <br /><br /> A violation of Technical Specifications resulted due to personnel error regarding the tardiness of the 10 CFR 50.72 four hour notification for the Main Steam Isolation Valve closure. Additional training regarding the reportability of occurrences will be developed.
220 | 2201987024 | 1987-12-07 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 95 | On December 6, 1987, at approximately 2100 hours, Operations personnel at Nine Mile Point Unit 1 (NMP1) observed that the reactor feedwater flow control system began to develop an instability. Attempts were made to dampen the resulting reactor water level oscillations by taking local manual control of a feedwater flow control valve. However, these attempts were unsuccessful and the reactor scrammed at 0054 hours on December 7, when the water level fell to the low level scram setpoint. The High Pressure Coolant Injection mode of feedwater also initiated and reactor water level was subsequently restored to normal level. <br /><br />The probable root cause of this event was debris in the instrument air control line to the feedwater flow control valves #13 North and South and #11 valve positioners. A secondary cause of this event was the fact that the feedwater master controller was out of adjustment. This prevented the flow control valves from responding properly to signals from the feedwater control system. <br /><br /> Corrective actions consisted of issuing station Work Requests to repair the feedwater control malfunction, recalibrating the feedwater master controller and initiating a Modification Request to install inline filters on the instrument air supply to the Feedwater Flow Control Valves.
220 | 2201987028 | 1987-12-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 98 | At 18:13:56 on December 19, 1987, Nine Mile Point Unit 1 (NMP1) was manually scrammed due to excessive vibration observed in the high pressure feedwater piping. The root cause of this event was determined to be fatigue fracture of the stem/valve plug assembly of Flow Control Valve 13A due to flow-induced vibration. The valve failure caused pressure surges which resulted in vibration of the feedwater piping and damage to adjacent pipe supports. The pressure-retaining boundary of the feedwater system was not damaged by this transient. A detailed visual inspection of the feedwater system piping and supports was conducted. Non-destructive examination of selected pipe welds in the feedwater system which were subjected to the highest stresses during the transient was performed with no discrepancies noted. The stem/valve plug assembly has been replaced with a new design which should provide greater reliability. <br /><br />This supplement is being submitted to describe the final determination of the root cause, the results of the inspections and analyses completed, and the corrective action taken. An additional supplement is not expected to be submitted.
220 | 2201990017 | 1990-08-06 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Nine Mile Pt. 1 | B | GE | PO | 19 | On August 6, 1990, with the reactor mode switch in the RUN position, reactor power at 19 percent, Nine Mile Point Unit 1 (NMP1) experienced turbine bearing vibration problems when starting up the turbine-generator. The turbine was manually tripped, condenser vacuum was broken, and a manual reactor scram was inserted. Consequently, a High Pressure Coolant Injection (mode of feedwater control) signal was received due to low reactor water level (53 inches) and a Main steam Isolation Valve isolation occurred on decreasing condenser vacuum (7 inches mercury Hg). <br /><br /> The immediate cause of this event was the failure of turbine bearing #5 due to a blank found installed in the bearing oil supply line. An incident investigation determined that the cause of the event was inadequate review of a policy change and personnel error. <br /><br /> Immediate corrective actions included repair of the bearing, inspection of the other bearing oil supply lines, inspection/cleanup of the turbine lube oil tank and screens, and revising the procedure/process that controls the blank installation. Additionally, a review of the NMPC turbine maintenance log was performed to identify any other potential weaknesses.
220 | 2201990020 | 1990-08-19 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Nine Mile Pt. 1 | B | GE | PO | 21 | On August 19, 1990, with the reactor mode switch in the run position, reactor power at approximately 21.5 percent, Nine Mile Point Unit 1 (NMP1) experienced turbine vibration problems when conducting Power Ascension Procedure N1-PAT-12-1, "Main Turbine-Generator Rotor System Torsional Screening Test". The turbine was manually tripped, subsequently a manual reactor scram was inserted prior to breaking vacuum to preclude an automatic reactor scram on low condenser vacuum. Consequently, a High Pressure Coolant Injection (HPCI) (mode of Feedwater control) signal was received due to low reactor water level (53 inches) and a main steam isolation valve isolation occurred on decreasing condenser vacuum (7 inches mercury Hg). <br /><br /> A root cause investigation determined that the most likely cause of the Low Pressure (L.P.) turbine rotor vibration was that a slow acceleration rate through an L.P. turbine critical speed range led to the L.P. turbine rotor developing an interstage packing rub and bowed rotor.<br /><br /> Immediate corrective action was to terminate N1-PAT-12-1. Additionally, revision to the turbine torsional test is being pursued by Engineering and General Electric to address the technical problems encountered during the initial run.
220 | 2201990026 | 1990-11-17 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Nine Mile Pt. 1 | B | GE | PO | 96 | On November 17, 1990, at 2109 with reactor power at 96 percent, Nine Mile Point Unit 1 (NMP1) experienced a full reactor scram, High Pressure Coolant Injection (HPCI) mode of feedwater initiation and Electromatic Relief Valve (ERV) initiation due to Main Steam Isolation Valve (MSIV) isolation. The MSIV isolation occurred as a result of an incorrect fuse being removed during a surveillance test of a Main Steam Line Radiation monitor. The plant was safely shutdown and no adverse safety consequences resulted. <br /><br /> The primary cause of this event was determined to be personnel error, specifically poor work practices.<br /><br /> Immediate corrective actions included placing the plant in a safe shutdown condition and resetting the reactor scram. Subsequent corrective actions included counseling and discipline of operations personnel involved in the test performance.
220 | 2201990019 | 1990-12-29 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 10 | On December 29, 1990, at 1719 hours, Nine Mile Point Unit 1 (NMP1) experienced a full reactor scram when a trip signal was received on Reactor Protection System (RPS) channel 11 due to a spike on Intermediate Range Monitor (IRM) 12. <br /><br /> At the time of the event the mode switch was in the "startup" position, reactor power was at approximately 10 percent and a RPS trip had been inserted on channel 12 due to the failure of a Main Steam Isolation Valve (MSIV) to meet its surveillance test requirements. <br /><br /> When the scram occurred the unit was conducting a forced shutdown due to the MSIV failure and increased drywell leakage. <br /><br /> The cause of the event was a spike on IRM 12 (RPS channel 11) coincident with a half-trip inserted on RPS channel 12 due to the MSIV failure. <br /><br /> The corrective action for the IRM spike is the continuation of the neutron monitoring troubleshooting and upgrade efforts.
220 | 2201991002 | 1991-02-12 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 78 | POWER LEVEL - 078%. ON FEBRUARY 12, 1991, AT 0942 HOURS, WITH THE REACTOR MODE SWITCH IN THE 'RUN' POSITION, REACTOR POWER AT ABOUT 78%, NINE MILE POINT UNIT 1 (NMP1) EXPERIENCED A FULL REACTOR SCRAM ON HIGH NEUTRON FLUX. THE TURBINE CONTROL SYSTEM HAD BEEN EXPERIENCING SMALL CONTROL VALVE POSITION OSCILLATIONS (<4%) DUE TO SUSPECTED PRESSURE REGULATOR PROBLEMS. AT 0942 HOURS THE TURBINE CONTROL VALVES CLOSED FROM APPROX. 83% OPEN TO 54% OPEN. THIS CAUSED THE REACTOR PRESSURE TO INCREASE FROM 1005 PSIG TO 1043 PSIG CAUSING NEUTRON FLUX TO INCREASE TO ABOUT 100%, WHICH WAS ABOVE THE AVERAGE POWER RANGE MONITOR (APRM) FLOW BIASED SCRAM SETPOINT OF ABOUT 100%. HIGH PRESSURE COOLANT INJECTION (HPCI) WAS INITIATED. THE EMERGENCY VENTILATION SYSTEM WAS INITIATED. THE CAUSE OF THE CONTROL VALVE PARTIAL CLOSURE PROBLEM WAS DUE TO THE PRIMARY VALVE LIMIT STOP LINKAGE BUSHING STICKING. THE STICKING LINKAGE CAUSED A MISOPERATION OF THE CONTROL VALVES. THE IMMEDIATE CORRECTIVE ACTION WAS TO RESPOND TO THE SCRAM AND TO PERFORM A NORMAL COOLDOWN OF THE REACTOR. THE CAUSE OF THE CONTROL VALVE OSCILLATIONS WAS INVESTIGATED.
220 | 2201991008 | 1991-07-18 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | SU | 3 | On July 18, 1991, at 0840 hours, Nine mile Point Unit 1 (NMP1) experienced an unplanned reactor scram on Intermediate Range Monitoring System (IRM) HI HI while in the process of a controlled plant shutdown. At the time of the event, the mode switch was in STARTUP with reactor coolant pressure and temperature at approximately 893 pounds per square inch gauge (psig) and 529 degrees Fahrenheit (degrees F), respectively. The reactor was operating at approximately 3% of rated thermal power. <br /><br /> The reactor scram occurred while attempting to terminate an unanticipated reactor pressure decrease. Possible causes are: neutron flux spike due to pressure perturbations resulting from isolating an auxiliary steam load, or spurious spiking of the IRM neutron monitors due to induced noise. <br /><br /> Corrective actions have been taken to address the equipment deficiencies that contributed to the reactor pressure decrease and to improve the Operations response in such situations (generation of a Lessons Learned Transmittal and revision of operating procedures for isolating steam loads at low power).
220 | 2201991012 | 1991-09-26 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 97 | On September 26, 1991, at 1728 hours, Nine Mile Point Unit 1 experienced Engineered Safety Feature (ESF) and Reactor Protective System (RPS) actuations. Specifically, a full reactor scram and a High Pressure Coolant Injection (HPCI) automatic initiation caused by a Main Generator trip. At the time of the event, the reactor mode switch was in the "RUN" position and reactor power was at approximately 97 percent power. <br /><br /> The cause of the Main Generator trip was the failure of one of three Unit Overall Differential Trip Relay Current Transformers installed on phase two neutral side of the Main Generator. A root cause investigation of the failed Current Transformer determined the failure was caused by moderately high localized temperature over a significant period of time. <br /><br /> The immediate corrective action was to respond to the scram and ensure safe shutdown conditions. Other completed corrective actions include evaluation of all Current Transformers associated with the Main Generator Protective Relaying Circuitry and replacement of the failed transformer and the other two Current Transformers mounted on phase two neutral. Periodic thermographic surveillance of Current Transformers will be implemented to preclude Main Generator trips caused by a failed Current Transformer.
220 | 2201991014 | 1991-12-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 97 | On December 4, 1991, at 0842 hours, with the mode switch in "RUN" and reactor power level at approximately 96.5% of rated, the Nine Mile Point Unit 1 (NMP1) Reactor experienced a reactor scram. The reactor scram was the result of a level transient that lowered reactor water level below the scram setpoint of greater than or equal to 53 inches. <br /><br /> The root causes were manufacturing defects and design inadequacies. The immediate cause of the event was equipment failure. A solder connection failed on the total steam flow meter in the Feedwater Level Control circuitry, causing an imbalance in the signals to the 3 element controller, which closed 13a and 13b Feedwater Flow Control Valves in response.<br /><br /> Initial corrective actions were to respond to the reactor scram and increase reactor water level to its normal range. The cause of the level transient was investigated, and the failed total steam flow meter was identified and replaced. The remaining meters in the Feedwater Control System were evaluated and those without electrical shunts were replaced. An evaluation will be performed of meters in other control circuits to prevent similar events.
220 | 2201992004 | 1992-02-16 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 94 | On February 16, 1992, at 0059 hours, with the reactor mode switch in the "RUN" position and reactor power at approximately 94 percent, Nine Mile Point Unit 1 (NMP1) experienced Reactor Protective System (RPS) actuations. Specifically, a full reactor scram caused by a turbine stop valve closure signal to RPS channels 11 and 12, and an automatic initiation of High Pressure Coolant Injection (HPCI) caused by a turbine trip. <br /><br /> The root cause was determined to be equipment failure. Specifically, a sticking pivot point and a worn pin to lever connection on the Turbine Stop Valve failed to adequately perform their intended functions. <br /><br /> Corrective actions include cooling down the reactor in accordance with plant procedures, and corrective maintenance on the turbine stop valve hydraulic control mechanisms.<br /><br /> This event is bounded by the discussion in the Final Safety Analysis Report (FSAR), Section XV. There were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event.
220 | 2201992008 | 1992-04-18 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 98 | On April 18, 1992 at approximately 1039 hours, with the mode switch in the "RUN" position and reactor power at approximately 98 percent, Nine Mile Point Unit 1 (NMP1) experienced a Reactor Protection System (RPS) actuation. Specifically, a full reactor scram caused by neutron flux exceeding the flow-biased Average Power Range Monitor (APRM) scram setpoint. Additionally, the High Pressure Coolant injection (HPCI) System initiated on low reactor water level, as expected. <br /><br /> The root cause of this event is failure of the MPR servo motor position indicator providing erroneous position indication of the MPR percent servo stroke. <br /><br /> Corrective actions were to stabilize and cool down the reactor in accordance with plant procedures; and to troubleshoot the MPR and correct the deficiency with the MPR's servo motor position indicator.
220 | 2201992003 | 1992-05-01 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 97 | On May 1, 1992 at 1434 hours, with the mode switch in the "RUN" position and reactor power at approximately 97 percent, Nine Mile Point Unit 1 (NMP1) experienced a Reactor Protection System (RPS) actuation. Specifically, a full reactor scram caused by neutron flux exceeding the flow-biased Average Power Range Monitor (APRM) scram setpoint. Additionally, the High Pressure Coolant injection (HPCI) System initiated on low reactor water level, as expected. <br /><br /> The cause of the high neutron flux scram was a small, but rapid, pressure increase. The most likely causes of the pressure increase are loose, oxidized and intermittent electrical connections at one of the Electronic Pressure Regulator's (EPR) four Linear Variable Differential Transformers (LVDTs) and electrical noise between adjacent field wiring. <br /><br /> Corrective actions were to stabilize and cool down the reactor in accordance with plant procedures, and to correct the EPR deficiencies identified during troubleshooting.
220 | 2201992009 | 1992-08-07 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 76 | On August 7, 1992 at 0413 hours with the mode switch in the 'RUN' position and reactor power at approximately 76 percent, Nine Mile Point Unit 1 (NMP1) experienced a Reactor Protection System (RPS) actuation. Specifically, this was a full reactor scram caused by a spurious spike on a Local Power Range Monitor (LPRM), while a half scram was manually inserted on the opposite RPS channel for testing. The spurious LPRM spike caused Average Power Range Monitor (APRM) 16 to reach its upscale scram setpoint. Following the scram, High Pressure Coolant Injection (HPCI) initiated on low reactor water level, as expected.<br /><br /> The cause of the LPRM spike is a failure of either the LPRM detector or the associated cable connector. A single LPRM upscale spike may cause the APRM to trip upscale when the APRM is near its scram setpoint. <br /><br /> Corrective actions were to stabilize and cooldown the reactor in accordance with plant procedures and to bypass the defective LPRM from the APRM averaging circuit as allowed by plant Technical Specifications.
220 | 2201993002 | 1993-01-26 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On January 26, 1993 at 0936 hours, Nine Mile Point Unit 1 (NMP1) received an automatic reactor scram initiation signal. Specifically, while performing a monthly calibration test on Average Power Range Monitor (APRM) Flow Converters, a high neutron flux trip signal was inadvertently initiated on Reactor Protection System (RPS) Channel 12 while a manual halfscram signal was inserted on RPS Channel 11. At the time of the event, the plant was operating at 100 percent rated thermal power with reactor pressure at 1030 pounds per square inch gauge (psig) and reactor temperature at 531 degrees Fahrenheit. <br /><br /> The root cause for this event has been determined to be personnel error by failure to follow a procedure.<br /><br /> Immediate operator actions included commencing scram recovery activities and initiating a controlled plant cooldown. Additional corrective actions included: 1) improving management expectations during pre-job briefing activities; 2) revising supervisory roles during surveillance testing and; 3) issuing a Lessons Learned Transmittal.
220 | 2201993006 | 1993-04-13 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | SU | 1 | On April 13, 1993, at 1810 hours, Nine Mile Point Unit 1 (NMP1) received an automatic reactor scram initiation signal resulting in a full scram. While performing N1-IPM-092-231, 'IRM Monitor Gain Adjustment to Reactor Power,' a spurious Intermediate Range Monitor (IRM) high-high neutron flux trip was received when 17 IRM was taken out of bypass. At the time of the event, the plant was being started up with the mode switch in the 'STARTUP' position and the reactor at the point of adding heat, reactor pressure was atmospheric and reactor temperature was 140 degrees Fahrenheit. <br /><br /> The root cause of this event was determined to be electrical noise generated by energizing/de-energizing the IRM bypass relays. <br /><br /> Immediate operator actions included commencing scram recovery activities. <br /><br /> Additional corrective actions included determining the cause for the IRM spike and installing a noise suppression circuit to correct the cause.
220 | 2201994002 | 1994-04-05 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On April 5, 1994 at 0451 hours, Nine Mile Point Unit 1 (NMP1) received an automatic scram initiation signal resulting in a full reactor scram. While preparing for maintenance on the #9 345KV line disconnect switch, breaker R925 was opened, at which time the #8 line breaker R915 tripped unexpectedly. This resulted in a main generator trip and full reactor scram. At the time of the event, the plant was operating at 100 percent of rated thermal power.<br /><br /> The apparent root cause of this event was an electrical short in the polarizing circuit within the distance directional relay 21B-1. <br /><br /> Immediate operator actions included commencing scram recovery activities and initiating a controlled plant cooldown. Additional corrective actions include: 1) replacing the faulty relay; 2) verifying the correct operation of a similar relay; and 3) training operators to identify the precursor to this event.
220 | 2201994004 | 1994-04-11 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | SU | 1 | On April 11, 1994, at 1920 hours, Nine Mile Point Unit 1 (NMP1) received an automatic reactor scram initiation signal resulting in a full scram. While performing a reactor startup, a spurious Intermediate Range Monitor (IRM) 'high-high' neutron flux trip occurred. At the time of the event, the plant was being started up with the mode switch in the 'STARTUP' position; a reactor heat up was in progress, and reactor pressure was 810 pounds per square inch gauge (psig). <br /><br /> The apparent cause of this event was determined to be IRM spiking caused by electrical noise generated from actuation of relays external to the neutron monitoring system.<br /><br /> Immediate operator actions included commencing scram recovery activities. Additional corrective actions included determining the cause for the IRM spiking and installing noise suppression circuits to correct the probable causes.
220 | 2201994005 | 1994-07-11 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 85 | On July 11, 1994 at 0001 hours, with the reactor mode switch in the 'RUN' position and reactor power at approximately 85 percent, Nine Mile Point Unit 1 (NMP1) experienced a Reactor Protection System (RPS) actuation. Specifically, a full reactor scram was caused by neutron flux exceeding the flow-biased Average Power Range Monitor (APRM) scram setpoint. Additionally, the turbine tripped and the High Pressure Coolant Injection (HPCI) System initiated on the turbine trip, as expected. <br /><br /> The immediate cause of this event was a malfunction in the Turbine Control System's Electrical Pressure Regulator (EPR). Extensive troubleshooting of the EPR failed to pinpoint the exact malfunction but has narrowed the cause of the malfunction to selected components within the EPR. A formal root cause analysis will be completed when failure analysis of these components is obtained from the EPR vendor. <br /><br /> The EPR's operational amplifier and steam line resonance compensator were replaced. Additional Data Acquisition & Analysis System (DAAS) points were added to the steam line resonance compensator for on-line monitoring. The mercoid switch for #12 Feedwater Pump suction pressure was replaced. An electrical connector for control rod position indication was repaired.
220 | 2201994007 | 1994-11-02 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 78 | On November 2, 1994 at 1004 hours, Nine Mile Point Unit 1 (NMP1) received a full automatic reactor scram initiation signal. Specifically, while performing a scheduled surveillance test on the Average Power Range Monitor (APRM) Flow Converters, a high neutron flux trip signal was inadvertently initiated on Reactor Protection System (RPS) Channel 12 while a manual one-half scram signal was inserted on RPS Channel 11. Additionally, High Pressure Coolant Injection (HPCI) initiated on low reactor water level. <br /><br /> The root cause of the event is failure of the Instrument and Control (I&C) technicians to use good work practices while implementing the self-checking and peer verification processes. A contributing factor was that the flow converter panel was not labeled with the RPS channel designation. Additionally, two weaknesses were identified. First, Control Room Operations oversight of this critical activity was inadequate because Management's expectations did not require the appropriate level of oversight. Second, the sequence of steps in the surveillance procedure for inserting one-half scrams was not adequate. <br /><br /> The technicians involved were counseled. I&C technicians were retrained in the self-checking and peer verification processes. The flow converter panels have been labeled with the RPS channel identification. Operations Management will develop new expectations for control room Operations personnel with respect to oversight of critical activities. Procedures have been revised regarding inserting one-half scrams during certain surveillances. A Rod Position Indication System probe buffer card has been replaced.
220 | 2201995002 | 1995-04-19 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On April 19, 1995 at 1035 hours, Nine Mile Point Unit 1 (NMP1) received an automatic scram initiation signal resulting in a full reactor scram. The immediate cause of the scram was a trip of the Main Generator Lockout Relay (86G2 Relay) which tripped the turbine and resulted in a reactor scram. The 86G2 relay trip was initiated by failure of an oil-filled capacitor in a generator protective relay. At the time of the event, the plant was operating at 100 percent of rated thermal power. No testing or plant evolutions were in progress that resulted in or contributed to the scram. <br /><br /> Immediate operator actions included commencing scram recovery activities and initiating a controlled plant cooldown. Corrective actions included replacing the faulty relay. In addition, the generator protective relay design is being evaluated to determine appropriate measures to increase reliability.
220 | 2201996004 | 1996-05-20 | QP5 | Excessive Feedwater Flow | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On May 20, 1996 at 13:18 hours, with the mode switch in "RUN", and reactor thermal power at approximately 100%, Nine Mile Point Unit 1 (NMP1) experienced a turbine trip and full reactor scram. The event was initiated by #13 feedwater flow control valve oscillations, which caused high reactor water level, which tripped the turbine and resulted in a reactor scram. <br /><br /> The cause of the event was a degraded actuator for the #13 feedwater flow control valve (FCV). Upon disassembly of the actuator, worn o-rings and bushings as well as a misaligned stem and bushing were found. <br /><br /> Two contributing factors have been identified. The first is that the design of the current configuration of the pneumatic controls leaves little margin for degradation of the actuator and causes the valve to operate at a high frequency cycle. This cycling may cause increased wear on the actuator bushings and rubber goods which could lead to volume booster needle valve clogging and cause instability in the control system. <br /><br /> The second is the misalignment of the actuator stem. This misalignment caused binding which could also have caused erratic operation. The probable cause of the misalignment was incorrect factory assembly of the actuator, resulting in a misalignment of the internal bushings. <br /><br /> The immediate corrective actions included commencing scram recovery activities and initiating a controlled plant cooldown. Other corrective actions included: replacing the valve positioner volume boosters and rebuilding the actuator. In addition, the control system design is being evaluated to determine appropriate measures to increase reliability.
220 | 2201996011 | 1996-11-05 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On November 5, 1996, at 2253 hours, Nine Mile Point Unit 1 (NMP1) received an automatic scram initiation signal resulting in a full reactor scram. The immediate cause of the scram was a trip of the main Generator Lockout Relay (86G1 Relay) which tripped the turbine and resulted in a reactor scram. At the time of the event, the plant was operating at 100 percent of rated thermal power. No testing or plant evolutions were in progress that resulted in or contributed to the scram. Subsequent to the scram, feedwater flow control valve #12 indicated closed but leaked excessively, causing water intrusion into the main steam lines and emergency condenser lines. The cause of the Generator Lockout Relay (86G1 Relay) activation is a failed flexible link in the generator exciter. The link severed and contacted ground initiating a ground fault. A failure analysis will be performed on the failed component.<br /><br /> The immediate corrective actions were to perform scram recovery actions, place the plant in a stable condition, and determine the cause of the scram. Subsequently, an evaluation was performed of the impact of water in the main steam lines, the failed flexible link was replaced, the feedwater flow control valve 12 was rebuilt and tested to ensure minimal leakage, and an evaluation of the emergency condenser piping movement was performed.
220 | 2201999004 | 1999-07-23 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On July 23, 1999, at 1558 hours, during post maintenance testing of the turbine mechanical pressure regulator controls, the Nine Mile Point Unit I reactor automatically scrammed from full power from a high neutron flux signal on Channel 11 and Channel 12 of the reactor protection system. Following the reactor scram, operators moved the mode switch through the "Shutdown" position, to the "Refuel" position. The operators did not subsequently reposition the mode switch to "Shutdown" as required by Special Operating Procedure N1-SOP-1, "Reactor Scram." This was a nonconformance with Nine Mile Point Unit 1 Technical Specifications, which permitted the mode switch to be positioned in "Refuel" above 212 degrees F reactor coolant temperature only during reactor coolant system pressure testing, control rod scram timing, and for scram recovery. Niagara Mohawk Power Corporation determined that the cause of the reactor scram was internal blockage in the pressure suppressor valve in the mechanical pressure regulator feedback loop. The vendor had treated the valve with excessive corrosion inhibitor, and the excessive corrosion inhibitor blocked internal passages. The cause of the inappropriately positioned mode switch was ineffective change management, with contributing factor of inadequate corrective actions for a previously identified issue. Corrective actions for the reactor scram included placing the plant in a stable condition, cleaning the pressure suppressor valve, and providing guidance for valve disassembly and inspection. Corrective actions for the mispositioned mode switch included revising procedures, and conducting training.
220 | 2202000004 | 2000-10-02 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Nine Mile Pt. 1 | B | GE | SU | 1 | On October 2, 2000, during Nine Mile Point Unit 1 plant startup, at approximately 0555 hours, control room personnel identified that Electromatic Relief Valve (ERV) 111 had lifted. The plant startup was stopped and actions to close the ERV initiated. Efforts to close the ERV were unsuccessful and at 0625 hours the plan t was manually scrammed. During the event, a 10-inch, ERV discharge line vacuum breaker, CKV-66-26, failed open. The most probable cause of ERV 111 lifting was a bent pilot valve stem combined with partial disengagement of the disc and stem assembly. The cause of the vacuum breaker failure was design deficiency in that inadequate valve specifications were supplied by the Mark I Program vendor to the valve vendor. Corrective action for the ERV lifting included checking the straightness of the pilot valve stems in the six ERVs, modifying procedures to include straightness criteria for the pilot valve stems and prohibiting the cycling of pilot valves with the solenoid in a depressurized condition, and replacing the stems in the pilot valves for ERV 111 and ERV 112. Corrective action for the vacuum breaker failure included checking the internals of the 10-inch ER V discharge line vacuum breakers and modifying the valve hinge bumper weld in the 10-inch vacuum breakers. Additionally, a design change to correct the design deficiency will be installed by the completion of refueling outage 17.
220 | 2202001001 | 2001-08-22 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On August 22, 2001 at 0508 hours, Nine Mile Point Unit I experienced an unplanned scram due to a generator trip from approximately 100 percent power. The reactor was operating at steady state conditions prior to the scram. The Immediate cause for the generator trip was actuation of the Negative Phase Sequence Current Relay in response to a grid perturbation. All control rods fully inserted. In response to the generator trip, reactor pressure rose to 1115 pounds per square inch gage (psig). The increase in pressure resulted in all six Electromatic Relief Valves (ERVs) opening briefly, as designed. Approximately 37 seconds post scram the Main Steam Isolation Valves (MSIVs) automatically closed due to the mode switch being in RUN and reactor pressure at 850 psig, Approximately six minutes after closing, the MSIVs were re-opened. The cause of the generator trip was a grid perturbation coupled with a malfunction of the Negative Phase Sequence Current Relay. The relay malfunction was due to a design flaw. A contributing cause was failure to utilize previous external operating experience. The MSIV closure was caused by lack of specific direction regarding when the mode switch should be taken to SHUTDOWN post scram. Corrective actions included replacing the relay with one of a new design and briefing the operating crews of the management expectation that the first immediate action after a scram is to place the mode switch in SHUTDOWN. Preventive action will involve reviewing General Electric Operating Experience not previously evaluated.
220 | 2202003002 | 2003-08-14 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On August 14, 2003 at approximately 1611 hours, Nine Mile Point Unit 1 automatically scrammed from 100% rated thermal power when the turbine tripped on a load rejection. A large disturbance in the electric grid had caused the turbine to trip. Both emergency diesel generators (EDGS) automatically started and supplied the emergency buses. The electric grid disturbance ultimately led to the loss of the reactor recirculation pumps, condensate pumps, and circulating water pumps. Reactor pressure and water level were maintained using the electromatic relief valves (ERVs), emergency condensers, and the control rod drive injection system. At 1633 hours an Unusual Event (UE) was declared due to grid instability. After grid stability had been established the EDGs were secured. EDG 103 was secured at 2339 hours on August 14, 2003 and EDG 102 was secured at 0018 hours on August 15,2003. The UE was terminated at 0120 hours on August 15, 2003. The cause of the event was the severe disturbance on the northeast electric grid. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) because of the critical reactor scram, and because of the automatic start of the EDGs.
220 | 2202004001 | 2004-05-02 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Nine Mile Pt. 1 | B | GE | PO | 19 | On May 2, 2004, at approximately 0209 hours, while conducting post-maintenance testing following plant startup, Electromatic Relief Valve (ERV) 123 would not reclose following remote manual actuation. Efforts to close the ERV failed and at 0217 hours the plant was manually scrammed. High Pressure Coolant Injection initiated on low Reactor Water Level due to the level transient associated with the scram as expected. Reactor cooldown rate exceeded Technical Specification limits for the first hour following the scram. An engineering evaluation concluded that 10 CFR 50 Appendix G requirements were not violated and that structural integrity of the Reactor Pressure Vessel (RPV) was not compromised. The root cause for the ERV failure to close was "inadequate use of procedures." The failure resulted from improper assembly of the pilot valve following maintenance. An extra gasket erroneously installed in the pilot valve assembly allowed bypass leakage around the pilot valve causing the main valve to remain open after the pilot valve was closed. The excessive cooldown rate resulted from the stuck open ERV, which limited the ability to control the rate of RPV depressurization and cooldown. The ERV was disassembled and reassembled correctly. Subsequent testing demonstrated satisfactory valve performance.
220 | 2202004004 | 2004-08-30 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On August 30, 2004, at approximately 0825 hours, with the mode switch in "RUN" and reactor thermal power at approximately 100%, Nine Mile Point Unit 1 experienced feedwater flow oscillations. Efforts to manually stabilize feedwater flow were unsuccessful. At approximately 0833 hours, a manual scram was initiated to shutdown the plant. The feedwater flow oscillations were caused by degradation of the #13 feedwater flow control valve positioner due to a ruptured diaphragm in the output pilot valve. The root cause was determined to be the original design did not adequately establish a service life that took into account operating the positioner at the maximum recommended air supply pressure, thereby decreasing the service life below the established preventive maintenance frequency. The positioner, including the failed pneumatic module, for the #13 feedwater flow control valve was replaced. Subsequent testing demonstrated satisfactory flow control capabilities. To prevent recurrence, the positioner will be replaced every two years.
220 | 2202005001 | 2005-03-07 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On March 7, 2005, at approximately 0437 hours, with the mode switch in "RUN" and reactor thermal power at approximately 100%, Nine Mile Point Unit 1 experienced an automatic reactor scram initiated by a turbine trip caused by a failure in the circuitry of a Moisture Separator Tank level switch. A spurious actuation of the Moisture Separator Tank level switch was caused by a short circuit between two terminal points caused by water intrusion into the associated junction box. Based on inspections performed, the most probable source of the water inside the junction box was condensation of steam from a packing leak in an instrument root valve in the near vicinity. Corrosion products accumulated at adjacent terminal points due to previous water intrusions which created moisture conditions over an extended period of time leading to a short circuit. To prevent recurrence, the terminal points were cleaned and all top and side external penetrations of the junction box were sealed. A design change to the trip logic of the Moisture Separator Tank level switches to prevent a trip on a single level switch contact failure was installed and tested in refuel outage 18. Inspections and repairs were performed in refuel outage 18 on a defined population of junction boxes with similar environmental conditions.
220 | 2202005003 | 2005-08-18 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On August 18, 2005, at approximately 0950 hours, with Nine Mile Point Unit 1 operating at approximately. 100 percent power, an automatic reactor scram was experienced. The scram occurred when Power Board 11 (PB-11) was de-energized due to inadvertent protective over-current relay actuations. The resulting loss of power to the Channel 11 side of the Reactor Trip Bus (RTB), concurrent with planned in-progress surveillance testing that introduced a half-scram signal an the opposite (Channel 12) side of the RTB, caused a full automatic reactor scram signal to be generated. PB-11 was de-energized due to inadvertent protective over-current relay actuations caused by mechanical jarring of the relays mounted on the cubicle door. This occurred when a 4.16 kV circuit breaker was being rolled into position within its PB-11 cubicle. The underlying cause of the event is failure to adequately identify, assess, and mitigate potential risks of conducting work. The potential plant impacts that could be caused by inadvertent actuation or damage to surrounding equipment due to planned work were not identified or effectively managed. Corrective actions have been developed such that, when completed, the work control process will yield consistent and effective risk assessments of work activities that will prevent the same type of inadvertent relay actuation and other similar events (i.e., events caused by failure to identify and effectively manage potential risks associated with surrounding equipment).
220 | 2202008002 | 2008-10-23 | QR6 | Manual Reactor Trip | [10 empty] | X | [30 empty] | X |  |  |  | Nine Mile Pt. 1 | B | GE | PO | 100 | On October 23, 2008, at 2126 hours, with Nine Mile Point Unit 1 (NMP1) operating at 100% steady state reactor power, operators initiated a manual scram when it was determined that the reactor pressure regulator was not functioning properly. The loss of reactor pressure control was due to an unresponsive Electrical Pressure Regulator (EPR) that prevented transfer of control to the backup Mechanical Pressure Regulator (MPR). During the shutdown, operators entered an Emergency Operating Procedure due to low reactor water level and took appropriate corrective actions. The High Pressure Coolant Injection (HPCI) system initiated as designed to restore reactor water level to normal. After the turbine trip, all Turbine Bypass Valves failed open due to EPR binding that prevented the bypass valves from closing. The Main Steam Isolation Valves (MSIVs) were manually shut to control reactor pressure and limit reactor cooldown rate. The MSIVs were reopened subsequent to regaining pressure control on the MPR. The cause of the EPR malfunction has been determined to be debris plugging of the internal filter of the EPR servo-valve. The most likely cause of the debris in the servo-valve was due to inadequate design of the EPR filters located immediately upstream of the servo-valve. On October 26, 2008, after replacement of the EPR servo-valve and the filters, the unit was restarted and on October 27, 2008, at 0131 hours, the unit was synchronized to the grid.
220 | 2202009003 | 2009-10-05 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | At 1158 on October 5, 2009, Nine Mile Point Unit One (NMP 1) was manually scrammed from approximately 100 percent rated power due to loss of control of the shaft-driven feedwater pump flow control valve (FCV), which resulted in an increasing feedwater flow rate and rising reactor pressure vessel (RPV) water level. Following the manual scram, the High Pressure Coolant Injection (HPCI) system automatically initiated on low RPV water level as designed. At 1159, RPV water level was restored above the HPCI low level actuation setpoint and the HPCI system initiation signal was reset. The root cause of the event was a programming error in the vendor-supplied firmware logic that prevented the proper operation of the transfer function of the FCV positioner when the operating positioner became mechanically bound. Instead, the FCV continued to open and raise reactor water level despite operator attempts to manually control the FCV. Immediate actions taken to prevent recurrence were to enable the FCV controller software setting for indication of a positioner spool piece binding and to increase the Position Excess alarm sensitivity. This will provide the operators with an early indication of feedwater FCV positioner degradation. The operations procedures were also improved to give direction to the operators on how to swap positioners if certain positioner alarms come in. The firmware for the FCV controller will be upgraded to ensure that conditions that indicate potential degradation in the performance of the positioner will result in a transfer to the redundant positioner.
220 | 2202010001 | 2010-11-10 | QL5 | Partial Closure of MSIVs | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | At 1056 on November 10, 2010, Nine Mile Point Unit 1 scrammed from full power operation due to closure of outboard Main Steam Isolation Valves (MSIVs) 01-03 and 01-04. Valves 01-03 and 01-04 closed following receipt of an invalid low-low reactor water level signal. The scram was the result of a combination of two latent preexisting plant conditions and performance of a quarterly instrument channel surveillance test. The first preexisting condition was misaligned connector pins on Grayboot splice connectors for outboard MSIV Channel 11 solenoid operated valves. The cause of the misalignment was determined to be insufficient rigor in the behaviors and knowledge (training) used in identifying appropriate post maintenance testing (PMT) requirements. The second preexisting condition was a misaligned contact spring in isolation logic Channel 12 relay 12K74 (General Electric (GE) Model CR305). The cause of this failure was excess material (plastic) left during fabrication of the relay's movable contact holder. Immediate actions were to repair the Channel 11 Grayboot splice connectors and replace Channel 12 relay 12K74. Training will be provided to planning personnel to ensure an adequate understanding of complex/redundant circuits for the proper determination of PMT requirements. Procedure/manuals governing Grayboot connector maintenance activities will be revised to include additional post assembly inspections and testing.
220 | 2202011001 | 2011-05-02 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 47 | At 2051 on May 2, 2011, Nine Mile Point Unit 1 (NMP1) experienced a turbine trip while operating at approximately 47 percent power (867 MWth). The main turbine master trip solenoid (MTS) actuated due to oil pressure fluctuations that allowed the pressure to drop below the MTS trip setpoint. These fluctuations were caused by leaking fittings on the MTS oil supply lines, binding of the secondary speed relay linkage, and main shaft oil pump discharge pressure fluctuations. The turbine trip initiated the high pressure coolant injection (HPCI) system as designed. The scram caused a drop in the reactor pressure vessel (RPV) water level that was mitigated by the HPCI injection. At 2052, RPV water level was restored above the HPCI low level actuation setpoint and the HPCI system initiation signal was reset. The root cause of the event was inadequate implementation of management job performance standards which resulted in the development and implementation of work performance documents which lacked sufficient detail associated with turbine maintenance activities. The immediate corrective action was to repair the turbine exciter/generator Falk coupling installation, replace the tubing and connections to the MTS supply lines, repair the secondary speed relay linkage, and repair the gears to the main shaft oil pump. Procedures will be developed to detail the disassembly, inspection, reassembly and testing of the NMP1 turbine, generator, exciter and control components. There have been no similar LERs at NMP1.
220 | 2202012001 | 2012-07-17 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On July 17, 2012, at 1118, Nine Mile Point Unit 1 (NMP1) experienced an automatic reactor scram on high neutron flux due to a failure of the Electronic Pressure Regulator (EPR). Following the reactor scram, the High Pressure Coolant Injection (I-IPCI) system automatically initiated on low Reactor Pressure Vessel (RPV) water level as designed. Failure of the Linear Variable Differential Transformer (LVDT) for servo position feedback (DT-1) to the EPR circuitry resulted in the EPR circuitry sending a close signal to the Turbine Control Valves (TCVs), resulting in a high neutron flux scram.<br /><br /> The root cause of this event is the Operational Decision Making Issues (ODMI) checklist and associated monitoring plan had unclear roles and responsibilities assigned which resulted in less than adequate communication, oversight of the plan's implementation, and assessment of the monitoring plan's data.<br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as a valid actuation of the reactor protection system and initiation of the high pressure coolant injection system.<br /><br /> Actions included removing the EPR from service, procedure revisions and training for ODMIs and abnormal condition monitoring and contingency planning. In addition, the EPR electronics and DT-1 were replaced in the 2013 NMP1 refueling outage. Previous LERs for similar EPR failures include 1987-014, 1992-003 and 1994-005.
220 | 2202012002 | 2012-09-20 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On September 20, 2012, at 0923, Nine Mile Point Unit 1 (NMP1) experienced an automatic reactor scram due to an automatic generator protective trip. The NMP1 main generator excitation controls failed to maintain reactive load below the trip setpoint when transferred from automatic regulation to manual regulation. Following the reactor scram, the High Pressure Coolant Injection system automatically initiated on low Reactor Pressure Vessel (RPV) water level as designed.<br /><br /> One root cause of this event is that in 2003, a failure to follow the existing administrative procedure guidance for procedure change evaluations resulted in an inadequate review of the procedure change and introduction of a latent error into the amplidyne operating procedure. Additionally, the single point vulnerability life cycle management (LCM) strategy for this system was not developed or implemented in a timely manner and did not address the increased risk from aging electronic/electrical components.<br /><br /> Corrective actions include replacing degraded electronic components of the automatic voltage regulator, revising LCM strategies and procedure revisions for amplidyne operation.<br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as a valid actuation of the reactor protection system and initiation of the high pressure coolant injection system.<br /><br /> There are no previous LERs for similar failures.
220 | 2202012004 | 2012-10-29 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On October 29, 2012 at 21:00:57 hours, Nine Mile Point Unit 1 (NMP1) experienced an unplanned, automatic, reactor scram due to a Turbine Trip from 100 percent power caused by activation of a generator lockout relay. The generator trip was an unexpected consequence and was initiated by a high fault current condition in the Scriba switchyard detected by both NMP1 instantaneous ground directional overcurrent relays. A polarity wiring error within the generator step up transformer neutral ground current transformers (CTs) caused the relay protection circuits to actuate on the fault in the Scriba switchyard. This was not expected because the relay protection circuits were designed to detect a fault condition between the main generator and the station output breakers. The error was caused by less than adequate oversight by CENG personnel of transformer XF-TB01 testing with respect to unclear specificity of requirements for vendor performed testing and inadequate methods of verification for ensuring vendor compliance with engineering specifications.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the reactor protection system and an actuation of the high pressure coolant injection system while the reactor was critical.<br /><br /> Corrective actions include correcting the wiring of the CT circuits, verifying all the requirements in the engineering specification have been met, revising the associated electrical drawings, and revising engineering procedures to require the listing of critical attributes for equipment/components and to define testing criteria/verification methods to be performed when factory acceptance testing or modification functional testing cannot be performed to verify the functionality of equipment/components.
220 | 2202012005 | 2012-11-03 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 24 | On November 3, 2012, at 0825, Nine Mile Point Unit 1 (NMP1) experienced an unexpected rise in reactor water level followed by a turbine trip and subsequent reactor scram on low Reactor Pressure Vessel (RPV) water level at 53 inches. During this sequence of events, multiple separate and valid initiation signals for High Pressure Coolant Injection (HPCI) occurred.<br /><br /> The initial rise in RPV water level was caused by a failure in the Feedwater System three element control of reactor water level resulting in a maximum demand open signal being sent to the 11 Feedwater flow control valve (11 FCV). Subsequent-level transients were due to the failure of the 11 FCV to operate properly to control water level. The root causes of this event were selection of an inappropriate Preventive Maintenance (PM) strategy and not changing the PM program to test electronic components for end-of-life failure mechanisms. Corrective actions to address the root cause include replacement of the failed electronic components, revision of the PM program for the feedwater FCVs and revision to the electronic module refurbishment program to check transistors.<br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as a valid actuation of the reactor protection system and initiation of the high pressure coolant injection system.<br /><br /> LERs for similar events are; 85-004, 86-024, 90-015, 96-004 and 04-004.
220 | 2202015004 | 2015-09-04 | QL5 | Partial Closure of MSIVs | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On Friday September 4th, 2015 at 09:16:04, Nine Mile Point Unit 1 automatically scrammed from approximately 100% rated power due to an inadvertent Main Steam Isolation Valve (MSIV) isolation. This event is reportable under 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). During quarterly surveillance testing, the MSIV failed to stop its close stroke and reopen automatically per design, due to a failed MSIV pilot test valve. The root cause of the event was an inadequate application of the designed pilot test valve for MSIV control, resulting in the pilot test valve internals binding during the surveillance test. The failed pilot valve spool and cage assembly were replaced. The corrective action to prevent recurrence is to replace the MSIV pilot valves with an industry proven design.<br /><br /> The event described in this LER is documented in the plant's corrective action program.
220 | 2202017001 | 2016-12-10 | QK4 | Steam or Feed Leakage | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 97 | On December 10, 2016 at 08:48, Nine Mile Point Unit 1 performed a manual scram of the reactor due to increased vibrations on the main turbine. Following the scram, the High Pressure Coolant Injection (HPCI) System automatically initiated. This event is reportable under 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.72(b)(3)(iv)(B). <br /><br /> During performance of a load drop to 95% power in support of Turbine Stop Valve Testing, main turbine bearing vibrations rose on several bearings. The Unit 1 Reactor was scrammed and the main turbine was secured when main bearing #1 reached procedural limits. The root cause of the event was a steam leak from a threaded pipe/cap connection that was not seal welded when originally supplied from the manufacturer. The connection has now been seal welded.<br /><br /> A combination of tight tolerance in conjunction with the location of the steam leak resulted in the vibrations when power level was changed. <br /><br /> The event described in this LER is documented in the plant's corrective action program.
220 | 2202017002 | 2017-03-20 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 4 | On March 20, 2017 at 02:27, Nine Mile Point Unit 1 performed a manual scram of the reactor due to pressure oscillations. This event is reportable under 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). <br /><br /> The Unit was offline and reactor shutdown was in-progress at the time of the scram. The cause of the scram was manual scram. The scram was required at approximately 4% reactor power when pressure oscillations occurred exceeding the procedurally required limit. The apparent cause of this event was Mechanical Pressure Regulator (MPR) oscillations caused by a combination of the fouling of the MPR's pressure sensing bellows line and a bypass relay linkage passing through a worn bushing which created a friction induced sticktion of the linkage. <br /><br /> The event described in this LER is documented in the plant's corrective action program.
220 | 2202017003 | 2017-09-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 100 | On September 6, 2017 at 1157, Nine Mile Point Unit 1 experienced an automatic reactor scram due to reactor vessel low water level. The automatic Reactor Protection System (RPS) actuation and reactor scram is reportable per 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). Following the automatic scram all plant systems responded per design including High Pressure Coolant Injection (HPCI) System automatic initiation. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. <br /><br /> The root cause of the scram was a failed power supply within the Proportional Amplifier, PAM-ID23E. This power supply failure resulted in the output from the module dropping out causing the #13 Feedwater Pump Flow Control Valve to close. The corrective action taken was the replacement of the failed Feedwater Level Control module, PAM-ID23E.
220 | 2202019001 | 2019-04-14 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 21 | On April 14, 2019 at 00:03, Nine Mile Point Unit 1 received an automatic scram of the reactor due to high reactor pressure. Due to the Turbine trip, the High Pressure Coolant Injection (HPCI) System automatically initiated, as designed. This event is reportable under 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.72(b)(3)(iv)(B). <br /><br /> The cause of the scram is that station personnel did not identify that the Restoring Arm Breakdown was incorrectly installed and therefore non-functional. This resulted in ineffective knowledge-based troubleshooting to correct a condition as opposed to corrections with controlled technical guidance and the right expertise. <br /><br /> The event described in this LER is documented in the plant's corrective action program.
220 | 2202019003 | 2019-04-29 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 1 | B | GE | PO | 82 | On April 29, 2019 at 16:33, Nine Mile Point Unit 1 inserted a manual reactor scram due to pressure and power oscillations. The High Pressure Coolant Injection (HPCI) System automatically initiated, on low reactor vessel water level, as designed. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).<br /><br /> The cause of the event is the organization did not effectively incorporate appropriate !earnings from previous NMP events and operating history that would have provided adequate flexibility in the operating strategy to mitigate the risks of increased oscillations. The scope of the corrective actions is to incorporate operational history and events into Special Operating Procedures (SOPs).<br /><br /> The event described in this LER is documented in the plant's corrective action program.
237 | 2371987016 | 1987-05-03 | QP5 | Excessive Feedwater Flow | [45 empty] | Dresden 2 | B | GE | PO | 31 | On May 3, 1987 at 0912 hours, the Dresden Unit 2 reactor scrammed from 31% rated thermal power on a low reactor water level scram signal. The root cause of the event was a poor connection between an instrument board and cabinet on a new Feedwater Level Control System which had been installed prior to the April 22, 1987 startup from a refueling outage. While inserting a calibration module into the cabinet during troubleshooting of steam flow inputs, the connection loosened and caused oscillations in the controlling signal to a feedwater regulating valve. The valve operator then locked up in the open position which caused the reactor water level to increase. The high reactor water level caused the turbine and feedwater pumps to automatically trip to prevent moisture carryover from the reactor into the turbine. The reactor automatically scrammed on a low water level signal before the feedwater pumps could be restarted. <br /><br />The safety significance of the event was minimal because the automatic low reactor water level scram occurred as designed, shutting down the reactor to ensure that sufficient reactor vessel inventory was maintained. The Reactor Operator responded to this event in accordance with approved procedures for transient level control and reactor scram. To prevent recurrence of this event, all connections between modules and the cabinet in the Feedwater Level Control System were verified secure and the manufacturer supplied a new firmware module to prevent signal oscillations. Three previous occurrences involving reactor scrams from a low water signal were reported by Licensee Event Reports #87-08 on Docket #050249, #84-10 on Docket #050249, and #84-09 on Docket #050237.
237 | 2371987023 | 1987-07-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Dresden 2 | B | GE | PO | 84 | On July 17, 1987 at 2328 hours with Unit 2 descending in power at a conservative average rate of 10 MWe/hour via recirculation flow, the reactor scrammed from 84% rated thermal power on a low reactor water level signal of plus eight inches water level. The root causes of the event were four Feedwater Regulating Valve (FWRV) component failures, and feedwater level control system difficulties. To determine the root cause of the system difficulties a task force was formed and a root cause analysis performed. Several major contributing factors were identified as being the cause of this and other similar previous events. Consequently, several modifications were initiated and will be completed during the upcoming 1988 Unit 2 refueling outage. In addition 24 operating procedures are being revised to include updated operating guidelines for feedwater and condensate system operation. <br /><br /> Corrective actions entailed maintenance repairs and replacements for the component failures, extensive feedwater level control testing, the implementation of numerous pre-startup directions and precautions, and additional Operator training. The safety significance was minimal since all emergency core cooling systems were available; however, no actuation was necessary, the feedwater level control system remained capable of manual control of reactor level at all times and the reactor scrammed at the specified conservative setpoint. Five previous occurrences were reported by Licensee Event. Reports #87-13 and #87-12 and #84-10 on Docket 050249 and #87-16 and #84-9 on Docket #050237.
237 | 2371987024 | 1987-08-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Dresden 2 | B | GE | PO | 93 | On August 21, 1987 at 1755 hours with Unit 2 at approximately 2350 MW thermal (93% power) the reactor scrammed on a low reactor water level signal of +8 inches. The root cause of the event was the failure of the 2A Feedwater Regulating Valve (FWRV). The stem and plug assembly of the 2A FWRV separated due to a fatigue crack. <br /><br />Corrective actions entailed replacement of the stem/plug assembly with a new welded stem/plug. Also to prevent recurrence a new trim package incorporating a lighter plug that is less susceptible to fatigue cracking will be considered as replacement parts in the future. This decision will be made following the testing being performed on Unit 3 as a result of the 8/7/87 Unit 3 scram due to feedwater system oscillating. <br /><br /> The safety significance was minimal since all emergency core cooling systems were available, however, no actuation was necessary, the feedwater level control system remained capable of manual control of reactor level at all times and the reactor scrammed at the specified conservative setpoint. Five (5) previous occurrences were reported by Licensee Event Reports #87-12 and #84-10 on Docket 050249 and #87-23, #87-16 and #84-9 on Docket 050237.
237 | 2371987032 | 1987-10-20 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 2 | B | GE | PO | 100 | On October 20, 1987, while Dresden Unit 2 was operating at 100% rated thermal power, Dresden Operating Surveillance (DOS) 1700-1, Main Steam Line (MSL) Radiation Monitor Scram and Isolation Functional Test, was being performed in accordance with Technical Specification Table 4.1.1 in order to verify proper operation of the MSL radiation monitor and isolation circuitry. At 0224 hours, while DOS 1700-1 was in progress, a primary containment Group I isolation and reactor scram occurred, due to a spurious half Group One isolation occurring coincident with the surveillance. Root cause was determined to be vibration of a MSL low pressure switch; the source of the vibration is believed to be the main turbine. In order to prevent recurrence, isolators were installed to make the MSL low pressure switches less susceptible to vibration-induced trips. Safety significance was minimal since the automatic isolation and scram logic functioned as designed. Although previous spurious low MSL pressure signals have been observed since the last refuel outage, these have not resulted in an automatic isolation or scram.
237 | 2371989012 | 1989-03-04 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Dresden 2 | B | GE | PO | 92 | On March 4, 1989 with Unit 2 in the Run mode at 92% rated core thermal power, the reactor scrammed on low reactor water level following the trip of both operating Reactor Feedwater Pumps (RFPs). At the time, Operations Department personnel were ground checking on the 125V DC battery system. The cause of the event as been determined to be personnel error. The High Voltage Operator (HVO) performing the ground check opened the wrong breaker which resulted in the trip of the RFPs. The ground detection procedure states that the breaker is only to be opened with permission of the Operating Engineer. The HVO did not have the procedure in hand at the time of the event. The labeling of the breaker also contributed to the event. The plant responded as designed during the event, therefore the event was deemed to be of minimal safety significance. A discussion was held with the HVO and all other shift personnel to emphasize attention to detail, communications and procedural adherence. The critical breakers have been relabelled so they will stand out from the remaining breakers. The ground detection procedures are being reviewed and will be revised as required to assure that critical breakers are clearly identified and the consequences of their operation understood. These procedures will be posted at the appropriate DC switchgear locations when the revisions are approved. The last reactor scram from power which was caused by personnel error occurred on November 10, 1986 as reported by LER 86-012/Docket 050249.
237 | 2371989019 | 1989-07-12 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 2 | B | GE | PO | 63 | On July 12, 1989 at 1049 hours with Unit 2 operating at 63% power while performing Dresden Technical Staff Surveillance (DTS) 500-2, Functional Testing of Reactor Protection System (RPS) Motor Generator (MG) Set and RPS Reserve Power Supply, Channel 'A' half primary containment Group I isolation and half scram signals could not be reset promptly due to difficulties encountered in resetting the 'A' main steam line (MSL) logrithmic radiation monitor (LRM). A spurious MSL tunnel area high temperature trip then occurred, resulting in a full primary containment Group I isolation and reactor scram. The cause of the MSL area high temperature trip was attributed to setpoint drift. The root cause of the MSL LRM reset difficulties (which occurred during transfer of power supplies in accordance with DTS 500-2) has been attributed to improper initialization of the LRM main computer and failure of the LRM power supply, as a result of high voltage transients on the 120 VAC supply line to the monitor. As corrective action, the 'A' MSL LRM was replaced, in addition to all of the Channel 'B' MSL tunnel area temperature switches. The safety significance of this event was minimal since the primary containment isolation and reactor scram functions occurred as designed. Operations Department personnel responded immediately by verifying that a valid Group I condition had not occurred and proceeded with a controlled scram recovery. A previous event involving a scram during the performance of DTS 500-2 was reported by LER 89-02/050249.
237 | 2371990001 | 1990-01-05 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 2 | B | GE | PO | 99 | At 2241 hours on January 5, 1990, with Unit 2 operating at 99.3% power, a Primary Containment Group I isolation and subsequent reactor scram occurred while an Instrument Mechanic (IM) was performing Dresden Instrument Surveillance (DIS) 250-1, Main Steam Line High Flow Isolation Switch Calibration. The root cause of the unplanned Group I isolation has been attributed to a procedural deficiency within DIS 250-1 such that inadequate controls were provided to prevent a potential pressure transient large enough to cause a trip on instruments in both trip channels, located on a common instrument sensing line header. Corrective action included a special test of the tripped high flow switch and isolation manifold, possible hardware changes to assist the IM in performing the surveillance, and a study to investigate feasibility of replacing the present switches with an analog trip. The safety significance of this event is minimal since the high flow switches responded as designed and tripped in response to pressure transient induced to the common header, thus initiating the automatic Group I isolation and reactor scram. A previous event was reported by LER 87-016/050249.
237 | 2371990002 | 1990-01-16 | H1 | Fire |  | X | [5 empty] | X | [7 empty] | X | [17 empty] | X | X | [10 empty] | Dresden 2 | B | GE | PO | 100 | At approximately 1724 hours on January 16, 1990, an automatic Unit 2 reactor scram on a low reactor water level (Technical Specification setpoint of eight inches above instrument zero) signal occurred. The 2D Condensate/Condensate Booster pump failed due to an internal motor fault approximately 13 seconds prior to the scram, precipitating automatic trip of the running reactor feed pumps on low suction pressure and thus resulting in reduction of reactor water level to the low level scram setpoint. Additionally, Reserve Auxiliary Transformer 22 tripped during automatic transfer of house loads, resulting in interruption of normal AC auxiliary power until the emergency Diesel Generators automatically loaded. Cold Shutdown conditions were achieved by 0210 hours on January 17, 1990. Comprehensive root cause investigations were immediately initiated for all component performance problems, and corrective actions implemented.
237 | 2371990006 | 1990-08-02 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Dresden 2 | B | GE | PO | 87 | On August 2, 1990, during normal power operation in the Run mode, the 2-203-3A Main Steam Target Rock Safety-Relief Valve (TRSRV) acoustic monitor alarmed, indicating that the valve had spuriously opened and was relieving reactor pressure to the suppression chamber. The reactor was subsequently manually scrammed from 87% power at 0116 hours. All Containment Cooling Service Water and Low Pressure Coolant Injection pumps were manually started for maximum suppression pool cooling. The maximum average cooldown rate when averaged over a one hour period reached 129.3 degrees F/hr, and maximum bulk suppression chamber water temperature was 122 degrees F. The opening of the TRSRV was apparently caused by steam cuts on the first stage pilot valve disc. Analyses were performed to verify that the cooldown rate and the bulk suppression chamber temperature attained during this event were within design limits. A satisfactorily leak tested, rebuilt TRSRV was installed. The Technical Staff will monitor the TRSRV tail pipe temperatures to verify proper pilot valve operation. The Station will routinely replace the entire TRSRV at each refuel outage. A previous TRSRV failure event was reported by LER 50-237/76-34.
237 | 2371991004 | 1991-02-13 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 2 | B | GE | PO | 63 | At 0232 hours on February 13, 1991 with Unit 2 at 63% power, a Primary Containment Group I Isolation and Reactor Scram occurred due to valid Main Steam Line High Radiation signals. Operations personnel were attempting to change resins from a Reactor Water Cleanup Demineralizer (2A) while a parallel demineralizer (2C) was in service and providing cleaning of the reactor coolant. Investigation revealed that two isolation valves, normally fully closed, were not closed despite remote handwheel indications to the contrary. Later, it was found that the remote operators were broken allowing remote indications to show the valve positions without actual manipulation of the valves. Corrective action included improved administrative controls restricting resin moves only upon system isolation and flushing of the system to the Main Condenser Hotwell prior to returning it to service, to prevent resins from entering the reactor. The safety significance was minimal since the main steam line radiation monitors properly initiated the isolation/scram logic, Operators promptly responded to the event, and the short duration coolant chemistry transient had minimal effects. A previous resin intrusion occurred on December 17, 1985 on Unit 2 from the condensate demineralizers but did not result in a reactor scram.
237 | 2371991011 | 1991-06-09 | QR5 | Turbine Trip | [45 empty] | Dresden 2 | B | GE | PO | 42 | At 0302 hours on June 9, 1991 with Unit 2 at 42% power, a reactor scram occurred due to a high reactor pressure signal. At the time, operations personnel were testing the turbine thrust bearing wear detector when a turbine trip occurred. All turbine bypass valves fully opened. However, reactor pressure began to increase due to loss of feedwater heating. The reactor operators attempted to control reactor pressure by inserting control rods in reverse sequence. One control rod had been inserted before reactor pressure reached 1048 psig and initiated a reactor scram. Investigation revealed that foreign material in the turbine bearing oil had fouled the thrust bearing wear detector causing it to drift close to the trip setpoint. During testing, the wear detector reached its setpoint before the turbine trip bypass interlocks had actuated. Review of thrust bearing plate temperatures revealed no abnormalities, indicating that an actual turbine thrust was not present. Corrective actions included a change to the thrust bearing wear detector testing procedure which lowers the acceptance criteria for movement of the detector, evaluation of an improved wear detector design, and simulator training. The safety significance was minimal, in that safety systems performed as required and post-scram recovery was normal. Operations personnel promptly responded to the scram in accordance with procedures and training.
237 | 2371991024 | 1991-08-26 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 2 | B | GE | PO | 28 | At 1113 hours on August 26, 1991, with Unit 2 at 28% power, a main turbine trip occurred, followed by an unplanned Primary Containment Group I Isolation caused by spurious Main Steam Line (MSL) low pressure signals. The reactor scrammed as a result of the Group I Isolation closure of the Main Steam Isolation Valves (MSIVs). Investigation revealed that the root cause of the turbine trip was inadequate clearances within the thrust bearing assembly, which required disassembly and installation of proper shim material. In order to diagnose the cause of the unplanned scram, a test program was developed to duplicate the initial conditions while instrumenting the MSL low pressure logic; during performance of this test on August 30, 1991, a similar Primary Containment Group I Isolation / reactor scram occurred. Review of the test data concluded that the root cause was a combination of resonating pressure waves within the MSLs and the MSL low pressure switch instrument lines. Procedural actions were implemented pending review of design changes to correct this phenomenon. Safety significance of these events was minimal as the Group I Isolation logic responded as expected when challenged by the spurious signals. Previous related events are reported by LERs 91-17/050237 and 88-17/050249.
237 | 2371991037 | 1991-11-13 | QR8 | Spurious Reactor Trip | [45 empty] | Dresden 2 | B | GE | SU | 1 | At 1541 hours on November 13, 1991, an automatic reactor scram occurred due to a spurious Hi-Hi neutron flux signal on the Intermediate Range Monitors (IRMs). A unit startup was in progress with reactor pressure at approximately 101 psig at the time of the scram. The scram functions that occurred were proper upon receipt of the spurious spikes. The spurious spikes occurred as a High Pressure Coolant Injection (HPCI) steam isolation valve was opened. An extensive investigation into the spiking determined the cause to be electromagnetic interference (EMI) produced by DC valve motor operation. The EMI was being picked up in the drywell by the IRM signal cables. During the last refueling outage, new stainless steel jacketed Whittaker signal cables were installed in the drywell outside of the IRM rigid conduit. Corrective actions involved rerouting the IRM signal cables in the drywell inside flexible conduit for additional shielding, and installation of varistors on HPCI 250 Vdc valve motor circuitry to reduce the amount of EMI produced by valve operation. In addition, the IRM signal cables will be routed inside permanent rigid conduit during the next refueling outage. Previous similar events are documented by LERs 90-15/050237, 90-17/050237, and 91-18/050237.
237 | 2371994005 | 1994-04-30 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [6 empty] | X | [8 empty] | X | [19 empty] | X | [5 empty] | Dresden 2 | B | GE | PO | 99 | On April 30, 1994 at 2334, Unit 2 was manually scrammed from 99% power due to rapid depressurization of the Instrument Air (IA) header. All systems operated as expected. The loss of Instrument Air was due to a mechanical failure of the threaded portion of the inlet air supply piping to the 2A IA Receiver Tank. Pipe failure is attributed to pipe wall thinning from moisture induced corrosion compounded by the original construction threaded pipe installation which was contrary to the original plant (butt weld) design specification. The 2A receiver tank and inlet pipe were replaced and the compressor returned to service. The safety significance of this event was minimal. The ADS system was available for reactor pressure relief and the LPCI and Core Spray systems were available for core cooling. A previous reactor scram on loss-of-instrument-air, reported on January 16, 1993, was caused by dryer and backup air supply system failures. Corrective actions from that event would not have prevented this event. <br /><br /> This event is reportable per 10 CFR 50.73(a)(2)(iv), any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS).
237 | 2371995009 | 1995-03-05 | QR6 | Manual Reactor Trip | [45 empty] | Dresden 2 | B | GE | PO | 100 | NULL
237 | 2371996002 | 1996-04-18 | QK4 | Steam or Feed Leakage | [45 empty] | Dresden 2 | B | GE | SU | 1 | At 0820 on April 18, 1996 during unit startup, it was determined that the temperature of the High Pressure Coolant Injection (HPCI)[BJ] discharge line would not decrease to less than 150 degrees F, as stated in the precaution section of DOS 2300-03, 'High Pressure Coolant Injection System Operability Verification', and a 24 hour LCO was entered in accordance with T.S. 3.5.C.3 for HPCI operability. shutdown because of the inability to meet the Limiting Condition for Operations (LCO) time requirements of TS 3.5.C.3. Unit shutdown was completed at 1300 on April 18, 1996 with the initiation of a manual scram in accordance with DGP 2-1, Normal Unit Shutdown. The cause of the elevated HPCI discharge piping temperatures was due to a steam leak from the Main Steam (MS) drain bypass line orifice plate which impinged on the HPCI discharge line piping, in conjunction with some minor leakage into the HPCI discharge line due to a modified valve lineup. Corrective Actions include permanent repair of the MS drain line orifice plate steam leak and modification of the HPCI 2-2301-8 valve, eliminating the need for the modified valving configuration.
237 | 2371996009 | 1996-05-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Dresden 2 | B | GE | PO | 45 | On May 31, 1996, at approximately 2037, with Unit 2 in the run mode at approximately 45% power while performing an on-line logic configuration change to the Bailey Network 90 Feedwater Control System (FWCS) a loss of reactor feedwater control occurred. 2B Feedwater Regulating Valve moved fully shut during a logic reconfiguration of the Bailey Network 90 FWCS. This was the result of a logic execution sequence error, which was a design characteristic of the Bailey system. The Unit 2 Nuclear Station Operator initiated a manual scram when reactor water level reached a pre-established limit established due to special procedural controls associated with the feedwater testing. The lowest water level in the reactor reached was approximately -13.6 inches after the scram, which is more than 10 feet above the top of active fuel. <br /><br /> The overall safety significance was determined to be minimal because all safety systems performed as required and there was no danger to health and safety at any time.
237 | 2371997010 | 1997-07-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Dresden 2 | B | GE | PO | 87 | On July 27, 1997, with Unit 2 at full power, the 2B RFP recirc valve failed open and a recovery plan was created by the Operating Team to secure and isolate the failed valve. On July 28, 1997, the oncoming Operating Team reviewed Operating procedures and amended the recovery plan, without Management authorization, by allowing performance of the RFP changeover at a higher power than stated within the plan. This decision caused a higher than expected level increase on the start of the standby RFP and resulted in the Operator taking manual control of feedwater. The NSO failed to properly manipulate the feedwater controls and caused the trip of a RFP. A manual scram was initiated in accordance with conservative operating philosophy. The cause of the event was a performance error by the Operating Team. Corrective actions include counseling of involved operators in accordance with station policy and training to all operators on the event. This event is reportable per 10CFR50.73(a)(2) (iv), any event or condition that results in automatic or manual actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS). L:\8360\8301\237\180\97\010
237 | 2371997019 | 1997-12-23 | QR8 | Spurious Reactor Trip | [45 empty] | Dresden 2 | B | GE | PO | 99 | On December 23, 1997, at approximately 1141, during performance of Dresden Instrumentation Surveillance (DIS) 0500-01, Reactor Vessel High Pressure Scram Pressure Switch Calibration, an unexpected Reactor protection System (RPS) Channel A half scram was received from a spiking Local Power Range Monitor (LPRM). This in conjunction with the expected RPS Channel B half scram already received during DIS 0500-01, resulted in an unexpected full reactor scram. Following the reactor scram, a feedwater transient occurred which could have resulted in water entering the High Pressure Coolant Injection (HPCI) steam supply. However, the HPCI system was isolated at the time of occurrence. The root cause of the LPRM spike was a design/manufacturing deficiency of the LPRM detector and an inadequate review of a GE SIL which provided actions to reduce the probability of spurious LPRM spikes. The root cause of the feedwater transient was design deficiency of the feedwater control system [SJ]. The corrective actions include: possible expediting of the schedule to replace the LPRM detectors with the improved type, reevaluating the GE SIL, and modification of the feedwater control system. The overall safety significance of the is event was minimal.
237 | 2371998002 | 1998-01-13 | QR8 | Spurious Reactor Trip | [45 empty] | Dresden 2 | B | GE | PO | 99 | On January 13, 1998 at 1904 hours with Unit 2 operating at 100 percent power a Main Turbine [TA] trip, 2B and 2C Reactor Feedwater pumps (RFP)[SJ] trip resulted in a subsequent reactor scram, as well as, a Group II and Group III isolation. At the time of the event, an Instrument Maintenance(IM) technician was valving in local level indicator 2-263-59A following calibration of the indicator per Dresden Instrument Surveillance (DIS) 0263-14, Local Reactor Level Indicator (Safe Shutdown) Yarways LI 2(3)-263-59A and LI 2(3)-263-59B Calibration. The level indicator is installed on a common sensing line with Rosemount level transmitters 2-263-23A and 23C. LT 2-263-23A and 23C initiate a turbine trip and feedwater pump trip on high reactor water level. The root cause of the Unit 2 scram was found to be inadequate design review during the modification of Yarway level switch replacement. During development of the modification, the impact that the modification would have on plant maintenance activities was not identified by the design team (Design Engineering, Plant Engineering, Maintenance, etc.). The safety significance of the event was minimal since all plant systems operated as designed. Corrective actions included revision to DIS 263-14 to be performed off-line only and emphasizing to design engineers the necessity of thorough design reviews, detail industry event database searches and the need for detailed questioning of maintenance and operations personnel during design scope meetings. There have been no previous occurrences of this type of event.
237 | 2371998008 | 1998-04-20 | QR5 | Turbine Trip | [45 empty] | Dresden 2 | B | GE | PO | 60 | On April 20, 1998 at 0858 hours, a main generator trip occurred causing a unit scram. The cause of the trip is attributed to a design error in a modification that was installed during D2R15 that added additional protective relaying for the Unit Auxiliary Transformer (UAT) T-21 as a design enhancement, New auxiliary current transformers (CT's) were added to obtain the required circuit configuration. A design error was made in connecting the secondary windings of the CT's that were used to re-establish the input to the existing transformer differential relays. With the unit at power and sufficient bus loading, the design error caused the differential relays to respond to a current mismatch that simulated a differential condition. The protective relays actuated causing initiation of a generator trip which led to a reactor scram. The safety significance of this event was minimal. No safety systems were required nor utilized in controlling the plant during scram recovery or cooldown to cold shutdown conditions. All safety systems were available during the event and the Reactor Protection System performed as designed. Immediate corrective action was taken to issue a modification addendum to correct the wiring error. A special test procedure was prepared to perform in-service testing of the modification, and the existing differential relays. The revised modification was installed and the unit was returned to service on April 22, 1998. With the unit synchronized to the grid, the special test procedure was performed and all relaying affected by the modification was verified to be functioning property. Long term corrective actions included review of past modifications to ensure adequacy of the modifications and independent review, preparation of an inter-department interface agreement on methods to handle similar modifications in the future, formalize requirement for Nuclear Operational Analysis Department (NOAD) test input to the design modification process, and a review of preparer/reviewer requirements with design engineers. A search of the INPO and Dresden PIF databases was performed and one similar industry event involving a relay design error was identified.
237 | 2371998010 | 1998-06-20 | QR5 | Turbine Trip | [45 empty] | Dresden 2 | B | GE | PO | 99 | On June 20, 1998, at 1206 hours, while performing Dresden Operation Procedure (DOP) 5650-01, Electro-Hydraulic Control (EHC) System Startup and Shutdown, a Main Turbine trip with subsequent reactor scram was experienced. Upon review of the event, it was identified that the Main Turbine trip was the result of a low pressure spike in the Main Turbine EHC supply system. An air-bleed valve was found stuck shut, unable to operate, preventing the release of accumulated air from the system upon start of the 2A EHC pump. . The immediate cause for the event was failure of the air-bleed valve. The System Materials Analysis Department determined the root cause for the air-bleed valve failure to be the component had reached the end of its useful service life. Corrective actions included the replacement of the failed air-bleed valve and the addition of the air-bleed valve component to the preventive maintenance program. The overall safety significance of this event was minimal because Emergency Core Cooling Systems (ECCS) were operable.
237 | 2372000004 | 2000-11-30 | QR5 | Turbine Trip | [45 empty] | Dresden 2 | B | GE | PO | 100 | On November 30, 2000, with Unit 2 in Mode 1 at 100%reactor power, Nuclear Operational Analysis Department (NOAD) and Sub Station Construction (SSC) personnel entered the 345Kv yard to perform work on the Oil Circuit Breaker (OCB) 2-7 circuit breaker, which was Out Of Service (OOS).To start the evolution, SSC personnel opened knife switches located in the upper portion of the OCB cabinet, per their approved procedure. Shortly thereafter, NOAD personnel opened 12 current transformer cutout knife switches. This was performed without procedure and resulted in a lack of configuration control to assure recovery of the switches following maintenance. SSC personnel remained unaware that this was performed for the duration of the event. At the conclusion of work for the shift, NOAD utilized inappropriate nomenclature when asking SSC personnel whether the knife switches had been re-closed. This resulted in the OCB being returned to service with the knife switches inappropriately positioned (open) causing a Unit 2 reactor scram from full power when the Operators attempted to close the OCB. The root cause, specific to the tripping of the 345Kv OCBs and reactor scram, was determined to be insufficient adherence to management standards, policies, and administrative controls by NOAD personnel. Corrective actions included: the NOAD Department Manager and DNPS NOAD First Line Supervisors were held accountable and disciplinary actions were taken in accordance with station policy; NOAD reinforced management expectations as delineated in procedure MM-AA-7001, "NOAD Management Expectations;" and development and implementation of an action plan that addressed NOAD's failure to instill and enforce management standards, policies and administrative controls.
237 | 2372001002 | 2001-04-03 | QR6 | Manual Reactor Trip | [45 empty] | Dresden 2 | B | GE | PO | 31 | On April 3, 2001 at 2008 hours, the 2B Motor Generator (MG) Set tripped causing a 2B Reactor Recirculation (RR) pump trip due to a loose connection in the control circuit in the operating oil pump (2B1) Motor Control Center (MCC) cubicle. This resulted in the plant being placed in single loop operation with the 2A RR pump in service. Approximately four hours after trip of the 2B MG Set, a bearing oil filter high differential pressure (dP) caused a trip of the 2A RR MG Set on low bearing header oil pressure. Operations observed the 2A breaker had tripped and manually inserted a reactor scram at 2358 hours per station procedures. The oil system was found to be contaminated with non-metallic particulate. An investigation of the MG Set oil system did not identify any material in the system design that could have been the cause of the contamination. The root cause for the multiple trips of the MG Sets is the inadequate design of the system circuitry that does not provide for automatic starting of the non-operating (standby) oil pump when the running oil pump trips. Corrective actions to prevent recurrence include revising the MCC bus and MCC cubicle model work orders, preventative maintenance work orders, and associated procedures to address tightening of the stationary terminal block female clips and wire terminations during bucket and bus maintenance, Review and revise as necessary the FME procedures used on RR MG Set coupler and cooler maintenance to provide more rigorous controls, install the auto start modification for the oil pumps in Unit 2 in D2R17, and Operations to institute practice of periodically rotating equipment (pumps, coolers) on oil systems to ensure reliable operation, including comprehensive monitoring practices (pressure, flow, oil sampling, etc.) following equipment swaps. The safety significance of this event has been determined to be minimal.
237 | 2372001005 | 2001-11-07 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Dresden 2 | B | GE | SU | 8 | On November 7, 2001, during start-up from D2R17 refueling outage, Dresden Nuclear Power Station Unit 2 automatically scrammed from 8 percent power in Mode 2. Initial investigation revealed that the high-pressure turbine first stage pressure had risen during shell warming activities, which defeated the stop valve closure scram bypass. As shell warming increased, a reactor scram was initiated when this high-pressure was sensed along with the turbine stop valves being closed. The Root Cause has been determined to be inadequate human performance in that the turbine first stage pressure setpoint was inadequately monitored (as required by procedure) due to it not being considered a critical parameter required for turbine startup. The corrective action to prevent recurrence was to train Operations on this event regarding the effect on Unit 2 with respect to turbine first stage SCRAM setpoint changes due to implementation of Extended Power Uprate and the relationship between shell warming and its impact on RPS logic. Included in the training was the relationship between the pressure versus power. All automatic protection responses, including reactor trip and its associated actuations were verified to have functioned properly as a result of the reactor trip signal. Based on the above, it is concluded that the event did not adversely impact the health and safety of the public. The safety significance for this event is considered minimal.
237 | 2372003003 | 2003-09-30 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Dresden 2 | B | GE | PO | 85 | On September 30, 2003, at 2014 hours (CDT), an automatic reactor scram occurred due to a low reactor water level scram signal. The low reactor water level was the result of the trip of the 2C Reactor Feedwater Pump. The 2C Reactor Feedwater Pump trip occurred due to a valid over current ground relay actuation from a fault in the B phase power cable to the 2C Reactor Feedwater Pump. The root cause of the cable fault was indeterminate as the section of the cable which contained the fault could not be retrieved. Testing of retrievable cable sections did not identify the failure mechanism. The cable was replaced. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. The loss of feedwater flow is an analyzed transient and is classified as a moderate frequency event in the Updated Final Safety Analysis Report. There were no subsequent major equipment malfunctions .
237 | 2372003007 | 2003-12-11 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Dresden 2 | B | GE | PO | 95 | On December 11, 2003, at 2335 hours (CST), with Unit 2 at 96 percent power in Mode 1, a manual scram was inserted as the result of the plant's response to high Stator Water Cooling System temperature. The high Stator Cooling Water System temperature was due to a failed temperature controller to the Stator Water Cooling System temperature control valve. The plant responded as expected to the manual scram. The root cause of the temperature controller failure was attributed to historical foreign material intrusion resulting from inadequate processes for maintenance on the instrument air system. The foreign material caused an internal temperature controller pneumatic relay valve to stick and not respond properly. The identified foreign material was 5 to 10 micron aluminum oxide particles from the instrument air system. The corrective actions to prevent reoccurrence are to establish equirements for a post maintenance flush of instrument air lines and to incorporate the requirements into maintenance work planning documents. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the manual scram. There were no subsequent major equipment malfunctions.
237 | 2372004002 | 2004-04-24 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 2 | B | GE | PO | 20 | On April 24, 2004, at 0603 hours (CDT), with Unit 2 at approximately 20 percent power in Mode 1 and the Main Turbine Generator off-line in preparation for a scheduled maintenance outage, an automatic scram occurred due to closure of the Main Steam Isolation Valves. During the event, Main Steam Isolation Valve 2-203-2B closed slower than allowed by Technical Specifications. There were no Electromatic or Safety Relief valve actuations and no Emergency Core Cooling System initiations. Primary Containment Isolation System Group 2 and 3 isolations occurred as expected. All other systems responded to the automatic scram as expected. The Isolation Condenser System was used for primary system pressure control and operated as expected for approximately 5 hours. On April 24, 2004, at 1050 hours (CDT), with Unit 2 at zero percent power in Mode 3, the Isolation Condenser System was declared inoperable when valve 2-1301-3 could not be fully opened. The Reactor Water Cleanup System and Gland Seal System were subsequently used for pressure control. The root cause of the Main Steam Isolation Valve closure and resulting scram was attributed to inadequate drainage of the Main Steam Lead Drain System. The corrective action to prevent reoccurrence is to inspect for foreign material in the Main Steam Lead Drain System and clean as necessary. The root cause of the failure of Isolation Condenser valve 2-1301-3 to open was attributed to procedural inadequacy associated with setting the valve's Open Torque Switch Bypass. The corrective action to prevent reoccurrence was to revise the procedure for setting the valve's Open Torque Switch Bypass.
237 | 2372004004 | 2004-04-28 | QR3 | Reactivity Control Imbalance | [45 empty] | Dresden 2 | B | GE | PO | 66 | On April 28, 2004, at 1536 hours (CDT), with Unit 2 at approximately 66 percent power in Mode 1, a manual scram was inserted by operations personnel due to the plant being in a region of the reactor's power to flow map that required an immediate scram. The power to flow condition was caused by the unexpected trip of the 2A Reactor Recirculation Pump and the manual scram was in accordance with immediate operator actions specified in procedure DOA 202.01,"Recirculation (RECIRC) Pump Trip - One Or Both Pumps." There were no Electromatic or Safety Relief valve actuations and no Emergency Core Cooling System initiations. Primary Containment Isolation System Group 2 and 3 isolations occurred as expected due to normal reactor water level decrease following the scram. All control rods fully inserted and all other systems responded to the manual scram as expected. The root cause of the trip of the 2A Reactor Recirculation pump and the manual scram was attributed to a lack of detailed rewinding and acceptance test requirements in the Exelon large motor standard that governed the rewind of the 2A Reactor Recirculation pump motor. The corrective action to prevent recurrence is to revise the Exelon Nuclear Engineering Standard NES-EIC-40.01, "Large Motor (>2 kv) Repair Requirements," to address the B-Stage rewind process to incorporate detailed B-Stage rewinding and acceptance-testing requirements similar to the requirements of the Vacuum Pressurization Impregnation Process used during the manufacturing of the original motor.
237 | 2372005002 | 2005-03-24 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 2 | B | GE | PO | 96 | On March 24, 2005, at 0529 hours (CST), with Unit 2 at approximately 96 percent power, two unexpected control room alarms were received for exceeding the Electro-Hydraulic Control System maximum combined flow limit setpoint and open Turbine Bypass Valves. Several seconds later, high flow in the Main Steam System resulted in a signal to close the Main Steam Isolation Valves that initiated an automatic reactor scram. All control rods fully inserted and all other systems responded to the reactor scram as expected, except for non-safety related equipment, the Turbine Generator Lube Oil Pump and the 2B Reactor Feedwater Pump Auxiliary Oil Pump, which did not operate as required. The root cause of this event is indeterminate. The most probable cause is attributed to an increase in electrical resistance between electrical pins 13 and 22 on the "A54" card within the Electro-Hydraulic Control System. The corrective actions to prevent recurrence are to replace the "A54" card backplane connector, remake all termipoints on the connector for the A54 card and to rework the remaining connectors between electrical pins 13 and 22. The "A54" card backplane connector was replaced and the all termipoints on the connector were remade prior to startup. The remaining connectors will be reworked during the next Unit 2 refueling outage.
237 | 2372006004 | 2006-07-04 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 2 | B | GE | PO | 98 | On July 4, 2006, at approximately 0259 hours (CDT), with Unit 2 at approximately 98 percent power, Dresden Nuclear Power Station Unit 2 received a Group I Isolation on a Main Steam Line High Flow signal. The Main Steam Line High Flow signal was caused by the unexpected closure of the 1A Main Steam Isolation Valve and the resulting redistribution of steam to the remaining three main steam lines. All Group I isolation valves closed and the reactor automatically scrammed. Reactor water level was automatically controlled and the reactor vessel level shrink resulted in an expected Group II and Group III isolation signals. All systems responded as required and the Isolation Condenser was manually initiated to control reactor pressure. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)." The root cause of the event was attributed to two potential failure modes, inadequate tightening of the compression fitting nut causing inadequate compression of the ferrule to the tubing to the 1A Main Steam Isolation Valve, or the existing tubing to the 1A Main Steam Isolation Valve is undersized. Corrective actions include replacement of the compression fitting to the 1A Main Steam Isolation Valve, implementation of corrective actions as required to address any knowledge weaknesses relating to proper compression fitting assembly and verification practices as determined through the appropriate training systems analysis, and to inspect the compression fittings and tubing associated with Unit 2 and Unit 3 Main Steam Isolation Valves.
237 | 2372007002 | 2007-05-04 | QP4 | Partial Loss of Condensate Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 2 | B | GE | PO | 100 | On May 4, 2007, at 2305 hours (CDT), with Unit 2 at approximately 100 percent power, Dresden Nuclear Power Station control room personnel noted decreasing reactor water level and manually scrammed the reactor. All controls rods inserted into the core. The decreasing reactor water level was due to a loss off feedwater transient caused by an unexpected closure of all Unit 2 Condensate Prefilter System valves. Prior to this event, technicians were replacing a failed Condensate Prefilter System Central Processing Unit card. The High Pressure Coolant Injection System was utilized to restore reactor water level. During the event, the Main Steam Isolation Valves closed, the Reactor Recirculation Pumps were tripped and the Unit 2 and 3 Emergency Diesel Generators automatically started as designed. Unit 2 was restored to the electrical grid at 1638 hours (CDT) on May 8, 2007. The root cause of the unexpected closure of all Unit 2 Condensate Prefilter System valves and the subsequent loss of feedwater transient was a vendor latent software deficiency that caused the valves to close when the new Condensate Prefilter Central Processing Unit card was energized. The corrective actions to prevent reoccurrence are to proceduralize the requirements for performing Condensate Prefilter System troubleshooting, maintenance and system restoration; and to develop a design specification for the Condensate Prefilter System Central Processing Unit software.
237 | 2372014002 | 2014-04-12 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Dresden 2 | B | GE | PO | 100 | On April 12, 2014 at 1012 CDT, the Main Power Transformer for Dresden Unit 2 faulted due to an internal flashover. Due to the trip of the transformer, an automatic reactor protection system actuation occurred. All control rods inserted to their full-in position, and following the reactor trip, all systems operated as expected.<br /><br /> The most probable cause of the transformer failure was determined to be a combination of insulation issues. As a result, the transformer was replaced. Improved manufacturer oversight is being developed and procedures are being revised to ensure critical inspections are implemented during manufacturing.<br /><br /> The safety significance of this event was determined to be minimal based upon the availability of the required systems to safely shut down the reactor.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the system listed in paragraph (a)(2)(iv)(B).
237 | 2372014003 | 2014-05-03 | QR5 | Turbine Trip | [45 empty] | Dresden 2 | B | GE | PO | 100 | On May 03, 2014, Dresden Station was performing a channel swap of the Unit 2 Automatic Voltage Regulator (AVR). While attempting to perform the channel swap, the AVR unexpectedly switched to manual mode which resulted in exciter VARS rapidly decreasing. An automatic reactor protection system actuation, Turbine/Generator Trip, was received and all rods inserted to their full-in position. Following the reactor trip, all systems operated as expected.<br /><br /> The cause of this event was determined to be attributed to insufficient validation of vendor products following major equipment upgrades to ensure reliability of the newly installed equipment. Affected components were replaced, and the Automatic Voltage Regulator was successfully tested. Additionally, procedural guidance is being implemented to address risks associated with vendor, sub-vendor design, and technical products including risks associated with digital technology.<br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the system listed in paragraph (a)(2)(iv)(B).
237 | 2372015001 | 2015-01-13 | QP5 | Excessive Feedwater Flow | [45 empty] | Dresden 2 | B | GE | PO | 100 | On January 13, 2015, operators inserted a manual scram on Unit 2 due to increasing reactor water level. It was determined that the Feedwater Level Control (FLWC) system had failed. All control rods inserted, all systems responded as expected. The FWLC system was repaired and the unit was returned to operation on January 16, 2015.<br /><br /> On February 6, 2015, during maintenance activities to continue troubleshooting FWLC alarms, a reactor water level transient was induced. An automatic scram occurred due to low reactor vessel water level. During the transient, High Pressure Coolant Injection (HPCI) was initiated, but proceduralized operator response actions prevented injection. The Unit 2 and 2/3 Emergency Diesel generators started but did not load on to their respective busses as offsite power was not lost.<br /><br /> During both events, main feedwater was maintained in accordance with station operating procedures. These events are being reported under 10 CFR 50.73(a)(2)(iv)(A) "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)... "<br /><br /> The cause of these events has been determined to be spurious power interruption on a historically improperly landed power supply ribbon cable connection for the digital FWLC system. These events are considered of very low safety significance. Corrective actions include repairs to the ribbon cable connection and improvements to the troubleshooting process implementation.
237 | 2372015001 | 2015-02-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Dresden 2 | B | GE | PO | 100 | On January 13, 2015, operators inserted a manual scram on Unit 2 due to increasing reactor water level. It was determined that the Feedwater Level Control (FLWC) system had failed. All control rods inserted, all systems responded as expected. The FWLC system was repaired and the unit was returned to operation on January 16, 2015.<br /><br /> On February 6, 2015, during maintenance activities to continue troubleshooting FWLC alarms, a reactor water level transient was induced. An automatic scram occurred due to low reactor vessel water level. During the transient, High Pressure Coolant Injection (HPCI) was initiated, but proceduralized operator response actions prevented injection. The Unit 2 and 2/3 Emergency Diesel generators started but did not load on to their respective busses as offsite power was not lost.<br /><br /> During both events, main feedwater was maintained in accordance with station operating procedures. These events are being reported under 10 CFR 50.73(a)(2)(iv)(A) "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)... "<br /><br /> The cause of these events has been determined to be spurious power interruption on a historically improperly landed power supply ribbon cable connection for the digital FWLC system. These events are considered of very low safety significance. Corrective actions include repairs to the ribbon cable connection and improvements to the troubleshooting process implementation.
237 | 2372019002 | 2019-05-09 | QR5 | Turbine Trip | [45 empty] | Dresden 2 | B | GE | PO | 100 | On May 9, 2019, at 0348 CDT, Unit 2 received an automatic reactor scram as the result of the main turbine tripping due to low oil pressure from the main shaft oil pump. Following the scram, all systems operated as expected, decay heat was being removed using the steam bypass valves to the condenser, and the safety relief valves did not lift. Inspection of the main turbine front standard and main oil pump revealed damage to the spline interface between the main gear quill shaft and the high-pressure control rotor. This damage led to a loss of power transfer between the main turbine and the main oil pump which supplies bearing header pressure. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section." The automatic actuation of the reactor protection system is listed in 10 CFR 50.73(a)(2)(iv)(B). The cause of the event was determined to be work order instructions contained an unrecognized critical activity that lacked the detail needed to prevent human error during installation of quill shaft oil gasket. Corrective actions include updating the model work orders for turbine front standard maintenance to include the proper level of detail and establishing new post-maintenance testing practices.
244 | 2441988003 | 1988-03-10 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Ginna | P | WE | PO | 27 | On March 10, 1988 at 1856 EST with the reactor power at approximately 27%, during a unit startup, a reactor trip occurred due to low "A" Steam Generator (SG) level coincident with Steam Flow - Feedwater Flow (SF/FF) mismatch. <br /><br /> The two reactor trip breakers opened as required and all shutdown and control rods inserted as designed. <br /><br /> The underlying cause of the event was the unanticipated reactor coolant system temperature control problems experienced by the control room operators during the start-up. <br /><br /> Immediate corrective action was to stabilize the plant per the Plant Emergency Operating Procedures for reactor trip. <br /><br /> Action taken to prevent recurrence was to temporarily change the reactor core model for the plant specific simulator to more closely simulate the RCS temperature control problems and train the operators to this new model prior to the startup. <br /><br /> Action planned to prevent recurrence is to investigate improved startup training and Westinghouse's Owner's Group trip reduction programs for steam generator level trips.
244 | 2441988005 | 1988-06-01 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Ginna | P | WE | PO | 98 | On June 1, 1988 at 1932 EDST with the reactor power at approximately 98%, a reactor trip occurred due to low level in the "B" Steam Generator coincident with steam flow - feedwater flow mismatch followed in approximately 3 minutes by a safety injection initiation from pressurizer low pressure. <br /><br /> The two reactor trip breakers opened as required and all shutdown and control rods inserted as designed. All safeguards equipment operated as designed with the exception of two valves. <br /><br /> The underlying cause of the reactor trip was a transient caused by a blown fuse in the "B" Steam Generator controlling feedwater flow channel power supply. The underlying cause of the safety injection initiation was a reactor coolant system cooldown caused by overfeeding the steam generators. <br /><br /> Immediate corrective action was to stabilize the plant per the Emergency Operating Procedures for Reactor Trip and Safety Injection. <br /><br /> Action taken to prevent recurrence was to investigate and replace all feedwater flow channel power supply fuses and to replace the power supply on the effected channel.
244 | 2441989004 | 1989-06-01 | QR5 | Turbine Trip | [45 empty] | Ginna | P | WE | PO | 53 | On June 1, 1989 at 1332 EDST, with the reactor at approximately 53% power, a turbine trip with subsequent reactor trip occurred due to a ATWS Mitigation System Actuation Circuitry (AMSAC) actuation. <br /><br /> The Control Room operators verified the reactor and turbine trips and performed the actions of E-0 (Reactor Trip or Safety Injection) and ES-0.1 (Reactor Trip Response). The plant was stabilized in the hot shutdown condition. <br /><br /> The intermediate cause of the AMSAC actuated turbine trip was determined to be due to a procedural inadequacy. <br /><br /> The root cause was due to miscommunication of information used to generate procedure changes concerning the AMSAC Modification. <br /><br /> After the cause of the event was identified, the procedure was changed based on formally approved information to prevent recurrence.
244 | 2441990007 | 1990-05-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Ginna | P | WE | PO | 88 | On May 10, 1990, at 0219 EDST, with the reactor at approximately 88% full power, a reactor trip occurred from "A" Steam Generator (S/G) Low Level coincident with "A" S/G Feed Flow/Steam Flow mismatch.<br /><br /> The two reactor trip breakers opened as required and all shutdown and control rods inserted as designed. <br /><br /> The reactor trip was due to a malfunctioning "A" S/G Main Feedwater Regulating Valve Control System. <br /><br /> The underlying cause of the malfunctioning "A" S/G main feedwater regulating valve control system was attributed to the shorting of two high gain AC amplifier transistors in the flow controller, due to the transistor cans touching each other.<br /><br /> Immediate corrective action was to stabilize the plant in hot shutdown. <br /><br /> Subsequent action was to physically separate the two transistor cans so that they could not touch each other.
244 | 2441990010 | 1990-06-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Ginna | P | WE | PO | 97 | On June 9, 1990, at 0411 EDST with the Reactor at approximately 97% full power, a reactor trip occurred from "A" Steam Generator (S/G) Low Level coincident with "A" S/G Steam Flow/Feed Flow mismatch. <br /><br /> The two reactor trip breakers opened as required and all shutdown and control rods inserted as designed. <br /><br /> The reactor trip was due to a malfunctioning "A" S/G Main Feedwater Regulating Valve Control System. <br /><br /> The underlying cause of the malfunctioning "A" S/G Feedwater Regulating Valve Control System was a faulty Feedwater Flow Controller. The failure of the controller was localized to a 4 Stage AC Amplifier section. <br /><br /> Immediate Corrective Action was to stabilize the plant in hot shutdown.<br /><br /> Subsequent action was to change out the existing controller with a spare.
244 | 2441990012 | 1990-09-26 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Ginna | P | WE | PO | 97 | On September 26, 1990, at 1100 EDST with the reactor at approximately 97% full power, a reactor trip occurred from an opening of the "A" Reactor Trip Breaker, followed in approximately seven (7) seconds by a low pressurizer pressure reactor trip signal and the opening of the "B" Reactor Trip Breaker. <br /><br /> The "A" Reactor Trip Breaker opening was caused by the inadvertent dropping of a flashlight on two of three turbine autostop trip relays. The low pressurizer pressure reactor trip was caused by the reactor coolant system cooldown due to the reactor being tripped with the turbine still on the line. <br /><br /> Immediate corrective action was to stabilize the plant in hot shutdown. <br /><br /> Corrective action to prevent recurrence will be based upon the recommendations of a Human Performance Enhancement System (HPES) evaluation of the dropped flashlight event. Corrective action for subsequent hardware malfunctions will also be taken.
244 | 2441990013 | 1990-12-11 | QR5 | Turbine Trip | [45 empty] | Ginna | P | WE | PO | 97 | On December 11, 1990 at 1517 EST with the reactor at approximately 97% full power, a turbine trip with subsequent reactor trip occurred due to a inadvertent ATWS Mitigation System Actuation Circuitry (AMSAC) actuation.<br /><br /> The Control Room operators verified the reactor and turbine trips and performed the appropriate actions of E-O (Reactor Trip or Safety Injection) and ES-0.1 (Reactor Trip Response). The plant was subsequently stabilized in the hot shutdown condition. <br /><br /> The intermediate cause of the AMSAC actuated turbine trip was determined to be due to a low voltage potential of a logic output from the AMSAC Logic Circuitry. <br /><br /> The underlying cause was determined to be a vendor circuit design deficiency. <br /><br /> Corrective action taken was to install the jumper omitted in the circuit design.
244 | 2441990016 | 1990-12-12 | QR8 | Spurious Reactor Trip | [45 empty] | Ginna | P | WE | SU | 3 | On December 12, 1990 at 2322 EST with the reactor at approximately 3% full power, a reactor trip occurred from one (1) out of two (2) Intermediate Range Nuclear Instrument High Flux Trip. <br /><br /> The two reactor trip breakers opened as required and all shutdown and control rods inserted as designed.<br /><br /> The reactor trip was due to one (1) out of two (2) Intermediate Range Nuclear Instrument System High Flux Trip Bistable becoming de-energized during the transfer of Bus 14 power from its normal supply to the "A" Emergency Diesel Generator. <br /><br /> Immediately, corrective action was to stabilize the plant in hot shutdown per Emergency Operating Procedures. <br /><br /> The underlying cause of the event was determined to be a design deficiency in the available means of transferring electrical loads to a Diesel Generator, during power operations. <br /><br /> Actions will be taken to identify the optimal methodology for transferring electrical power supplies.
244 | 2441990019 | 1990-12-21 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Ginna | P | WE | PO | 16 | On December 21, 1990 at 1237 EST, with the reactor at approximately 16% full power, a reactor trip occurred due to Lo Lo level ("A" Steam Generator.)<br /><br /> The Control Room operators immediately performed the appropriate actions of E-O (Reactor Trip or Safety Injection) and ES-0.1 (Reactor Trip Response). Both main steam isolation valves were subsequently closed to limit an RCS cooldown and the plant was stabilized in hot shutdown. <br /><br /> The intermediate cause of the event was the "A" main feedwater pump tripping due to feed pump seal water low differential pressure caused by a condensate low header pressure transient. <br /><br /> The underlying cause of the event was a deficiency in the operating philosophy for the proper number of condensate pumps running during low power conditions. <br /><br /> Corrective action will be to change the appropriate procedures involved, to be consistent with the new operating philosophy.
244 | 2441992002 | 1992-02-03 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Ginna | P | WE | PO | 23 | On February 3, 1992 with the reactor at approximately 23% full power, just subsequent to a turbine trip while at 47% reactor power, a reactor trip occurred due to Lo Lo Level ( (S/G).<br /><br /> The Control Room operators immediately performed the appropriate actions of Emergency Operating Procedures E-0 (Reactor Trip or Safety Injection) and ES-0.1 (Reactor Trip Response). Both Main Steam Isolation Valves (MSIVs) were subsequently closed to limit a Reactor Coolant System (RCS) cooldown and the plant was stabilized at hot shutdown. <br /><br /> The underlying cause of the event was the inability to control the "A" S/G level above the reactor trip setpoint due to design and transient induced perturbations. (This event is NUREG-1022 (x) Cause Code). <br /><br /> Corrective action taken or planned are discussed in Section V of the text.
244 | 2441992003 | 1992-02-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Ginna | P | WE | PO | 97 | On February 29, 1992 at approximately 1346 EST, with the reactor stable at approximately 97% reactor power, just subsequent to a main feedwater pump trip, a reactor trip occurred due to Lo Lo level ( Steam Generator (S/G). <br /><br /> The Control Room operators immediately performed the appropriate actions of Emergency Operating Procedures E-0 (Reactor Trip Or Safety injection) and ES-0.1 (Reactor Trip Response). Both Main Steam Isolation Valves (MSIVs) were subsequently closed to limit a Reactor Coolant System (RCS) cooldown and the plant was stabilized at hot shutdown. <br /><br /> The underlying cause of the event was plugged instrument tubing for the "A" Feedwater Pump Seal Injection Differential Pressure (D/P) switch which tripped the main feedwater pump. (This event is NUREG-1022 (X) cause code.) <br /><br /> Corrective action taken was the unplugging of the instrument tubing by flushing and the replacement of one section of tubing and connections. Corrective actions to prevent recurrence are discussed in section V of the text.
244 | 2441993006 | 1993-11-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Ginna | P | WE | PO | 97 | On November 10, 1993, at approximately 0848 EST, with the reactor at approximately 97% reactor power, the ability to control the "A" main feedwater regulating valve was lost. This resulted in steam generator level transients. At 0850 EST, the reactor tripped on Lo Lo level ( 17%) in the "A" steam generator. The Control Room operators performed the actions of procedures E-0 and ES-0-1. <br /><br /> The underlying cause was determined to be disconnection of the "A" main feedwater regulating valve positioner feedback linkage arm from the valve actuator linkage rod, due to disengagement of the connecting screw and nut. (This event is NUREG-1220 (B) cause code.)<br /><br /> Corrective action was to install a new screw and nut. Corrective action to preclude repetition is outlined in Section V (B).
244 | 2441994007 | 1994-04-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Ginna | P | WE | PO | 45 | On April 27, 1994, at approximately 1407 EDST, with the reactor at approximately 45% reactor power, the ability to control the "A" main feedwater regulating valve was lost. At 1410 EDST, the reactor tripped on Lo Lo level ( operators performed the actions of procedures E-0 and ES-0.1. <br /><br /> The underlying cause was determined to be an improperly secured stroke adjust set screw for the valve positioner signal diaphragm assembly for the "A" main feedwater regulating valve. This event is NUREG-1022 Cause Code (B), "Design, Manufacturing, Construction/Installation." <br /><br /> Immediate corrective action was to install a new valve positioner of a previous design. Corrective action to preclude repetition is outlined in Section V (B).
244 | 2441995008 | 1995-08-25 | QL7 | Degraded condenser vacuum | [45 empty] | Ginna | P | WE | PO | 97 | On August 25, 1995 at approximately 0541 EDST, with the plant at approximately 97% steady state reactor power, the 'B' condenser water pump tripped. This resulted in a reduction in a reduction of turbine- condenser heat removal capability. Immediate action was to decrease turbine load to less than 50%, as per procedure AP-CW.1. However, due to a secondary system transient that followed the reduction in heat removal capability, at approximately 0543 EDST, the Shift Supervisor conservatively ordered a manual reactor trip, all systems operated designed, the reactor was stabilized at hot shutdown conditions. <br /><br /> The underlying cause of the tripping of the 'B' condenser circulating water pump was due to a sheared bolt that affected the motor exciter. The cause of the reactor trip was manual operator action. <br /><br /> This event is NUREG-1022 Cause Code (B). <br /><br /> Corrective action to prevent recurrence is outlined in Section V. B.
244 | 2441996002 | 1996-03-07 | QL7 | Degraded condenser vacuum | [45 empty] | Ginna | P | WE | PO | 97 | On March 7, 1996, at approximately 1814 EST, with the plant at approximately 97% steady state reactor power (Mode 1), the 'B' condenser circulating water pump tripped. This resulted in a reduction of main condenser heat removal capability. Immediate action was to decrease turbine load to less than 50%, as per procedure AP-CW.1 . However, due to condenser backpressure increasing above the limit for the satisfactory operating region for the main turbine, at approximately 1822 EST, the Shift Supervisor conservatively ordered a manual reactor trip. The Control Room operators performed the actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized at hot shutdown conditions (Mode 3). <br /><br /> The underlying cause of the tripping of the 'B' condenser circulating water pump was due to actuation of the power factor protection relay, which tripped the circuit breaker for the pump. The cause of the reactor trip was manual operator action. <br /><br /> This event is NUREG-1022 Cause Code (E). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
244 | 2441996012 | 1996-08-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Ginna | P | WE | PO | 100 | On August 20, 1996, at approximately 1442 EDST, with the plant in Mode 1 at approximately 100% steady state reactor power, the 'B' main feedwater regulating valve went to the fully closed position. At 1443 EDST, the reactor tripped on Lo Lo level in the 'B' Steam Generator. The Control Room operators performed the actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized in Mode 3. <br /><br /> The underlying cause of the closure of the 'B' main feedwater regulating valve was determined to be a loss of electrical continuity, caused by a missing screw in the current-to-pressure transducer for the 'B' main feedwater regulating valve. <br /><br /> Corrective action was to replace the missing screw. <br /><br /> This event is NUREG-1022 Cause Code (A). <br /><br /> Corrective action to prevent recurrence is outlined in Section V.B.
244 | 2441999007 | 1999-04-23 | QR8 | Spurious Reactor Trip | [45 empty] | Ginna | P | WE | PO | 35 | On April 23, 1999, at approximately 0748 EDST, with the plant in Mode 1 at approximately 35% reactor power and a power escalation in progress after the 1999 refueling outage, Instrument and Control technicians inadvertently pulled fuses from the wrong nuclear instrument channel, causing a reactor trip due to high range flux trip. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized in Mode 3. The underlying cause of the reactor trip was a personnel error, in that fuses were pulled on the wrong nuclear instrument channel. Further evaluation of the event has resulted in more accurately categorizing the root causes. Immediate corrective action was taken to stabilize the plant in Mode 3. Corrective actions to prevent recurrence are outlined in Section V.B.
244 | 2441999008 | 1999-04-27 | QR8 | Spurious Reactor Trip | [45 empty] | Ginna | P | WE | PO | 90 | On April 27, 1999, at approximately 1248 EDST, with the plant in Mode 1 at approximately 90 percent reactor power and a power escalation in progress after the 1999 refueling outage, Instrument and Control technicians had placed one channel of the reactor protection system in the tripped condition for calibrations. A bistable in a different channel entered the tripped condition, resulting in two channels tripped and causing a reactor trip due to Overtemperature Delta T. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized in Mode 3. The underlying cause of the reactor trip was a faulted bistable. Immediate corrective was taken to stabilize the plant in Mode 3. The faulted bistable was subsequently replaced. Corrective action to prevent recurrence is outlined in Section V.B.
244 | 2442000005 | 2000-10-21 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Ginna | P | WE | PO | 71 | On October 21, 2000, at approximately 1418 EDST, with the plant in Mode 1 at approximately 71% steady state reactor power, the "B" condenser circulating water pump tripped. At approximately 1419 EDST, following procedural direction, the reactor was manually tripped. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized in Mode 3. The tripping of the "B" condenser circulating water pump was caused by failure of the excitation voltage transformer, which resulted in loss of excitation field to the pump motor. The cause of the reactor trip was manual operator action. Corrective actions included replacing the excitation voltage transformer. Corrective action to prevent recurrence is outlined in Section V.B.
244 | 2442002001 | 2002-02-05 | QR6 | Manual Reactor Trip | [45 empty] | Ginna | P | WE | PO | 100 | On February 5, 2002, at approximately 0911 EST, with the plant in Mode 1 at approximately 100% steady state reactor power, the "A" condenser circulating water pump tripped. The Control Room operators entered Abnormal Operating Procedure AP-CW.1 for loss of the circulating water pump. At approximately 0912 EST, following procedural direction, the reactor was manually tripped. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all safety systems operated as designed, and the reactor was stabilized in Mode 3. The tripping of the "A" condenser circulating water pump was caused by the failure of a pump motor field wire. The circulating water pump motors are synchronous motors. When the wire failed, motor field current was lost and the motor was tripped by its power factor relay protection. The field wire failure was preceded by the failure of a constant voltage transformer in the motor excitation circuit.
244 | 2442003002 | 2003-08-14 | QR5 | Turbine Trip |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Ginna | P | WE | PO | 100 | On August 14, 2003, the plant was in Mode 1 at approximately 100% steady state reactor power. At approximately 1611 EDST, a major electrical grid disturbance occurred, affecting the Northeastern United States and areas of Southern Canada. The disturbance caused a complete loss of electrical load and an automatic Reactor Trip. The Shift Supervisor conservatively declared an Unusual Event at 1646 EDST based on Emergency Action Level 6.1.1, "Loss of ability to supply power to the safeguard trains from offsite circuits 751 and 767 for greater than 15 minutes," and exited the Unusual Event at 2108 EDST. The cause of the Reactor Trip was 2/4 Over Temperature Delta T (OTDT) channels reaching their setpoints due to the load rejection and ensuing Reactor Coolant System transient.
244 | 2442003005 | 2003-10-15 | QR6 | Manual Reactor Trip | [45 empty] | Ginna | P | WE | SU | 1 | During start-up from the 2003 Refueling Outage (RFO) on October 15, 2003, high wind conditions resulted in the loss of off-site Circuit 751. With the electrical system in the normal start-up alignment, the loss of Circuit 751 resulted in the loss of the bus powering the B Reactor Coolant Pump (RCP). Following the loss of the BRCP, the operators manually tripped the reactor as required by Abnormal Operating Procedure AP-RCS.2, Loss of Reactor Coolant Flow. Safeguards busses 16 and 17 were also lost due to the loss of Circuit 751, but were subsequently re-energized by the B Emergency Diesel Generator (EDG) as designed. The A and B Motor Driven Auxiliary Feedwater Pumps started as designed. The plant was stabilized in Mode 3 using the appropriate procedures. Corrective action to prevent recurrence is outlined in Section V.B.
244 | 2442005001 | 2005-02-16 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Ginna | P | WE | PO | 100 | On February 16, 2005, at approximately 2112 EST, with the plant in Mode 1 at approximately100% steady state reactor power, the reactor automatically tripped. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all safety systems operated as designed, with the exception of the control function for the main steam atmospheric relief valves (ARVs). The reactor was stabilized in Mode 3. The tripping of the reactor was caused by a turbine trip as the result of an anticipated-transient-without-scram (ATWS) mitigation actuation circuitry (AMSAC) signal. The AMSAC signal was the result of low feedwater flow signals, caused by the failure of redundant advanced digital feedwater control system (ADFCS) power supplies. The ARV automatic and remote manual operation was also affected by the failed power supplies.Corrective action to prevent recurrence is outlined in Section V.B.
244 | 2442007001 | 2007-01-27 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Ginna | P | WE | PO | 100 | On January 27, 2007, at approximately 2040 EST, with the plant in Mode 1, initially at 100% steady state reactor power, an event occurred resulting in an automatic reactor trip. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all safety systems operated as designed. The reactor was stabilized in Mode 3. The reactor trip was the result of a loss of electrical load transient, which is attributed to a failure in the Main Turbine Electro Hydraulic Control (EHC) system that caused the four high pressure turbine control valves to rapidly close simultaneously. The loss of electrical generation resulted in a heat-up of the reactor coolant system and an actuation of the Reactor Protection System (RPS) on Over-Temperature Differential Temperature. Corrective action to prevent recurrence is outlined in Section V.B.
244 | 2442007002 | 2007-03-16 | QL5 | Partial Closure of MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Ginna | P | WE | PO | 100 | On March 16, 2007, at approximately 2209 EST, with the plant in Mode 1, initially at 100% steady state reactor power, an event occurred resulting in a safety injection signal and an automatic reactor trip. The Control Room operators performed the appropriate actions of procedures E-0 and ES-1.1. Following the reactor trip, all safety systems operated as designed. The reactor was stabilized in Mode 3. The safety injection signal and subsequent reactor trip resulted from the B Main Steam Isolation Valve (MSIV) unexpectedly closing and a low steam line pressure condition occurring when the 'A' Steam Generator attempted to handle the full steam load requirements at the time. The cause of this event was a lack of configuration control associated with the actuator for the 'B' MSIV. Corrective action to prevent recurrence is outlined in Section V.B.
244 | 2442009002 | 2009-12-30 | QR5 | Turbine Trip | [45 empty] | Ginna | P | WE | PO | 100 | On December 30, 2009, the R.E. Ginna Nuclear Plant experienced an automatic plant trip from full power. The trip was initiated upon a signal of two out of two turbine stop valves being fully closed. The two stop valves closed when the electro-hydraulic control system (EHC) could not maintain adequate EHC system pressure to keep the stop valves in the fully open position. The control room operators performed the appropriate actions of procedures E-0, Reactor Trip or Safety Injection and ES-0.1, Reactor Trip Response. Following the reactor trip, all safety systems operated as designed. The reactor was stabilized in Mode 3. The cause of the EHC pressure loss was a common mode failure of both EHC pumps caused by the incorrect seal material being used during vendor refurbishment of the pumps that were installed during the 2009 refueling outage (RFO). The specified material was Viton, however evaluation identified that Buna-N was provided which is incompatible with the EH fluid. Corrective actions to prevent recurrence are summarized in Section IV.B.
244 | 2442011003 | 2011-10-11 | QR5 | Turbine Trip | [45 empty] | Ginna | P | WE | PO | 100 | On October 11, 2011, the R.E. Ginna Nuclear Power Plant experienced an automatic reactor trip from 100% power. The trip was caused by a failure of the turbine lube oil piping internal to the turbine lube oil reservoir. The failed piping resulted in the main turbine Auto Stop Trip oil pressure switches activating on low oil pressure. The control room operators performed the appropriate actions of procedures E-0, Reactor Trip or Safety Injection and ES-0.1, Reactor Trip Response. Following the reactor trip, all safety systems operated as designed. The reactor was stabilized in Mode 3 while repairs were performed. The cause of the piping failure was determined to be high piping stresses from original construction in combination with substandard welding, routine maintenance, and cyclical fatigue. Corrective actions to prevent recurrence include a redesign of the piping to facilitate maintenance of associated check valves and to eliminate stress risers inherent to the original weld configuration. Additional corrective actions are summarized in section IV.B.
244 | 2442013002 | 2013-07-24 | QR5 | Turbine Trip | [45 empty] | Ginna | P | WE | PO | 100 | On July 24, 2013 at 1419, the R.E. Ginna Nuclear Power Plant (Ginna) experienced an automatic Reactor Trip from full power during Main Generator Reactive Power Testing.<br /><br /> The Reactor Trip was caused by a reactor protection system (RPS) actuation signal from a Turbine Trip, which was caused by a Generator Trip. All Control Rods inserted on the trip, and Auxiliary Feedwater started automatically, as expected. The cause of the generator trip was determined to be an incorrect configuration of two generator protection digital relays while implementing a modification during the 2012 refueling outage. An alarm was expected while raising voltage during reactive power testing, but due to the incorrect configuration of the relays, a trip signal was received which tripped the main generator. The protective relays' outputs were configured incorrectly to trip at the alarm setpoint.<br /><br /> The trip functions of the digital relays were removed, returning Ginna to the alarm indication and trip protections prior to the 2012 refueling outage.
245 | 2451987007 | 1987-03-22 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Millstone 1 | B | GE | PO | 48 | On March 22, 1987 at 1751 hours, while operating at 48% power (530 degrees Fahrenheit 990 psig), a Reactor Scram and Group I isolation occurred during a transfer from the Mechanical Pressure Regulator (MPR) to the Electrical Pressure Regulator (EPR). The event occurred when Main Steam Line pressure decreased below the Group I Isolation setpoint of 825 psig as the EPR was placed in service. As a consequence of the Main Steam Isolation Valve closure, the Isolation Condenser was manually initiated to control Reactor pressure. All other systems operated as expected. No safety consequences resulted from this event. <br /><br />Root cause of event: Operator Error
245 | 2451987034 | 1987-08-14 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Millstone 1 | B | GE | SU | 1 | On August 14, 1987 at 2150 hours during reactor start-up following a scheduled refueling outage, continuous control rod withdrawal resulted in a large reactivity addition and reactor scram due to Intermediate Power Range Monitor (IG) (IRM) hi-hi flux. The event is attributed to operator error. All systems responded as required. There were no consequences.
245 | 2451987036 | 1987-08-26 | QR8 | Spurious Reactor Trip | [45 empty] | Millstone 1 | B | GE | PO | 100 | On August 26, 1987 at 1059 hours, instrument technician error during performance of surveillance procedure SP 404C, APRM Calibration and Functional Test, resulted in a reactor scram from full power. In normal response to the scram, the Standby Gas Treatment System initiated due to a Group II Isolation on reactor vessel low water level. There were no safety consequences.
245 | 2451987038 | 1987-09-03 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Millstone 1 | B | GE | PO | 100 | On September 3, 1987 at 1421 hours, while operating at 100% power, a Reactor Scram occurred due to low scram air header pressure that resulted from a loss of Instrument air (LD) pressure. As a result of the scram, a low Reactor water level existed which caused a Group II isolation signal, and hence the initiation of the Standby Gas Treatment System (SBGT) (BH). The Reactor was brought to a safe shutdown and there were no safety consequences as a result of this event.
245 | 2451988003 | 1988-03-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 1 | B | GE | PO | 100 | On March 12, 1988 at 0518 hours while at 100 percent reactor power (530 degrees F, 1033 psig) a full reactor scram occurred on low reactor water level (+8 inches). The low reactor water condition was the result of the trip of "A" Reactor Feed Pump. Operations personnel manually started a standby feed pump but due to problems in the feedwater flow control circuitry reactor level continued to decrease with subsequent full scram and standby gas treatment system initiation. All other systems functioned as expected. No safety consequences resulted from this event.
245 | 2451989005 | 1989-04-07 | QR5 | Turbine Trip | [45 empty] | Millstone 1 | B | GE | PO | 80 | On April 7, 1989 at 1238 hours, while the Unit was at 80 percent reactor power (530 degrees F and 1030 psig), as part of the shutdown for a scheduled refueling outage, a Reactor Scram occurred on Turbine Stop Valve Closure. As a result of the scram a Group II isolation occurred and the Standby Gas Treatment System (BH), which is an Engineered Safeguards System, initiated. The Turbine Stop Valve Closure signal was received from a Moisture Separator high level switch initiation. An investigation determined that Moisture Separator Drain Tank level control valve (LCV) (1-HD-17B) failed to maintain normal level in the drain tank. Tank condensate level was lost and steam entered the drain piping. This transient caused vibration of the associated piping which caused the false Moisture Separator high level switch (LS) actuation. <br /><br /> All systems functioned as required and no safety consequences resulted from this event.
245 | 2451989015 | 1989-06-02 | QL7 | Degraded condenser vacuum | [45 empty] | Millstone 1 | B | GE | SU | 1 | On June 2, 1989 at 1037 hours during reactor startup, a reactor scram occurred due to main condenser low vacuum. At the time of the event, reactor conditions were 580 psig and 480 degrees F at approximately one (1) percent power. The cause of the event was lack of attention to detail on the part of the reactor operator. The plant responded as designed and all applicable post-scram procedures were correctly followed. There were no consequences.
245 | 2451989021 | 1989-10-19 | QP5 | Excessive Feedwater Flow | [45 empty] | Millstone 1 | B | GE | PO | 70 | On October 19, 1989 at 1515 hours with the plant at 70% power (530 degrees Fahrenheit and 1000 psig) a full reactor scram occurred as a result of a Main Turbine Trip (Turbine Stop Valves greater than 10% closure). The Main Turbine Trip was the result of a high reactor water level turbine trip signal (+48"). The high reactor water condition was the result of "A" Feedwater Regulating Valve becoming a stuck in the open position which occurred while returning "B" Feedwater Regulating Valve to service. During the level decrease which followed the scram, Standby Gas Treatment system initiated as expected. All systems functioned as expected. No safety consequences resulted from this event.
245 | 2451990015 | 1990-09-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 1 | B | GE | PO | 100 | On September 14, 1990, with the plant at 100% power (530 degrees Fahrenheit and 1030 psig), a full reactor scram occurred on low reactor water level (+8 inches) after the feedwater regulating valves began to close. The feedwater regulating valves were responding to a high indicated reactor water level signal from the 'A' channel of the feedwater control system, which was controlling feedwater flow. At the time of the scram, a technician was performing a calibration on a pressure switch which senses pressure from an instrument line common to the reference leg of the 'A' feedwater control system. <br /><br /> All safety systems functioned as required and no safety consequences resulted from this event.
245 | 2451990016 | 1990-10-04 | QL4 | Loss of Non-safety-Related Cooling Water |  |  |  |  | X | [5 empty] | X | [10 empty] | X | [18 empty] | X |  |  |  |  | Millstone 1 | B | GE | PO | 100 | On October 4, 1990, at 1849, while reducing power during storm conditions, a manual reactor trip from 45% power (530 degrees F, 1030 psi) was initiated because of degraded conditions in the Service Water and Circulating Water supplies. Seaweed buildup on the intake structure traveling screens exceeded the Screen Wash system removal capability. Debris was carried over the Traveling Screen head shaft. Operators stopped the traveling screen rotation to conduct cleaning. Circulating Water Pumps were not tripped in accordance with the Operating Procedure 323. Three of five traveling water screens incurred damage to the outer baskets because of high differential pressure. Service Water pressure decreased due to pump cavitation and Self Cleaning Strainer fouling. A manual scram was initiated when low service water pressures were noted combined with increasing containment temperature, pressure and decreasing condenser vacuum. The containment temperature/pressure increase was the consequence of degraded Reactor Building Closed Cooling Water heat exchanger performance. The Service Water system recovered once the pumps regained adequate submergence. Cold shutdown was achieved with the remaining intact Traveling Screens, Circulating Water Pumps, and Service Water Pumps. The Service Water Strainer Bypass valve provided additional sea water cooling reliability. A second Reactor Protection system trip due to low reactor vessel level was experience during recovery from the initial event.
245 | 2451992028 | 1992-12-03 | QL5 | Partial Closure of MSIVs | [45 empty] | Millstone 1 | B | GE | PO | 100 | On December 3, 1992, at 0920 hours, with the plant operating at 100% power (530 Degrees F and 1030 psig), a reactor scram occurred during the performance of a routine surveillance test on the Isolation Condenser system. During performance of the surveillance procedure, an operator inadvertently closed two Main Steam Isolation Valve (MSIV) switches which resulted in a Group 1 Containment Isolation signal on high main steam flow and a subsequent reactor scram. All safety systems functioned as required throughout the event.
245 | 2451993018 | 1993-10-05 | QR8 | Spurious Reactor Trip | [45 empty] | Millstone 1 | B | GE | PO | 100 | On October 5, 1993, at 0859, while operating at 100% power, a spurious reactor scram occurred. The scram event was not preceded by any warning or annunciation. Operators performed actions specified in appropriate procedures and stabilized the plant. As a result of the scram, reactor vessel water level decreased to the Group II isolation setpoint, and as expected initiated the Standby Gas Treatment (SGT) System. Other than the Reactor Protection System (RPS) and SGT, no other safety systems were called upon during this event.<br /><br /> The scram cause is unknown and it has been determined to be spurious. Because the cause was unknown, all surveillances related to the RPS were performed as specified in the Scram Recovery procedure. The surveillance results indicated that the RPS is fully functional and operated according to its intended design.
247 | 2471987004 | 1987-02-10 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On February 10, 1987 at 22:03, while operating at 100% reactor power, a trip of reactor protection Train B occurred. This resulted in a reactor/turbine (RCT/TRB) trip. Following the trip, 6.9 KV bus (BU) 2 failed to transfer from the station power supply to offsite power. This resulted in the deenergization of reactor coolant pump 24 and 480 volt bus (BU) 2A and the automatic start of 21 and 23 emergency diesel generators (DG). All safety related equipment operated properly following the reactor trip and the plant was stabilized in hot shutdown conditions. At 23:30, while matching CCR switch positions with field breaker (BRK) positions, 6.9 KV bus 3, 480 volt bus 3A and reactor coolant pump 23 were inadvertently deenergized. The health and safety of the public were not affected. <br /><br /> The reactor trip and 6.9 KV bus 3 deenergization were determined to be caused by personnel error. The failure to achieve automatic transfer to offsite power for 6.9 KV bus 2 was caused by a malfunctioning breaker (BRK) cell switch which was subsequently repaired.
247 | 2471987009 | 1987-06-27 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On June 27, 1987, while adjusting steam generator (SG) low-low level setpoints, a reactor trip occurred when Reactor (RCT) Trip Breaker "A" opened. The trip occurred immediately after steam generator No. 24 channel III bistable was placed in the test (trip) condition in order to adjust the trip setpoint. <br /><br />The steam generator (SG) low-low level trip circuit is configured in a two-out-of-three logic. A contact in the trip circuit from one of the other two channel relays (RLY) on steam generator No. 24 was not made up properly, allowing the trip logic to be made up. The relays (RLY) are Westinghouse BF-57F relays. Relays (RLY) LC-447BX and LC-447DX were replaced with new relays prior to returning the plant to service. <br /><br />All other safety-related equipment operated as required. The health and safety of the public were not affected.
247 | 2471988002 | 1988-01-25 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Indian Point 2 | P | WE | PO | 15 | On January 25, 1988 during plant start-up operations, a reactor trip occurred when the intermediate range high flux trip setpoint was exceeded shortly after synchronizing the turbine-generator to the power grid. A high rate of increase in turbine power (steam demand) after synchronization induced a reactor coolant system cooldown and pressure decrease. The operator responded by manually withdrawing control rods to raise reactor power and thereby increase reactor coolant temperature and pressure. The reactor tripped at approximately 15% power via one of two intermediate range nuclear power channels (N 36). Post trip testing revealed that channel N 36 trip setpoint was conservatively set at 15% power (nominally 25%). All systems operated as per design. The intermediate range high flux trip setpoint for channel N 36 was subsequently readjusted closer to but less than 25% reactor power. The operating personnel were readvised concerning the rate of steam demand increase during plant start-ups. The health and safety of the public were not affected.
247 | 2471988006 | 1988-06-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On June 17, 1988, while the plant was at 100% power, an unplanned reactor trip occurred. A contract employee performing cleaning functions on the conventional side of the plant inadvertently depressed the manual trip button for 21 Main Boiler Feedwater Pump. During the subsequent attempted recovery from the loss of one feedwater pump the main generator tripped on high water level in 22 steam generator. The generator trip caused a main turbine, and subsequent reactor trip. The reactor protection system functioned normally and the public health and safety were not affected. The use of contract employees for cleaning in the vicinity of critical operating equipment at the station is being reviewed.
247 | 2471988018 | 1988-11-22 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On November 22, 1988 at approximately 1208 hours, a unit trip from full power occurred. The main generator 86P lockout relay was identified as the initiating signal by the first out indication on the computer-generated sequence of events report. A target relay in the Control Room identified the trip signal as being initiated from the Regulator Cabinet on the 33 foot elevation in the Turbine Building. Subsequent troubleshooting and signal verification of the circuit identified the generator volts/hertz trip system as the probable source of the trip signal. There was no impact on public health and safety.
247 | 2471988019 | 1988-11-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On November 26, 1988, at approximately 0623 hours, Steam Generator #24 steam flow/feed flow mismatch alarm annunciated in the Control Room as a result of main feedwater regulating valve FCV-447 failing closed. Control Room operators attempted to open FCV-447 by placing it in the manual mode, however the valve would not respond. The feedwater low flow valve FCV-447L was placed in the full open position, however it could not supply sufficient flow to prevent a low steam generator level mismatch trip. The cause of the regulating valve failing closed was traced to a failed fuse in its control circuit. Loss of control power de-energized the regulating valve solenoids, and allowed instrument air to vent, closing the valve. There was no adverse impact on public health and safety.
247 | 2471989002 | 1989-02-22 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Indian Point 2 | P | WE | PO | 100 | On February 28, 1989, while the plant was at full power, a reactor trip occurred on an overpower Delta T signal.<br /><br /> Immediately prior to the trip, an instrument air line for the control of the heater drain tank discharge control valves parted at a soldered connection. The resultant loss of instrument air caused the discharge valves to go to the full open position. A heater drain tank low level signal tripped the heater drain tank pumps. A third condensate pump, which would have normally started under these circumstances, had its auto-start controls out of service due to a routine surveillance test.<br /><br /> Pump loss was observed in the control room, and plant operators reduced turbine load and inserted rods while simultaneously placing the third condensate pump in service manually. Approximately three minutes into the event the reactor tripped. With the load being reduced and rods . inserted, the delta flux in the core increased from - 4% to greater than - 20%. Because of the delta flux penalty, the reactor tripped when the loop delta T exceeded the lowered trip setpoint during the transient. <br /><br /> All rods inserted on the reactor trip signal, and all safety systems 1, functioned as designed.
247 | 2471989013 | 1989-12-13 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On December 13, 1989, while the plant was at 100% power, a momentary decrease in main turbine governor oil pressure, brought a bout by operator action actuated the "turbine tripped" logic (turbine still reset) which in turn generated a reactor trip signal. The subsequent reactor trip generated a turbine trip signal causing a turbine and generator trip. Following the trip and data review it was determined that Reactor Coolant System letdown isolation did not occur, and that loop 23 pressurizer spray flow was unexpectedly reduced to an insufficient amount due to an incorrect bypass valve position, causing lower than expected temperatures in the associated spray line.
247 | 2471991001 | 1991-01-07 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 2 | P | WE | PO | 96 | On January 7, 1991 at approximately 11:02 a.m., with the unit operating at 96.5% power, the reactor tripped. The trip was generated by the reactor protection system (RPS) two out of four coincidence logic for a low pressurizer pressure. The low pressurizer Pressure logic actuation occurred as a result of maintenance activity on pressurizer pressure transmitter PT 455. The operators responded to the event in accordance with established plant procedures and the plant systems responded as designed, with the exception of auxiliary feedwater pump No. 21. This pump started and tripped after running for approximately 120 seconds. Consequently, at 11:05 a.m., the plant entered a 72 hour limiting condition of operation (LCO) as required by Technical Specification 3.4.B(1)(a). Also during the event, the isolation of the chemical volume control system normal letdown occurred and the bank "C" rod "L3" bottom light did not illuminate as required by design. <br /><br /> The plant achieved hot shutdown at approximately 11:30 a.m. and restart was subsequently initiated with the generator breakers closed on the grid on January 8, 1991 at approximately 8:36 p.m. No NRC limit was exceeded. Likewise there was no impact on public health and safety.
247 | 2471991013 | 1991-07-25 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 2 | P | WE | PO | 90 | On July 25, 1991 at 1556, with the unit operating at approximately 90% power and Reactor Protection System channel calibrations in progress, the reactor tripped. The trip was generated by the reactor protection system two out of four coincidence logic for Over Temperature Delta Temperature. The operators responded to the event in accordance with established plant procedures and plant systems responded as designed.<br /><br /> Following the review of the events by the Station Nuclear Safety Committee a reactor restart was initiated with the generator breakers closed on the grid on July 26, 1991 at approximately 1814. There was no impact on the health and safety of the public.
247 | 2471992002 | 1992-01-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On January 27, 1992 the plant was operating at 100% power when a reactor trip occurred due to steam flow-feedwater flow mismatch. Subsequently, a high steam flow-low Reactor Coolant System (RCS) average temperature conditions resulted in a Safety Injection (SI) signal. The reactor trip was caused by a main feedwater regulating valve going to the closed position unexpectedly. The SI signal arose from a decrease in RCS temperature in response to the reactor trip coincident with high steam flow signals from two steam generators (although very high steam flow conditions indicating a steam line break did not exist). <br /><br /> Following the SI signal, containment isolation, phase A, could not be reset without use of installed keyed bypass switches. In the subsequent event evaluation it was determined that an open circuit in the SI interlock circuitry prevented reset. Given the initiating event (closure of the feedwater regulating valve) and the SI signal, all plant safety system reacted in accordance with design. The reactor tripped and the appropriate containment valves closed. There was no impact upon the health and safety of the public.
247 | 2471992007 | 1992-04-13 | QP5 | Excessive Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 25 | On April 13, 1992 at approximately 2213 hours, with the Unit operating at 25% power, a reactor trip was initiated by a turbine trip. The turbine trip occurred as a result of a high level in steam generator (SG) No. 23. The SG level excursion occurred as a result of operator actions in response to a condenser low hotwell level condition due to misalignment of condenser hotwell 22 B outlet valve CS-1-3. The operators responded to the plant trip event in accordance with established plant procedures and the plant systems responded as expected, with the exception of the motor driven auxiliary feedwater pumps (MDAFWP). MDAFWP 21 started and tripped several times within a period of approximately 74 seconds, and MDAFWP 23 did not auto start at all due to low suction pressure. This condition was rectified by the closing of condensate level control valve LCV-1128 which was opened earlier by the operators in response to the low hotwell level condition. Also, the main boiler pump was noted as cycling through trip/reset several times after the reactor trip. <br /><br /> The plant entered normal recovery procedures at approximately 2227 hours. No NRC limit was exceeded and there was no impact on public health and safety.
247 | 2471992018 | 1992-09-26 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 44 | On September 26, 1992 at 0055 hours, one of the four turbine control valves for the Main Turbine Generator closed automatically. Upon review of existing plant guidance on out-of-normal control valve configurations and discussions with engineering personnel, a controlled shutdown was commenced as a conservative measure to prevent main turbine rotor unbalance. At 0204 hours, with the unit operating at approximately 44% power, the turbine was manually tripped resulting in a reactor trip. The turbine was tripped when the previously closed turbine control valve began erratically opening and closing. <br /><br /> Upon completion of a post trip review and a further review of the events by the Station Nuclear Safety Committee, a reactor restart was initiated. <br /><br /> The generator breakers were closed on the grid at approximately 0051 hours on September 27, 1992. There was no impact on the health and safety of the public.
247 | 2471995001 | 1995-01-17 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Indian Point 2 | P | WE | PO | 89 | On January 17, 1995, with the unit operating at 89% power, a turbine trip occurred due to low autostop oil pressure. The turbine trip in turn caused a reactor trip. All automatic actions occurred as expected And the plant responded to the transient as expected with the exception of a greater than expected cooldown of the Reactor Coolant System. Manual operator action was taken to restore pressures, levels and temperatures to expected values. The cause of the low autostop oil pressure was determined to be a solenoid valve which had a degraded pilot seat. Upon completion of a post trip review and a further review by the Station Nuclear Safety Committee, a reactor restart was initiated. On January 19, 1995, during startup with the unit operating at 16% power, a turbine trip occurred due to high steam generator level. This caused an automatic feedwater isolation which includes the automatic actuation of auxiliary feedwater pumps. The cause of the high steam generator level was attributable to operator execution of manual feedwater control.
247 | 2471995016 | 1995-06-12 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 90 | On June 12, 1995, with the unit operating at 90% power, an electrical generator trip occurred due to the actuation of a pilot wire relay at the Buchanan Substation. The generator trip initiated a main turbine trip, which in turn initiated a reactor trip. As expected, the sudden loss of electrical load caused by the direct generator trip resulted in a main turbine and generator overspeed of approximately 120%. Subsequent to the trip, the main feedwater regulating valves for steam generators 21, 22 and 24 failed to close on both automatic and manual signals. The main feedwater pumps were secured by the operators which terminated feedwater flow. As reactor power decreased into the intermediate range, nuclear instrument N36 failed, requiring the operators to manually initiate the source range instruments. It was determined that the main feedwater regulating valves failed due to over torquing of the valve packing, which has since been corrected. further review by the Station Nuclear Safety Committee, a reactor restart was performed.
247 | 2471996003 | 1996-03-05 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On March 5, 1996, with the unit operating at 100% power, an electrical generator trip occurred due to the false actuation of a back-up pilot wire relay associated with the generator output feeder. The generator trip initiated a main turbine trip, which in turn initiated a reactor trip. As expected, the sudden loss of electrical load caused by the direct generator trip resulted in a main turbine and generator overspeed of approximately 120%. Subsequent to the trip, motor driven auxiliary boiler feedwater pump 23 failed to automatically start when the steam generator levels reached the automatic start setpoint for the auxiliary feedwater pumps. Motor driven auxiliary boiler feedwater pump 21 automatically started as designed and fed steam generators 21 and 22. Steam driven auxiliary boiler feedwater pump 22 automatically started as designed and was manually aligned to feed steam generators 23 and 24. A defective component of a switch in the control circuit of auxiliary feedwater pump 23 caused the failure of the pump to start. This switch component and similar switch components in other safeguards equipment control circuits were inspected and replaced as necessary. Upon completion of the switch repairs and inspections, post trip review and Station Nuclear Safety Committee reviews, a reactor and plant restart was performed.
247 | 2471996012 | 1996-05-23 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On May 23, 1996, with the unit operating at 100% power, an incorrect 6.9 kV breaker was installed and failed causing 6.9 kV Bus 4 to trip. Inspection of the breaker prior to installation was not adequate. This resulted in a loss of power to Reactor Coolant Pump 22. The reactor tripped on the loss of flow that followed the loss of the reactor coolant pump. The generator tripped 30 seconds following the reactor trip as designed. Following the generator trip, 6.9 kV Bus 3 did not transfer from the unit source of power to the offsite source of power as designed due to the concurrent loss of Bus 4. This resulted in the loss of a second reactor coolant pump and 480 V Bus 3A which tripped motor driven Auxiliary Feedwater Pump 21. The three emergency diesels started following the loss of Bus 3A. The operators manually aligned steam driven Auxiliary Feedwater Pump 22 in accordance with emergency operating procedures. Sufficient inventory was maintained in the steam generators. The reactor was safely brought to hot shutdown conditions.
247 | 2471996015 | 1996-08-19 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On August 19, 1996, with the unit operating at 100% power, a reactor trip occurred with all control rods fully inserting. This initiated a turbine trip, and the generator tripped 30 seconds following the reactor trip as designed. The cause of the reactor trip was traced to the de-energization of a logic relay which monitors the 6.9 kV breaker for Reactor Coolant Pump 24. There was no condition that would have required the breaker to open during this event, and the breaker did not open. A high resistance in a relay contact in the coil circuit of the logic relay was identified. It was determined that the most probable cause of the trip was an anomaly associated with the de-energization of this logic relay. All safety related equipment performed as expected, and the reactor was safely brought to hot shutdown conditions.
247 | 2471996016 | 1996-08-22 | QP5 | Excessive Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 21 | On August 22, 1996, during startup of the unit, approximately an hour after the generator was connected to the grid, a turbine trip occurred. This initiated a reactor trip with all control rods fully inserting. The generator tripped 30 seconds following the reactor trip as designed. The cause of the turbine trip was a high level in Steam Generator 23. This level excursion occurred during the switching of the main feedwater regulating valves from manual to automatic operation. Due to inadequate level control in the automatic mode, the operator switched back to the manual mode and attempted to close the main feedwater regulating valve that was supplying Steam Generator 23. The valve went open, although the controller was calling for the valve to close, resulting in an overfeeding of Steam Generator 23. This initiated the high steam generator level turbine trip. Since reactor power was 21% at this time, the turbine trip initiated a reactor trip. The most likely cause of the failure of the main feedwater regulating valve supplying Steam Generator 23 was debris in the instrument air line at the valve positioner. Following the reactor trip, all safety related equipment performed as expected, and the reactor was safely brought to hot shutdown conditions.
247 | 2471997002 | 1997-01-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | SU | 14 | On January 26, 1997, with reactor power at approximately 14 percent and a unit shutdown in progress, a manual turbine trip was initiated due to steam generator level variations. Feedwater regulating valves for 21, 22, 23, and 24 steam generators had been placed in manual prior to the trip due to inconsistent response experienced during the shutdown. Feedwater flow to the steam generators was being controlled primarily with 21 Main Boiler Feed Pump speed. 21 Main Boiler Feed Pump recirculation valve opened as designed on low flow, causing a reduction in feedwater to all steam generators. A manual turbine trip was initiated in accordance with management direction, which caused a further reduction in steam generator levels due to "shrink." The combined effect of reduced feedwater flow and "shrink" resulted in a low steam generator level reactor trip. All control rods fully inserted and the generator tripped 30 seconds following the turbine trip as designed. Following the reactor trip all safety-related equipment performed as required with the exception of the 21, 22, and 24 Main and 23 Low-flow Feedwater Regulating Valves which did not fully close, as required. A multi-discipline team was promptly assembled to investigate the cause of the Main and Low-flow Feedwater Regulator valve non-closures. The reactor was safely brought to hot shutdown conditions.
247 | 2471997018 | 1997-07-26 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 99 | On July 26, 1997, with the unit at 99.4 percent power, misoperation of a protective directional relay in transformer TA-5 at the Buchanan substation resulted in tripping the power transmission system load from the IP2 main generator. The load shed of the main generator's external loads caused the main turbine to trip on mechanical overspeed which in turn generated a reactor trip. The main generator electrical output to the unit auxiliary transformer increased in frequency due to the overspeed condition of the main turbine, which caused an increase in the rpm of all electrical pump motors connected to the unit auxiliary transformer at the time of the event. Approximately seven (7) seconds later an overcurrent condition on the unit auxiliary transformer tripped the electrical generator. The frequency mismatch at the time of transfer between the 6.9 kV buses powered by the unit auxiliary transformer and those powered by 138 kV supply to the station auxiliary transformer prevented automatic transfer of loads to the station auxiliary transformer. This caused loss of power to four (4) 6.9kv buses and their associated loads. Loss of power to the reactor coolant pumps (RCP's) brought the plant into a natural circulation cool down condition. The natural circulation condition lasted 40 minutes, after which a RCP was started and forced circulation was restored. Plant systems operated as designed.
247 | 2471997021 | 1997-08-23 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On August 23, 1997, with the unit operating at 100% power, a reactor trip occurred with all control rods fully inserting. This initiated a turbine trip, and the generator tripped 30 seconds following the reactor trip as designed. The cause of the reactor trip was traced to the de-energization of a logic relay which monitors the 6.9 kV breaker for Reactor Coolant Pump 23. There was no condition that would have required the breaker to open during this event, and the breaker did not open. The resistance across a relay contact in the coil circuit of the logic relay was found to vary with no observable plunger motion. The cause of this resistance variation was corrosion on the surfaces of the relay contacts. Such variation can cause intermittent interruption of the circuit. This is the most probable cause of the de-energization of this logic relay which in turn caused the reactor trip. All safety-related equipment performed as designed, and the reactor was safely brought to hot shutdown conditions.
247 | 2471999015 | 1999-08-31 | QR8 | Spurious Reactor Trip |  | X | X | [12 empty] | X |  | X | [27 empty] | Indian Point 2 | P | WE | PO | 99 | On August 31, 1999 the Instrument and Control (I&C) group was replacing a defective bi-stable PC-457A, the pressurizer low pressure trip bi-stable for Protection Channel 3. To support this maintenance, the Over Temperature Delta Temperature (OTDT) channel trip for Protection Channel 3 was placed in the trip position. A spurious electrical spike occurred on the OTDT Protection Channel 4. This made up the "two out of four" reactor trip logic causing an OTDT reactor trip. After the reactor tripped, a sustained undervoltage condition on 480 VAC bus 5A or 6A caused the station blackout logic matrix to generate a blackout signal, stripping the 480 VAC buses and reloading them onto the emergency diesel generators (EDG). Bus 6A loaded onto its EDG and then tripped off due to an over-current trip on the EDG output breaker. Battery Charger 24 is powered from bus 6A. The battery supported the DC loads for approximately 7.4 hours. During that period of time, power was not restored to Battery Charger 24. Subsequently Instrument Bus 24 was lost when the voltage on DC bus 24 became too low for Inverter 24 to provide AC power to the instrument bus. As a result, a Notification of Unusual Event (NUE) was declared based on Emergency Action Level (EAL) 7.3.1 due to an unplanned loss of approximately 75% safety system annunciators for greater than 15 minutes. The NUE was exited at 03:30 hours on September 1, 1999 when power was restored.
247 | 2472000001 | 2000-02-15 | F1 | Steam Generator Tube Rupture PWR (SGTR) | [5 empty] | X | [18 empty] | X | [20 empty] | Indian Point 2 | P | WE | PO | 99 | On February 15, 2000 at 19:29,Eastern Standard Time (EST), with Indian Point Station, Unit 2 operating at 99 percent reactor power, operators manually shut down the unit and declared an Alert due to a primary to secondary leak in 24 steam generator. The emergency response organization was activated. Operators began cooling down and depressurizing the reactor coolant system as required by procedures. 24 steam generator was isolated at about 20:34. At about 21:00, the rate of the plant cooldown that was in progress was observed to increase. Pressurizer level could not be maintained greater than 9 percent, and at about 21:05, operators manually initiated safety injection. Pressure in the reactor coolant system and 24 steam generator was equalized by 22:50.However, later events caused reactor coolant water to flow into the steam generator secondary side. The cooldown continued, including a transition to the residual heat removal system, on February 16 at 12:40. The plant was brought to cold shutdown on February 16 at 16:57, and the Alert was terminated at 18:50. There was no detectable increase in normal background levels of radioactivity as measured by offsite environmental sampling and monitoring equipment. As a result of the Alert, initial notifications to the State, local county authorities, and the NRC resident inspector were made on February 15 at 20:05. The NRC Operations Center was notified via the Emergency Notification System at 20:08. This report is being made pursuant to 10 CFR 50.73 (a)(2)(I)(A)due to the completion of a plant shutdown required by Technical Specifications as a result of the declaration of the Alert classification.
247 | 2472001007 | 2001-12-26 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On December 26, 2001 at 0720 hours Indian Point Unit 2 experienced an automatic reactor trip with all control rods fully inserting. The trip was initiated by a main turbine trip on auto stop oil. The auto stop oil turbine trip was caused by a trip of over frequency relays actuated by a disturbance associated with the 345 Kv Bus W93. This disturbance caused generator output breaker 9 to open. The cause of the over frequency relays actuation was failure of the blocking relay [EIIS:FK:68] on Consolidated Edison's 345 Kv feeder Y94. This failure caused the breakers on Y94 to open causing loss of load to the main generator and an over frequency trip. The over frequency trip caused the turbine trip. The turbine trip resulted in the generator trip. The generator trip caused the Indian Point 2 345 Kv generator output breaker 7 to open. The resultant trip placed the plant in natural circulation with 480-volt buses 2A and 3A de-energized as per design. All three Emergency Diesel Generators (EDGs) started and buses 2A and 3A were manually energized by 22 EDG, this was an expected response. 480-volt buses 5A and 6A remained energized from off-site sources during this event. No steam generator or pressurizer safety valves lifted and actuation of the Safety Injection System was not required. No radioactive release to the environment occurred as a result of this transient.
247 | 2472003003 | 2003-04-28 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On April 28, 2003 at 1648 hours Indian Point Unit 2 experienced an automatic reactor trip with all control rods fully inserting. The trip was initiated by a main turbine trip on auto stop oil. The auto stop oil turbine trip was caused by a trip of the over frequency relays actuated by a disturbance associated with the 345kV North Ring Bus at the Buchanan Substation and the Consolidated Edison 138kV system. Following the grid disturbance breakers 11 and 7 opened followed by a Phase A ground fault on breaker F7. When Consolidated Edison attempted to re-close breaker 11, a relay [EIIS:FK:681] malfunction occurred causing Unit 2 output breaker 9 to open resulting in a turbine trip. The resultant trip placed the plant in natural circulation with 480-volt buses 2A and 3A de-energized as per design. All three Emergency Diesel Generators (EDGs) started and buses 2A and 3A were manually energized by 22 EDG, this was an expected response. 480-volt buses 5A and 6A remained energized from offsite sources during this event. No steam generator or pressurizer safety valves lifted and actuation of the Safety Injection System was not required. No radioactive release to the environment occurred as a result of this transient.
247 | 2472003004 | 2003-08-03 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On August 3, 2003, at approximately 0430 hours, Indian Point Unit 2 experienced an automatic reactor trip event (JE) initiated by a main turbine trip on auto stop oil . The auto stop oil turbine trip was caused by an electrical disturbance associated with the 345kV North Ring Bus at the Buchanan Substation. Subsequent failure of a carrier power supply {JX} prevented the generation of a transfer block signal, which would have prevented the occurrence of this event. Prior to this event, Indian Point Unit 2 was operating at 100 percent, steady-state power conditions. During the unit trip the internal 6.9kV buses were de-energized resulting in a loss of all four (4) reactor coolant pumps (RCP). This placed the plant in natural circulation. The loss of the internal 6.9kV buses resulted in the loss of 480V buses 2A and 3A as per plant design. All three (3) emergency diesel generators (EDG) {EK) started and buses 2A and 3A were manually energized by 22EDG. No steam generator or pressurizer safety valves lifted and actuation of the safety injection system was not required. No radiological releases or adverse safety implications to the public occurred as a result of this event. In accordance with 10 CFR 50 .72 (b)(3)(iv)(A), the NRC was notified (Event Number 40045) of this event at 1110 hours on August 3, 2003. This report is submitted pursuant to 10 CFR 50 .73 (a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of the reactor protection system.
247 | 2472003005 | 2003-08-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Indian Point 2 | P | WE | PO | 100 | On August 14, 2003, at approximately 1611 hours during 100% steady state power, Indian Point Unit 2 experienced an automatic reactor trip initiated as a result of low reactor coolant loop flow due to the trip of the 22 Reactor Coolant Pump (RCP) breaker. The 22 RCP breaker tripped due to electrical supply bus under-frequency caused by an unstable off-site power grid (Northeast blackout). Off-site power was lost and all three Emergency Diesel Generators started and energized their assigned safety buses. Main feedwater isolated and the Auxiliary Feedwater (AFW) pumps automatically started. A Notification of Unusual Event (NUE) was declared at 1625 hours, in accordance with the Emergency Plan when off-site power was unavailable for greater than 15 minutes. The NUE was terminated on August 15, at 0210 hours, when off-site power was restored. The cause of the event was a loss of off-site power due to an unstable power grid. Corrective actions to address the cause of the event included a post trip review, root cause evaluation and plant assessment. There were no nuclear safety concerns exhibited during the event and all fission product barriers remained intact. There was no impact on the health and safety of the general public.
247 | 2472004001 | 2004-09-01 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On September 1, 2004, at approximately 0005 hours, Operations manually tripped the reactor as a result of oscillating Feedwater (FW) flow and 22 Steam Generator (SG) level with flow perturbations and FW pipe movement in the Auxiliary FW Pump Building. All control rods fully inserted and all primary systems functioned properly. The 22 FW flow control valve (FCV)-427 failed to fully close. Operators initiated 22 FW isolation by closing the 22 FW isolation valves. At 0021 hours, a 22 SG High-High level trip was actuated at 73% SG level initiating closure of the Main FW pump discharge valves and Main FW and Low Flow FW regulating and isolation valves. The plant was stabilized in hot standby with decay heat being removed by the main condenser. Off site power remained available and therefore the emergency diesel generators did not start. The Auxiliary FW (AFW) system automatically started as a result of a SG low level normally experienced on trips from full power. The cause of the event was a disengaged valve cage in FCV-427 from the valve body web. The cause of the valve cage loosening was improper installation in 1997 due to inadequate guidance in the maintenance procedure used to verify that the cage was fully seated and properly torqued into the valve body web. Significant corrective actions were inspection and repair of FCV-427 with revised guidance and revision of the valve maintenance procedure (AOV-B-012-A) to incorporate steps to verify that the cage is fully engaged and torqued into the valve body. The event had no effect on public health and safety.
247 | 2472004002 | 2004-09-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On September 24, 2004, at approximately 11:55 hours, Operations manually tripped the reactor as a result of decreasing 23 Steam Generator (SG) level. Prior to the event Control Room(CR) operators observed decreasing 23 SG level and received an alarm for 23 SG level control deviation. CR operators attempted manual control of 23 FW regulating valve(FRV) FCV-437 without success in restoring SG level. The 23 SG level continued to decrease and as directed, the CR operator tripped the reactor at 15 percent SG level. All control rods fully inserted and all primary systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. Offsite power remained available therefore the emergency diesel generators did not start. The Auxiliary FW system automatically started as a result of a SG low level due to shrink effect. The cause of the event was de-energization of Solenoid Operated Valve (SOV)FCV-SOV-437-E due to disconnection of wiring to the SOV coil causing the SOV to fail open resulting in closure of 23 FW FCV-437. The failed connection was caused by the in correct orientation of the SOV due to a modification that lacked sufficient information due to a failure to follow the Planning and Engineering procedure for the modification and lack of a questioning attitude. Significant corrective actions were replacement of the FCV-437-SOV-E solenoid, inspection of remaining SOV connections and coaching on maintaining a questioning attitude. Planning and Engineering procedures are to be reviewed and revised as necessary. The event had no effect on public health and safety
247 | 2472004005 | 2004-11-26 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 92 | An automatic Reactor Trip occurred on November 26, 2004, at 1322 hours, due to a Main Generator/Turbine trip as a result of low stator cooling water pressure from an erroneous low inlet pressure trip on the Main Generator Stator Cooling Water System (SCWS). All control rods fully inserted and all primary systems functioned properly. The Auxiliary Feed Water (AFW) system automatically started as a result of a Steam Generator low level due to shrink effect. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. Offside power remained available therefore the emergency diesel generators did not start. The cause of the event was an incorrect pressure washstand for the SCWS due to inadequate integrated system and post-work testing and setup of the system, inadequate operational procedure guidance for start-up/fill and venting of SCWS and inappropriately attempting to adjust SCWS control valve Y-63. Significant corrective actions included performance of a setup process of the SCWS in accordance with engineering's evaluation and recommendations including setting of the SCWS flow control valve Y-63 hot at 465 gpm (range 454-477) before plant re-start. An integrated SCWS post work test procedure will be prepared including complete development of I&C PM's for the post work test procedure, and improvements in operational procedure guidance. The event had no effect on public health and safety.
247 | 2472006001 | 2006-03-01 | QR3 | Reactivity Control Imbalance | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On March 1, 2006, at 1435 hours, operators initiated a manual reactor (RT) trip due to 12 of 53 control rods (CRs) dropping into the reactor core. All primary safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained in-service. The Auxiliary FW system automatically started as a result of the RT. The cause of the event was personnel error due to inadequate work practices and inadequate interface requirements. Supplemental personnel were erecting scaffolding in the cable spreading room where the power cabinets for the CRs are located. During this work activity, a scaffolder inadvertently bumped the disconnect switch associated with rod control power cabinet 1AC. Those CRs that lost power dropped into the core. Inadequate preparation practices resulted in not having a ladder required for the work and resulted in a worker stepping on the cabinet. The computer work flow process bypassed the work management process (procedure IP-SMM-WM-100) which requires operations/planning to assess risk and authorize work. Significant corrective actions included coaching personnel on management expectations on work control and interim measures requiring operations review and approval of scaffold work orders. The work flow process will be revised to match the work management procedure; the scaffold procedure will be revised to require operations notification for scaffold work and the pre-job briefing checklist will require identification and staging of tools. The event had no effect on public health and safety.
247 | 2472006003 | 2006-08-23 | QR3 | Reactivity Control Imbalance | [45 empty] | Indian Point 2 | P | WE | PO | 68 | On August 23, 2006, at 1035 hours, control room (CR) operators initiated a manual reactor trip (RT) due to a mismatch between reactor power and turbine load. Power was initially reduced to 77% for loss of Heater Drain Tank (HDT) pumps then further reduced per Technical Specification 3.2.3 due to axial flux difference outside its required operating limit. CR operators initiated a RT during the further power reduction due to a mismatch between reactor power and turbine load from cyclic operation of the high pressure steam dump (HPSD) valves. All primary safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained in-service. The Auxiliary Feedwater system (AFWS) started due to steam generator (SG) low level from shrink effect. Feedwater (FW) isolation and actuation of the AFWS occurred due to a 22 SG high level as a result of overfeed from leakby through the 22 FW low flow bypass valve. The cause of the RT was improper gain settings on the HPSD temperature modules which caused the HPSDs to respond increasingly disproportional to the input signal. The improper settings were attributed to inadequate review during implementation of actions for the Power Uprate Project in 2004. The cause of the loss of the HDT pumps was a failed HDT level controller power supply. Contributing causes included incorrect information in the HPSD module calibration procedure and inadequate procedural guidance. Corrective actions include properly setting the HPSD modules, replacement of the HDT power supply, preparation of a calibration procedure for the HPSD modules, calibration training and procedure revisions. The event had no effect on public health and safety.
247 | 2472006005 | 2006-11-15 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On November 15, 2006, at 1400 hours, with reactor power at 100%, an automatic reactor trip (RT) was initiated as a result of a turbine trip due to a main generator exciter protective trip during troubleshooting of the exciter Generrex power supply. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink effect. A post transient evaluation was performed prior to restart. The apparent cause was believed to be a momentary loss of electrical ground to the alarm cards that monitor primary and redundant Generrex power supplies for the main generator exciter. After replacement of the #1 power supply circuit card, resistance measurements of a pin electrically connected to a common ground resulted in an output spike in the redundant power supply. The operating power supply spiked low dropping the voltage below the trip set point which initiated a main generator exciter protective trip. A screw terminal where the grounds are mounted was found to be loose. Corrective actions included providing proper connections for the common ground, repairs to the Generrex +15V/#1 Power Supply and checking all remaining +/-15 Volt pins and terminal points for proper operation. The Generrex power supply #1 will be replaced with a refurbished power supply. The event had no effect on public health and safety.
247 | 2472007004 | 2007-02-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On February 28, 2007, control room operators manually initiated a reactor trip (RT) at approximately 0633 hours, after receiving speed control trouble alarms for the 21 and 22 Main Boiler Feedwater Pumps (MBFPs) and observing decreasing MBFP speed and steam generator (SG) levels. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink effect. The cause of the RT was loss of main feedwater (FW) flow due to the failure of the power supply (PQ-408B) for the MBFP suction pressure transmitter (PT-408B). The power supply failed due to a failure of its filter capacitors as a result of age degradation. The root cause of the power supply failure was insufficient verification of the existing plant programs to address capacitor age degradation due to human error. Significant corrective actions include replacement of power supply PQ-408B and pressure transmitter PT-408B. An instrument power supply Preventive Maintenance (PM) will be implemented in accordance with the ENS PM template, and a capacitor program will be developed and implemented to address age degradation of capacitors. The event had no effect on public health and safety.
247 | 2472008001 | 2008-03-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 95 | On March 23, 2008, at 2216, with reactor power at 94.5%, as part of a planned coast down for a scheduled refueling outage, a manual reactor trip (RT) was initiated as a result of 22 Main Boiler Feed Pump (MBFP) rapid speed reduction causing lowering steam generator levels. All control rods inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as off-site power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink. The direct cause was radio frequency interference (RFI) from camera use near a MBFP speed control signal processer. The root cause of the event was lack of knowledge that a digital camera is an RFI source that can produce adverse effects on digital control components. Contributing causes were a poor choice of the controlling procedure for camera activity, poor change management in implementing the review requirements without providing adequate review tools, failure to follow procedure. Corrective actions include preparation of specific procedural guidance on electronic interference sources, creating a change management plan to track implementation of the new procedure and process, perform a needs analysis for training, and a site communication of this event and lessons learned from the event. The event had no effect on the public health and safety.
247 | 2472008003 | 2008-04-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 35 | On April 21, 2008, during power ascension following a scheduled refueling outage, Operations initiated a manual reactor trip as a result of observing decreasing steam generator levels and a turbine runback. Troubleshooting discovered a failed bistable permissive (PC-412B-1) in the loss of main boiler feedwater pump (MBFP) main turbine runback system. The system circuitry uses MBFP speed signals, main turbine steam inlet pressure representing percent power, and an Arm/Defeat switch to actuate a runback. The failed bistable gave the runback system a signal that the turbine was greater than 76.5 percent. With one of two MBFPs below the runback speed limit and the Arm/Defeat switch Armed, the circuit coincidence for runback was completed. The direct cause of the event was a failed bistable for main turbine steam inlet pressure. The causes identified were weak procedural guidance for placement of the Arm/Defeat switch in the Defeat position at power levels below 76.5%, failure to follow the startup procedure due to human performance error, and failure to document status control per the intent of the procedure for conduct of operations. Corrective actions include replacement of two turbine inlet pressure bistables, revision of plant operating procedures for Arm/Defeat switch positioning and coaching involved operators on procedure use and adherence. Management expectations will be re-enforced on expected actions when components are not in needed positions, operations will be briefed on the event and expectations, and training will revise the simulator for event and include lessons learned in operator training. The event had no effect on public health and safety.
247 | 2472009002 | 2009-04-03 | QR6 | Manual Reactor Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On April 3, 2009, Control Room Operators initiated a manual reactor trip as a result of observing decreasing steam generator (SG) levels following loss of the 21 Main Boiler Feedwater Pump (MBFP), a large steam flow to feedwater flow mismatch, and failure of the main turbine to automatically runback. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser which was subsequently shifted to the atmospheric dump valves. The direct cause of the decreasing SG levels was the trip of MBFP 21 due to a autostop oil tubing/fitting failure on the MBFP Autostop oil header. The root cause was improper tubing installation due to poor worker practices. A straight tubing installation with no bends to allow for expansion and contraction or to allow for motion under load resulted in vibration induced stress failure. The cause of the turbine runback failure was indeterminate but most likely an intermittent failure of the digital speed tachometer assembly. Corrective actions included replacement of the tubing for both MBFPs reconfigured to meet established installation requirements, performance of an independent equipment failure evaluation of the failed fitting, and implementation of a troubleshooting plan on the runback feature to confirm functionality. Five year maintenance requalification training for Swagelok fitting installation will be established and supplemental worker training for Swagelok fitting installation will be developed. The event had no effect on public health and safety.
247 | 2472009005 | 2009-11-02 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On November 02, 2009, an automatic reactor trip (RT) was initiated as a result of a turbine-generator protective trip (86P Lockout Relay). All control rods fully inserted and all required safety systems functioned properly. The Main Steam Isolation Valves (MSIVs) were closed after reports that one of the four turbine stop valves did not indicate fully closed. The plant was stabilized in hot standby with decay heat being removed by the Steam Generators (SG) via the Atmospheric Steam Dump Valves. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. The direct cause was a high resistance connection on the common ground terminal between the Generrex power supplies and alarm cards. The cause of the event was a poor Original Equipment Manufacturer (OEM) design of the common ground wiring connections on the Generrex power supply distribution block. Corrective actions included repairs to the Generrex power supply connection and installation of a second ground connection in the exciter cabinet. A Generrex system upgrade is planned for the refueling outage 19 in the spring of 2010 which includes upgrading to solid state power supplies and testing the ground wire. The event had no effect on public health and safety.
247 | 2472010001 | 2010-01-11 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On January 11, 2010, an automatic reactor trip (RT) was initiated as a result of turbine trip due to a loss of main generator excitation. The plant was stabilized in hot standby with decay heat being removed by the main condenser {SG}. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. Prior to the RT one of four rectifiers (#24) of the main generator excitation system was believed to be electrically isolated and its cooling was isolated to stop an existing cooling leak. Investigations determined the rectifier disconnect switch that was believed to be open remained in a closed condition. This condition allowed current to continue to flow through the 24 rectifier diodes and because there was no cooling water the diodes failed resulting in a loss of field voltage to the exciter actuating a trip signal. The direct cause of the RT was loss of generator field excitation due to loss of two diodes within the # 24 Generrex rectifier cabinet. The root cause was failure of management to implement critical decision making. A significant contributing cause was an improper lubricant used on disconnect switch contact surfaces. Corrective actions included a brief of station personnel on the event and lessons learned. A Generrex upgrade modification will be implemented including new disconnect switches in the spring 2010 refueling outage, case study training will be completed, computer based training (CBT) from the case study will be prepared and included in training curriculum, Alarm Response Procedure (2-ARP-SJF) and System Operating Procedure (2-SOP-24.4) will be revised for operation of the new disconnect switches, and maintenance personnel will be instructed on appropriate application of greases. The event had no effect on public health and safety.
247 | 2472010007 | 2010-09-03 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 41 | On September 3, 2010, during a scheduled plant shutdown, an automatic reactor trip (RT) was initiated as a result of a turbine trip due to a high steam generator (SG) water level. All control rods did not indicate fully inserted as the Individual Rod Position Indicator (IRPI) for rod H-8 indicated 38 steps withdrawn and its rod bottom light failed to light. Rod H-8 was verified to be fully inserted by alternate means. All primary systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as designed due to automatic trip of the MBFPs as a result of closure of the MBFP discharge valves from the SG high level trip. The direct cause of the RT was a turbine trip on a high SG level. The root cause was inadequate design control of the proportional band and reset tuning settings for critical plant controllers. There was less than optimum controller settings on the MBFP speed controller, Feed Regulatory Valve (FRV) flow controllers, and the SG level controllers for low power operation. Significant corrective actions include: I&C procedures developed from I&C Preventive Maintenance documents have been reviewed to ensure that the instrument calibration requirements have been transferred into the I&C procedures, a list of critical controllers was generated and the Equipment Data Base (EDB) updated with known existing settings, I&C procedures will be reviewed to identify changes to ensure controller calibrations maintain required settings and procedures will be revised to incorporate testing of critical parameters, an engineering evaluation will be issued and the EDB updated in the work control program with findings on controller settings. The event had no effect on public health and safety.
247 | 2472010009 | 2010-11-07 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Indian Point 2 | P | WE | PO | 100 | On November 7, 2010, an automatic reactor trip (RT) was initiated as a result of a turbine-generator trip due to actuation of the main generator primary and back-up lockout relays. All control rods fully inserted and all primary systems functioned per design except for the 138 kV Station Auxiliary Transformer tap changer. The plant was stabilized in hot standby with decay heat being removed by the main condenser {SG}. Based on reports of two explosions an Alert was declared in accordance with the emergency plan which was terminated at 22:18 hours. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. The direct cause of the RT was due to actuation of the 86P and 86BU relays that sensed a fault from the failure of 21 main transformer (MT) as a result of a low impedance fault of the 345 kV Phase B bushing. The root cause was an internal failure of the phase B bushing due to a vendor design/manufacturing deficiency. Corrective actions include replacement and acceptance testing of the 21 MT, external visual inspections of the 22 MT HV bushings, Unit Auxiliary Transformer (UAT), Iso-phase bus and 345 kV feeder W95, testing of the 22 MT, UAT, Iso-phase bus and HV components. Damaged HV components were replaced. The bushings for the 21 and 22 MT were replaced with another manufacturers bushing. The event had no effect on public health and safety.
247 | 2472012006 | 2012-06-06 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On June 6, 2012, an automatic reactor trip (RT) was initiated as a result of a main Turbine-Generator trip due to a trip of the Generator backup lockout relay 86 BU on loss of main generator field excitation. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. Investigations determined the 86 BU relay actuation was triggered by relay 62BU1/AUX which serves as a time delay for the KLF-40 loss of field relay. The actuation of the loss of field relay was in response to a loss of generator excitation field from the Generrex voltage regulator system. The direct cause of the RT was loss of generator field excitation due to failure of the Generrex C-Phase Trigger Generation Card. The root cause was indeterminate but most likely due to premature failure of the U5 operational amplifier on the C-Phase Trigger Generation Card causing the U3 and U6 operational amplifiers to also degrade. Corrective actions included replacement of the C-Phase Trigger Generator and AC/DC Gate cards with new cards which were then calibrated and monitored for proper operation, and shipped failed card to a vendor for an equipment failure analysis. The event had no effect on public health and safety.
247 | 2472013001 | 2013-02-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 85 | On February 13, 2013, operators initiated a manual reactor trip (RT) as a result of lowering steam generator (SG) levels. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser {SG}. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. An investigation determined the decreasing SG levels was due to reduced main feedwater (FW) flow from a loss of Heater Drain Tank (HDT) pumps. The HDT pumps tripped during valve diagnostics on HDT level control valve LCV-1127B which resulted in HDT Large Dump valves failing open. The open HDT large dump valves resulted in low HDT level and trip of the HDT pumps. The HDT large Dump valves failed open when the current/pressure (I/P) lead was lifted during air operated valve (AOV) diagnostics per procedure 0-IC-PC- AOV. Loss of HDT flow to the main feedwater pumps (FWPs) caused the FWPs speed controller cutback to reduce FW flow to the SGs. The root cause (RC) was inadequate procedure design and content. Corrective actions from the RC will be to revise Maintenance procedures 0-IC-PC-AOV and 0-VLV-404-AOV to: 1) Eliminate conditional steps for equipment setup that allows changes to work scope to be made in the field without proper review prior to performing work, 2) Eliminate the subject Caution block, and 3) Include signature blocks for review of drawings and validation that lifting a I/P lead or disconnecting the instrument tubing will not affect any other valve or component. The event had no effect on public health and safety.
247 | 2472013003 | 2013-07-03 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Indian Point 2 | P | WE | PO | 100 | On July 3, 2013, operators initiated a manual reactor trip as a result of lowering steam generator (SG) levels due to the loss of feedwater (FW) from the trip of both main FW pumps. A11 control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as expected. Investigations determined the decreasing SG levels were due to a loss of main FW flow as a result of the closure of the FW regulating valves. The FW regulating valves closed due to a loss of instrument air (IA) pressure. The IA pressure was lost when a two inch copper IA tubing in the 22 Main Transformer moat separated at a soldered coupling. Prior to the event piping lines including the IA line buried in the main transformer moat were excavated and temporary supports installed. The apparent cause was poor legacy workmanship assembling the IA tubing coupling during original plant construction. The IA tubing was not fully inserted into the coupling resulting in reduced joint strength. Corrective actions included reassembly and soldering of the IA joint with full insertion, acoustic emission and snoop testing on repaired coupling. Axial and thrust restraints were installed on the IA line in the moat. A caution was placed in the Buried Piping Program database associated with buried copper tubing identifying the potential for the separation of soldered joints when the line is excavated and the need for restraints or other contingencies to minimize the probability of a line separation. The event had no effect on public health and safety.
247 | 2472015003 | 2015-12-05 | QR3 | Reactivity Control Imbalance | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On December 5, 2015, control room operators initiated a manual reactor trip (RT) after observing indications consistent with multiple dropped control rods (CR) following an alarm for the trip of Motor Control Center (MCC)-24/24A. No Control Rod indication was available due to MCC-24 being de-energized. All primary safety systems functioned properly except the primary rod control cabinet power supply (PS1) which was in a degraded condition prior to the event and failed to function as required. The plant was stabilized in hot standby. There was no radiation release. The Auxiliary FW system automatically started as designed. The direct cause of the event was loss of MCC-24 due to an internal fault at the line side leads at cubicle 2H where they connect to the bucket stab assemblies (load side fault). This caused the supply breaker feed to open per design and clear the fault. The de-energization of MCC-24 removed the functioning backup Control Rod (CR) power supply and the remaining degraded primary power supply failed to function as required. The apparent cause was an unanticipated loss of power to the CR system due to the degradation of the primary CR power supply (PS1) which failed to function when the operating power supply (PS2) was lost. MCC-24/24A was lost due to a design error that allowed the positioning of a mounting plate too close and obstructing the line side wiring resulting in contact. Vibration over time resulted in degraded wiring insulation which eventually shorted. Corrective actions included inspection and testing of the MCC-24 bus and control wiring. The degraded Rod Control power supply (PS1) was replaced. Maintenance procedures will be revised to provide more in-depth inspection criteria. The event had no effect on public health and safety.
247 | 2472016009 | 2016-07-06 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On July 6, 2016,Instrument and Control (I&C) technicians were preparing to perform 2-PT-2M3A (RPS Logic Train B Actuation Logic Test and Tadot). Prior to starting the test, the I&C technicians were unable to locate key #184 that was identified in the test as associated with the reactor trip breaker B bypass key switch. Control Room staff recommended obtaining key #183 associated with reactor trip breaker A bypass key switch to use in lieu of key #184. To ensure the key would work prior to starting the test, the train B bypass key switch was positioned by an I&C technician to the Defeat position. Because reactor trip Bypass Breaker B was in the racked out position, when the key switch was taken to the Defeat position, it caused the normal Reactor Trip Breaker B to open, which initiated a reactor trip (RT) and auxiliary feedwater system actuation. The direct cause was an I&C technician turned the key interlock to defeat on switchgear Channel B Reactor Protection Logic without having the BYB Bypass breaker racked in and closed. The root cause was Indian Point personnel emphasized work culture production goals without fully recognizing the need to maintain fundamental standards and expectations for nuclear workers. Key corrective actions included site all-hands meeting discussing the event, lessons learned, reinforced expectations and the Fleet Refocus Initiative. As an interim action, all essential work that effects generation was required to have direct oversight by a superintendent or above, all work start authorizations provided by operations undergo a work challenge utilizing a new checklist from this event. Complete the actions associated with the Fleet Refocus Observation program. The event had no effect on public health and safety.
247 | 2472017001 | 2017-06-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On June 26, 2017, Operations commenced a downpower from 100 percent to 93 percent reactor power to support performance of the Main Turbine Stop and Control Valve Test. With reactor power at 94 percent, the 22 Main Boiler Feed Pump Turbine (MBFPT) speed control trouble alarm annunciated coincident with pump speed swings of 800 revolutions per minute (rpm). The operators ceased the downpower and placed the 22 Main Boiler Feedwater Pump (MBFP) in Manual speed control to control the rpm swings. This was unsuccessful, and the rpm swings continued. The 22 MBFPT low pressure (LP) governor valves were observed to be cycling from full-closed to full-open. The decision was made to take local pneumatic control of the 22 MBFP to stabilize pump speed. Two minutes after establishing local pneumatic control, the LP governor valves went to full closed. With the rapid reduction in 22 MBFP speed, the pump was no longer delivering feedwater flow to the SGs. An automatic main turbine runback signal should have been generated on a low speed signal; however, there was no turbine runback actuation. In response, the operators commenced a manual runback to reduce main turbine load, but the decreasing SG levels reached 15 percent, and at 1531 hours a manual reactor trip was initiated. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The direct cause of the reactor trip was that the shoulder screws used on the 22 MBFPT LP governor valve servomotor linkage had backed out and detached. This caused the LP governor valves to fail closed, shutting off the turbine steam supply. This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission (NRC) on June 26, 2017 under 10 CFR 50.72(b)(2)(iv)(B), 50.72(b)(2)(xi), and 50.72(b)(3)(iv)(A).
247 | 2472018002 | 2018-04-19 | QR6 | Manual Reactor Trip | [45 empty] | Indian Point 2 | P | WE | PO | 8 | On April 19, 2018, at 2100 hours, during initial plant startup following the Spring 2018 refueling outage (2R23), Indian Point Unit 2 commenced performance of the main turbine generator startup procedure to conduct turbine overspeed testing. At 2107 hours, the control room received main feedwater supervisory and panel alarms, and the main turbine control valves were observed to have opened rapidly. The unexpected rapid opening of the turbine control valves caused steam flow to increase, which in turn, caused all four steam generator water levels to swell. The high steam generator levels initiated an automatic main feedwater isolation and main turbine trip, with both Main Boiler Feedwater Pumps (MBFPs) tripping on closure of their discharge valves as part of the main feedwater isolation actuation. At 2108 hours, with reactor power at 8 percent and no MBFPs running, a manual reactor trip was inserted by the control board operators in accordance with the abnormal operating procedure for loss of main feedwater. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System (AFWS) automatically started as expected on the tripping of the MBFPs to maintain steam generator inventory. The direct cause of the event was main turbine control oil stop valve LO-Z being out of its required position (closed instead of open). The root cause was main turbine generator startup procedure (2-SOP-26.4) provided a weak barrier to maintain the proper configuration of the main turbine control oil system. Corrective actions primarily involved the resolution of configuration control and management vulnerabilities. <br /><br /> This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission on April 19, 2018 under 10 CFR 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A).
247 | 2472019001 | 2019-03-15 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 100 | On March 15, 2019 at approximately 1300 hours Eastern Standard Time, Indian Point Unit 2 experienced an automatic reactor trip on a turbine trip, which was in response to a main generator trip. The main generator trip was initiated by actuation of the generator Protection System due to a main generator loss of excitation. <br /><br /> All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as expected on steam generator low level to provide feedwater flow to the steam generators. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The direct cause of this event was a failure of both diodes in the C-phase middle diode stack of the 24 Rectifier. The root cause of this event was the fact that the power diode test method was unable to detect component degradation. <br /><br /> This event had no effect on the public health and safety. This event was reported to the Nuclear Regulatory Commission on March 15, 2019 under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(2)(iv)(B) as an event that resulted in the automatic actuation of the Reactor Protection System when the reactor is critical and a valid actuation of the Auxiliary Feedwater System.
247 | 2472019002 | 2019-03-24 | QR5 | Turbine Trip | [45 empty] | Indian Point 2 | P | WE | PO | 95 | On March 24, 2019 at approximately 1445 during a power ascension from a previous trip with indicated reactor power at approximately 96%, the reactor automatically tripped on a turbine trip due to a direct trip from the Main Generator regulator cubicle. All control rods fully inserted and plant equipment responded normally to the unit trip. This reactor protection system (RPS) actuation was reported under 10 CFR 50.72(b)(2)(iv)(B). <br /><br /> The auxiliary feedwater system actuated following the automatic trip as expected. This specified system actuation was reported under 10 CFR 50.72(b)(3)(iv)(A). During the event offsite power remained available and stable. No primary or secondary reliefs lifted, and all required safety systems functioned properly. The plant was stabilized in hot standby (Mode 3) with decay heat being removed via the steam generators to the atmospheric steam dumps.<br /><br /> This event had no effect on the public health and safety.
249 | 2491987006 | 1987-03-21 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 99 | On March 21, 1987 at 1125 hours with Unit 3 at 98.5% power, a full reactor Generator Load Reject scram signal, followed by Group II and III isolations, was received. The scram was reset at 1134 hours. <br /><br />The root cause of the event was personnel error. At the time of the scram, Substation Construction personnel were pulling cables through a cable tray in the Unit 2/3 Auxiliary Electric Room and an electrical worker jarred panel 903-29 causing SGC 12A main generator negative sequence relay to trip, thus causing the scram. <br /><br />The safety significance of the event was minimal since the Reactor Protection System (RPS) performed as designed. There were no equipment malfunctions or degraded equipment as a result of this event. <br /><br />As corrective actions, Substation Construction personnel discussed the scram and its cause and were instructed to exercise care when working in the Auxiliary Electric Room and anytime near sensitive equipment. Dresden Station personnel and Operational Analysis Department performed a walkdown of the Auxiliary Electric Room and identified all cabinets containing sensitive equipment. The cabinets will be posted to require the Shift Engineer's approval before performing any work. Also, an administrative procedure will be developed to address the proper precautions when working in potential reactor trip areas throughout the plant. The last previous event related to instrument jarring or vibration was Licensee Event Report #85-02 on Docket #050249.
249 | 2491987010 | 1987-04-09 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Dresden 3 | B | GE | PO | 43 | On April 9, 1987 at 2335 hours with Unit 3 in the run mode at approximately 43% rated thermal power, the reactor was manually scrammed due to high condensate demineralizer inlet temperature of 130 degrees Fahrenheit and main condenser low vacuum decreasing to the scram setpoint of 23 inches of mercury. <br /><br /> The root cause of the event was component failure. The "C" low pressure turbine bearing cone waste water and oil drain to the Turbine Building equipment sump was determined to have broken inside the condenser. <br /><br /> The safety significance of the event was minimal since the Reactor Operators and Shift Supervisors controlled the plant in a conservative condition in accordance with approved procedures for loss of condenser vacuum. <br /><br />Corrective actions were to cut the turbine bearing cone drains and install plugs at the inlet and outlet for each low pressure turbine bearing cone. Repairs were completed under Work Request D64292. <br /><br />A similar previous event was reported by Licensee Event Report #86-16 on Docket #050237.
249 | 2491987011 | 1987-05-12 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Dresden 3 | B | GE | PO | 99 | During normal operation at 99 percent power at 0209 hours on May 12, 1987, an automatic reactor scram and Group II and Group III Primary Containment isolations were received from a low reactor water level signal. Prior to the reactor scram the Reactor Feed Pumps (RFPs) had automatically tripped on low suction pressure. Reactor water level subsequently decreased to the low level setpoint, resulting in the automatic reactor scram and Primary Containment isolations. Upon investigation it was determined that the root cause of the event was an automatic 3C Condensate Booster Pump Trip on instantaneous motor overcurrent. <br /><br />Corrective actions will include replacement of the 3C Condensate Booster Pump Motor, review of possible design changes, and review of this event with licensed personnel. The safety significance of this event was minimal because the automatic low reactor water level scram occurred as designed, thus ensuring sufficient inventory was maintained in the reactor vessel. The Emergency Core Cooling Systems (ECCS) were also available to provide reactor vessel makeup if necessary. A previous event involving a low reactor water level scram is recorded in Reportable Occurrence #87-8 on Docket #050249.
249 | 2491987012 | 1987-07-11 | QP5 | Excessive Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 3 | B | GE | PO | 25 | On July 11, 1987 at 0210 hours the Dresden Unit 3 reactor scrammed from 25% rated thermal power following an automatic primary containmant Group I isolation. Reactor power was being reduced in preparation for separating the unit from the grid for repairs to the main generator neutral grounding transformer. The root cause of the event was feedwater system instabilities which occurred while operating the feedwater level control (FWLC) system in three-element mode at low power levels. Vibrations at the feedwater regulating station induced a malfunction of the 3A feedwater regulating valve; increasing reactor water level initiated an automatic trip of the main turbine. Trip of the main turbine is believed to be the source of vibrations to instruments which initiated the Group I isolation and resulting reactor scram. Safety significance was minimal due to the availability of the high pressure coolant injection system to supply reactor inventory if necessary. Corrective actions to prevent recurrence include procedural changes and evaluation of new instrument rack designs. A previous event involving an automatic turbine trip due to FWLC problems on Dresden Unit 2 is listed under Reportable Occurrence 87-016 on Docket #050237.
249 | 2491987013 | 1987-08-07 | QR6 | Manual Reactor Trip | [45 empty] | Dresden 3 | B | GE | PO | 30 | On August 7, 1987 at 0808 hours with reactor power at 30% and a unit shutdown in progress, significant oscillations in feedwater and condensate system pressures were observed. A 3A feedwater regulating valve (FWRV) lockout was received in addition to high vibration alarms for the reactor feedwater pumps (RFP) and the feedwater regulating station. The unit shutdown was caused by failure of containment vent valve AO3-1601-63 to this Standby Gas Treatment System. <br /><br />The piping vibrations caused an instrument line break on the 3C RFP piping and a drain line break in the reactor water cleanup (RWCU) system. The reactor was manually scrammed to allow for isolation of the leaks. During cooldown, a Group V primary containment isolation occurred which resulted in a second reactor scram conditions on low reactor water level at 1029 hours. The vent valve failure was attributed to air operator wear and the 3A FWRV lockout was caused by a shorted coil on 3A FWRV air supply solenoid valve. Further testing was performed to determine the cause of the feedwater oscillations and Group V isolation. The RFP and RWCU piping, and the FWRV air operator were repaired. The FWRV solenoid valve was replaced. <br /><br />The safety significance was minimal since venting of the containment can b accomplished by utilization of the reactor building ventilation system and emergency core cooling systems were available. A previous occurrence is documented in LER 050-249/87-12.
249 | 2491987016 | 1987-09-28 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 3 | B | GE | PO | 78 | On September 28, 1987 at 0231 hours with the Unit 3 reactor operating at 78% rated power, a primary containment Group I isolation and subsequent reactor scram occurred while an Instrument Mechanic (IM) was performing a calibration procedure for the Main Steam Line (MSL) high flow switches. <br /><br />The root cause of the Group I isolation has been attributed to apparent personnel error by the IM in not properly isolating MSL high flow switch DPIS 3-261-2N during the surveillance. Prior to loading the pressure switch for calibration, the IM vented the high and low side legs of the pressure switch. During the venting process, an unexpected increase in differential pressure occurred. The IM immediately closed the equalizing valve in an attempt to stop the pressure increase. This action caused a pressure spike in the common header, in which three other pressure switches are connected, and resulted in the Group I isolation and subsequent reactor scram on Main Steam Isolation Valve (MSIV) closure. Corrective action included discussion of this event with the IM, and testing/inspection of the instrument valve manifold. The instrument valve manifold, which contains the high and low isolation valves and equalizing valve, was replaced and pressure switch DPIS 3-261-2N was calibrated. The surveillance procedure will also be revised. <br /><br /> The safety significance of this event was minimal since the instrument high side isolation valve is open during power operation and all four pressure switches operated as designed, thus initiating the Group I isolation. The last occurrence of an instrument valve manifold failure was reported by Licensee Event Report #86-001 on Docket #050237.
249 | 2491988017 | 1988-11-27 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 3 | B | GE | PO | 17 | At 0111 hours on November 27, 1988, with Unit 3 at 17% rated core thermal power with a normal Unit shutdown in progress for a planned maintenance outage, an automatic trip of the main turbine on a high vibration signal occurred. Immediately following the turbine trip a spurious Primary Containment Group I Isolation occurred resulting in the automatic closure of various Primary Containment Isolation valves, including the Main Steam Isolation Valves (MSIVs).<br /><br /> As a result of the MSIVs closing a reactor scram then occurred. The root cause of the spurious Primary Containment Group I Isolation and resulting reactor scram was attributed to vibration of a Main Steam Line (MSL) low pressure switch instrument rack during the turbine trip. Safety significance was minimal since the automatic isolation and scram logic functioned as designed, Corrective actions included disassembly and inspection of turbine components, improvement of the MSL low pressure switch mounting configuration, and development of a startup testing plan. A previous Dresden Unit 2 scram caused by a similar spurious Primary Containment Group I Isolation is reported under LER 87-32/050237.
249 | 2491989001 | 1989-03-25 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Dresden 3 | B | GE | PO | 89 | At approximately 0133 hours on March 25, 1989, while Unit 3 was operating at 89% rated core thermal power, a fault occurred within 345 KV switchyard power circuit breaker (PCB) 8-15. Local Breaker Backup logic circuitry then automatically isolated PCB 8-15; this de-energized Unit 3 reserve auxiliary transformer (TR) 32, causing a loss of offsite power (LOOP) to Unit 3. The automatic transfer of 4 KV Bus 32 from TR 32 to Unit 3 auxiliary TR 31 did not occur quickly enough to prevent undervoltage trips of the 38 reactor feed pump (RFP) and the 38 reactor recirculation pump. When the standby 3C RFP automatically started, reactor water level rose to the main turbine and RFP trip setpoint and a reactor scram on turbine stop valve closure resulted. The Main Steam Isolation Valves (MSIVs) were manually closed to conserve reactor inventory and the Isolation Condenser was used for reactor pressure control. Mildly contaminated condensate was initially used to supply the Isolation Condenser shell side because the clean demineralized water supply valve was unavailable. This resulted in low level contamination to the area surrounding the Isolation Condenser vent. Cold shutdown conditions were achieved by 2230 hours on March 25, 1989. Corrective actions included inspection, testing and repair of various breakers and logic circuits and surveys/cleanup of the areas affected by the Isolation Condenser vent. Conservative calculations found the release was less than 0.01% of 10CFR20 Appendix I Quarterly Objectives. Safety significance was minimal as the Automatic Depressurization and Core Spray Systems were available. A previous LOOP event involving Unit 2 was reported by LER 85-34/050237.
249 | 2491989002 | 1989-03-30 | QR8 | Spurious Reactor Trip | [45 empty] | Dresden 3 | B | GE | PO | 70 | On March 30, 1989 at 1253 hours with Unit 3 operating at 70% rated core thermal power, a reactor scram occurred while the Technical Staff was performing Dresden Technical Surveillance (DTS) 500-2, Functional Testing of RPS MG Set and RPS Reserve Power Supply. The cause of the scram was due to a spurious trip of Electrical Protection Assembly (EPA) breaker 3A-1 on Reactor Protection System (RPS) Bus B with a concurrent lock-up condition of the 3A Main Steam Line (MSL) radiation monitor. The RPS Bus B trip occurred at the same time attempts to reset the half scram on RPS Channel A were taking place. The Nuclear Station Operator (NSO) was unable to reset the RPS Channel A half scram due to the lock-up condition on the 3A MSL radiation monitor. The lock-up condition has the potential of occurring upon re-energizing the monitor following a momentary (less than approximately one second) power interuption. During the lock-up condition the radiation monitor remains in a tripped condition. The condition is corrected by de-energizing the monitor for approximately ten seconds after which time the monitor is re-energized. A second and third reactor scram occurred at 1338 hours and 1742 hours respectively. The second scram was caused by Operations Department personnel transferring over power supplies to RPS Bus A in an attempt to clear the radiation monitor lock-up condition. The third scram was caused by another spurious trip of EPA breaker 3A-1. Corrective actions for this event included shipping the 3A-1 EPA breaker to the manufacturer for determination of the failure mode, evaluation of a potential modification to the logic card for the MSL radiation monitors and revisions to the RPS testing procedures regarding this potential radiation monitor lock-up condition. The safety significance was minimal since the RPS System operated as designed. This was the first occurrence of its type at Dresden.
249 | 2491989006 | 1989-04-15 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 3 | B | GE | PO | 92 | On April 15, 1989 at 0320 hours with Unit 3 operating at 92% rated core thermal power, a reactor scram occurred during surveillance testing of the main turbine stop valves (TSVs). The cause of the scram was determined to be component failure. High contact resistance on a normally open contact prevented its, required closure during testing of the #2 TSV. This failure resulted in the remaining three TSVs starting to close when #2 TSV started to close. Also during this event the main generator output circuit breakers failed to open on reverse power. Consequently the main turbine was manually tripped at 0323 hours. The root cause of this failure was also attributed to component failure. Upon inspection of the main generator secondary reverse power relay, dirt was found between the bearing and contact pivot arm on the relay directional unit preventing proper operation. As corrective actions for this event two TSV control relays were replaced. The main generator secondary reverse power relay was cleaned and verified to operate properly. To help prevent future failures of reverse power relays the calibration procedure will be revised to specifically address mechanical binding of the contact pivot arm. Prior to Unit startup all of the turbine control valves, stop valves, and combined intermediate valves were functionally tested. The safety significance of this event was considered to be minimal since all reactor scram functions operated properly and the primary reverse power relay was available to prevent damage to the main generator. Two previous similar occurrences were reported by LER 89-002/050249 and LER 86-025/050249.
249 | 2491990005 | 1990-03-10 | QL5 | Partial Closure of MSIVs | [45 empty] | Dresden 3 | B | GE | PO | 94 | At approximately 2030 hours on March 10, 1990, an automatic Unit 3 scram on an Average Power Range Monitor (APRM) high flux signal occurred. The air line to the pilot solenoid for Outboard Main Steam Isolation Valve (MSIV) 3-203-2A had failed prior to the scram causing closure of the MSIV and a resulting reactor vessel pressure transient which led to the scram on APRM high flux. The resulting main steam line flow increase and corresponding low reactor water level condition resulted in Group I, II and III Primary Containment Isolations via main steam line high flow (greater than 120% of rated steam flow) switch and +8 inch reactor water low level switch actuations. Corrective action included repairs, inspection of other similar lines, and evaluation of improved air line configurations. The safety significance of this transient was mitigated by the fact that reactor water was maintained well above the automatic Emergency Core Cooling System (ECCS) initiation setpoint at all times and multiple systems were available for reactor pressure control including Isolation Condenser, High Pressure Coolant Injection (HPCI) and Main Steam Relief valves. Although previous failures of inboard MSIV pneumatic lines at the manifold block have occurred, this is believed to be the first failure of an outboard air line fitting connection.
249 | 2491991006 | 1991-08-17 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 56 | On August 17, 1991, at 0116 hours, with Unit 3 operating at 56% rated core thermal power, a reactor scram occurred during surveillance testing of the Main Turbine Stop Valves (MSVs). While testing the #2 MSV, the Fast Acting Solenoid Valve (FASV) was not positioning properly, thus allowing a drop in the Emergency Trip System (ETS) oil pressure. This allowed the Combined Intermediate Valve Stop Valve (CIV SV) disk dump valves to actuate, resulting in the subsequent fast closure of the CIV SVs. Generator load dropped from 394 MWe to 25 MWe. As Reactor Recirculation flow was reduced, the Generator electrical output dropped to -1.5 MWe. This caused the generator to trip on reverse power. The generator trip caused a subsequent turbine trip, which resulted in an automatic reactor scram when the turbine MSVs closed. Subsequent testing of the MSVs, following the event, could duplicate closure of only one of the CIV SV's. <br /><br /> Following the reactor scram, voltage on Bus 33-1 dropped below 4000 volts (normal is 4160 volts). The voltage drop was addressed and compensatory actions were taken per Operating Order #20-91, Compensatory Actions Associated with Degraded Voltage. As corrective actions for this event, the #1 and #2 MSV FASVs were replaced. Periodic replacement of the FASVs will be made a preventative maintenance item. Also, orifice plugs will be installed at the ETS inlet to FASVs to prevent temporary loss of ETS pressure. These plugs will be installed during the current Unit 3 Refuel Outage. The safety significance of this event was considered to be minimal since all reactor scram functions operated properly and the reverse power relay functioned to prevent damage to the main generator. MSV FASV failures of this type have not been a previous adverse trend.
249 | 2491992021 | 1992-10-13 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Dresden 3 | B | GE | PO | 97 | At approximately 22:49 hours on October 13, 1992, while Unit 3 was operating at 97% thermal power, an automatic Unit 3 Reactor Scram on low Reactor Water level (Technical Specification setpoint of eight inches above instrument zero) signal occurred. The 3B Condensate/Condensate Booster pump (C/CBP) failed due to an internal motor fault prior to the scram, precipitating an automatic trip of the running Reactor Feed Pumps on low suction pressure and thus resulting in reduction of reactor water level to the low level scram setpoint.<br /><br /> A comprehensive root cause investigation was immediately initiated for all component performance problems and corrective actions implemented. The root cause of this event was due to an electrical failure of the 3B C/CBP motor. The safety significance of this transient was mitigated by the fact that Reactor water level was maintained well above the automatic emergency core cooling system initiation setpoint at all times, and multiple systems were available for reactor pressure control including the Isolation Condenser, the High Pressure Coolant Injection System and the Main Steam Relief Valves. Previous events involving Condensate/Condensate Booster Pump Motor failures are reported by LER 87-011-0/050249 and LER 90-002-1/050237.
249 | 2491992025 | 1992-12-25 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 73 | On December 25, 1992 at 21:43:35 hours with Unit 3 operating at a steady thermal power of 73%, an automatic reactor scram occurred due to the Main Turbine tripping on a high vibration trip signal. The 3A Feedwater Regulating Valve (FWRV) locked out during the turbine trip. There were no surveillances being performed and the 3A FWRV and 3B FWRV were in auto and manual respectively. A root cause investigation was initiated to determine the cause of the high vibration trip of the turbine and the FWRV lockout. It was determined that there was no actual high vibration on the main turbine during or after the scram; if it had been a real vibration problem then excessive vibration readings would have been present from full speed to below critical speed on the coastdown. It was found during troubleshooting of the turbine trip circuitry that the reference trip signal required for turbine bearing #3 had failed low. There have been no previous Main Turbine trips resulting from failed vibration alarm cards found in a history search. The 3A FWRV lockout is believed to be the result of electrical load changes, due to equipment starts and stops occurring in the plant. The failed vibration alarm card was replaced with a new unit. It was noted after the scram that Main Steam Safety Valves (MCCV) 3-203-4B and 3-203-4D were weeping, according to the temperature fluctuations noted on the leak detection recorder.
249 | 2491993004 | 1993-01-16 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Dresden 3 | B | GE | PO | 83 | At 1213 hours on January 16, 1993, with Unit 3 at 83% power, a Unit 3 Instrument Air [LD] Header Pressure low Alarm was received in the Control Room [IB]. At 12:15:43, a Scram Header Low Pressure Alarm A-1 was received on the Sequence of Events Recorder (SER). Instrument Air Header pressure was observed to be decreasing rapidly. At 12:15:53, the Unit 3 NSO manually scrammed the reactor in accordance with Dresden Operating Abnormal Procedure DOA 4700-01. The Unit 2 and Unit 3 RX Building Ventilation System [VA] auto isolated and the 2/3 'B' SBGT system [BH] auto started at 12:16 on a Group II Isolation. At 1219 the 2/3 'B' SBGT train tripped and the 'A' train auto started. <br /><br /> Loss of Instrument Air is attributed to mechanic al failure of the 3A Instrument Air Compressor dryer inlet valve to close during the dryer purge cycle with concurrent failure of the backup Service Air to Instrument Air Cross-tie valve to promptly open on a low instrument air pressure signal. Corrective action include replacing the SA/IA cross-tie valve air regulator and pressure relief solenoid, replacement of the dryer inlet and purge valves and solenoid operators. <br /><br /> The safety significance of this event is minimal sinc e a manual reactor scram was initiated and all safety systems performed as required. A previous un-reportable event occurred on March 10, 1990, where a dryer exhaust valve failed in an open position following valve replacement. The root cause was attributed to inadvertent reverse connection of the switching valve air supply lines.
249 | 2491993007 | 1993-02-26 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Dresden 3 | B | GE | PO | 99 | On February 26, 1993, at 16:17 hours with Unit 3 operating at a steady thermal power of 99.4%, an automatic reactor scram occurred due to high reactor pressure. Review of plant data indicated that the high reactor pressure was caused by a flow blockage in the high pressure turbine. Disassembly revealed that foreign objects had entered in the first stage of the high-pressure turbine. One of the objects, or debris from internal damage, came in contact with the rotating assembly and caused damage which restricted steam flow. The safety systems functioned as designed during the subsequent scram recovery. Damage to the first-stage diaphragm and rotor will be repaired. The Foreign Material Exclusion (FME) program will be enhanced to prevent further events of this nature. A history search revealed there were no similar events of objects entering the turbine and causing damage at Dresden.
249 | 2491993014 | 1993-07-10 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Dresden 3 | B | GE | PO | 93 | While in the process of performing DOP 4400-8 'Circulating Water flow Reversal', a Unit 3 Reactor Scram occurred on Main Condenser Low Vacuum at 0358 on July 10, 1993 with Unit 3 at 93% power and 996 psig pressure.
249 | 2491994018 | 1994-08-06 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Dresden 3 | B | GE | SU | 3 | On August 6, 1994, at 07:40 hours, during plant startup, Unit 3 scrammed from 3W reactor power on Low Reactor Water Level. While attempting to place a third Condensate Demineralizer into service, the operating shift crew became distracted monitoring Condensate/Condensate Booster (C\CB) pump amps and demineralizer differential pressure, and failed to monitor reactor water level. In the course of manipulating the C/CB pump minimum flow bypass valve to control amps and demineralizer differential pressure, the valve was fully opened, diverting nearly all condensate flow to the Main Condenser. Reactor water level decreased to the scram setpoint. <br /><br /> The C/CB pump minimum flow valve was closed down to establish normal flow. Recovery from the Scram was completed per procedures and the reactor was cooled down to cold shutdown condition. The licensed operators involved in the event were temporarily relieved of shift duties to assess their performance and assist in the investigation of the event.
249 | 2491995001 | 1995-01-09 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 89 | On January 9, 1995, at 1833 hours, with Unit 3 at 89% rated core thermal power, while performing Dresden Operating Procedure (DOP) 3500-03, Removing High Pressure Feedwater Heaters From Service in preparation for replacement of the 3D1 high pressure feedwater heater level switch, the Main Turbine tripped on the 3B Moisture Separator level high high. The Main Turbine trip caused the Unit 3 Reactor to scram on Turbine Stop Valve closure. The 3A Moisture Separator Drain Tank (MSDT) emergency drain valves (3-3510A and 3-3510B) failed to open when required due to the drain valves' controller being out of calibration. In addition, previous similar events provided opportunities to identify the potential for failure but were not recognized in a timely manner. The 3A MSDT emergency drain valves were inspected, their controllers were refurbished, calibrated, and the entire control loop was tested. Development of a preventive maintenance program for critical feedwater heating components is being performed. Safety significance of this event is considered minimal, all safety systems were operational but were not required during this event.
249 | 2491995008 | 1995-05-28 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 100 | On May 28, 1995, at 0923, during steady state power operation at approximately 2527 MWT, Unit 3 scrammed from Main Turbine Stop Valve closure due to Main Turbine High vibration. Journal Bearing 7 on the C Low Pressure (LP-C) Turbine experienced radial vibration displacement of 14.4 MILS, exceeding the high vibration trip setpoint of 10.0 MILS. The high vibration was caused by the failure of a blade in the LP-C Turbine Rotor. Subsequent to the scram, a feedwater transient was experienced which resulted in water entering the High Pressure Coolant Injection steam line. The root cause of the Turbine blade failure was fatigue fracture of the stellite shield due to an out of specification grade of materials used. The root cause of the Feedwater Control System failure was a design deficiency of the control logic. Corrective actions included replacement of the failed blades and changes to the feedwater control system logic initiation points. The safety significance of this event was evaluated and determined to be moderate.
249 | 2491995017 | 1995-09-28 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 77 | On September 28, 1995, at 2157, while Unit 3 was at 615 MWe with a 10 Mwe/hour ramp up rate to 650 MWe, Unit 3 scrammed from the Main Generator Load Reject due to a Generator trip on Loss of Generator Field current. A resistor was found open circuited in the voltage regulator circuit. <br /><br /> The failed resistor was replaced and the voltage regulator was satisfactorily tested. All safety equipment and Group Isolations performed as required. A Group II and III Isolation occurred due to inventory shrink after the scram, but level was restored. A second Group II and III isolation occurred approximately 18 minutes after the scram. This second isolation was caused by an improperly set relief valve on the Reactor Water Cleanup System which hampered attempts to establish vessel blowdown. The relief valve has been reset and a review of relief valve setpoints for similar problems is being performed. The safety significance of this event is considered minimal.
249 | 2491995019 | 1995-10-29 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Dresden 3 | B | GE | PO | 60 | On October 29, 1995, at 0914 hours, with Unit 3 in the run mode at 60% core thermal power, the 3E and 3F Circulating Water Travelling Screens became obstructed to the point of significantly reducing net positive suction head to the 3C Circulating Water Pump. Reactor power was reduced and a manual scram was initiated at 0914 on October 29, 1995, in accordance with conservative operating standards to prevent a loss of Circulating Water to the unit. The blockage to the travelling screen was later found to be caused by debris, silt, and an unusually large amount of fish. Some individual screen modules on the 3F Travelling Screen were bowed from the weight of the debris. The plant response upon scramming was uneventful, including Group 2 and 3 Isolation. The reactor heat removal was accomplished by using the Isolation Condenser, and Reactor Water Cleanup System. Corrective actions included cleaning and inspection of the affected bays and future evaluation of fish populations.
249 | 2491996004 | 1996-05-15 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Dresden 3 | B | GE | PO | 83 | On May 15, 1996, at approximately 1043, with Unit 3 in the run mode at approximately 83% power, a feedwater transient was experienced which resulted in the initiation of an automatic reactor Scram due to low reactor water level and Emergency Core Cooling System (ECCS) actuation on low low reactor water level. The plug from the 3B Feedwater Regulating Valve (FWRV) separated from the stem resulting in an isolation of feedwater flow to the reactor. The cause of the stem separation was fatigue cracking. In addition, 2 Group I isolation valves improperly re-opened upon resetting the isolation signal. The cause for isolation valves re-opening is a manufacturing defect and is potentially reportable under 10CFR21. Corrective actions include; replacing the 3B valve stem to existing specifications, operational limits and vibration monitoring of the valve upon resumption of power operations, and future reconfiguration of the 3B FWRV, and replacing the relays. The overall safety significance was determined to be minimal because all safety systems performed as required and there was no danger to health and safety at any time.
249 | 2491998003 | 1998-04-09 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 3 | B | GE | PO | 99 | At approximately 0040 on 4/9/98, while the A Primary Containment Isolation System (PCIS) channel was in the tripped condition, a spurious Group 1 isolation on the B channel of PCIS caused the Main Steam Isolation Valves (MSIVs) to close. At less than 90 percent MSIV full open, a Reactor scram signal was appropriately received. Subsequent to the Reactor Scram, a valid Group 1, Containment Isolation occurred on Low Main Steam Line pressure. Additionally, a Group 2 and 3 containment isolation occurred on the level shrink after rod insertion. Reactor vessel level was recovered using the Feedwater system. Feedwater was secured with vessel level at approximately at 35 inches above instrument zero. The Isolation Condenser was placed in service to control reactor pressure. With the MSIVs closed and reactor pressure greater than 600 psig, the scram signal could not be reset. The inability to reset the scram resulted in the control rod drive system injecting water into the reactor vessel which caused an increase in reactor vessel water level. Prior to establishing reactor water blowdown using the reactor water cleanup system vessel level increased to approximately 60 inches. Approximately 20 minutes into the event, a High Pressure Coolant Injection (HPCI) inlet drain pot high level alarm was received which indicated that water had entered the HPCI steam supply piping. Operations personnel manually isolated the HPCI system by closing a steam supply isolation valve. The root cause of the spurious B channel, PCIS group 1 half isolation signal was dirty, oxidized contacts on a relay in the Main Steam Line Low Pressure sensing logic concurrent with a previously existing PCIS A channel half isolation signal. The relay contacts which resulted in the spurious signal were cleaned. Other similar relays in Main Steam Line Low Pressure sensing logic were inspected to ensure similar conditions did not exist. The safety significance of this event was minimal. All safety systems operated as designed. During the time HPCI was isolated, all other ECCS systems were available to mitigate the consequences of an accident.
249 | 2491998004 | 1998-05-16 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Dresden 3 | B | GE | PO | 35 | On 5/16/98 at 2252 hours, Unit 3 was manually scrammed in response to a decrease in Main Condenser vacuum and increase in condensate demineralize temperature, caused by the stuck open Main Turbine Crossaround Relief Valve Number 3 (CAR3). Prior to the manual scram, Operations experienced a decrease in Condenser vacuum during the initial main turbine reset and requested Engineering assistance in identifying possible air inleakage. During investigation of the suspected air in-leakage, Plant Engineering personnel found that the CAR3 valve tailpipe was warmer than other CAR valve tailpipes. The Engineer and Operations personnel believed the valve was in satisfactory condition. The decrease in vacuum on the initial turbine reset was a result of air in the turbine supply piping due to the plant having been shutdown. The cause of this event was the CAR3 valve not being in the full closed position. The valve was disassembled and visually inspected and found to be slightly cocked, corrosion products and dirt build up on internal parts. It is suspected that the rust and dirt build-up on the disc holder prevented the proper closure of the valve. A contributing cause was failure to thoroughly investigate the leakage through the CAR3 valve. The safety significance was considered minimal since no emergency systems were needed to stabilize the plant following the scram. Subsequent to the scram, Group 2 and 3 isolation signals occurred as a result of the typical shrink in vessel level. All plant systems responded as designed. There were no identified occurrences where a CAR valve was found stuck open.
249 | 2491999006 | 1999-12-11 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 100 | On December 11, 1999, at 0111 hours, operations personnel were performing the Main Turbine weekly surveillances per DOS 5600-02, "Weekly Turbine Checks." The Unit 3 tripped from Main Turbine Stop Valve closure initiated by the turbine overspeed test circuits. The cause of this event was determined to be a faulty XK3 relay socket that resulted in the turbine lockout solenoid being de-energized during the oil trip testing. The de-energization of lockout valve caused the Electro Hydraulic Control (EHC) Emergency Trip System (ETS) hydraulic pressure to bleed off from the system pressure. This cause was determined through the measurement of AC voltages before the Xk3 relay contact and after the contact that supplies voltage to the lockout valve. The cause of this event was the failure of the XK3 relay socket. Corrective actions included replacement of the defective socket for the XK 3 relay. The overall safety significance of this event was minimal. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv), which requires the reporting of any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS).
249 | 2492000002 | 2000-05-03 | QR8 | Spurious Reactor Trip | [45 empty] | Dresden 3 | B | GE | PO | 100 | On May 3, 2000, at 0946 hours, Dresden Operating Department began to transfer the "B" Reactor Protection System (RPS) Bus from its Normal Power Supply to its Reserve power supply per station procedure DOP 0500-03, "Reactor Protection System Power Supply Operation." The "3A" MG Set Drive Motor feeds the "3B" RPS bus. During this evolution, the breaker to the "3B" MG Set Drive Motor (hence "3A" RPS Bus) tripped on thermal overloads causing a loss of the "3A" RPS Bus and an automatic reactor SCRAM. The cause for the "3B" MG Set Drive Motor breaker tripping on thermal overloads was due to the breaker thermal overload trip setpoint being set too low due to the wrong acceptance criteria utilized by the electrician during the performance of a preventive maintenance activity. The reason for not identifying the wrong acceptance criteria prior to returning the breaker to service was failure to verify acceptance criteria. The safety significance of this event was minimal. All safety systems operated as designed and all ECCS system s were available to mitigate the consequences of an accident.
249 | 2492000003 | 2000-05-04 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Dresden 3 | B | GE | PO | 44 | On May 4, 2000, at 2018 hours, Operations inserted a manual reactor scram per station procedure when the condensate inlet temperature to the demineralizers reached 135 degrees. A degrading condenser vacuum during a plant startup, coupled with an increasing condensate temperature characterize d this event. A manual scram was initiated per procedure, on high condensate temperature, to protect the condensate demineralizer resins. The root cause of this event determined four specific areas of failure that in the aggregate establish the conditions that resulted in Operations inserting a manual scram. The four specific areas include, 1) failure of the 3A Offgas (OG) system was determined to be installation of an incorrectly sized orifice, 2) failure to follow procedures by the system engineer involved with post modification testing of the system, 3) failure of system flow indication was caused by inappropriate application of the installed flow element, and 4) failure of the Seal Steam Bypass valve yoke was determined to be a procedural deficiency which allowed inappropriate use of the valve at Reactor pressures higher than designed. Corrective actions include installation of correctly sized orifice into the 3A OG system, revised operating procedures t o ensure the 3A OG Condenser is not overloaded under normal operating conditions, revised operating procedure to ensure Seal Steam bypass valve is operated <250 psig Reactor pressure and counseled the system engineer on the importance of strictly following the post modification testing and special procedures, including creating proper acceptance criteria. The safety significance of this event was minimal. Plant equipment response was per design. The Operations decision to manually scram was proper per procedure and pre-briefed in accordance with conservative decision making philosophy. With exception of the abnormalities causing and contributing to the need for a manual scram, plant equipment response was per design and required no operator action.
249 | 2492001002 | 2001-04-27 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Dresden 3 | B | GE | PO | 99 | On April 27, 2001, at 14:49, approximately 10 minutes after a minor Reactor Recirculation (RR) flow increase demand, the 3B RR Motor Generator (MG) increased from 94 percent until it reached its electrical stop for speed control. This runup was due to debris in the RR MG scoop tube positioner motor. This resulted in the RR MG output frequency operating in an unstable region for the RR MG voltage regulator. This caused RR MG output frequency to vary significantly. Several attempts to trip the RR MG were unsuccessful due to the RR MG drive motor breaker logic's (52 H) relay contact not having continuity. The unstable RR MG operation caused its field breaker to trip on high excitation current. Without field excitation, the RR pump was not magnetically coupled to the RR MG's momentum. Therefore, the RR Pump quickly slowed, dynamically braking the 3B RR pump flow. The Reactor Water Level (RWL) increased due to the decrease in RR pump flow resulting in the Feedwater Level Control System (FWLCS) decreasing feedwater flow. A feedwater / steam flow mismatch occurred resulting in a decrease in RWL. RWL reached the automatic scram setpoint and Dresden Unit 3 scrammed on low RWL as designed. The debris in the RR MG Scoop Tube Positioner Motor has been removed. RR MG operation is not normally permitted in the unstable operating region for the RR MG voltage regulator. The drive motor breaker logic relay 52 H contact has been correctly aligned and verified by post maintenance testing. The safety significance of this event has been determined to be minimal.
249 | 2492001003 | 2001-07-05 | E4 | Partial loss component cooling water |  |  |  |  | X | [18 empty] | X | [21 empty] | Dresden 3 | B | GE | PO | 100 | On July 5, 2001, at 1006 hours, a manual Scram was initiated on Dresden Nuclear Power Station (DNPS) Unit 3 due to increasing drywell pressure. Drywell pressure increased because of rising containment temperature due to a disc to stern separation of the Reactor Building Closed Cooling Water (RBCCW) Temperature Control Valve (TCV) that supplies cooling water to the RBCCW heat exchangers. One of the RBCCW loads is the drywell coolers. After the manual scram was initiated, drywell pressure continued to increase to a value above the Emergency Core Cooling System (ECCS) initiation setpoint. ECCS systems automatically initiated at 1.7 psig drywell pressure. The High Pressure Coolant Injection (HPCI) was placed in pull-to-lock to prevent a cold water injection. A Group 2 and Group 3 isolation also occurred during this event and all isolation valves successfully closed or isolated. All ECCS initiated and performed as designed. A General Station Emergency Plan (GSEP) Alert was conservatively declared based on the assumption that the drywell pressure increased due to Reactor Coolant System (RCS) leakage. Subsequently, containment sampling and sump data determined that drywell atmospheric activity levels had remained normal, and no abnormal sump inputs had occurred (no indication of RCS leakage). The GSEP Alert was terminated on July 5, 2001 at 1602 hours. The root cause of this event was the inappropriate torqueing of the valve stem into the valve disc by the manufacturer of the plug assembly. The cause of the manufacturer's failure to properly assemble the valve is unknown. The contributing causes of this event are poor communication of a similar previous event at Quad Cities, improper pin material being supplied by the vendor and Dresden's dependency on a single RBCCW train. The safety significance of this event has been determined to be minimal.
249 | 2492002002 | 2002-07-21 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 100 | On July 21, 2002, at 2033 hours Dresden Nuclear Power Station received an automatic reactor scram as the result of the main turbine tripping. The turbine trip was due to low discharge pressure from the turbine shaft bearing oil pump. Previous to the scram, on July 15, 2002, the turbine was taken off-line following identification of damage to the Permanent Magnet Generator (PMG). Following inspection of the PMG, the unit was returned to service on July 16, 2002. On July 21, 2002, low discharge pressure from the turbine shaft bearing oil pump caused the Unit 3 turbine to trip and consequently, a reactor scram occurred. The cause was determined to be the degradation of the auxiliary control rotor gear coupling insulation, resulting in current flow through the gear shafts which caused electrolysis and accelerated wear of the bearings. The corrective actions include revising turbine front standard procedures to include dismantling and inspection of the extension tube, inspecting and meggering the insulated coupling splines, and inspecting the front standard insulation kit per General Electric specifications. At no time did this condition compromise the health and safety of the public. The failure of the Main Shaft Oil Pump (MSOP) resulted in low turbine oil pressure, which initiated a turbine trip and reactor scram as designed. All safety systems functioned as designed following the reactor trip.
249 | 2492004001 | 2004-01-24 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 96 | On January 24, 2004, at 0037 hours (CST), with Unit 3 at 96 percent power in Mode 1, an automatic scram occurred while performing the weekly surveillance of the Main Turbine Master Trip Solenoid Valves. The surveillance testing was performed in accordance with procedure DOS 5600-02, "Periodic Main Turbine, EHC and Generator Tests." The event was caused by a malfunction of the Main Turbine Master Trip Solenoid Valves, which resulted in the depressurization of the Emergency Trip Supply hydraulic header and the resulting momentary closure of the Main Turbine Stop Valves below 90 percent full open. The Reactor Protection System actuated as a result of the Main Turbine Stop Valve position and, as designed, automatically scrammed the reactor. The plant responded as expected to the automatic scram. The root cause of the malfunction of the Main Turbine Master Trip Solenoid Valves was attributed to an improperly designed position switch rod and its associated housing by the Original Equipment Manufacturer, General Electric. The corrective actions to prevent reoccurrence are to replace the Main Turbine Master Trip Solenoid Valves with valves of a different design. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the automatic scram. There were no subsequent major equipment malfunctions
249 | 2492004002 | 2004-01-30 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 97 | On January 30, 2004, at 1155 hours (CST), with Unit 3 at 97 percent power in Mode 1, an automatic scram occurred due to a Main Turbine trip from low lube oil pressure. The event occurred during a swapping of lube oil coolers. After the scram, reactor water level increased above the Reactor Feed Pump High Level trip set point. Reactor water level was subsequently restored to normal and the Reactor Feed Pumps were restarted. On February 1, 2004, at 0400 hours (CST), subsequent investigations into the January 30, 2004, event determined that the High Pressure Coolant Injection Systems for Dresden Units 2 and 3 were inoperable. The inoperability was due to evaluations that determined that the Feedwater Level Control System would not maintain the post scram reactor water level below that which would prevent water from entering the High Pressure Coolant Injection System's turbine steam line. The root cause of the automatic scram was inadequate procedural guidance for the swapping of Main Turbine lube oil coolers. The root cause of the High Pressure Coolant Injection System inoperability was low margin in the Feedwater Level Control System to accommodate changes to the post-scram vessel level response. The corrective action to prevent reoccurrence of the scram is to modify procedure DOP 5100-04, "Turbine Oil Cooler Operation? The corrective action to prevent reoccurrence of the High Pressure Coolant Injection Systems inoperability is to modify the post-scram response of the Feedwater Level Control System.
249 | 2492004003 | 2004-05-05 | B1 | Loss of Offsite Power (LOOP) |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Dresden 3 | B | GE | PO | 100 | On May 5, 2004, at 1327 hours (CDT), with Unit 3 at 100 percent power in Mode 1, an automatic scram occurred due to a Main Generator Load Reject when a loss of offsite power occurred. The Emergency Diesel Generators automatically started and powered their respective electrical busses. All control rods fully inserted and Group I, II and III isolations occurred as expected. Operations personnel manually initiated the Isolation Condenser System for reactor pressure control, the High Pressure Coolant Injection System for reactor water level control, and the Low Pressure Coolant Injection System for Torus cooling. All systems initially responded to the scram as expected except the Standby Gas Treatment System was unable to maintain the Secondary Containment at the Technical Specification Surveillance Requirement limit of greater than or equal to 0.25 inches of vacuum water gauge. An Unusual Event for the loss of offsite power was declared at 1342 hours (CDT) and terminated at 1601 hours (CDT) on May 5, 2004. Additionally, during restoration of offsite electrical power to Bus 33, the Emergency Diesel Generator 2/3 output electrical breaker tripped. The root causes associated with the load reject and loss of offsite power and the low Secondary Containment vacuum were respectively, equipment failure in the "C" phase of the 345 kilovolt circuit breaker 8-15 and a degraded Secondary Containment boundary not detected due to an inadequate leak rate test procedure. The investigation into the apparent cause of the Emergency Diesel Generator output breaker trip was indeterminate.
249 | 2492009001 | 2009-10-03 | QR8 | Spurious Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Dresden 3 | B | GE | PO | 100 | On 10/03/2009 at approximately 1735 hours while at full power, Unit 3 experienced an automatic reactor scram and Group I primary containment isolation signal. Due to the Group I isolation signal, the inboard and outboard main steam isolation valves closed as designed. Prior to the reactor scram, operators were restoring the reactor water clean-up (RWCU) system per the applicable station procedure. The Probable Cause for the Group I isolation signal and reactor scram is attributed to a hydraulic pressure transient when restarting the RWCU system due to a latent procedure deficiency. The procedure for restarting the RWCU has been revised. During the reactor scram, the shared Unit 2/3 emergency diesel generator automatically started when auxiliary power transferred from the main to the reserve power source. The safety significance of this event is minimal as plant response and operator actions were consistent with the protection of public health and safety and personnel safety.
249 | 2492010001 | 2010-10-11 | QR8 | Spurious Reactor Trip | [45 empty] | Dresden 3 | B | GE | PO | 100 | During preparation for planned maintenance to perform testing of the Electrical Protection Assembly breakers, plant personnel transferred the Reactor Protection System from its normal power supply to its reserve power supply in accordance with approved plant procedures. While transferring from the normal to reserve power supply, the main control room received an expected half-scram signal due to the 3A RPS bus undergoing a dead-bus transfer. The breaker for the reserve power supply was closed which provided power to the 3A RPS bus. However, prior to the half-scram being reset, a power supply failure occurred in the Oscillation Power Range Monitoring System on the opposite RPS division. The concurrent half-scram signals resulted in a full RPS actuation. All control rods fully inserted. Reactor water level was maintained using the Condensate and Feedwater Systems. Reactor pressure was controlled using the Main Turbine Bypass Valves to the Main Condenser. Following the scram, the Auxiliary Power System transferred from its main power source to the reserve power source, as designed. During this transfer, the Unit 2/3 Emergency Diesel Generator automatically started. This automatic start occurred as the result of the EDG start logic momentarily sensing both the main power source breaker and the reserve power source breaker contacts being open concurrently. Since there was no undervoltage signal received, the automatic start of the EDG is considered invalid. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).
249 | 2492021001 | 2021-10-16 | QR5 | Turbine Trip | [45 empty] | Dresden 3 | B | GE | PO | 100 | On October 16, 2021, at 0428 CDT, an automatic reactor protection system actuation occurred due to failure of the main power transformer. The safety significance of this event was minimal. All control rods inserted to their full-in position. Following the reactor scram, all systems operated as expected. <br /><br /> The cause of this event was due to a sudden, unanticipated, catastrophic failure of the main power transformer high voltage oil impregnated paper bushing. <br /><br /> Corrective actions included replacement of the failed main power transformer and restricting use and/or procurement of the specific type of bushing that failed. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), an event that resulted in automatic actuation of a system listed in paragraph 10 CFR 50.73(a)(2)(iv)(B), specifically the reactor protection system including reactor scram.
250 | 2501987003 | 1987-01-12 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | Turkey Point 3 | P | WE | PO | 35 | At 0859 on January 12, 1987, while Unit 3 was at 100% power, annunciator E 8/3, Generator Field Ground, alarmed. An investigation was begun which discovered a turbine plant cooling water (TPCW) leak in the exciter housing. At 0912 a unit 3 shutdown was commented as per general operating procedure (GOP) 3-GOP-103, Power Operation to Hot Standby, to investigate the TPCW leak and affect repairs. Due to the rapid load reduction the average reactor coolant temperature (T-avg) increased causing two (2) steam generator (SG) safety valves to lift and reseat properly. At the same time the steam dump to condenser valves (FCV-3-2827 and FCV-3-2828) armed but FCV-3-2827 failed to open. FCV-3-2828 opened and operated properly. This helped to create a large difference between T-avg and the reference temperature (T-ref) determined by turbine load. During the rapid load reduction the alarm for the extra low rod insertion limit was received and the operator initiated emergency boration according to procedure. The emergency boration decreased the reactor coolant system (RCS) pressure until the reactor trip setpoint of 1843 psig was reached and a reactor trip occurred. An event response team was formed to review this event. A post trip review was completed which verified that the plant response to this event was as expected for a reactor trip of this kind.
250 | 2501987009 | 1987-02-15 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Turkey Point 3 | P | WE | PO | 7 | On February 15, 1987, at 2020, with Unit 3 at 7% power, maintenance personnel backed out the orifice adjusting screw for the turbine governor oil impeller pressure, so that it became totally disengaged, causing a loss of turbine auto-stop oil pressure. The governor, sensing the decreasing pressure, attempted to increase turbine power by increasing the steam demand. This increased turbine first stage pressure above the P-7 value of 10% of full power, enabling the P-7 permissive, and making up half of the turbine trip upon power > 10% coincident with auto-stop oil pressure < 45 psig logic. As the oil pressure decreased below 45 psig, the above logic was completed, and the reactor, then the turbine tripped. The cause of the trip was personnel error in that insufficient attention was being paid to the orifice adjustment, with the consequence that it was not realized that the adjusting screw was about to become totally disengaged. Guidance during the evolution was being provided by a vendor technical representative. The original cause for the maintenance was low impeller oil pressure. The turbine control oil, lube oil, and seal oil piping will be cleaned during the next refueling outages for each unit.
250 | 2501987010 | 1987-03-06 | QR6 | Manual Reactor Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 95 | On March 6, 1987, at 2140, with Unit 3 at 95% power, the reactor was manually tripped following a loss of turbine load. At 2138 with the control rods under manual control, a planned load reduction had commenced to investigate turbine vibration. At 2140, the Generator Motoring Trip alarm actuated, and electrical load had dropped from approximately 698 MW to 0 MW, without any decrease in reactor power. In anticipation of a generator/turbine/reactor trip, the Reactor Control Operator (RCO) tripped the reactor. The cause of the loss of electrical load was a malfunction of the governor control oil system. The cause of the malfunction was dirt induced grooves in the stub shaft of the control oil system. The turbine control oil, lube oil, and seal oil piping will be cleaned during the next refueling outages for each unit. The impeller stub shaft and sleeve will be replaced, and the governor control block will be overhauled during the present refueling outage on Unit 3. An Event Response Team was formed and will continue to evaluate further corrective actions.
250 | 2501987023 | 1987-09-13 | QR8 | Spurious Reactor Trip | [45 empty] | Turkey Point 3 | P | WE | SU | 5 | On September 13, 1987, Unit 3 experienced a safety injection (SI) system actuation and subsequent reactor trip from approximately 5% power. On September 12, 1987, 1 of 2 high steam flow protection channels on the 3A steam generator (SG), FT-3-475, failed low and was taken out of service as per procedure. On September 13, 1987, a load reduction was commenced for Unit 3 to perform a turbine overspeed test as per operating procedure (OP) 8004.1, Turbine Generator Overspeed Trip Test. The test was begun with the low reactor coolant system (RCS) average temperature (Tave) input to the SI logic for a SI signal on low Tave of 2 out of 3 RCS loops coincident with high steam flow on 2 out of 3 SGs, alarmed on the A, B and C RCS loops. Upon completion of the test a high steam flow transmitter for the 3C SG, spiked, began cyclic operation and subsequently failed which locked in the high steam flow signal for the 3C SG and completed the logic for a SI actuation and subsequent reactor trip. The cause of the trip was component failure along with personnel error. An event response team was formed to determine root cause and corrective actions. A review was performed to assess proper plant operation which determined that the plant response to the transient was as expected. After completion of necessary reviews and equipment repairs the unit was returned to service on September 22, 1987.
250 | 2501987034 | 1987-12-29 | QR6 | Manual Reactor Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 70 | On December 29, 1987, Unit 3 experienced a reactor trip from approximately 70% reactor power. The reactor control operator (RCO) began a load increase on unit 3 from 50% power to 75% power at a ramp rate of approximately 3% per hour. Various secondary alarms came in for turbine overspeed protection, and for generator anti-motoring trip. The RCO immediately noticed that the turbine generator electrical load had dropped to approximately 24 megawatts (MW) electrical and the load limit on the turbine generator was indicating approximately 1 pound per square inch (psi) with no appreciable decrease in reactor power. At this time the Plant Supervisor - Nuclear (PSN) authorized a manual reactor trip which was completed by the RCO. The reactor trip occurred as designed and the plant was stabilized in mode 3 (hot standby). An event response team (ERT) was formed to review this event to assist in determining the root cause and corrective actions. The root cause for the loss of turbine load was stuck contacts on the overspeed controller 20% underpower relay. The relay contacts were freed and cleaned. The inputs to the relay were satisfactorily calibrated. Upon completion of the post trip review and appropriate maintenance, the unit was returned to service on December 31, 1987.
250 | 2501989020 | 1989-12-23 | QL5 | Partial Closure of MSIVs | [45 empty] | Turkey Point 3 | P | WE | PO | 94 | At 2314, on December 23, 1989, with Unit 4 in Mode 1 at 94 percent power, a reactor trip occurred due to closure of the 4A Main Steam Isolation Valve (MSIV). The sudden loss of steam flow from the 4A steam generator caused an increase in pressure in that steam generator. The pressure increase caused the steam generator level to "shrink" 'to the low-low level setpoint of 15 percent. The Auxiliary Feedwater System responded as designed. Corrosion across terminal board contacts supplying vital 125 VDC power to one of two 4A MSIV opening solenoid valves caused a fuse to blow. Upon de-energization, the opening solenoid failed to the vent position. This allowed air to bleed from the bottom of the MSIV piston. The MSIV disc dropped down into the steam flow, resulting in rapid closure of the MSIV. The accelerated corrosion rate was due to stray DC leakage currents. Upon inspection of the terminal boards supplying vital 125 VDC power to the opening and closing solenoid valves for the 3A, 3B and 3C MSIVs, corrosion was identified on one of the two terminal boards for each the 3B and 3C MSIVs. The 3B and 3C MSIVs were declared inoperable and Unit 3 entered Technical Specification (TS) 3.0.1 at 2300 on December 24, 1989. The two terminal boards were replaced, the 3B and 3C MSIVs were declared operable, and Unit 3 exited TS 3.0.1 at 0455 on December 25, 1989.
250 | 2501990011 | 1990-06-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Turkey Point 3 | P | WE | PO | 26 | On June 9, 1990, at 0648 EDT, with Unit 3 in Mode 1 (Power Operation) at 26 percent power and Unit 4 in Mode 1 at 100 percent power, Unit 3 experienced a Hi-Hi steam generator water level turbine trip and subsequent reactor trip. All safety systems performed as designed. After the trip, the operators stabilized the unit in Mode 3 (Hot Standby) by using applicable procedures. The cause of this event was a malfunction of the 3C feedwater regulator hand/auto station open pushbutton switch for valve controller FC-3-498F. The switch is a momentary action switch designed to spring back to the "no contact" position upon release. The switch was found sprung back to the "no contact" position, but the switch contacts were still closed. This resulted in a full open demand signal causing the 3C feedwater regulating valve to fully open. The failed 3C feedwater regulating valve hand/auto station and the hand/auto station for the 3B feedwater regulating valve were replaced with hand/auto stations having new style switches. The hand/auto station for the 3A feedwater regulating valve had been replaced in June, 1989. On June 9, 1990, at 0716 EDT, the NRC was notified of this event in accordance with 10 CFR 50.72 (b) (2) (ii).
250 | 2501990013 | 1990-06-15 | QR5 | Turbine Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 10 | On June 15, 1990, at 1203 EDT, with Unit 3 in Mode 1 (Power Operation) at 10 percent power and Unit 4 in Mode 1 at 100 percent power, Unit 3 experienced a reactor trip when the Operator raised power above 10 percent with the turbine in a tripped condition. Reactor power above 10 percent automatically resets the P-10 reactor trip permissive (reactor power greater than 10 percent) which in conjunction with a turbine trip provides a reactor trip. The unit was stabilized in Mode 3 (Hot Standby) in accordance with approved plant procedures. This event was caused by cognitive personnel error in that a licensed operator while attempting to correct a low reactor coolant temperature by pulling rods, failed to consider plant parameters with respect to reactor trip set points. This event will be reviewed with all applicable Operations personnel to increase awareness of the potential for undesirable results due to a failure to mentally review the consequences of actions being performed. <br /><br /> In addition, the necessity of adequate communications between the different operators and the Plant Supervisor Nuclear is also being stressed during the operator review since inadequate communications was determined to have been a significant contributing cause of this event. On June 15, 1990, at 1253 EDT, the NRC was notified of this event in accordance with 10 CFR 50.72 (b) (2) (ii).
250 | 2501991008 | 1991-10-03 | QR6 | Manual Reactor Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 50 | On October 3, 1991, at 1200 EDT, with Unit 3 at 50 percent power and Unit 4 in Mode 6 (Refueling) the Unit 3 reactor was tripped manually due to a loss of main turbine generator load. The unit was stabilized in Mode 3 (Hot Standby) with steam generator water levels being maintained by the Main Feedwater System and steam being dumped through the atmospheric dump valves. An Event Response Team was formed to determine the cause of this event and to recommend applicable corrective actions. As part of this investigation, a pipe break was discovered in the control oil piping to the North-East Intercept valve. Examination of the break area indicated the cause of the pipe break to be fatigue failure at the root of the pipe nipple at the control orifice. The fatigue was caused by pipe vibration. A significant contributor to the vibration was a spring-can support for the low pressure steam line that had one of the compression nuts restraining spring-can movement. The broken pipe was repaired and the spring retainers have been removed from the spring-cans. The nipples upstream of the other three Unit 3 intercept valves will be replaced during the next refueling outage. The supports for the control oil piping on both units will be modified to prevent excessive vibration. The Unit 4 nipples upstream of the intercept valves were replaced and the removed nipples inspected for fatigue damage. No fatigue damage was found.
250 | 2501994006 | 1994-12-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | On December 26, 1994, Turkey Point Unit 3 was in Mode 1 at 100% power. At 0141, Eastern Standard Time, the 'C' main feedwater control valve failed closed. After the valve closed an automatic reactor trip/turbine trip occurred after a Steam Generator Water Level - Low Coincident With Steam/Feedwater Flow Mismatch trip signal was received. The valve closed because a screw terminal found loose on the 'C' valve electro-pneumatic transducer caused an intermittent open circuit which resulted in a closed valve position demand to the feedwater control valve. The transducer was replaced. Operation of the valve was monitored prior to the trip and subsequent to the return of the plant to full power.
250 | 2501995007 | 1995-10-17 | QR3 | Reactivity Control Imbalance | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | On October 17, 1995, Florida Power & Light Company's Turkey Point Unit 3 was operating in Mode 1 at 100% power. <br /><br /> At 0449 hours a Rod Control Urgent Failure alarm was received along with indication of 4 dropped control rods. The reactor was manually tripped twenty-two seconds later. Off Normal Operating Procedure 3-ONOP-028.3, 'Dropped RCC,' requires the reactor to be tripped if more than two control rods drop into the core. <br /><br /> The cause of the dropped rods was water intrusion into rod control power cabinet 2BD. The design of the drain in an air conditioner evaporator drip pan was found to be inadequate for the level of humidity in the cable spreading room. <br /><br /> The NRC operations center was notified at 0553 in accordance with 10 CFR Section 50.72(b)(2)(ii), Reactor Protection System Actuation.
250 | 2501996002 | 1996-02-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Turkey Point 3 | P | WE | PO | 60 | On February 09, 1996, Florida Power & Light Company's Turkey Point Unit 3 was operating in mode 1 at 60% power to support condenser waterbox cleaning. <br /><br /> At 2329 the 'B' Steam Generator Feed Pump (SGFP) was stopped to monitor its discharge check valve closing stroke. The discharge check valve did not stroke closed as expected. At 2334 the resulting feed flow transient caused the 'C' Steam Generator (S/G) level to increase, resulting in a turbine trip. A reactor trip by turbine trip occurred immediately thereafter. <br /><br /> The cause of the turbine trip/reactor trip was cognitive personnel error. The operator failed to effectively control the 'C' S/G level during the feed flow transient. <br /><br /> The NRC operations center was notified at 0035 on February 10, 1996, in accordance with 10 CFR 50.72 (b) (2) (ii), Reactor Protection System Actuation.
250 | 2501996006 | 1996-03-27 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | On March 27, 1996, Florida Power & Light Company's (FPL) Turkey Point Unit 3 was operating in Mode 1 at 100% and Unit 4 was in a refueling outage. The 4C transformer and 4C 4160 volt bus were out of service for planned maintenance. <br /><br /> At 1715 while performing the 4C transformer lockout trip test of 3AC01 breaker, the 3C transformer locked out resulting in a trip of the 3B steam generator feedwater pump (SGFP). Since an automatic turbine runback was not observed, a manual turbine runback was initiated and a manual reactor trip was performed due to decreasing steam generator levels. All control rods fully inserted into the core and all the rod position indication rod bottom lights turned on after the reactor trip. <br /><br /> The cause of the 3C transformer lockout was mechanically induced vibration experienced after opening the 3AC01 breaker which resulted in inadvertent actuation of the GE Model 12SAM11B21A (SAM) timer relay. The failure to obtain the expected automatic turbine runback was due to a closed root valve to pressure switch PS-31604-1 which senses first stage turbine pressure, which prevented the initiation of the automatic turbine runback. <br /><br /> The NRC Operations Center was notified at 1816 on March 27, 1996 in accordance with 10 CFR 50.72(b)(2)(ii), Reactor Protection System Actuation and Engineered Safety Feature Actuation.
250 | 2501997006 | 1997-07-22 | QR3 | Reactivity Control Imbalance | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | On July 22, 1997, Florida Power & Light's (FPL) Turkey Point Unit 3 was operating in Mode 1 at 100% power. At 12:42:51 hours, 12 control rods dropped into the core and the Reactor Control Operator (RCO) manually tripped the reactor at 12:42:57 hours. The 12 control rods dropped in the core due to a failure of the redundant pair of +24 Vdc rod control power supplies, PS1 and PS2, located in the 1AC power cabinet. Following the reactor trip, all safety related equipment functioned properly with one exception. The Train 1 Auxiliary Feedwater (AFW) flow control valve to Steam Generator (SG) "C", FCV-3-2818, would not fully close due to failure of its corresponding controller, HIC-3-1458A. The RCOs took manual action to isolate Train 1 AFW to the "C" SG. A post trip review established that the response of pertinent plant parameters was as expected. A total of 12 power supplies were replaced in the rod control logic and power cabinets. The remaining Unit 4 power supplies manufactured by the same vendor will be replaced during the next refueling outage.
250 | 2501997007 | 1997-07-30 | QL5 | Partial Closure of MSIVs | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | On July 30, 1997, Florida Power & Light (FPL) Company's Turkey Point Unit 3 was operating in Mode 1 at 100% power. At 1506 hours, the 3B Main Steam Isolation Valve (MSIV) failed closed. The resultant level decrease in the 3B Steam Generator (SG) caused the reactor to trip automatically on low-low level in the 3B SG. All control rods fully inserted. A 3B steam line Main Steam Safety Valve (MSSV) opened then reseated as expected during the initial transient, as pressure in the 3B SG exceeded the MSSV setpoint pressure of 1085 psig. The A Auxiliary Feedwater (AFW) Pump tripped on overspeed during the event. Plant response was otherwise as expected. The cause of the MSIV closure was attributed to a failed BFD22S relay. The six relays on the 3A, 3B, and 3C MSIV's were replaced. The most probable cause of the A AFW pump overspeed trip was a spurious electronic overspeed signal caused by the A AFW pump tachometer module. A plant change was implemented to disable the electronic trip function of all three AFW pumps to enhance their reliability.
250 | 2501998001 | 1998-02-16 | QR6 | Manual Reactor Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | At 0438 hours, the Unit 3 turbine intercept and control valves closed due to a loss of turbine control oil pressure. The reactor was manually tripped subsequent to high steam flow alarms, automatic control rod insertion, and loss of turbine load. Auxiliary Feedwater (AFW) automatically initiated due to low steam generator levels. The Main Steam Isolation Valves were manually closed to control Reactor Coolant System temperature. The loss of control oil pressure was due to a test lever in the turbine auxiliary governor which was overly sensitive to very small movement. Apparently the lever was inadvertently bumped during nearby maintenance. The sensitive test lever was removed. Following the reactor trip a secondary side steam leak occurred. The steam leak was from a two inch drain line that branched off the 4 inch Train 2 AFW steam supply line. Despite the steam leak, the AFW system provided adequate feedwater flow to the steam generators for the duration of the event. To isolate the steam leak, AFW Train 2 was secured. The steam leak was due to outside diameter (OD) corrosion resulting from water trapped under insulation next to a support. The AFW piping susceptible to OD corrosion was inspected. About 50 feet of AFW steam drain piping was replaced, and both units' AFW steam piping was pressure tested.
250 | 2501998004 | 1998-09-21 | QR8 | Spurious Reactor Trip | [45 empty] | Turkey Point 3 | P | WE | SU | 8 | During a routine shutdown to begin the Unit 3 Cycle 17 refueling outage, an automatic reactor trip occurred at approximately 8 percent Rated Thermal Power (RTP). The reactor trip was initiated by one of two Intermediate Range Neutron Flux Instrumentation (IR NI) channels. The high flux reactor trip signal (set for 25 percent RTP) occurred when the IR NI high flux reactor trip was automatically unblocked at 8 percent RTP. The IR NI high flux reactor trip bistable for Channel N-35 had not reset prior to unblocking the IR NI high flux reactor trip below the P-10 reset point of 8 percent RTP which initiated a reactor trip signal when unblocked. The IR NI high flux reactor trip bistables should have automatically reset at approximately 19 percent RTP. The causes of this event are: 1) inadequate calibration of the IR NI high flux reactor trip bistable, 2) inadequate supervisory oversight of the IR NI high flux reactor trip reset before reducing power below the P-10 reset point, and 3) inadequate guidance in the plant shutdown procedure regarding verification of the IR NI high flux reactor trip reset prior to decreasing power below the P-10 reset point. Corrective actions include improved calibration of IR NI channels, enhanced applicable plant procedures, and operator and technical training on this event.
250 | 2501999001 | 1999-06-23 | QR3 | Reactivity Control Imbalance | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | On June 23, 1999, FPL's Turkey Point Unit 3 was operating in Mode 1 at 100% power. At approximately 11:38 AM, Shutdown Bank B, Group 1 rods (4 control rods) dropped to the bottom of the core. The Reactor Control Operator (RCO) manually tripped the reactor approximately 8 seconds after receipt of rod drop indications. The remaining rods inserted as expected when the reactor trip breakers were opened. The immediate cause of the reactor trip was manual action taken by the RCO in response to indications of more than two control rods dropped in the core. The underlying cause of the trip was failure of a Stationary Gripper Regulating circuit card in the Rod Control System. The card failure was due to fracture of an uninsulated solder terminal post. The terminal post fracture was located flush with the top of the circuit board below a resistor lead solder joint. Failure of the card caused the group 1 rods in Shutdown Bank B to be released by their Stationary Gripper Coils, allowing the rods to drop into the core. Corrective actions included inspections and repairs of Stationary Gripper Regulating cards, and post maintenance testing.
250 | 2502001003 | 2001-08-15 | QL7 | Degraded condenser vacuum | [45 empty] | Turkey Point 3 | P | WE | PO | 16 | On August 15, 2001, at 4:49 AM, with the unit operating at approximately 16% reactor power, a manual reactor trip was initiated in response to low condenser vacuum. Prior to the event, Unit 3 was operating at full power but reduced generation due to a known condenser tube leak in the 3A South Waterbox. Condenser tube leakage resulted in chemistry conditions which forced a unit downpower. At approximately 16% reactor power, a manual reactor trip was initiated in response to indicated low vacuum in the condenser. The root cause of this event was inadequately designed sensing lines for the control room condenser vacuum instrumentation and the turbine low vacuum alarm. Contributing causes were diaphragm leakage in the turbine trip block and inadequate operating procedures for dealing with high condenser air in-leakage events. Corrective actions include upgrading of sensor lines for condenser vacuum trip and indication instrumentation to eliminate the buildup of condensate and revisions to operating procedural guidance.
250 | 2502003002 | 2003-01-27 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Turkey Point 3 | P | WE | PO | 100 | On January 27, 2003, with the unit operating at approximately 100% reactor power, Unit 3 was manually tripped due to low steam generator level on the 3C steam generator. The low steam generator level was caused by a momentary loss of running instrument air compressors. The degraded instrument air pressure affected the air-operated main feedwater control valves, causing them to drift closed. The Control Room Operator took prompt procedurally driven actions to reduce power in response to the transient and to manually load the diesel driven instrument air compressors. Steam generator levels decreased, with the 3C steam generator level reaching approximately 12 percent, when the Unit 3 Control Room Operator initiated the manual trip of the unit. Following the manual reactor trip, all three turbine-driven auxiliary feedwater pumps started as expected and instrument air was restored. All control rods fully inserted. The plant was stabilized in Mode 3. This event is reported per the requirements of IOCFR50.73(a)(2)(iv)(A). The cause of this event was a failure of the 4CM motor driven instrument air compressor, with the 3CM compressor out of service for maintenance. A contributing cause was the failure of the 3CD and 4CD diesel-driven compressors to autostart. Corrective actions included the installation of temporary instrument air compressors. Evaluation of the 4CM motor driven compressor failure and the 3CD and 4CD diesel-driven instrument air compressors failure to autostart was completed and corrective actions were implemented.
250 | 2502003008 | 2003-05-20 | QR6 | Manual Reactor Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 30 | On May 20, 2003, Florida Power and Light's (FPL) Turkey Point Unit 3 was operating in Mode 1 at 100% power. At 09:16 hours during the performance of the quarterly surveillance Rod Cluster Control Assembly Periodic exercise, Group 1 Shutdown Bank B did not move out with demand for withdrawal and an urgent failure alarm [AA:JD] was received from rod control [AA:ROD] power cabinet 1 BD [JD:CAB, JC]. Group 1 of the Shutdown Bank B was declared inoperable. Operations entered the Off Normal Operating Procedure for Reactor Control System Malfunction and Technical Specifications (TS). In accordance with TS 3.1.3.5, Shutdown Rod Insertion Limit, and 3.0.3, the reactor was manually tripped from 30% power at approximately 15:43 hours. The inability to move the Shutdown Bank B was caused by a Rod Control System failure due to a loss of the logic UPSPX signal on the 1 BD Movable Slave Cycler Decoder Card A41 1, pin 24. During the shutdown, all Unit 3 control rods properly inserted into the reactor core. As such, they performed their design basis function of inserting into the reactor core on demand. The health and safety of the public were not affected by this event. This event is reported under the requirements of 10 CFR 50.73 (a) (2) (i) (A) for the completion of any nuclear plant shutdown required by the plant's Technical Specifications.
250 | 2502004006 | 2004-12-14 | QR6 | Manual Reactor Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Turkey Point 3 | P | WE | PO | 100 | On December 14, 2004, at 11:40 with Units 3 and 4 operating in Mode 1 at 100 percent power, a fire was reported at the North end of the Unit 3 High Pressure Turbine, beneath the turbine deck. At 11:45 Unit 3 was manually tripped due to the fire in the High Pressure Turbine area. The fire brigade responded and the fire was extinguished at 11:49. No damage to equipment or personal injury occurred and no Engineering Safety Feature Actuation was required as a result of the manual reactor trip. The fire was caused by the ignition of oil vapors generated by oil leaking from the number 2 bearing seal onto the High Pressure Turbine lower shell insulation. The cause of the seal oil leak was a result of poor workmanship performed during the spring 2003 refueling outage turbine seal overhaul. Specifically, the leaking oil was caused by improper bolting of the seal, inadequate gasket, inadequate sealing compound and shims introduced during the seal overhaul performed during the spring 2003 Unit 3 refueling outage. The Unit 3 turbine shaft seals were rebuilt, oil soaked insulation was removed, metal lagging added where necessary, and insulation replaced. The turbine fire did not affect any of the Unit 3 safety systems. All safety systems responded as designed; therefore, the health and safety of the public were not affected by the turbine fire and manual reactor trip.
250 | 2502004007 | 2004-12-28 | QR6 | Manual Reactor Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 70 | On December 28, 2004 at 22:46 Turkey Point Unit 3 reactor was manually tripped from 70% power following a fast load reduction from 100%. The load reduction was initiated when it was recognized that the Turbine Plant Cooling Water (TPCW) leakage exceeded the makeup capability to the TPCW surge tank. The reactor trip was initiated following the discovery of water in the Turkey Point Unit 3 Main Generator exciter housing. The apparent cause of the exciter TPCW air cooler leak was found to be a failed gasket at the joint between the cooler channel head and the air cooler assembly. The root cause of the cooler failure is determined to be poor workmanship on the part of the refurbishment vendor along with inadequate technical guidance to the supplier for the repairs. Immediate corrective actions included the identification and repair of the TPCW leak source and drying of electrical components. Although parts of the 3B 4160 Volt safety related switchgear enclosure at the lower elevation were wetted due to water intrusion through the conduit penetrations in the overhead, the bus remained energized throughout the event. All plant parameters remained within the design envelope for this type of transient. All plant safety systems functioned as designed and there were no adverse effects on the operating crew's ability to safely shutdown the reactor and stabilize the plant. The health and safety of the public was not challenged nor adversely affected by this event.
250 | 2502005005 | 2005-10-15 | QP2 | Partial Loss of Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Turkey Point 3 | P | WE | PO | 99 | At 0702 hours on October 15, 2005, the Turkey Point Unit 3 Reactor was manually tripped from 99.9 % power due to a decrease in the 3C Steam Generator (SG) level. The loss of SG level control was due to feedwater [SJ] control system malfunctions. At approximately 0701 hours, the 3C SG level started to decrease. The main feedwater flow control valve, FCV-3-498, [SJ:FCV] would not modulate open even in manual control. Subsequent to the trip, Operations closed the Main Steam Isolation Valves (MSIVs) in response to observing that one of the four steam to reheat isolation valves did not close. Closure of the MSIVs [SB:ISV] resulted in loss of the normal heat removal path. The root cause of losing control of FCV-3-498 was found to be insufficient work instructions that allowed the valve clip in the positioner to be installed with some looseness. Corrective actions include the replacement of the valve positioner for FCV-3-498, and revision to the inspection instructions to include explicit installation details. This event had no adverse effect on the operating crew's ability to safely shutdown the reactor. Therefore, this event did not adversely affect the health and safety of the public.
250 | 2502008001 | 2008-02-26 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | On February 26, 2008 at approximately 1309 hours, a momentary grid voltage disturbance occurred that caused a reactor trip of both Turkey Point Units 3 and 4 when both channels of safety-related 4 KV bus undervoltage relays for each unit actuated after a one second time delay. In addition, at approximately 1620, while shutting down the Unit 4 4A steam generator feed pump after transferring to standby feedwater, auxiliary feedwater (AFW) automatically actuated due to a red flag semaphore still present on the 4B SGFP control switch since the switch had not been taken to the stop position. This AFW actuation was inadvertent. The grid voltage disturbance occurred due to human error when a Protection and Control field engineer disabled both levels of local protection at an electrical substation which then failed to actuate when a fault occurred during equipment troubleshooting. The inadvertent AFW actuation occurred due to inadequate procedural guidance. Since plant response to the grid disturbance was as designed and AFW was not required to mitigate any plant condition at that time, the safety significance of the plant trips and inadvertent AFW actuation are minimal. Corrective actions relating to the grid disturbance include a new procedure setting requirements related to disabling protection. Corrective action for the inadvertent AFW actuation entails future procedure changes to ensure the control switches for various components powered by the 4C 4 KV bus are placed in the appropriate position after a loss of power and to verify the control board switches are green flagged.
250 | 2502010003 | 2010-09-23 | QR5 | Turbine Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | On September 23, 2010, with Unit 3 operating at 100% power, an unplanned automatic reactor trip occurred at approximately 17:14:40 when an electrical flashover on the high side of the Unit 3 Generator Step Up (GSU) transformer occurred. All systems responded as designed. At 17:52, a notification (EN# 46274) was made to the NRC Operations Center in accordance with 10 CFR 50.72(b)(2)(iv)(B) due to actuation of the Reactor Protection System with the reactor critical and 10 CFR 50.72(b)(3)(iv)(A) due to Auxiliary Feedwater System actuation. The Unit 3 reactor and turbine tripped due to a generator differential protection relay trip. This event was entered into the Corrective Action Program as AR 582206. All systems functioned as normal with the exception of Control Rod G5 in Control Bank A which indicated 18 steps. The unit entered and exited E-0 "Reactor Trip" and ES-0.1 "Reactor Trip Response." All 4kV buses had power from the Unit 3 Start Up Transformer. Heavy weather (rain and wind) conditions existed at the time of the reactor trip. The root cause was an external flashover to ground of the "C" phase high voltage (HV) bushing. The Unit 3 GSU Transformer High Voltage Bushings (all phases) were replaced with longer bushings. Transformer Surge Arresters, Stand Off Insulators, Conductors, and Generator Radial Lead Seals were replaced.
250 | 2502010006 | 2010-11-15 | QR6 | Manual Reactor Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Turkey Point 3 | P | WE | PO | 100 | With Unit 3 at 100% power, at approximately 0604 on November 15, 2010, the reactor was manually tripped when the 3A2 Circulating Water Pump was stopped due to an overheated packing gland. The manual trip was in anticipation of an automatic turbine/reactor trip on low condenser vacuum. While Auxiliary Feedwater automatically actuated, a train of normal feedwater remained available to feed the steam generators. During the reactor trip, the 3B Steam Dump to Atmosphere valve opened automatically, as designed, but failed to close on operator demand as required by procedure. It was locally isolated with a manual isolation valve stopping the cooldown. The reactor coolant system (RCS) temperature was stabilized at 487F and borated as required by procedure. The RCS returned to normal operating temperature and pressure and the unit was stabilized in Mode 3. Two root causes were identified: 1) There were inadequate administrative controls for pump packing consolidation for applicable non-nuclear safety (NNS) related pumps, and 2) A healthy skepticism and recognition of risk was not adequately considered or communicated. Corrective actions include: 1) Incorporate information on packing consolidation break-in period, system perturbation information, temperature bands, and minimum/maximum levels for packing leak-off for NNS pumps into the post maintenance testing procedure, 2) implement plan for Recommendation 1 of SOER 10-2: Engaged, Thinking Organizations, 3) inspect Unit 3 and 4 pumps that utilize packing, 4) replace 3A2 CWP pump shaft packing and packing follower, and 5) repair 3B Steam Dump to Atmosphere valve.
250 | 2502011001 | 2011-03-06 | QL6 | Condenser Leakage | [45 empty] | Turkey Point 3 | P | WE | PO | 23 | At approximately 11:35 on March 6, 2011, a sodium spike was detected in the 3AS hotwell. Subsequently the 3A1 and 3A2 circulating water pumps (CWP) were stopped. A rapid power reduction was commenced after a second sodium spike was experienced, in accordance with plant procedures 3-ONOP-100, "Fast Load Reduction", to approximately 23% power. A manual reactor trip was initiated per procedure at 16:44 (EST). Unit 3 was stabilized in Mode 3. All rods fully inserted and all safety systems functioned as required and there was no impact on the health and safety of the public. The NRC was notified of the event due to manual actuation of the Reactor Protection System [JC] (Event Number 46660) at approximately 19:38 (EST) on March 6, 2011. The cause of the sodium intrusion event was due to a tube flaw near the tubesheet of tube [SG, COND] R305/T5 in the 3BS tube bundle. High cycle, low stress fatigue, and cold work induced residual stresses likely contributed to the event. Corrective actions involved plugging several tubes and applying an overcoat of Duromar after tube plugging. Eddy Current Testing was performed on a selected tube population. A combination of foam/dimple plug testing was performed. Several tubes in the 3AN and 3BS water boxes were plugged and coated. A root cause analysis was performed. Long term, the Unit 3 and Unit 4 condenser tube bundles will be replaced under the Extended Power Uprate Project.
250 | 2502013002 | 2013-02-11 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Turkey Point 3 | P | WE | PO | 99 | On February 11, 2013, a turbine gland sealing steam spillover valve was being bypassed in preparation for calibration of the actuator. Opening the bypass valve created a flow path for gland steam to the condenser, which caused a reduction in gland sealing steam pressure and decrease in main condenser vacuum. Main condenser vacuum reached the turbine trip setpoint, which caused an automatic reactor trip. The Auxiliary Feedwater (AFW) System actuated automatically due to low steam generator (SG) levels following the reactor trip. Recovery from the reactor trip was uncomplicated. AFW was secured and main feedwater was used for SG water level control. Decay heat removal was to atmosphere via the steam dump valves.<br><br> The root cause was determined to be ineffective implementation of the operational standards as demonstrated by: 1) improper monitoring of plant parameters during the manipulation of the spillover bypass valve, and 2) utilizing an equipment clearance order in lieu of an operating procedure when bypassing the gland seal spillover valve. Corrective actions include: 1) Revise procedural guidance for bypassing spillover valves, and 2) Implement an improvement plan to reinforce operational standards.
250 | 2502013003 | 2013-02-18 | QR6 | Manual Reactor Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 72 | On February 17, 2013, with the Unit 3 reactor in Mode 1 at approximately 99% power, the 3A Reactor Coolant Pump (RCP) No. 1 seal leak-off became elevated and erratic. A unit shutdown was commenced on February 18, 2013 at approximately 0055 when seal leak-off increased to 5.5 gpm. At approximately 0130, the reactor was manually tripped at approximately 72% power when seal leak-off flow reached 6 gpm. The 3A RCP was then secured and No. 1 seal leak-off was isolated. The Auxiliary Feedwater (AFW) System actuated as designed based on low steam generator (SG) levels as a result of the reactor trip. At approximately 0316, AFW was secured with main feedwater supplying the SGs and decay heat removed via the atmospheric relief valves. There were two causes: 1) The seal runner o-ring was damaged during installation. 2) The RCP shaft shoulder critical criterion of 60% minimum mating surface area was not attained after manual machining (stoning). Corrective actions include replacing the 3A RCP seal, review of performance of other RCP seals at both Turkey Point units, and revision of the RCP maintenance procedure to provide additional guidance for proper seal installation and post-machining inspections.
250 | 2502013005 | 2013-03-12 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Turkey Point 3 | P | WE | SU | 3 | On March 12, 2013 at approximately 1431 with Unit 3 in Mode 2 at approximately 3% rated thermal power, an automatic reactor trip occurred due to a turbine inlet pressure spike during turbine control valve (TCV) testing. Turbine inlet pressure enables the Reactor Protection System (RPS) at power reactor trips. One at power reactor trip is a turbine trip initiated by closure of both turbine stop valves (TSV). The pressure spike enabled the at power trips while the TSVs were closed causing the reactor trip. All control rods inserted and plant parameter response was as expected. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The cause of the reactor trip was the unexpected pressure spike resulting from a quick opening of the No. 3 TCV of sufficient magnitude to satisfy the P-7 interlock with the TSVs closed. Corrective actions include the following procedure changes: 1) Close main steam isolation valves and turbine stop drain valves when testing TCVs, 2) Caution that TCV testing can lead to turbine inlet pressure spikes which could result in reactor trip, and 3) Ensure that the main steam header is depressurized prior to cycling a TCV during post maintenance testing. With plant response as expected, the risk associated with this low power trip is judged very low.
250 | 2502013007 | 2013-05-10 | QR5 | Turbine Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 25 | On May 10, 2013, Unit 3 reactor was manually tripped in response to a sudden loss of turbine load at approximately 25% reactor power. Plant power was being reduced during a controlled shutdown for planned maintenance. The operating crew observed generator megawatts suddenly reduced to zero, with no operator action. The crew manually tripped the reactor. All systems responded as expected, except for source range nuclear instrument N-3-32 which experienced a loss of detector voltage. <br><br> The root cause was determined to be an incorrect deadband pressure value of the Load Drop Anticipatory (LDA) circuit in the turbine control system. <br><br> Corrective actions included reducing the dead band of the LDA pressure arming setpoint and adding indicator lights to the turbine control system display to identify armed status.
250 | 2502014005 | 2014-08-11 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Turkey Point 3 | P | WE | PO | 100 | On August 11, 2014 at approximately 1028 hours with Unit 3 at approximately 100% reactor power, a manual reactor trip was initiated in response to a loss of instrument air (IA). The Auxiliary Feedwater System automatically initiated as designed. The unit was subsequently stabilized in Mode 3 with IA restored. An automatic safety injection (SI) actuation occurred as a result of main steamline high differential pressure. High head safety injection (HHSI) pumps, residual heat removal (RHR) pumps, and emergency diesel generators (EDG) automatically started as designed due to the SI signal. Based on plant conditions, the HHSI and RHR pumps did not inject into the reactor coolant system. The running compressor was unloaded inadvertantly at approximately 1020 hours and the standby compressors started but did not load due to a latent design error in the start logic. Although the standby compressors were restarted and loaded by approximately 1029 hours, IA decreased below the pressure required for the reactor trip. The SI actuation was caused by inadequate control of primary plant parameters during a loss of IA to containment. Corrective actions include: Removing an unneeded permissive in the standby compressor control logic which prevented the compressor from loading, and revising the loss of IA procedure to provide additional guidance on control of pressurizer level and pressure when IA is lost.
250 | 2502017001 | 2017-03-18 | C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) |  |  | X | [13 empty] | X | [28 empty] | Turkey Point 3 | P | WE | PO | 100 | On March 18, 2017 at approximately 1107 hours, the Turkey Point Unit 3 reactor tripped from 100% power as a result of an electrical fault on the 3A 4kV vital bus. The Auxiliary Feed Water System actuated as expected, and the 3A Emergency Diesel Generator started but did not load, as designed, due to the lockout of the 3A 4kV bus. The 3A 4kV bus remained de-energized and the reactor was stabilized in Mode 3. Both Unit 4 High Head Safety Injection (HHSI) pumps were out of service for maintenance. The 3A HHSI pump was unable to be powered from the 3A 4kV bus resulting in a loss of the Safety Injection safety function for approximately 2.5 hours on both Units 3 and 4. The safety function is achieved by operation of two of the four pumps which are shared by both units. The loss of the 3A 4kV bus was caused by an electrical fault created by a conductive foreign material that had entered the current-limiting reactor cubicle that bridged an air gap between an uninsulated bus bar and the cubicle wall. The foreign material was a carbon fiber mesh used to reinforce a Thermo-Lag installation taking place in the 3A 4kV switchgear room. Corrective actions include: 1) The Thermo-Lag installation procedure will be revised to incorporate additional precautions for handling Thermo-Lag materials, and 2) the Engineering product risk and consequence assessment process will be revised to ensure a review is conducted of Safety Data Sheets for material being considered in the design. This event had no effect on the health and safety of the public.
250 | 2502019001 | 2019-05-18 | QR6 | Manual Reactor Trip | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | On 5/18/19 at 11:08am, the Turkey Point Unit 3 reactor was manually tripped from 100% power due to lowering levels in all three Steam Generators. Auxiliary Feedwater automatically actuated and was subsequently secured at 11:53am during plant post-trip restoration. The cause of the event was a grid disturbance that resulted in the Turbine Control Valve (TCV) position deviation faults. All four of the TCVs drifted closed in response to the faults by design. As a result, levels in all three Steam Generators steadily decreased, prompting the Unit 3 Reactor Operator to initiate a manual trip of the Unit 3 reactor. All systems responded as designed during the transient.
250 | 2502020002 | 2020-08-17 | QP5 | Excessive Feedwater Flow | [45 empty] | Turkey Point 3 | P | WE | PO | 86 | On 8/17/2020 at 2109 hours with Unit 3 at 100% power, the Low Pressure Feedwater Heater Bypass Control Valve inadvertently opened, causing an automatic turbine runback. Due to a deficiency associated with the design of the turbine runback program, levels in the Steam Generators increased in response to the runback. At approximately 86% reactor power, when 3C Steam Generator level increased to 78%, the reactor was manually tripped as directed by procedure. Following the reactor trip the Auxiliary Feedwater System automatically initiated, as expected, to maintain levels in the Steam Generators while Main Feedwater remained in service. Unit 3 was maintained stable in Mode 3 following the event. <br /><br /> This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for the manual reactor trip and automatic initiation of the Auxiliary Feedwater System, which is listed as a reportable safety system by 10 CFR 50.73 (a)(2)(iv)(B)(6).
250 | 2502020004 | 2020-08-20 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Turkey Point 3 | P | WE | PO | 34 | On 8/20/2020 at 23:58 hours the Unit 3 reactor was manually tripped from 34% power following an automatic trip of the 3B Steam Generator Feed Pump (SGFP). The 3B SGFP had tripped as a result of a low suction pressure condition that occurred when the pump recirculation valve was manually closed, which is the normal position for the plant conditions. The valve was open due to inadvertent mispositioning of the SGFP Recirculation Master Controller. The Auxiliary Feedwater System automatically initiated in response to the trip of the 3B SGFP. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for actuation of the Reactor Protection System (RPS) and Auxiliary Feedwater System (AFW).
250 | 2502021001 | 2021-03-01 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Turkey Point 3 | P | WE | PO | 100 | On 3/1/21 at 11:08 hours, Turkey Point Unit 3 experienced an unplanned reactor trip from 100% power. Restoration from a routine test of the Reactor Protection System (RPS) was in progress when the reactor trip occurred. As expected for the conditions, the Auxiliary Feedwater System (AFW) automatically initiated in response to the reactor trip to maintain Steam Generator levels in normal bands. All equipment required for the immediate reactor trip response functioned normally. <br /><br /> A malfunction of the B-train Reactor Trip Breaker cubicle cell switch during the RPS test restoration caused the reactor trip. The breaker and cell switch have since been replaced and Unit 3 returned to normal power operation. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) for initiation of the Reactor Protection [10 CFR 50.73(a)(2)(iv)(B)(1)] and Auxiliary Feedwater [10 CFR 50.73(a)(2)(iv)(B)(6)] systems.
251 | 2511987001 | 1987-01-06 | QR8 | Spurious Reactor Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On January 6, 1987, while unit 4 was at 100% power, a reactor trip occurred. During the performance of operating surveillance procedure (OSP) 4-OSP-059.4, Power Range Nuclear Instrumentation Analog Channel Operational Test, the acceptance criteria for the delta-flux input to the over-power delta temperature (OPDT) and over temperature delta temperature (OTDT) setpoints was not met for the nuclear power range instrumentation channel N-42. N-42 was declared out of service and the associated bistables for the reactor protection channel II were tripped. Later on that day a 40 msec spike was received on channel III OTDT and OPDT which completed the 2 out of 3 channels tripped logic for the OTDT and OPDT reactor trip signals and a reactor trip occurred. The cause of the momentary spike was first attributed to a cracked test jack. After the unit was returned to power operation, additional spiking on channel III was observed. Further investigation discovered that the isolation amplifier for the lower flux to f(delta-q) on power range channel N-43, was experiencing intermittent failures. The isolation amplifier was replaced. A post trip review was completed which verified that the plant response to this event was as expected for a reactor of this type.
251 | 2511988010 | 1988-08-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | At 2121 on August 19, 1988, with Unit 4 at 100% power, a reactor trip occurred due to Lo-Lo steam generator (SG) level on the B SG. At 1650, the Instrumentation and Controls group commenced procedure 0P 14004.1, "Steam Generator Protection Channel - Periodic Test." While performing the SG pressure portion of the periodic on the B SG, the B feedwater regulating valve drove shut resulting in reduced flow and ultimately in a reactor trip. The cause of the trip was cognitive personnel error in that contrary to the procedure, the incorrect channel of steam flow input to the B feedwater regulating valve was selected. Contributing causes were an inadequate independent verification of switch position and a lack of identification of the channel number on the switch placard. After troubleshooting of the entire control circuit, feedwater regulating valve, and actuator to assure that no failures had contributed to the transient, and following completion of the post trip review, the unit was returned to service .on August 22, 1988. Similar load threatening periodic tests where incorrect channel selection could place the unit in a transient will have the channel selections independently verified by a qualified operator. The identification placards will be changed to reflect protection channel numbers.
251 | 2511989011 | 1989-09-15 | QR5 | Turbine Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | At 0426, on September 15, 1989, with Unit 4 operating at 100 percent power, a manual reactor trip was initiated. A High Pressure (HP) turbine stop valve Auto Stop Oil line weld leak identified at 0045 led to closure of the stop valve. When the control rods failed to insert in automatic or manual in response to the sudden turbine power decrease, as called for by a T-AVE/T-REF mismatch signal, a manual reactor trip was initiated. A failure of the 4C Steam Generator foodwater control valve to close during a subsequent Feedwater Isolation (slow closure) signal resulted in overfeed of the Steam Generator and "shrink" of the Reactor Coolant System inventory. A manual Safety Injection signal was initiated by procedure because pressurizer level dropped below 12 percent. The Auto Stop Oil line weld failure was due to inadequate field installation and fatigue failure. The failure of the control rods to drive in automatically was due to an inadequacy in the refueling Preventive Maintenance program. The Automatic Rod Control Speed Signal output summator was out of calibration. The feedwater control valve failure to close is due to an inadequate procedure used during a recent modification. The thermal transient experienced did not affect the structural integrity of Reactor Coolant System components. Various corrective actions have been/will be performed.
251 | 2511990003 | 1990-04-09 | QR8 | Spurious Reactor Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On April 9, 1990 at 1814 EDT, with Unit 4 in Mode 1 (Power Operation) at 100 percent power, a Reactor Protection System actuation occurred due to a failure of a Reactor Coolant Pump (RCP) underfrequency relay power supply capacitor. <br /><br /> The reactor trip occurred because one of three reactor coolant pump power supply breakers opened with the reactor at greater than 45 percent power. The faulty underfrequency relay was replaced and Unit 4 was returned to service. The RCP power supply underfrequency relays on both Unit 3 and Unit 4 have been replaced with new models. A review of the failure modes of the replacement relays will be performed and planned maintenance will be developed as appropriate. <br /><br /> On April 9, 1990, at 1914 EDT, a four hour report of the event was made to the NRC in accordance with 10 CFR 50.72.
251 | 2511990004 | 1990-05-26 | QR6 | Manual Reactor Trip | [45 empty] | Turkey Point 4 | P | WE | SU | 1 | On May 26, 1990, at 0556 EDT, during start-up of both units, with units 3 in Mode 3 (Hot Standby) and Unit 4 in Mode 2 (Start-up) at approximately one (1) percent power, a licensing trainee under the direction of the Unit 4 reactor operator manually tripped the Unit 4 reactor. This occurred during the restoration phase of the turbine valve test on Unit 4. The Unit 4 reactor was manually tripped in an erroneous response to step 7.2.59 of procedure 4-OSP-089 "Main Turbine Valves Operability Test." Subsequent to the trip, the operators verified the unit to be in a stable condition by using applicable emergency operating procedures. <br /><br /> This event was caused by cognitive personnel error on the part of plant licensed operators. To preclude recurrence of this event, Procedures 3-OSP-089 AND 4-OSP-089 have been revised to clarify the intent of step 7.2.59. In addition, this event is being reviewed with applicable operations personnel. <br /><br /> On May 26, 1990, at 0634 EDT, the NRC was notified of this event in accordance with 10 CFR 50.72 (b) (2) (ii)
251 | 2511990008 | 1990-08-12 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | At 1625, on August 12, 1990, with Unit 4 in Mode 1 at 100 percent power, the 4B condensate pump motor automatically tripped on overcurrent. The 4A condensate pump automatically started as designed. The 4A steam generator feedwater pump tripped unexpectedly and initiated a turbine runback. The turbine runback and the reduced feedwater flow caused the steam generator levels to decrease. Operator actions were taken in an attempt to restore steam generator water levels. At 1628, a two-out-of-three Steam Generator A low-low level trip signal initiated an automatic reactor trip and subsequent automatic turbine trip. The unit was stabilized in Mode 3 (Hot Standby) using existing site procedures. The 4B condensate pump motor trip was caused by a phase-to-phase short. FPL postulates that a weak spot in the insulation was created when the motor was rewound in 1980. The weak spot degraded to the point that moisture could penetrate the insulation. The moisture provided an electrical short across the coils. The unexpected 4A steam generator feedwater pump (SGFP) trip was caused by an incorrect setpoint on an Agastat time delay breaker trip relay. The 4A and 4B SGFP breaker trip relays have been recalibrated. The condensate pump is being repaired.
251 | 2511992004 | 1992-03-26 | QR8 | Spurious Reactor Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 28 | On March 26, 1992, unit 4 was operating at approximately 28% power. At 1015 hours, during the performance of Procedure OP 4004.4, "Containment Isolation Racks QR50 and QR51 Periodic Test," a reactor trip occurred. All systems responded as designed. <br /><br /> During the completion of OP 4004.4, the two out of three actuation logic was completed but the train 4B initiation signal was not blocked. As a result, a B train Safety Injection, and a B train Containment Phase A Isolation was initiated, followed by an automatic reactor trip. <br /><br /> The cause of the event was a worn test switch resulting in a contact "race" between the actuating contact set and the blocking contact set in the test switches. A contributing cause was a procedural inadequacy. <br /><br /> Corrective actions include switch replacement and a procedure revision.
251 | 2511993002 | 1993-06-22 | QR5 | Turbine Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 33 | On the morning of June 22, 1993, Turkey Point Unit 4 was at 100% power and conducting a turbine trip test on the main turbine in accordance with procedures and procedural requirements. At the successful completion of the turbine trip test, the plant operators were unable to relatch the turbine trip. Turkey Point Unit 4 was reduced in power with the intent of taking the turbine off line to trouble shoot and repair, if necessary, the turbine trip latching mechanism. <br /><br /> At 1231 Eastern Daylight Time (EDT), with reactor power having been reduced to approximately 33% power, loss of turbine control oil pressure resulted in a turbine anti-motoring trip followed by a generator lockout. Based on the turbine anti-motoring indication and the generator lockout, plant operators manually tripped the turbine. A reactor trip at 1232 EDT resulted from the manual turbine trip. The NRC was notified in accordance with 10 CFR 50.72 (b) (2) (ii) June 22, 1993, at 1315 EDT.<br /><br /> Extensive investigations of probable cause for the turbine anti-motoring trip and generator lockout were completed. The investigations concluded that the cause was an inadvertent operation of the auxiliary governor trip lever by personnel restoring the turbine controls to normal after the turbine trip test. The unrelated inability to relatch the turbine trips was caused by incorrect clearances in the overspeed trip block between the trip relay and the relay bushing, and between the relay cup valve and the relay cover plate. These clearances were corrected and Unit 4 was returned to service on June 26, 1993.
251 | 2511993003 | 1993-08-16 | QP5 | Excessive Feedwater Flow | [45 empty] | Turkey Point 4 | P | WE | PO | 28 | On August 16, 1993, Turkey Point Unit 4 was in Mode 1 at 28% power. The two high pressure feedwater heaters were being placed in service. The restoration of the feedwater heaters was not done smoothly, and feed flow to the steam generators was severely curtailed. The loss of flow was recognized, an extra condensate pump and feed pump were started, and steam generator levels began to recover. Simultaneously, both feedwater heaters were completely restored to service in an attempt to aid in the recovery of feed flow. As a result steam generator levels rose faster than the reactor operators could control them. At 2233, the turbine tripped on high-high level in the 4C steam generator, which generated an automatic reactor trip.<br /><br /> The cause of the event was personnel error in that the high pressure feedwater heaters were not returned to service correctly. Contributors were an inadequate pre-evolution briefing, inadequate knowledge of the operation of the heater inlet valves, inadequate communications, and existing equipment failures which required both high pressure feedwater heaters to be valved out. <br /><br /> The operators involved were counselled, the procedure is being revised, management expectations for briefings are being emphasized, and operators are being trained on the operation of the three-way inlet valves.
251 | 2511994004 | 1994-09-23 | QR3 | Reactivity Control Imbalance | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On September 23, 1994, Unit 4 tripped automatically from 100% rated power. Personnel working in the 4C 4160 VAC bus switchgear inadvertently caused a bus lockout, resulting in a loss of the backup power supply to the rod control system. The normal power supply to the 1AC rod control cabinet (already degraded), also failed, and 12 rods dropped. The resultant pressure drop and negative flux difference lowered the OT delta T setpoint below actual delta T, and the reactor tripped on OT delta T. <br /><br /> The C bus lockout was caused by the jarring of a differential relay, due to an interference between a breaker cubicle door and the wall of the switchgear room. The backup power supply failure was due to a faulty regulator transistor. <br /><br /> The reactor trip on OT delta T progressed as expected, and therefore did not impact the health and safety of the public. <br /><br /> The faulty backup power supply was replaced, and 15 similar power supplies were inspected. Maintenance history for the power supplies was reviewed. Replacement power supplies are being evaluated. The interference between the cubicle door and the wall is being removed. The differential relays, as well as others with the potential to cause a spurious bus lockout, are being relocated off the cubicle doors.
251 | 2511994006 | 1994-11-30 | QR5 | Turbine Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On November 30, 1994, Unit 4 tripped automatically because of the failure of a flexible link connection between the main generator B phase bus and its associated isolated phase bus bar. The flexible link came loose and grounded against the isolated phase bus duct work causing a generator lockout, turbine trip and automatic reactor trip. At the time of the trip Unit 4 was in Mode 1 operating at approximately 100% power. All systems responded as expected to the automatic reactor trip.
251 | 2511996001 | 1996-04-09 | QR6 | Manual Reactor Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 17 | On April 09, 1996, Florida Power & Light Company's Turkey Point Unit 4 was operating in mode 1 at 17% power. Unit 4 was being returned to service following a successful turbine overspeed test. <br /><br /> At 1759 on April 09, 1996, turbine electric load increased from approximately 90 megawatts electric (MWe) to approximately 237 MWe with no operator action. Steam flow greater than feed flow alarms were received on all three steam generators. Average Reactor Coolant Temperature (Tave) began to lower in response to the increased steam demand. A manual reactor trip was directed. At 1800 the manual reactor trip was executed. The plant responded as expected with the exception that Rod Position Indication (RPI) for control rod N-9 indicated approximately 16 steps immediately following the trip. All Rod Bottom Lights were energized, confirming that all Rod Control Cluster Assemblies had inserted past the 20 step withdrawn position. Subsequent testing confirmed an RPI console meter problem only; all control rods promptly and fully inserted following the reactor trip. <br /><br /> The cause of the reactor trip was prompt manual action on the part of the operating crew in response to degrading plant conditions. The cause of the unexpected electrical load increase was corrosion products interfering with impeller oil flow in the speed sensing portion of the turbine governor. <br /><br /> The governor valve was disassembled and inspected for cleanliness and corrosion products. The impeller oil orifice was cleaned and the governor reassembled.
251 | 2511997002 | 1997-04-23 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Turkey Point 4 | P | WE | PO | 100 | On April 23, 1997, Unit 4 tripped from 100% power. An I&C Specialist, working inside the back of the Main Control Board, apparently bumped a relay, causing a false Turbine Overspeed Protection signal. The signal caused turbine control valves to close (loss of load), and the reactor tripped on Over Temperature Delta-T. The root cause of the event was inadequate physical protection. The contact arm on this relay is not enclosed, and can be actuated with very slight force. Contributors were inadequate work controls and a loss of lighting inside the panel during the work. The work document did not indicate that the work had the potential to trip the unit. This relay and others like it will be evaluated to determine if they can be enclosed or relocated, to prevent inadvertent actuation. Until the evaluation is complete, Nuclear Plant Supervisor (NPS) permission is required to work inside this panel, and the NPS will brief the workers on the location and sensitivity of the relays. Administrative procedures governing the inadequate work controls will be revised to capture the lessons learned.
251 | 2512000001 | 2000-01-24 | QP5 | Excessive Feedwater Flow | [45 empty] | Turkey Point 4 | P | WE | PO | 95 | At approximately 7 :30 AM on January 24, 2000, FPL's Turkey Point Unit 4 reduced power to 95% t o investigate main feedwater flow instabilities caused by the "A" Steam Generator (SG) Feedwater Flo w Control Valve, FCV-4-478. At approximately 11:14 AM feedwater flow appeared to increase causing a SG level deviation. The Operators placed FCV-4-478 in manual operation. A preliminary determination of valve internal problems versus control problems resulted in the decision to shut down the Unit b y performing a fast load reduction. At approximately 11:42 AM, the Reactor Control Operator (RCO) manually tripped the reactor due to difficulty in controlling SG levels. All rods were fully inserted and all systems except Feedwater functioned as designed. The immediate cause of the reactor trip was a manual action taken by the RCO in response to Mai n Feedwater flow instabilities. The underlying cause of the trip was a failure in FCV-4-478 valve internals. The valve cage had disengaged from the valve body web. The root cause of the failure of FCV-4-478 is inadequate change management in the 1980's when the practice of periodic replacement of the cage was stopped; specifically, FPL failed to require periodic re-torque of a re-used FCV cage. FCV-4-478 was repaired. FPL established inspection controls to monitor for signs of valve degradation. Cage torque will be verified for all feedwater FCV at the next opportunity.
251 | 2512001001 | 2001-01-25 | QR3 | Reactivity Control Imbalance | [45 empty] | Turkey Point 4 | P | WE | PO | 45 | On January 25, 2001, Turkey Point Unit 4 was at 100% power performing periodic rod exercises. At 1535, while driving in Shutdown Bank B, rod H-6 of Shutdown Bank B partially dropped into the core to about 120 steps. At 1545, reactor power was reduced to less than 75% power, in accordance with Technical Specification 3.1.3.1. FPL decided to not recover the partially dropped rod or withdraw Shutdown Bank B, requiring shutdown of Unit 4. At 1950, rod H-4 in Control Bank D dropped to about 150 steps while Control Bank D was being inserted as part of the reactor shutdown. At 1951, the reactor operator manually tripped the reactor due to a single dropped rod in two different banks. All systems operated as designed and the plant was stabilized in Mode 3. The root cause of the initial partially dropped rod was an open circuit in the Movable Gripper circuit caused by a dark green substance. The substance is being analyzed to determine its nature and origin. The root cause of the second dropped rod and the manual reactor trip is human error in communicating real time configuration while troubleshooting in-service equipment, due to weakness in the troubleshooting plan. Personnel involved in the event were counseled and training briefs were issued to all plant personnel. Procedures will be revised to enhance the communications during troubleshooting on in-service equipment.
251 | 2512004002 | 2004-05-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On May 14, 2004, at about 1729 hours, an automatic reactor trip occurred from 100% reactor power after the 4A Steam Generator (S/G) Feedwater Flow Control Valve FCV-4-478 closed unexpectedly. This resulted in an automatic reactor trip actuated by steam flow/feedwater flow mismatch coincident with 4A S/G low-level. The Reactor Operator (RO) identified the condition causing the "S/G A Level Deviation" annunciation and placed FCV-4-478 In manual control. The RO then attempted to manually trip the reactor; however, the reactor automatic trip Initiated first. All three turbine driven auxiliary feedwater (AFW) pumps started as expected, supplying the S/Gs. The spurious closure of FCV-4-478 was caused by the failure of a capacitor in the Hagan feedwater flow controller, which caused the controller output to drive to zero closing the feedwater regulating valve. This caused the steam flow/feedwater flow mismatch coincident with the 4A steam generator low level. An Engineering Evaluation of the failed component determined that the capacitor failure mode was a short circuit and the capacitor was being utilized in a circuit for which it was exposed to an operating voltage above its ratings. The root cause of the event was inadequate implementation of a plant design change to eliminate an originally supplied undersized capacitor design. Immediate corrective actions included replacement of the Hagan Flow Controller FC-4-478 and the associated Hand/Auto Station FC-4-478F, followed by automatic transfer testing and Post Maintenance Testing. Controller power loss manual/auto fail-over tests were also successfully performed on FC-4-488 andFC-4-498 (in the other two control loops). Equipment operated as expected during the event and all parameters were within the envelope of the Updated Final Safety Analysis Report (UFSAR) analysis for Loss of Normal Feedwater. As a result, the event did not compromise the health and safety of the public.
251 | 2512004004 | 2004-12-25 | QL7 | Degraded condenser vacuum | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On December 25, 2004, at 07:36 EST with Unit 4 operating in Mode 1 at 100 percent power, Turkey Point Unit 4 experienced a declining vacuum in the main condenser. When condenser vacuum reached less than 22 inches Hg, reactor trip criteria was met and the plant was manually shut down. Decay heat was removed via theAtmospheric Steam Dumps. The Auxiliary Feedwater System automatically started as expected. All rods inserted correctly and all systems functioned as designed. The apparent cause of the lowering condenser vacuum was failure of a turbine slop drain line inside the condenser. Corrective action was taken to temporarily plug the inlet and outlet ends of the leaking slop drain until the condenser could be accessed and permanent repairs completed during the 2005 Spring Refueling Outage. The apparent cause of the failed slop drain line was determined to be a poor bi-metallic weld coupled with a weak joint design and inadequate supports. Lab analysis of the failed bi-metallic weld indicated it failed in high cycle fatigue. Failure of both of the piping U-bolt supports allowed vibration to cycle the bi-metallic weld to the point of failure. The health and safety of the public were not affected by this event. Unit 3 is susceptible to the same failure; therefore, the slop drains have been plugged. They will have similar repairs in the next refueling outage.
251 | 2512005001 | 2005-03-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On March 22, 2005, at 0346 hours the 4A Steam Generator Feed Pump (SGFP) tripped on over-current due to a fault within the pump motor. As a result, a turbine runback from 100% power to 78% power occurred and Steam Generator levels decreased to 15%. At that time, the reactor was manually tripped in accordance with station procedures. The operating crew verified the reactor and turbine were tripped, and that emergency power to the 4 KV buses and safety injection were not required. The plant was verified to be stable prior to transitioning from power operation to hot standby. All control rods inserted as expected. Auxiliary Feedwater automatically actuated as expected when Steam Generator narrow range levels decreased below 10%. Plant systems functioned as designed to remove heat and safely shut down the reactor. The health and safety of the public were not affected by this event.
251 | 2512005002 | 2005-06-27 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Turkey Point 4 | P | WE | PO | 100 | On June 27, 2005, at 0316, Turkey Point Unit 4 reactor was automatically tripped from 100% power following a turbine trip due to a Main Generator lock out generated from an electrical fault of the Unit 4 Main Transformer. The transformer was recently installed during the refueling outage in Spring 2005. The fault ruptured the transformer tank releasing oil and caused a fire that damaged the transformer and adjacent equipment. At 0327, an Unusual Event was declared based on the fire in the plant protected area lasting longer than 10 minutes. The site fire brigade responded and extinguished the fire. Offsite fire fighting assistance was requested, but was not used to extinguish the fire. The fire was extinguished and the Unusual Event was terminated at 0500. All plant systems functioned as designed during and after the event. The operating crew controlled and stabilized the plant, and therefore the health and safety of the public was not adversely impacted by this event. The root cause for the Turkey Point Unit 4 Main Transformer failure was a failed manufacturing process employed by the vendor's supplier of the clamping ring. Corrective actions included replacement of the Main Transformer and repair/replacement of components damaged by the resultant fire.
251 | 2502008001 | 2008-02-26 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On February 26, 2008 at approximately 1309 hours, a momentary grid voltage disturbance occurred that caused a reactor trip of both Turkey Point Units 3 and 4 when both channels of safety-related 4 KV bus undervoltage relays for each unit actuated after a one second time delay. In addition, at approximately 1620, while shutting down the Unit 4 4A steam generator feed pump after transferring to standby feedwater, auxiliary feedwater (AFW) automatically actuated due to a red flag semaphore still present on the 4B SGFP control switch since the switch had not been taken to the stop position. This AFW actuation was inadvertent. The grid voltage disturbance occurred due to human error when a Protection and Control field engineer disabled both levels of local protection at an electrical substation which then failed to actuate when a fault occurred during equipment troubleshooting. The inadvertent AFW actuation occurred due to inadequate procedural guidance. Since plant response to the grid disturbance was as designed and AFW was not required to mitigate any plant condition at that time, the safety significance of the plant trips and inadvertent AFW actuation are minimal. Corrective actions relating to the grid disturbance include a new procedure setting requirements related to disabling protection. Corrective action for the inadvertent AFW actuation entails future procedure changes to ensure the control switches for various components powered by the 4C 4 KV bus are placed in the appropriate position after a loss of power and to verify the control board switches are green flagged.
251 | 2512008001 | 2008-02-29 | QP5 | Excessive Feedwater Flow | [45 empty] | Turkey Point 4 | P | WE | PO | 10 | On February 29, 2008, Turkey Point Unit 4 was in Mode 1. Power escalation was in progress following an automatic reactor trip that occurred on February 26, 2008 due to an under voltage condition on the electrical grid. At 0447, following the turbine and main generator synchronization the operating crew loaded the main generator abnormally fast. The operator at the feedwater controls was using the Main Feedwater Regulating Bypass Valves to control steam generator (SG) levels in manual. The increasing steam demand resulted in SG level fluctuations causing the SG levels to "swell." The operator did not stabilize SG levels and he did not communicate his concerns to the operating crew. The 4A SG level exceeded 75% Narrow Range (i.e., the procedural upper limit for performing a manual reactor trip due to high steam generator level). At 0451, with Turkey Point Unit 4 reactor power at 10%, the operating crew initiated a manual reactor trip due to high level in the 4A steam generator. There were no equipment issues, and no adverse effects on plant parameters. The root cause of the event is insufficient guidance for the initial loading of the main generator and for stabilizing power while preparing to transfer to automatic feed regulating valve control. Corrective actions include procedural changes to provide guidance for ramp rates during initial turbine loading and appropriate hold points to ensure proper control of plant parameters. Additional corrective actions have been generated to address control room oversight and effective communications.
251 | 2512010002 | 2010-01-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Turkey Point 4 | P | WE | PO | 30 | On January 11, 2010, at approximately 1058 an unplanned manual reactor trip on Unit 4 was initiated due to Steam Generator (SG) level being greater than 75%. The unit was stabilized in Mode 3 on off-site power with main feed for decay heat removal. The unit trip was precipitated by the manual stop of the 4A SG feedwater pump (SGFP) due to a degrading oil inventory. Plant response to the loss of the 4A SGFP and the subsequent reactor trip was as expected. The root cause of the loss of the 4P1A SGFP lube oil level was determined to be unresponsive seal water injection controls to the pump outboard bearings which resulted in inadequate seal water injection flow to the 4P1A SGFP outboard seal coincident with SGFP bearing cavity drain blockage. Corrective actions include: 1) Replace obsolete Unit 3 and 4 SGFP seal water hand controller stations with more responsive controller stations. 2) A preventive maintenance activity will be established to verify the bearing seal cavity drains are clear on a periodic basis, after completion of maintenance and prior to SGFP start following an outage.
251 | 2512010004 | 2010-09-08 | QR8 | Spurious Reactor Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On September 8, 2010, with Unit 4 operating at 100% power, an unplanned automatic reactor trip occurred at approximately 13:45 during replacement of the 4B Reactor Protection System (RPS) Left Turbine Stop Valve Closure Logic Relay 4-SL-X-B [JC:RLY]. All rods fully inserted and all systems responded as designed and the unit was stabilized in Mode 3. At 15:52, an 4-hour report (EN# 46235) was made to the NRC Operations Center in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) due to an automatic reactor trip and actuation of the Auxiliary Feedwater System. The reactor trip was caused by the opening of the 4B RPS trip breaker due to the de-energizing of reactor trip relays RT-9 and RT-10 when the two leads were lifted off terminal 1 of relay 4-SL-X-B during the replacement evolution. Deficiencies in the work order package and guiding procedure failed to establish and/or verify the plant conditions required to successfully complete the evolution. Corrective actions included replacement of the degraded relay 4-SL-X-B and revisions to the work order package and guiding procedures to ensure the Reactor Trip Bypass Breaker shall be in the closed position when replacing any reactor protection relay while the unit is in operational Modes 1 or 2.
251 | 2512010006 | 2010-09-21 | QR8 | Spurious Reactor Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On September 21, 2010, at approximately 2017, with Turkey Point Unit 4 operating at 100% power, an unplanned automatic reactor trip occurred while the quarterly surveillance for the Channel II High Pressurizer Pressure Protection Loop (P-4-456) was in progress. The cause of the trip was attributed to Channel I spurious trip signal of the High Pressurizer Pressure Protection Loop (P-4-455) coincident with Channel II being already tripped due to the surveillance procedure. All rods fully inserted and all systems responded as designed and the unit was stabilized in Mode 3. At 2228, a report (EN#46265) was made to the NRC per 10 CFR 50.72(b)(2)(iv)(B) for actuation of Reactor Protection System with the reactor critical and per 10 CFR 50.72(b)(3)(iv)(A) for actuation of the Auxiliary Feedwater System. Excessive separation found in the electrical bifurcated pins of the ELCO connectors of the NUS instrument Comparator (PC-4-455A) module caused the Channel I spurious trip signal. Corrective actions include replacement of Comparator PC-4-455A, providing formal training for Maintenance personnel to properly inspect NUS modules with ELCO connectors, adding quantitative criteria in site procedures to perform connector inspection, and inspecting other NUS module connectors installed at the plant that could have electrical pins with excessive separation.
251 | 2512010008 | 2010-12-09 | QL6 | Condenser Leakage | [45 empty] | Turkey Point 4 | P | WE | PO | 17 | At 22:00 on December 9, 2010, Unit 4 had indication (high sodium) of a condenser tube leak. A rapid power reduction to less then 5% was commenced in accordance with plant procedures as the sodium levels increased to greater than 250 ppb (action level 3). Chemistry confirmed that the high sodium level was due to salt water intrusion from the 4BN Main Condenser tube bundle. A management decision was made to shutdown the reactor in accordance with plant procedures by manually opening the reactor trip breakers at about 22:58:13 from approximately 17.5% power. All systems functioned as designed and there was no impact on the health and safety of the public. The NRC was notified (Event Number 46471) at approximately 01:25 (EST) on December 10, 2010. Corrective actions involved plugging the failed tube and four other tubes with minimal indications. The failed tube was removed during the next refueling outage (RFO PT4-26) and sent for analysis. The analysis indicated the root cause to be axial cracking caused by high cycle fatigue. Eddy Current Testing was performed during RFO PT4-26 with conservative plugging criteria to plug all tubes with indications of greater than 50% wall-loss. Long term, the Unit 3 and Unit 4 condenser tube bundles are currently planned for replacement under the Extended Power Uprate Project.
251 | 2512013002 | 2013-04-19 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Turkey Point 4 | P | WE | PO | 29 | On April 19, 2013 with Unit 4 in Mode 1 at approximately 29% of rated power, a reactor trip occurred as a result of degraded voltage at the 480V load centers. Upon receipt of the degraded voltage signal, loads were shed on the vital buses, and both Emergency Diesel Generators started and repowered the buses. The reactor tripped due to the loss of the Reactor Coolant Pumps during bus load shedding. All control rods inserted. The unit stabilized via natural circulation in Mode 3. The Auxiliary Feedwater System initiated to maintain water level in the steam generators. Offsite power was restored to the vital buses in approximately 30 minutes. The event was initiated by lowered exciter voltage during generator testing after an extended power uprate outage to obtain data to establish generator protection relay settings. The use of a test instruction instead of a plant test procedure for the test, and inadequate risk recognition by station personnel were detemined to be the root causes. Corrective actions include eliminating the option to use test instructions for controlling plant operation, and developing and implementing a comprehensive program on risk recognition and management.
251 | 2512014002 | 2014-05-25 | QR5 | Turbine Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 20 | On May 25, 2014, with Unit 4 at approximately 20% reactor power during a shutdown to repair an unrelated equipment issue, an automatic reactor trip occurred due to low condenser vacuum. The transfer of steam supply to the gland sealing steam system from the Unit 4 main steam system to the Unit 3 auxiliary steam system while the unit was on-line caused the decrease in main condenser vacuum. Main condenser vacuum reached the turbine trip setpoint, which resulted in the automatic reactor trip. Trip response was uncomplicated.<br /><br /> The root cause was operations personnel did not adequately address the integrated system status as part of the decision making process used to realign the steam supply to the gland sealing steam system. Corrective actions include: 1) Revising procedural guidance to specify that steam supply to the gland sealing steam system cannot be transferred from the main steam system to the auxiliary steam system with a unit in Mode 1 or 2, and 2) Providing training to all licensed operators to demonstrate the integrated system response aspect of risk-based decision making.
251 | 2512015002 | 2015-05-12 | QR5 | Turbine Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 80 | On May 12, 2015 at approximately 0430 hours with Unit 4 at approximately 80% rated thermal power, an automatic reactor trip occurred in response to a turbine trip. The turbine trip was caused by a generator differential lockout that opened the generator output breaker. During the reactor trip response, the Auxiliary Feedwater System automatically initiated as expected. The unit was subsequently stabilized in Mode 3. All systems responded correctly to the trip. The direct cause of the event was an open circuit caused by a loose connection at a main generator current transformer (CT). The root cause was that the vendor recommended torque value for a stud lugged connection was not used during the engineering change (EC) and work order planning process. The tightening requirement for this type of connection is considered to be skill of the craft; therefore, no torque specification was listed in the EC or work instructions. Corrective action includes: 1) The preventive maintenance procedure and electrical specification will be revised to include connection torque requirements per the vendor work instruction manual for the type of terminal used in the CTs and, 2) A preventive maintenance task will be implemented to periodically inspect and test the Unit 3 and 4 main generator CT connections.
251 | 2512017001 | 2017-09-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Turkey Point 4 | P | WE | PO | 88 | On September 10, 2017 at approximately 1855 hours, the Turkey Point Unit 4 reactor was manually tripped from 88% power due to lowering level in Steam Generator (SG) C. The reactor was stabilized in Mode 3. Auxiliary Feed Water actuated as expected on low level in SG C and was secured at approximately 1933 hours. At the time of the event, the Turkey Point site was experiencing high winds with rain associated with Hurricane Irma. The B and C Main Feedwater Regulating Valves (MFRV) had been in manual control when the C MFRV failed closed. The cause of the event was a degraded signal due to water intrusion into the C MFRV valve positioner hand selector switch enclosure resulting from a less than adequate design and installation. Corrective actions include modifications to the Unit 3 and 4 MFRV hand selector switch enclosures and enclosure penetrations, and repair of a failed component associated with the 4C MFRV. Additionally, the terminal/pull box specifications will be revised to improve direction for installation activities. Safety significance is very low because the unit responded as designed to the trip.
251 | 2512020001 | 2020-07-05 | QR5 | Turbine Trip | [45 empty] | Turkey Point 4 | P | WE | PO | 100 | On 7/5/2020 at 21:09 hours, while Unit 4 was operating in Mode 1 at 100% power, a Main Generator Lockout caused the Unit 4 Turbine to trip, automatically tripping the Reactor. The Main Generator Lockout was caused by a loss of two Voltage Regulator power supplies. All safety systems operated as required in response to the equipment failure. The Auxiliary Feedwater System automatically initiated as designed. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A), due to automatic actuation of the Reactor Protection System and Auxiliary Feedwater System. <br /><br /> Corrective actions included replacement of the Exciter PMG and rotating assembly and re-sealing the Exciter housing.
254 | 2541987005 | 1987-03-17 | QR5 | Turbine Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 92 | On March 17, 1987, Quad Cities Unit One was at 92 percent core thermal power. At 1102 hours, a reactor scram occurred due to turbine stop valve closure i.e., a turbine trip. The turbine trip was caused by a high level in moisture separators 1C and 1D. The level control valve LCV 1-3508A from the 1B Moisture Separator Drain Tank (MSDT) to the 1D1 high pressure feedwater heater was stuck open. When this valve was isolated for repairs, the two other LCVs from the 1B MSDT to the 1D2 and 1D3 heaters and the emergency drain valve failed to compensate for this action. This caused a high level in two moisture separators which resulted in the turbine trip and reactor scram. <br /><br />The cause for this event was attributed to the level controllers being out of adjustment. Contributing causes were equipment failure (stuck valve) and inadequate preparation and planning prior to isolating LCV 1-3508A. A program will be developed to track setpoint changes to level control valves on this and other systems. The stuck LCV was freed and stroked successfully several times. Discussions were held with the individuals involved. This report is submitted to comply with 10CFR50.73(a)(2)(iv).
254 | 2541988016 | 1988-12-05 | QR5 | Turbine Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 100 | On December 5, 1988, Quad Cities Unit One was in the RUN mode at 100 percent core thermal power. At 1445 hours, a reactor scram occurred due to turbine stop valve closure. The stop valve closure was the result of a turbine trip. All safety feature actuations occurred as designed. A normal scram recovery followed. NRC notification of this event was completed at 1733 hours to satisfy the requirements of 10CFR50.72(b)(2)(ii). <br /><br /> The cause of this event could not be determined. The Instrument Maintenance Department performed extensive tests and checks on limit switches, pressure switches and fuses related to turbine trip logic. No instrumentation problem which could have caused the trip was found. At the time of the trip, no work was in progress in the areas of instruments involved in the turbine trip logic, and the Instrument Maintenance Department was not involved in any calibrations or surveillances. <br /><br /> Unit One was started up at 1648 hours on December 6, 1988, and put on-line at 0940 hours on December 7, 1988. No turbine trips have occurred since the startup. This report is provided to comply with 10CFR50.73(a)(2)(iv).
254 | 2541989003 | 1989-04-12 | QR6 | Manual Reactor Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 64 | On April 12, 1989, Quad Cities Unit One was in the RUN mode at approximately 74 percent of rated core thermal power. At 1136 hours, a manual reactor scram was initiated due to main turbine bypass valves opening. One bypass valve had oscillated open during the night before, but at 1126 hours, all nine bypass valves had opened in sequence. NRC notification was completed at 1210 hours to comply with 10 CFR 50.72(b)(2)(ii). <br /><br /> An investigation revealed that the cause for this event was component failure. A circuit board within the combined maximum flow limit circuit had a decreasing output. The board limits the opening of control valves, and as a result of the decreasing output, caused the control valves to close. The bypass valves were opening as designed to control reactor pressure. The circuit board was replaced. This report is provided to satisfy 10 CFR 50.73(a)(2)(iv).
254 | 2541989004 | 1989-04-17 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Quad Cities 1 | B | GE | PO | 10 | On April 17, 1989, Quad Cities Unit One was in the RUN mode at 10 percent of rated core thermal power following a maintenance outage. At 0330 hours, the reactor was manually scrammed due to the 1-203-3D electromatic relief valve being stuck open. This occurred while the Operating Department was performing routine relief valve testing. At 0331 hours, an Unusual Event was initiated. NRC notification was completed at 0347 hours to comply with 10 CFR 50.72(a)(1)(i). At 0753 hours, the unit was in cold SHUTDOWN, and the Unusual Event was terminated.<br /><br /> An investigation revealed that the cause for this event was component failure. The pilot valve showed signs of steam leakage and the drain orifice in the disc retainer of the main valve was plugged. The electromatic relief valve and the pilot valve were replaced. The electromatic relief valves are tested every six months or after maintenance. This report is provided to satisfy: 10 CFR 50.73(a)(2)(ii) and 10 CFR 50.73(a)(2)(iv).
254 | 2541989010 | 1989-06-29 | QR5 | Turbine Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 94 | On June 29, 1989, Quad Cities Unit One was in the RUN mode at 94 percent of rated core thermal power. At 2239 hours, a reactor scram occurred due to turbine stop valve closure. The stop valve closure was the result of a turbine trip. All safety feature actuations occurred as designed. Emergency Notification System (ENS) notification was completed at 2330 hours on June 29, 1989, to comply with the requirements of 10 CFR 50.72(b)(2)(ii). <br /><br /> An investigation revealed the cause for this event was a loose connection on the 1-5600-PS-105B condenser low vacuum pressure switch indicating lamp. When the lens cover for the lamp was put on, the loose wire induced a voltage in the K2D18 relay and energized the master trip bus. This resulted in a turbine trip.
254 | 2541990004 | 1990-03-10 | QR5 | Turbine Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 98 | On March 10, 1990, Quad Cities Unit One was in the RUN mode at approximately 98 percent of rated core thermal power. At 0114 hours, a reactor scram occurred due to a turbine-generator (TG) load mismatch. The turbine-generator load mismatch was the result of a generator trip. All safety feature actuations occurred as designed. Emergency Notification System (ENS) phone notification was completed at 0209 hours on March 10, 1990, to comply with the requirements of 10 CFR 50.72(b)(2)(ii).<br /><br /> An investigation revealed the cause for this event was a failure of the negative sequence time overcurrent relay. When a fault occurred on line 0402, the relay actuated resulting in a generator trip. The fault was most likely a result of a lightning strike. The relay was repaired. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73 (a)(2)(iv).
254 | 2541991025 | 1991-12-11 | QP5 | Excessive Feedwater Flow | [45 empty] | Quad Cities 1 | B | GE | PO | 78 | On December 11, 1991, Quad Cities Unit One was in the RUN mode at 78 percent of rated core thermal power. At 0425 hours, a reactor scram occurred due to turbine stop valve closure as a result of a high reactor water level turbine trip. The high reactor water level was caused by a feedwater regulating valve failing full open. All safety feature actuations occurred as designed. Emergency Notification System (ENS) notification was completed at 0632 hours on December 11, 1991, to comply with the requirements of 10CFR50.72(b)(2)(ii).<br /><br /> An investigation revealed the cause of the event to be due to misalignment of the 1A Feedwater Regulating Valve causing the valve to bind. The manual operator assembly broke in an attempt to close the valve manually which allowed the valve to open fully due to spring force. The failed open feedwater regulating valve caused the high reactor water level and subsequent turbine trip.
254 | 2541992004 | 1992-02-07 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Quad Cities 1 | B | GE | PO | 100 | At 0201 hours on February 7, 1992, Unit One was in the RUN mode at 100% power. A Channel "B" Main Steam Line (MSL) high flow annunciator was received in the Control Room. Immediately thereafter, a full Primary Containment Isolation Group I isolation occurred and a subsequent reactor scram. <br /><br /> All automatic actuations occurred as designed with the exception that Reactor Feed Pumps (RFP) did not trip on +48 inches reactor high level. <br /><br /> Additionally, the "C" Electromatic Relief Valve (ERV) failed to open upon manual initiation. Reactor shutdown was accomplished by 1100 hours. <br /><br /> The root cause of the Group I isolation could not be determined. It is believed to be due to spurious initiation of MSL high flow instrumentation. Monitoring instrumentation was installed to evaluate future similar events.<br /><br /> The RFP high level trip did not occur due to setpoint drift. The applicable instruments were calibrated and functionally verified. The "C" ERV did not actuate due to loss of continuity between solenoid electrical contacts. The ERV's were inspected and all worn parts were repaired or replaced. <br /><br /> This report is being submitted to comply with 10 CFR 50.73 (a)(2)(iv).
254 | 2541993023 | 1993-12-16 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Quad Cities 1 | B | GE | PO | 97 | At 2355 hours on December 16, 1993, the Unit-1 main turbine [TA] tripped from 97 percent reactor core thermal power. The turbine stop valve closure initiated a reactor scram. Spurious main steam line low pressure signals generated a group one primary containment isolation (PCI) [JM]. The turbine trip was caused by a main condenser [SG] low vacuum signal, but vacuum was found to be normal. The main steam isolation valves were reopened and a reactor cooldown was started. A relay contact for condenser low vacuum turbine trip was found to have failed in the closed position. <br /><br /> The root cause of this event was a relay failure due to manufacturing specification. A contributing cause of this event was design analysis. <br /><br /> The relay was replaced like for like and tested satisfactorily. Other trip relays that provide turbine trip signals, but are not routinely tested through periodic surveillance were tested prior to start up. The station is investigating options for improving the reliability and possibly adding redundancy to the turbine trip logic.
254 | 2541994008 | 1994-08-20 | QR6 | Manual Reactor Trip | [45 empty] | Quad Cities 1 | B | GE | SU | 4 | At approximately 1200 on 08/20/94, Unit-1 was in the start up mode at approximately 4% power. The Operations Department had satisfactorily completed the uncoupled overspeed test for the High Pressure Coolant Injection (HPCI) Periodic Pump Operability Run (QCOS 2300-1). <br /><br /> During the HPCI low pressure operability run, oscillations in flow and speed were detected in the Control Room (CR) at 1908 hours. The HPCI test was terminated, and trouble shooting activities were started. <br /><br /> At 0538 hours, on 08/21/94, the Unit-1 reactor was manually scrammed by procedure to achieve a shutdown condition required by Technical Specifications. <br /><br /> Trouble shooting activities identified a broken feedback wire on the HPCI flow convertor instrument loop Linear Variable Displacement Transducer (LVDT). Causal Factors attributed for the broken wire are Work Practices, and Maintenance/Testing.<br /><br /> The HPCI front standard instrument wiring, and general material condition, was inspected for Unit-1 and Unit-2 with special attention given to wire crimping integrity. All wires to the effected unit HPCI LVDT had the wire terminal lugs replaced with new parts, and double crimping placed on all of them. The Unit-1 HPCI FIC instrument loop was functionally checked, calibrated, and verified operational.
254 | 2541996017 | 1996-08-25 | L3 | Turbine Bypass Unavailable | [10 empty] | X | [30 empty] | X |  |  |  | Quad Cities 1 | B | GE | SU | 4 | On 8/25/96 at 0447 hours, Unit 1 was in Startup Mode at 04% power. Reactor pressure was holding at approximately 115 psig in preparation to perform High Pressure Coolant Injection and Reactor Core Isolation Cooling post-maintenance turbine overspeed testing in accordance with an interim procedure when all of the turbine bypass valves unexpectedly opened dropping reactor pressure and raising reactor water level. <br /><br /> Approximately 16 seconds after the bypass valves opened, a manual reactor scram was inserted at 43 inches of reactor water level increasing as directed by the Unit Supervisor in accordance with the manual scram action point of 44 inches set at the preshift meeting. <br /><br /> The root cause of this event was an inadequate procedure and a contributing cause was inadequate training. Corrective actions include a revision of the applicable procedure, training, and counselling of the responsible instructor. <br /><br /> The safety significance of this event is minimal as no automatic functions were challenged.
254 | 2541998018 | 1998-06-27 | QR8 | Spurious Reactor Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 100 | On 06271998 at 1711. a Unit One full reactor SCRAM occurred from 100% power during the performance of Technical Specification weekly APRM surveillance QCIS 0700-07 Power Operation APRM Functional Test by, Instrument Maintenance. The expected Reactor Protection System (RPS) 1/2 SCRAM signal from an APRM 2 Hi Hi on RPS Channel A was in process of verification when a 1/2 SCRAM signal coincidental initiated from the RPS Channel B Scram Discharge Instrument Volume (SDIV) Hi level due to a spurious trip from a level transmitter. The plant and the operations crew responded properly to the SCRAM. All control rods inserted and all safety systems functioned as expected. A prompt investigation into the cause determined from the Sequential Events Recorder (SER) that the B RPS SCRAM trip from the SDIV Hi level was received after the APRM 2 Hi Hi was recorded. The investigation determined that ITT Barton electronic level transmitter 1-302-109D for the SDIV level had initiated a spurious trip causing the 1-500 100D RPS Channel B relay to de-energize as designed. The safety significance to health and safety of onsite personnel and to the public was minimal. Corrective actions included replacing the level transmitter, reviewing industry information applicable to the ITT Barton 764/765 transmitters, performing appropriate testing to ensure operability, and evaluating the operability of the remaining transmitters. Root cause investigation revealed mechanical binding of the process sensor bellows by particulate crud caused a zero shift that resulted in the apparent level exceeding the setpoint. There was no correlation found with this spurious trip and previous 10CFR Part 21 issues documented for this type transmitter.
254 | 2541998022 | 1998-09-30 | QP5 | Excessive Feedwater Flow | [45 empty] | Quad Cities 1 | B | GE | PO | 100 | On 09/30/1998 at 0206, Unit 1 was in Power Operation at approximately 100% power when a low reactor water level scram occurred due to a feed water flow transient during an equipment Out of Service (OOS). Note: An equipment tagout is referred to as an OOS. The OOS had been prepared to repair a drain valve for a Reactor Feed Pump (RFP) flow element with the feed water level control in 3-element control (inputs from reactor level, feed flow, and steam flow.) The Operations personnel responsible for preparing the OOS did not implement adequate provisions to prevent an impact on feed water level control due to their erroneous understanding that the RFP flow element was not an input with the RFP breaker open. When the OOS was performed, a high differential pressure was sensed resulting in a high flow signal which closed down on the feed water regulating valves, resulting in a rapid level decrease to the low level scram. Following placement of feed water level control in single-element, level increased until the RFP's tripped automatically at 0207, approximately one minute after event initiation. Based on initial indications of high feedwater flow and decreasing reactor water level, operators did not trip the RFP's. The cause of the event was inadequate review of drawings during preparation of the OOS, which would have corrected the operator's misunderstanding. Corrective actions include operator training, precautionary labeling, heightened risk assessment for OOS activities, reviewing the OOS process for changes and evaluating disciplinary actions. A review for previous events did not identify any similar events in the last 2 years. The safety significance of this event was minimal. The plant systems responded with an automatic reactor scram and a trip of the RFP's as expected to place the plant in a safe condition.
254 | 2541999002 | 1999-05-21 | QR8 | Spurious Reactor Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 100 | On May 21, 1999, while at 100% power, Unit 1 scrammed from a Scram Discharge Volume (SDV) high level signal due to steam intrusion into the SDV. A Reactor Water Cleanup (RWCU) relief valve had lifted due to a pressure transient event in the system, discharging hot water and steam. The steam back-flowed into the SDV through common drain piping, and actuated the SDV high level scram signal. Following the scram, when off-site power transferred from the Unit Auxiliary Transformer (T11) to the Reserve Auxiliary Transformer (T12), the Unit 1 Emergency Diesel Generator (EDG) started without loading to the emergency bus. The EDG was secured after it was verified that there was no loss of off-site power. The root causes of the scram are that (1) given the current RWCU design, less than adequate procedural guidance was provided for RWCU system startup, and (2) there was steam actuation of the SDV level sensing devices. RWCU system startup procedures were changed, and the SDV level sensing devices will be reviewed for sensitivity adjustments. The scram event was not safety significant. The Reactor Protection System tripped as designed, and no water was introduced into the SDV until after the scram. The root cause for the EDG auto-start is an inadequate design. The existing logic provides a momentary auto-start signal during 4KV Bus auto-transfer. Because the EDG conservatively auto-started and ran as designed, this event is not safety significant.
254 | 2542000010 | 2000-12-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Quad Cities 1 | B | GE | PO | 100 | At 0940 hours on December 6, 2000, with reactor power at 100%, Unit One reactor water level started to decrease and the low-level alarm was received. The operators took the Feedwater Level Control System (FWLC) out of three-element control and placed it in single-element control. They then took manual control of the 'B' Feedwater Regulating Valve (FWRV) and opened the valve, causing reactor level to increase. At about 0941 hours reactor level started to decrease rapidly and the 'A' FWRV locked up. A reactor scram signal was received at 0942 hours, with indicated reactor water level at 20 inches. All automatic actions occurred consistent with a low-level reactor scram. The root cause of this event was an age-related failure of a solder joint on the master controller for the ‘A' FWRV. Additionally, operations procedures and training did not support reducing power to mitigate or prevent the reactor scram as an immediate operator action. The safety significance of this event was minimal. Although the event resulted in a reactor trip, all safety systems responded as designed. This report is submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(iv).
254 | 2542005005 | 2005-06-17 | QR5 | Turbine Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 85 | At 1120 hours (CDT) on June 17, 2005, the Unit 1 reactor automatically scrammed from 85% power due to a valid high reactor pressure signal. The maximum reactor pressure was approximately 1044 psig during the event. All control rods inserted to their full-in position. The reactor pressure increase was caused by a malfunction in the Electro-Hydraulic Control (EHC) system, which resulted in closure of the main turbine control valves. The main turbine bypass valves (nine) opened as expected in response to the pressure increase. No reactor pressure vessel safety or relief valves were required to actuate during the event. Reactor water level decreased to approximately -20 inches, which resulted in automatic Group 2 and 3 isolations as expected. All systems responded properly to the event. The cause of the scram was a failure in one of the Control Valve Input Circuit Cards in the EHC system. Laboratory analysis was unable to identify the specific cause of failure. The circuit cards were replaced.
254 | 2542006002 | 2006-02-22 | QR5 | Turbine Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 85 | On February 22, 2006, at 0122 hours, an automatic reactor scram occurred on Unit 1 in response to a turbine/generator load reject due to a trip of the main power transformer (MPT) B phase differential overcurrent relay. The relay trip was caused by degraded wiring insulation, resulting in a ground in the current transformer C phase wiring at a box mounted on the MPT. The degraded wiring insulation resulted in a direct short to ground and resultant trip of the protective differential overcurrent relay. All control rods inserted to the full-in position. The reactor was brought to the hot shutdown condition using normal methods and was maintained in hot shutdown during investigation and repair of the MPT issue until the reactor was returned to power operation on February 24, 2006. The degraded wiring insulation was caused by inadequate MPT wiring assembly design and installation. Corrective actions include repair of degraded wiring, inspection of accessible wiring and design changes.
254 | 2542010002 | 2010-08-12 | QL7 | Degraded condenser vacuum | [45 empty] | Quad Cities 1 | B | GE | PO | 100 | On August 12, 2010, Quad Cities Unit 1 performed a scheduled reversal of the direction of flow through the main condenser [KE]. During the flow reversal, two valves [ISV] failed to operate, resulting in low condenser vacuum. In response to the low condenser vacuum, the main turbine [TRB] tripped and the reactor [RCT] scrammed. There were no complications during the turbine trip and reactor scram, and all systems functioned as required. The root cause for this event was determined to be foreign material from the manufacturing process in an auxiliary contact unit [29] for the breaker [BKR] of one of the valves involved in the main condenser flow reversal process. This caused the valve to fail to open. A contributing cause to the event was the setpoint of a thermal overload [TS] for a separate main condenser flow reversing valve that did not anticipate the specific conditions of this event and caused this valve to trip at mid-position. The reactor and turbine responded as designed to the low condenser vacuum. Although the turbine trip occurred prior to the expected vacuum level, it was determined that this is due to the location of the instrument taps in the condenser for the turbine trip being at a higher elevation than the location of the instrument taps for the reactor protection system (RPS) [JD] and main control room [NA] indication. Corrective actions included auxiliary contact and thermal overload replacement and testing, procedure changes, and reviews for potential setpoint and design changes. The safety significance of this event was minimal. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram or reactor trip.
254 | 2542011002 | 2011-06-13 | QK4 | Steam or Feed Leakage | [45 empty] | Quad Cities 1 | B | GE | PO | 34 | On June 13, 2011, Quad Cities Unit 1 was performing startup from refueling outage Q1R21. During power ascension while at 61% power (560 MWe) a steam leak was identified on the main steam line downstream of turbine control valve #1 (1-5699-CV1). Reactor power was reduced and the reactor was manually scrammed. The steam leak occurred at a recently repaired sensing line that had previously leaked. A forced outage was initiated to investigate and performs repairs. The reactor and turbine responded as designed. Operators performed required actions safely and in accordance with procedures and training. There were no complications during the reactor scram and turbine trip, and all systems functioned as required. The root cause for the manual scram due to a steam leak from a pressure sensing line repair was that the capped pipe stub repair failed due to a fatigue induced flaw that was not known to exist at the time of the repair. Corrective actions included replacing the Unit 1 sensing line sock-o-lets with gamma plugs. Future corrective actions include replacement of the equivalent Unit 2 sensing line sock-o-lets with gamma plugs. The safety significance of this event was minimal. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram.
254 | 2542015005 | 2015-04-02 | QR6 | Manual Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Quad Cities 1 | B | GE | PO | 20 | On April 2, 2015, at 1810 hours, with Unit 1 in Mode 1 and operating at 100% power, an alarm was received in the control room indicating that two of three turbine throttle pressure transmitters on Unit 1 had failed low. Reactor power was reduced to 20% and the main turbine was secured. A steam leak was confirmed to have originated between the turbine throttle pressure transmitter sensing line isolation valve and the 30 inch main steam D-Ring header. Since the steam leak could not be isolated with Unit 1 at power, a manual scram was inserted on Unit 1 at 2133 hours, and the main steam isolation valves (MSIVs) were manually closed. A forced outage was initiated to investigate and perform repairs.<br /><br /> The reactor and turbine responded as designed. Operators performed required actions safely and in accordance with procedures and training. Operators needed to use relief valves to control reactor pressure since the turbine bypass valves were unavailable for normal pressure control after closing the MSIVs to isolate the steam leak at the D-ring. A drywell pressure rise occurred due to a relief valve tailpipe vacuum breaker which had inadvertently stuck open; the relief valve was then closed, a drywell cooler was started, and drywell pressure returned to normal.<br /><br /> The root cause of the failure of the sensing line was determined to be inadequate monitoring of the sensing line supports that allowed each of the clamps to degrade and loosen over time resulting in high cycle fatigue cracking and eventual fracture of the sensing line.<br /><br /> Corrective actions included replacing the 3/4 inch carbon steel section of the failed sensing line, including the isolation valve, and replacing the associated degraded supports. Future corrective actions include conducting focused inspections of small bore piping/tubing on both accessible and inaccessible systems.<br /><br /> The safety significance of this event was minimal. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(iv)(A) which requires the reporting of any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).
254 | 2542018004 | 2018-09-26 | QR5 | Turbine Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 100 | On September 26, 2018 at 19:08, Quad Cities Unit 1 received an automatic Reactor SCRAM from 100% power. The SCRAM was the result of a Turbine-Generator Load Reject Trip that occurred when the status of the load reject contacts on one Unit Output Breaker was being tested while the other Unit Output Breaker was open. <br /><br /> The cause of the Turbine-Generator load reject trip was ineffective procedural controls for ensuring both unit output breakers were closed prior to performing contacts status verifications. The immediate corrective actions include procedure revisions to provide enhanced guidance for performing contact checks. <br /><br /> The issue is reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).
254 | 2542019002 | 2019-08-25 | QR5 | Turbine Trip | [45 empty] | Quad Cities 1 | B | GE | PO | 100 | On August 25, 2019, at 1102 hours CDT, Quad Cities Nuclear Power Station (QCNPS) Unit 1 experienced an automatic reactor SCRAM from 100 percent power. The SCRAM was the result of a generator trip that occurred when leakage current measured by the Generator Stator Ground Detection Relay exceeded its threshold and actuated the Generator Primary Lock Out Relay (86 Device). Following the Reactor SCRAM, water was found in the "A" Isolated Phase Bus Duct (IPBD) between the Unit Aux Transformer (UAT) and the wall of the Turbine Building. It was determined that water entered through a degraded access cover gasket located on the IPBD and the resulting condensation within the duct caused current leakage through one or more of the insulators that support the bus. The corrective actions include replacement of the insulators that were impacted by the water, replacing the degraded gaskets and implementing additional preventative maintenance activities on the IPBD system.<br /><br /> This is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in automatic actuation of the reactor protection system (RPS) and containment isolation signals for Groups 2 and 3 affecting containment isolation valves in more than one system.
255 | 2551987011 | 1987-04-12 | QR6 | Manual Reactor Trip | [45 empty] | Palisades | P | CE | PO | 75 | On April 12, 1987, a manual reactor trip was initiated by Operations personnel. The manual activation of the Reactor Protection System (RPS) was undertaken after the failure of a turbine Electric Hydraulic Control (EHC) fluid pump (TG;P) caused EHC fluid pressure to drop and the main turbine governor valves (TG;PC4) to begin closing. The reactor power level was 75% at the time of the event. <br /><br />The EHC pump failure was caused by a tooth breaking off the pumps rotor. This failure caused excessive pump vibration resulting in an EHC pump discharge line cracking and inlet suction valves for the pumps to move toward the closed position. The standby turbine EHC fluid pump started, however, due to a failed check valve along with the discharge line leaking, the main turbine governor valves began closing, causing a reduction in turbine generator load. <br /><br />A manual reactor shutdown was initiated by the operators to terminate the transient.
255 | 2551987016 | 1987-05-22 | K1 | Steam Line Break Outside Containment | [9 empty] | X | [26 empty] | X | [8 empty] | Palisades | P | CE | PO | 40 | On May 22, 1987 at 0007, Operations personnel manually tripped the reactor from approximately 35 percent of rated power following the errant closure of main feedwater pump turbine driver exhaust valve, MV-159FW. At the time of the event, Operations personnel were redirecting the moisture separator and reheater drain lines from the main condenser to the feedwater heaters. Two Plant Auxiliary Operators (AO) were performing the valve line-up. At approximately 0004, an AO errantly closed the turbine driver's exhaust valve and subsequently, the turbine drivers overpressure protection rupture disc operated causing high temperature steam to be expelled and actuate the local fire protection system sprinklers. Upon personal evaluation of the situation, the SS directed Control Room personnel to trip both the turbine and reactor. At 0013, the Plant was confirmed to be sub-critical and returning to stable conditions. The errant valve closure was the result of poor communication between the AOs performing the valve lineup and inattention to detail on the part of the AO who closed the wrong valve. Disciplinary time off has been given to the involved AOs. Additionally, the AOs are speaking with each Operations Department shift, describing the event, its cause, and how it could have been avoided. All Operations personnel will receive training on effective communications techniques. This personnel error is being independently reviewed by the Human Performance Evaluation System (HPES) Coordinator to determine if additional actions are warranted. Plant Safety Engineering's review of this event determined that the resultant Plant transient was relatively minor and that overall Plant response was consistent with normal equipment operation.
255 | 2551987021 | 1987-07-10 | QR6 | Manual Reactor Trip | [45 empty] | Palisades | P | CE | PO | 70 | On July 10, 1987 at approximately 0121 the reactor was manually tripped from 14 percent of rated power due to an oil leak from the upper reservoir of primary coolant pump P-50D (AB;P). With the Plant at approximately 70 percent of rated power, a low level alarm was received for primary coolant pump P-50D's upper motor oil reservoir. Approximately one hour later at 0100, a three degree temperature increase was seen within the upper guide bearing of the primary coolant pump motor. <br /><br />At 0112 a rapid power reduction was initiated and at 0121 the reactor was manually tripped from 14 percent of rated power to allow shutdown of the affected primary coolant pump. Actions were initiated to place the reactor in hot shutdown condition and P-50D was secured at 0142 in accordance with standard operating procedures. <br /><br />The oil leak was initiated from a crack in the discharge line of backstop lube oil pump P-83D. The affected piping has been replaced and the three unaffected primary coolant pumps inspected. No leaks or other abnormalities were identified.
255 | 2551987024 | 1987-07-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Palisades | P | CE | PO | 91 | On July 14, 1987 at 1322 a loss of offsite power occurred while the reactor was critical and operating at 91 percent of rated power. At 1330 the Site Emergency Plan was activated and an Unusual Event was declared based on the loss of offsite power. <br /><br />The loss of offsite power occurred due to a fault on the 1-2 startup transformer (EA;XFMR). The fault on the 1-2 startup transformer actuated protective relays which tripped the breakers for the 1-1, 1-2, and 1-3 startup transformers resulting in a loss of off-site power. The fault was preceded by the inadvertent actuation of the deluge fire protection system (KP) for the main transformers. A combination of the deluge water contamination and wind currents are attributed with providing the necessary path to ground for the fault. The deluge system was inadvertently activated during maintenance to correct an alarm problem on the deluge system for the main transformer. <br /><br /> After observing the loss of offsite power, the Shift Supervisor ordered a manual reactor trip because of the loss of cooling tower pumps (KE;P) which provide flow for the secondary heat sink. The Plant's two emergency diesel generators (EK;DG) provided power until 2048 on July 14, 1987 when offsite power was restored. The Unusual Event was terminated at 2049. After the trip the plant was maintained in hot shutdown using natural circulation flow until forced circulation flow was restored at 2221.
255 | 2551987025 | 1987-08-17 | QR6 | Manual Reactor Trip | [45 empty] | Palisades | P | CE | PO | 68 | On August 17, 1987 at 0404, Control Room operators manually initiated a reactor trip following the failure of an electro-hydraulic control (EHC) system supply line TG;PSX!. The reactor was critical with the Plant operating at 68 percent of rated power at the time of the event. Shortly before 0404, the turbine generator governor valves TG;FCV! began to close due to a rapid loss in EHC system fluid pressure. As primary coolant system pressure began to increase in response to governor valve closure, the reactor was manually tripped. <br /><br /> Investigation into the loss of EHC fluid determined that a flexible fluid supply hose to governor valve CV-0576 had ruptured. The cause of the failure was determined to be vibration induced fretting of the hoses braided stainless steel sheath at a point where two hoses were in contact. This fretting caused the stainless steel wires to be abraded and exhibit a "knife-edge" appearance, thereby weakening the hose and increasing susceptibility to rupture. <br /><br /> The flexible hose was removed from all four turbine generator governor valves. Dye penetrant examinations were performed on the flared ends of the rigid stainless steel tubing removed prior to flexible hose installation. No positive indications of cracking were revealed. This rigid tubing was then reinstalled and the flexible hose restraints removed.
255 | 2551987027 | 1987-08-23 | QR5 | Turbine Trip | [45 empty] | Palisades | P | CE | PO | 93 | On August 23, 1987 at 0630, an automatic reactor trip occurred due to a loss of field in the main generator (TL;PMG). The reactor was critical with the Plant operating at 93 percent of rated power at the time of the event. <br /><br />The loss of field in the main generator initiated a Loss of Load signal and automatic reactor protection system actuation. The loss of field was caused by the failure of a bias supply potentiometer in the voltage regulator Trinistat power amplifier. Subsequently, amplifier output essentially went to zero, causing under-excitation of the Main Generator and tripping of the Main Turbine which generated the Loss of Load signal. <br /><br />The Plant responded as designed to the transient with no significant abnormalities. The bias supply potentiometer was replaced, satisfactorily tested and the Plant returned to service.
255 | 2551989020 | 1989-08-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palisades | P | CE | PO | 80 | On August 4, at 1945, a reactor trip from 80% power occurred due to a blown fuse JB;FU! in a flow indicating controller SJ;FIC! that caused the feedwater regulating valve SJ;LCV! for the B steam generator to close, thereby decreasing feedwater flow to the steam generator and resulting in a reactor trip on low steam generator level. The plant response to the trip was considered normal with no safety significant deviations or anomalies observed.<br /><br /> On August 5, 1989 at 0300, an unanticipated start of auxiliary feedwater pump P-8B BA;P! occurred while the plant was in the hot shutdown condition. The spurious signal was caused by a failure by the operators to reset the AFAS signal following the reactor trip. <br /><br /> Corrective actions to be taken in response to these incidents include a review of the fuse control program and a revision to post trip operating procedures that will add instructions to the operators for resetting alarms and activated actuation signals.
255 | 2551990001 | 1990-01-09 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Palisades | P | CE | PO | 35 | On January 9, 1990, at 0514 hours, with power at a steady state of 35 percent, the reactor was manually tripped following the loss of all main feedwater flow. Main feedwater was lost at 0512 when "A" main feedwater pump was secured as part of the normal power reduction procedure for preparation for condenser SG;COND! tube leak identification and repair. The plant response to the trip was considered normal with no safety significant deviations or anomalies observed.
255 | 2551990002 | 1990-02-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palisades | P | CE | PO | 80 | At 1826 hours on February 28, 1990, Palisades experienced an unanticipated trip of the "B" main feedwater pump (MFP). During recovery from the pump trip, a reactor trip was initiated by an automatic actuation of the Reactor Protection System (RPS). Prior to the feedwater pump trip the reactor had been operating at 80 percent power, with both feedwater pumps operating and the Primary Coolant System (PCS) at 556 degrees F and 2060 psia. When the reactor trip occurred, the Plant was operating at 55 percent reactor power. <br /><br /> The initating event for the reactor trip was cooldown of the PCS during recovery from loss of a main feedwater pump. The reactor trip was not caused by personnel error. However, operator actions which could have been taken to control the effects of the cooldown transient and prevent the reactor trip were impaired by a momentary loss of audible annunciator system and a malfunction of the automatic start feature for charging pump "C". The cause of the MFP trip remains indeterminate. Investigation of the feedwater pump trip remains in progess. Temporary monitors have been installed on the MFPs in order to provide additional information should there be any further MFP abnormalities or trips. Licensed operators will receive training on the circumstances surrounding the reactor trip and procedures will be enhanced to warn operators of the potential for a PCS cooldown during recovery from loss of a feedwater pump. This event was contributed to a failed annunciator chime bell (Edwards, Catalog Number 339-P1).
255 | 2551991012 | 1991-07-03 | QR8 | Spurious Reactor Trip | [45 empty] | Palisades | P | CE | PO | 100 | On July 3, 1991, at 1435 hours, with the plant operating at 100% power, the reactor tripped. Troubleshooting and repair of the channel "A" Thermal Margin/Low Pressure (TM/LP) protection circuit was in progress at the time of the trip. Investigation into the cause of the trip indicated that a reactor trip signal was created when, during the performance of troubleshooting and repair of the TM/LP channel "A" circuit, a trip coil to test coil short, which existed in the circuit, activated the reactor protective system (RPS) trip relays for the A-D logic matrix. <br /><br /> The cause of the event was the failure of electrical components in the reactor protective system circuitry. <br /><br /> Corrective action for this event includes evaluating periodic monitoring the RPS test circuitry for indications of failed bistable trip relays, evaluating isolating signal ground from earth ground at the Thermal Margin Monitor (TMM) and Auxiliary Feedwater Actuation System (AFAS), evaluating isolating Feed Only Good Generator (FOGG) system from RPS, evaluating a PM prog am to perform a coil to coil resistance test on all trip relays in the RPS and reviewing a proposed modification to the RPS circuitry to determine if a similar failure mechanism will exist. <br /><br /> The event involved the failure of electrical components in the reactor protective system circuitry.
255 | 2551991015 | 1991-07-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palisades | P | CE | PO | 100 | On July 12, 1991, at 1838 hours, with the plant operating at 100% power, the plant tripped. At the time of the trip, troubleshooting of an indication of low bearing oil pressure on the K-7A main feedwater pump turbine was in progress. Based on alternate indications, the System Engineer felt that the indication was incorrect. He tapped the pressure gauge with his hard hat which caused the main feedwater pump turbine to trip. The reactor tripped 54 seconds later on low steam generator level. <br /><br /> The cause of the event was a combination of personnel error and equipment failure. <br /><br /> Corrective action from this event includes electrical check out of all feedwater pump turbine instruments and controls, replacement of selected feedwater pump turbine trip circuit components, repair of control cabinet oil and steam leaks and briefing instrument and control (I&C) technicians on proper equipment control.
255 | 2551992001 | 1991-12-09 | QR5 | Turbine Trip | [45 empty] | Palisades | P | CE | PO | 20 | On December 9, 1991, at 1630 hours, with the plant operating at 100% power, the turbine building auxiliary operator observed that seal oil pressure on the air side of the electrical generator had decreased from the previous shift reading. Automatic and manual action was taken to restore the seal oil pressure however, pressure continued to drop. It was also observed that hydrogen pressure on the main electrical generator was dropping. At 1715 hours, the Shift Supervisor ordered an emergency power reduction due to a continuing loss of electrical generator hydrogen pressure. During the emergency power reduction, the level in the "B" steam generator went to its high level setpoint which caused the automatic closure of the feedwater regulating valve. Steam generator level continued to increase. At 1722 hours, control room operators initiated both a manual reactor trip and a manual turbine trip due to increased steam generator level. At 1722 hours, with the plant operating at approximately 20% power, an automatic reactor trip on loss of load occurred when the turbine trip was initiated slightly before the reactor trip. <br /><br /> The cause of the event was a malfunction in the electrical generator seal oil system due to a plugged filter. No root cause for the plugging of the filter was determined. <br /><br /> Numerous short term corrective actions related to minor equipment problems observed during the emergency power reduction were taken prior to re-start of the plant. Long term corrective action includes evaluation and troubleshooting of the main generator air side seal oil system.
255 | 2551992034 | 1992-07-01 | QR5 | Turbine Trip | [45 empty] | Palisades | P | CE | PO | 100 | On July 1, 1992, at approximately 1232 hours, the plant was stable, operating at 100% power with all systems in a normal full power alignment, when the reactor automatically tripped on a loss of load signal. A turbine generator trip was generated by the turbine generator digital electrohydraulic (DEH) control system, resulting in a loss of load signal to the reactor protection system (RPS). The plant was taken to a hot shutdown condition after the event. All safety systems responded as designed. The apparent cause of the turbine generator trip was a momentary loss of power to the turbine DEH system computers which caused a turbine trip. The turbine trip resulted in a reactor trip due to loss of load. Corrective actions taken in response to the July 24, 1992 plant trip (LER 92-035) will assure that this event will not recur.
255 | 2551992035 | 1992-07-24 | QR5 | Turbine Trip | [45 empty] | Palisades | P | CE | PO | 100 | On July 24, 1992 at 1007 hours, with the reactor operating at 100% power, the reactor tripped due to a loss of the turbine digital electrohydraulic (DEH) control system. The loss of the DEH control system resulted in a simultaneous turbine trip and automatic reactor trip. The automatic reactor trip was successfully completed with no major plant equipment problems identified. Just prior to the reactor trip, technical specifications surveillance procedure (TSSP) QO-1, 'Safety Injection System Surveillance Test,' was initiated. <br /><br /> The cause of this event was a momentary loss of power to the turbine digital electrohydraulic (DEH) system computers which caused a turbine trip. The turbine trip resulted in a reactor trip due to loss of load. <br /><br /> Corrective action for this event included replacing the power supply switching circuits in the turbine DEH computers with an updated version and adding an un-interruptable power supply to the turbine DEH computers. <br /><br /> Maintenance on other plant equipment, such as the motor operated disconnect switch, is planned for the next appropriate outage.
255 | 2551992037 | 1992-08-14 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Palisades | P | CE | PO | 100 | On August 14, 1992 at 0017 hours, with the plant operating at 100% power, the control room receive a low steam generator level alarm on the 'A' steam generator. Indicated flow to the steam generator 'A' was approximately of the normal feedwater flow. Based on the control room indications the main feedwater regulating valve control signal and the main feedwater pumps appeared to be responding properly to the alarmed condition; however, water level in the 'A' steam generator continued to drop until it reached the reactor protective system (RPS) setpoint. The reactor automatically tripped on low level in the 'A' steam generator. <br /><br /> The cause of this event was a broken air supply line between the position operator controller and solenoid valve that supplies air for the open signal of the valve actuator, which allowed the valve to partially close and restrict flow to the 'A' steam generator.<br /><br /> Corrective action for this event prior to plant re-start included replacing all the air lines on both main feedwater regulating valves, inspection of other key control valves in the turbine building for evidence of leaking Swagelok connections. Proposed corrective action includes reviewing the maintenance department's installation methods for compression fittings, inspecting the air lines to critical valves to determine the amount of vibration during plant operation and evaluating a method of repair, and evaluating the need for criteria for the re-use of compression fittings.
255 | 2551992038 | 1992-08-25 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Palisades | P | CE | PO | 100 | On August 25, 1992 at 0129 hours, with the plant operating at 100% power, and all systems in a normal full power alignment, the reactor tripped. The reactor trip resulted from a loss of the preferred ac bus Y-20, coincident with a blown fuse in another portion of the reactor protective system (RPS). The automatic reactor trip was successfully completed with no major plant equipment problems identified. The plant was maintained in hot shutdown for evaluation of the trip. <br /><br /> The cause of this event was the loss of preferred ac bus Y-20 that resulted in the loss of one channel of the reactor protective system (RPS), coincident with a blown fuse in a second channel of the RPS, which resulted in the initiation of an RPS trip signal. Preferred ac bus Y-20 was lost due to the failure of inverter ED-07. It was later determined that improper internal wiring connecting the transformers within ED-07 caused accelerated aging of the transformer coils and resulted in the failure of two transformers.<br /><br /> Corrective action for this event included checking all the fuses in the RPS system for proper sizing, completing a Procurement Engineering Checklist for the SOLA transformers to identify critical characteristics to be used during the procurement process, updating plant drawings and vendor manuals of the inverters to properly show the use of functionally equivalent SOLA transformers, and reviewing this event with electrical maintenance department personnel to reinforce the importance of requiring attention to the proper connection of components that have multiple windings. Additional corrective action regarding the pressurizer level control circuitry is being developed and will be reported in a supplemental licensee event report.
255 | 2551992039 | 1992-10-30 | QR5 | Turbine Trip | [45 empty] | Palisades | P | CE | PO | 100 | On October 30, 1992 at 0700 hours, the plant was operating at 100% power. As a result of a turbine generator trip the reactor automatically tripped on a loss of load signal. The turbine generator trip was initiated by coincident shutdown of the primary and backup computers in the turbine generator digital electrohydraulic (DEH) control system. Plant response to the event was good, with no safety significant deviations or anomalies noted. <br /><br /> By design the DEH computers were being supplied from a single uninterruptable power supply (UPS). The cause of this event was a failure of the UPS to maintain proper voltage at the input to the DEH power supplies. Voltage variations at the UPS output (i.e., the DEH input power supply) could not be handled by the DEH system and all four DEH computers automatically went to their fail safe condition tripping the turbine generator.<br /><br /> Corrective action for this event included adding redundancy to the computer power circuits; adjusting voltage and installing new cables on the existing power source, installing two new voltage regulating transformers in the back-up power source; installing new power supplies in all four DEH data processing computers, and adding alarms to the DEH control room console.
255 | 2551995003 | 1995-05-22 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Palisades | P | CE | PO | 46 | On May 22, 1995, at 1110, with the plant operating at 46% power, the reactor was manually tripped. At the time of the trip, K-7A and K-7B main feedwater pump turbines had both tripped, resulting in a loss of all main feedwater. The vibration on K-7A had increased earlier and System Engineering was brought in to investigate the problem. A decision was made to reduce reactor power and take K-7A off line. While preparing to reduce reactor power, K-7A tripped. Later, the trip was attributed to a failure in the layshaft assembly which uncoupled the governor controls from the main turbine shaft and resulted in the turbine tripping on overspeed. K-7B and ramped the turbine up to full speed, as required by Off Normal Procedure ONP-3, 'Loss of Main Feedwater.' Later when 'B' Steam Generator (E-50B) level was recovering too quickly, the control room operator took manual control of the feedwater regulating valve (CV-0703) to manually throttle the valve. The 'B' Steam Generator level reached the high level override setpoint which immediately closed the feedwater regulating valve CV-0703. Rapidly closing the feedwater regulating valve CV-0703 caused an immediate drop in load and K-7B turbine speed increased above the overspeed trip, resulting in the turbine tripping on overspeed. After verifying that K-7B had tripped, the control room operator manually tripped the reactor. <br /><br /> The cause of this event was the failure of the locknut on the layshaft assembly of K-7A, allowing the layshaft drive gear to walk down the shaft.
255 | 2551998010 | 1998-07-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palisades | P | CE | PO | 100 | On July 21, 1998, at 1452 hours, with the Plant operating at 99.6% power, the reactor was manually tripped due to a partial loss of main feedwater [SJ]. At the time of the reactor [RCT] trip one of the two main feedwater pumps [P] had tripped. The Control Room received an oil system trouble alarm [AA] on the "A" main feedwater pump turbine driver, followed immediately by a trip of the main feedwater pump. In response to the trip of the main feedwater pump, the reactor was manually tripped in accordance with operating procedures. When the steam generator low level set point was reached, the auxiliary feedwater system [BA] actuated as expected. The main feedwater pump trip was caused by failure of the coupling which drives the feedwater pump's main lube oil pump, resulting in a feedwater pump trip on low lubricating oil pressure. The main lube oil pump coupling [CPLG] and associated components were replaced and satisfactorily tested in conjunction with returning the plant to operation.
255 | 2552000003 | 2000-04-04 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Palisades | P | CE | PO | 100 | On April 4, 2000 at approximately 0620 hours with the plant operating at 99.9%power,an error by an auxiliary operator (AO) while attempting to rack-out the 2400 volt Emergency Diesel Generator 1-1 (EDG 1-1) output breaker 152-107,resulted in the EDG 1-1 output breaker being closed onto 2400 Volt Safeguards Bus 1-C with the EDG not in operation. The resultant voltage transient on the Safeguards Transformer and Bus 1-C led to the automatic starting of both emergency diesel generators, a manual reactor trip in accordance with operating procedures and an auxiliary feedwater actuation (AFAS). The safety significance of this event was minimal. Applicable safety systems functioned as expected, and there was no damage to plant equipment caused by this event. The automatic starting of both emergency diesel generators, the manual actuation of the reactor protection system and the auxiliary feedwater actuation are reportable to NRC in accordance with 10 CFR 50.73(a)(2)(iv)as Engineered Safety Feature (ESF) actuations.
255 | 2552002002 | 2002-12-01 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Palisades | P | CE | PO | 100 | On December 1, 2002, at approximately 2154 hours, with the plant operating at 100% power, an automatic reactor trip occurred on main generator loss of load. The loss of load occurred when a transmission tower's static line hanger failed, allowing one of two static lines to contact a 345 KV transmission line, tripping the main generator. The static line also contacted the rear bus in the switchyard that supplies the plant non-1E 4160 volt startup transformers. The rear bus tripped on a fault-to-ground causing a loss of non-1E 4160 volt AC buses. Consequently, both main feedwater pumps tripped, and the auxiliary feedwater system started automatically on low steam generator level, as expected. The plant was maintained at or near normal operating pressure and temperature subsequent to the trip, on natural circulation, since startup power for primary coolant pumps was also lost. The plant was returned to service on December 5, 2002. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic reactor trip and automatic actuation of the auxiliary feedwater system.
255 | 2552004001 | 2004-08-31 | P1 | Total Loss of Feedwater Flow | [7 empty] | X | [5 empty] | X | [19 empty] | X | [10 empty] | X | Palisades | P | CE | PO | 95 | On August 31, 2004, at 0715 hours, the plant was operating at approximately 100% power. A rapid plant down power was commenced following report of a fire in the vicinity of the P-2B condensate pump lower motor bearing. At 0718 hours, the reactor was manually tripped from approximately 95% power, in conjunction with securing the P-2B condensate pump, and the imminent loss of main feedwater. Following the reactor trip, the auxiliary feedwater system started automatically to maintain steam generator water level. The plant was stabilized in Mode 3. Overheating, and ultimately fire, at the condensate pump lower motor bearing were caused by pump and motor misalignment following maintenance in July 2004. The pump and motor misalignment occurred as a result of inadequate maintenance instructions. Proper alignment criteria were established and incorporated into the work instruction when the repaired motor was reinstalled in September 2004. The safety significance of this event was minimal. All safety systems functioned as expected during the plant trip. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the reactor protection system and automatic actuation of the auxiliary feedwater system.
255 | 2552005001 | 2005-01-09 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Palisades | P | CE | PO | 75 | On January 9, 2005, at 1117 hours, with the plant operating at approximately 100% power, a rapid plant down power was commenced following an unexpected lowering of condenser vacuum. At 1127 hours, the reactor was manually tripped from 75% power. Following the reactor trip, the auxiliary feedwater system started automatically to maintain steam generator water level. The plant was stabilized in Mode 3 to investigate and repair the cause of the low condenser vacuum. All safety systems functioned as expected during the plant trip. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the reactor protection system and automatic actuation of the auxiliary feedwater system.
255 | 2552005005 | 2005-09-01 | QR6 | Manual Reactor Trip | [45 empty] | Palisades | P | CE | PO | 100 | On September 1, 2005, at 1025 hours, with the plant operating at 100% power, the reactor was manually tripped due to a hydrogen leak associated with the main generator. The manual reactor trip was a precautionary measure to facilitate expeditious removal from service of the main generator to allow hydrogen to be isolated and purged from the main generator, and preclude the potential for formation of an explosive hydrogen/air mixture. Following the reactor trip, the auxiliary feedwater system started automatically to maintain steam generator water level. The plant was stabilized in Mode 3 to investigate and repair the cause of the hydrogen leak. The hydrogen leak was at a socket weld at a piping tee connection on the main generator's leak detection line. The socket weld was repaired by grinding out the weld area and re-welding the connection. The most probable causes are cyclic fatigue of the weld due to vibration of the line and a weld flaw. The safety significance of this event was minimal. All safety systems functioned as expected during the plant trip. This event does not involve a safety system functional failure. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the reactor protection system and automatic actuation of the auxiliary feedwater system.
255 | 2552006005 | 2006-05-10 | QR3 | Reactivity Control Imbalance | [45 empty] | Palisades | P | CE | PO | 22 | On May 10, 2006, an unexpected quadrant power tilt was identified during reactor core startup physics testing. At the time of discovery, plant power was being maintained at approximately 22% following initial power ascension from a recently completed refueling outage. Subsequent analysis determined the most probable cause of the quadrant power tilt to be Control Rod 33 fully inserted into the core as opposed to being fully withdrawn as indicated. A shutdown was initiated to facilitate further troubleshooting. The reactor was manually tripped from approximately 11% power. On May 13, 2006, investigation determined that Control Rod 33 was uncoupled from its drive assembly, having not been successfully coupled during the refueling outage. Consequently, Control Rod 33 had remained fully inserted into the core throughout plant startup from the refueling outage. Prior to discovery, the upward mode changes into Mode 2 and Mode 1 that occurred on May 9 and May 10, 2006, respectively, were performed in violation of Technical Specification (TS) 3.0.4, since the intent of TS 3.1.4.D.1 is to prevent a reactor startup with an immovable control rod. Consequently, this event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation which was prohibited by Technical Specifications. In addition, the manual reactor protection system actuation is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A).
255 | 2552007005 | 2007-05-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palisades | P | CE | PO | 100 | On May 8, 2007, with the plant at approximately 100% power, an automatic reactor trip occurred due to low level in the "B" steam generator. The "B" steam generator low level condition was the result of an inadvertent closure of the "B" main feedwater regulating valve (MFRV). The MFRV closure occurred when an incorrect link was opened during a maintenance work activity associated with the position indication for the MFRV. The purpose of the work activity was to correct a failed control room position indicator for MFRV CV-0703. The technician intended to open link 32 to isolate the instrument loop, which would have only affected the position indication for CV-0703. However, due to human error, link 33 was opened instead of link 32, which de-energized the MFRV controller. The loss of power to the controller caused MFRV CV-0703 to close with a resultant loss of feedwater to "B" steam generator. As expected, the auxiliary feedwater system started automatically to recover steam generator level. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of both the reactor protection system and the auxiliary feedwater system.
255 | 2552008001 | 2008-01-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Palisades | P | CE | PO | 100 | On January 13, 2008, with the plant in Mode 1 at 100% power, main feedwater pump P-1B tripped unexpectedly. Operators entered the loss of main feedwater procedure and appropriately carried out the procedurally directed action to manually trip the reactor. As expected, the auxiliary feedwater system started automatically to recover steam generator level. The immediate cause of the main feedwater pump trip was low lube oil pressure. The low lube oil pressure resulted from the loss of the main feedwater pump's shaft-driven lube oil pump, which occurred when its drive coupling became disengaged. An incorrect shaft key allowed the lower hub to slide down the shaft, making only partial engagement with the sleeve. The partial tooth engagement between the lower hub and sleeve was not sufficient to withstand the shaft torque, which ultimately resulted in stripping the splines on the coupling sleeve and decoupling the lube oil pump's shaft drive. The lube oil pump was rebuilt, incorporating a design change that added a spacer beneath the lower hub to prevent the hub from sliding down the shaft and losing engagement with the coupling sleeve. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an actuation of both the reactor protection system and the auxiliary feedwater system.
255 | 2552008003 | 2008-05-23 | QR5 | Turbine Trip | [45 empty] | Palisades | P | CE | PO | 100 | On May 23, 2008, at 1249 hours, with the plant in Mode 1 at 100% power, an actuation of the 346 generator negative sequence relay caused an actuation of the 386C coastdown lockout relay. The 386C relay actuation caused the main generator output breakers in the switchyard to open, causing a turbine trip, which actuated the reactor protective system to trip the reactor. As expected, the auxiliary feedwater system started automatically to recover steam generator level. The cause of the generator negative sequence relay could not immediately be determined. The relay spuriously failed. The relay was replaced and sent to Asea Brown Boyeri (ABB) for analysis. The problem could not be reproduced at ABB. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an actuation of both the reactor protection system and the auxiliary feedwater system.
255 | 2552011002 | 2011-01-22 | QR5 | Turbine Trip | [45 empty] | Palisades | P | CE | PO | 100 | On January 22, 2011, at 1735 hours, with the plant in Mode 1 at 100% power, the operation of relay 251-2/SPG3, station power transformer 1-3 neutral to ground, actuated relay 386B, generator direct trip lockout relay (backup), opening the main generator output breakers to the transmission system causing a turbine trip. The turbine trip actuated the reactor protective system to trip the reactor due to a loss of load. As expected, the auxiliary feedwater system started automatically to recover steam generator level. The cause for operation of the neutral to ground relay, and subsequent automatic plant trip, was a ground fault on a medium voltage cable that provides electrical power to bus 1G, via breaker 252-401, from station power transformer 1-3. The probable cause of the ground fault on the cable was determined to be flaws in the insulation, with the effects of moisture acting on these flaws over time, causing the insulation to degrade. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an actuation of both the reactor protection system and the auxiliary feedwater system.
255 | 2552011006 | 2011-09-16 | QG9 | Primary System Leak | [45 empty] | Palisades | P | CE | PO | 79 | On September 16, 2011, at 1402 hours, with the plant in Mode 1 at 100% power, primary coolant system (PCS) unidentified leakage increased to greater than one gallon per minute (gpm) for greater than four hours, and was unable to be reduced to within Technical Specification (TS) limiting condition for operation (LCO) 3.4.13 limits. TS 3.4.13, Required Actions B.1 and B.2 were entered, which required the plant to be in Mode 3 in 6 hours and Mode 5 in 36 hours. Power reduction commenced at 12% per hour. Subsequently, leakage increased to greater than 10 gpm. The site entered an unusual event at 1450 hours. The reactor was manually tripped at 1454 hours, and an emergency notification was made in accordance with the Site Emergency Plan. As expected, the auxiliary feedwater system started automatically to recover steam generator level. The unusual event was exited at 1934 hours The cause of the increased leakage requiring the reactor trip is attributed to a failed packing on a pressurizer spray control valve. The valve was repaired and the reactor was returned to full service on September 21, 2011. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an actuation of both the reactor protection system and the auxiliary feedwater system.
255 | 2552011007 | 2011-09-25 | C3 | Loss of Vital dc Bus |  |  | X | [7 empty] | X | [7 empty] | X | [20 empty] | X | [5 empty] | Palisades | P | CE | PO | 98 | On September 25, 2011, at 1506 hours, during planned maintenance activities on a direct current (DC) electrical distribution (ED) panel, ED-11-2, a short circuit fault between the positive and negative bus bars was introduced into the system. The fault was caused by the accidental contact between bus bar connectors within the panel. Subsequently, a partial loss of DC electrical system power occurred, causing an automatic reactor trip and multiple safety system actuations. The fault from ED-11-2 propagated upstream, resulting in a loss of left train DC power to two-of-four inverters and subsequent loss of alternating current (AC) power from the inverters to two-of-four preferred busses. The loss of power initiated a reactor trip via the automatic actuation of the reactor protection system (RPS). Additional automatic actuations include the closure of the main steam isolation valves (MSIVs), actuation of the safety injection system (SIS), actuation of the containment isolation system (CIS), and actuation of the auxiliary feedwater system (AFS). The MSIVs, RPS, SIS, CIS and AFS performed as designed for the loss of power condition. The root cause of the event was attributed to risk management processes not being followed, resulting in the failure to adequately manage the risk associated with the maintenance on the ED-11-2 panel. In addition, there was insufficient breaker and fuse coordination for the left train of the 125 volt DC system. An engineering change was approved and installed to reduce the probability of recurrence. Repairs to the affected DC electrical system components were completed and the reactor was returned to full power operation on October 3, 2011.
255 | 2552011008 | 2011-12-14 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Palisades | P | CE | PO | 100 | On December 14, 2011, main feedwater (MFW) pumps, P-1A and P-1B, tripped due the loss of suction pressure. Operators entered the loss of MFW procedure and appropriately carried out the procedurally directed action to manually trip the reactor. As expected, the auxiliary feedwater system started automatically to recover level in the steam generators. The immediate cause for the loss of suction pressure to the MFW pumps was the spurious opening of MFW pump, P-1A, recirculation control valve, CV-0711. The spurious opening of CV-0711 resulted from a loss of electrical control power to the valve. The loss of electrical control power to CV-0711 was due to insufficient contact between the fuse holder clip and a fuse ferrule within a fuse block assembly of the control power circuitry. The possible causes for the lack of sufficient contact between the fuse holder clip and the fuse ferrule were the stretching of the fuse holder clip during the installation/removal of a fuse tag-out device, and/or fatigue of the fuse holder clip, induced by the repetitive removal/installation of the fuse. The control power circuitry, for CV-0711, was rerouted through an acceptable spare fuse block assembly and reenergized. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the reactor protection system and the automatic actuation auxiliary feedwater system.
255 | 2552015001 | 2015-09-16 | QR5 | Turbine Trip | [45 empty] | Palisades | P | CE | PO | 85 | On September 16, 2015, at approximately 0117 hours, an anomaly within the digital electro-hydraulic (DEH) turbine control system initiated a turbine trip. As designed, the turbine trip actuated the reactor protection system to automatically trip the reactor due to a loss of load and the auxiliary feedwater system started automatically to recover steam generator levels. <br /><br /> The direct cause of the event is the turbine tripped due to actuation of the "DEH controller loss of power" turbine trip logic. Troubleshooting and analysis determined there was a failure of a power supply module on a circuit board in the DEH turbine control system. Subsequent to the power failure on the circuit board, a second failure, either a loss of power to the overspeed protection control (OPC) distributed processing units (DPUs) or a loss of communications between the primary and backup OPC DPUs, occurred resulting in an actuation of the "DEH controller loss of power" turbine trip logic. <br /><br /> The root cause of the event is that the design of the DEH system contains unnecessary trip logic associated with turbine overspeed monitoring. Corrective actions include a modification to remove the DEH system OPC loss of power and loss of communications trip logic.
255 | 2552019001 | 2019-01-03 | QR6 | Manual Reactor Trip | [45 empty] | Palisades | P | CE | PO | 85 | On January 3, 2019, while the reactor was in mode 1 at 85% power, the linear variable differential transformer (LVDT) core on CV- 0576, "High Pressure Turbine #4 Governor Valve," broke, causing uncontrolled cycling of the valve and an excursion in generator output. Upon control room notification of the uncontrolled movement of CV-0576, the operators placed the turbine controls in manual operation. However, CV-0576 proceeded to open and close independently of valve controls. Due to the inability to maintain positive control of CV-0576 manually, the operators manually tripped the reactor in accordance with site procedures. The required safety systems and shutdown equipment performed as expected, resulting in an uncomplicated trip. The condition was reported on January 3, 2019 (Event Number 53813) in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) for a valid reactor protection system (RPS) actuation and an auxiliary feedwater (AFW) actuation. <br /><br /> This condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the actuation of both the RPS and the AFW. <br /><br /> The condition was attributed to a high-cycle fatigue failure of the LVDT core, which led to the uncontrolled movement of CV-0576. Corrective actions were taken to replace the LVDT cores on all four governor valves before returning to power operations.<br /><br /> The investigation led to a corrective action to create preventative maintenance tasks to replace the governor valve LVDTs during normally scheduled actuator inspection and refurbishment.
255 | 2552019002 | 2019-01-09 | QR8 | Spurious Reactor Trip | [45 empty] | Palisades | P | CE | PO | 100 | On January 9, 2019, maintenance personnel were performing a calibration of NI-6, "Power Range Safety Channel." The plant was in mode 1 at 100% power. At approximately 10:28 EST, maintenance personnel removed the panel on EC-06, "Reactor Protection System (RPS) cabinet," and observed an arc in the vicinity of incoming AC power. It was immediately observed that the entire RPS B channel had lost power. Approximately six minutes after the loss of power to RPS B channel, the reactor tripped. Following the reactor trip, it was identified that the RPS D channel matrix BD power supply was not lit, indicating no output. <br /><br /> The required safety systems and shutdown equipment performed as expected, resulting in an uncomplicated trip. The condition was reported on January 9, 2019 (Event Number 53819) in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) for both a valid reactor protection system (RPS) actuation and an auxiliary feedwater actuation (AFW).<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in a valid actuation of both the RPS and the AFW.<br /><br /> The cause was attributed to shorted capacitors in the B RPS cabinet and a blown input fuse to the RPS D channel BD matrix power supply. Corrective actions were taken to replace the capacitors with insulated capacitors, and to replace the RPS D channel BD matrix power supply and fuse.
259 | 2592007002 | 2007-05-24 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 1 | B | GE | SU | 1 | On May 24, 2007, at 0211 CDT, Unit 1 operators initiated a manual scram due to an Electro-Hydraulic Control (EHC) [TG] leak that could not be isolated. The reactor was in the startup mode and the generator was not tied to the grid. TVA's causal analysis indicates the inadequate application of the work control process during Unit 1 recovery activities. Weakness in the work control process used during Unit 1 restart activities allowed work to be performed on the EHC System using a generic work order while the system was pressurized. A common practice during recovery of Unit 1 restart effort was to use generic work orders to provide the broadest scope of work and maximum flexibility for the craft personnel. The current work control process has checks and balances to ensure that work is properly evaluated, planned and documented, commensurate with the sensitivity of the equipment and the risk of the activity. The damaged tubing was removed and the connection repaired. TVA is reporting this event in accordance with 10 CFR 50.73(a)(2)(iv)(A). This scram event is reportable within 4 hours under 10 CFR 50.72(b)(2)(iv)(B), any event or condition that results in a valid actuation of the Reactor Protection System, and within 8 hours under 10 CFR 50.72(b)(3)(iv)(A), any event that results in an actuation of the specified systems. This event also required a 60-day written report in accordance with 10 CFR 50.73(a)(2)(iv)(A).
259 | 2592007005 | 2007-06-09 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 1 | B | GE | PO | 80 | On June 9, 2007, at approximately 1100 hours central daylight time (CDT) Unit 1 automatically scrammed following a turbine trip from a 1A2 main steam moisture separator tank high level signal. Prior to the scram, at 1019 hours CDT, the Moisture Separator Reservoir High Level Dump Valve was noted opening. At approximately 1040 hours CDT operations received a low level alarm for the 1A2 moisture separator. Subsequently, at approximately 1100 hours CDT a turbine trip signal was initiated from an indicated main steam moisture separator high tank level. This was followed by an automatic reactor scram. The root cause of the event is the sizing of the Moisture Separator 1A2 Level Control Dump Valve. TVA is reviewing the design for the Moisture Separator Dump Valve and controls to determine if modifications are required. If necessary will either modify or replace the Unit 1 valves and controls.
259 | 2592007007 | 2007-08-11 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Browns Ferry 1 | B | GE | PO | 100 | On August 11, 2007, at 1751 hours central daylight time (CDT) Unit 1 automatically scrammed from a Neutron Monitoring Average Power Range Monitor (APRM) signal. Just prior to the scram, a Reactor Recirculation system flow sensing line separated from the Recirculation Pump 1B Flow Transmitter (1-FT-068-081B). This resulted in a false indicated recirculation system low flow with a high reactor core thermal power (100 percent) to the Neutron Monitoring system. Based on these conditions, the neutron monitoring system initiated an APRM Simulated Thermal Power Flow Biased Reactor Scram. TVA's causal analysis concluded the root cause of this event was a lack of rigorous worker practices in the use of place keeping and flagging to keep up with the work steps during the Unit 1 recovery activities. This resulted in inadequate assembly of the compression fitting. TVA is submitting this report in accordance with 10 CFR 50.73(a)(2)(iv)(A); as an event that resulted in a manual or automatic actuation of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B) (i.e., reactor protection system including reactor scram or trip, and general containment isolation signals affecting containment isolation valves in more than one system).
259 | 2592007008 | 2007-09-03 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 1 | B | GE | PO | 72 | On September 1, 2007, at approximately 1955 hours CDT, Unit 1 Operations was notified that there was a small EHC leak in the Unit 1 Moisture Separator (MS) room in the Turbine Building. Unit 1 was operating at 100 percent power. Video monitoring was established by 0657 hours CDT. Operations noted the leak rate was approximately 120 drops per minute. On September 3, 2007, at 0214 hours CDT Operations noted that the leak rate was increasing and manually scrammed the reactor from approximately 72 percent power. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in a manual or automatic actuation of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B) (i.e., reactor protection system including reactor scram or trip, and general containment isolation signals affecting containment isolation valves in more than one system).
259 | 2592007009 | 2007-10-12 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 1 | B | GE | PO | 100 | On October 12, 2007, at 0803 hours central daylight time (CDT), Unit 1 automatically scrammed following a turbine trip from a 1A1 main steam system moisture separator false high level signal. At approximately 0739 hours CDT, prior to the automatic turbine trip, the Unit 1 operator received an alarm indicating a low level in the 1A1 moisture separator drain tank. At 0803 hours CDT, Unit 1 received a moisture separator 1A1 high level turbine trip signal followed immediately by a reactor scram. TVA submits this report in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in a manual or automatic actuation of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B) (i.e., reactor protection system including reactor scram or trip, and general containment isolation signals affecting containment isolation valves in more than one system).
259 | 2592009001 | 2009-02-18 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 1 | B | GE | PO | 100 | February 18, 2009, at 0351 hours Central Standard Time (CST), following a scheduled preventative maintenance activity, Unit 1 reactor automatically scrammed from a turbine trip due to a power load unbalance signal on the main generator. Specifically, at 0349 hours CST, Operations swapped the Unit 1 Main Generator Isophase Bus Duct System cooling fan from the running to the alternate fan. When the alternate fan started, water entrapped in the fan housing was expelled into the bus provided a path to ground inside the bus duct. This resulted in actuation of the generator protective relays and a turbine trip and automatic reactor scram, which resulted in the automatic actuation of the reactor protection system. Water that had settled in the idle bus duct cooling fan housing was expelled into the main generator isophase bus duct upon fan startup providing a conductive path to ground. The root cause of this event was less than adequate design process guidance for consideration of seasonal variations in the operating conditions for heating ventilation and air conditioning (HVAC) system design. The design process does not consider full range of operation of HVAC systems using raw cooling water as a cooling medium during the winter months. BFN inspected the Unit 1 isophase bus for damage. No damage was identified. BFN installed a drain with a site glass on each Unit 1 bus duct cooling fan housing. General Operating Instruction, Operations Round Logs, was revised requiring verification that there is no water in the idle fan and to drain any water that may have accumulated prior to placing it into service. BFN will modify the design change technical considerations checklist to provide design process guidance for consideration of seasonal variations in operating conditions for HVAC design.
259 | 2592011001 | 2011-04-27 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Browns Ferry 1 | B | GE | PO | 75 | On April 27, 2011, severe weather in the Tennessee Valley Service Area caused grid instability and loss of all 500-kV offsite power sources that resulted in automatic scrams of all three units. All three units were in Mode 1 at the time of the event. All scram systems were actuated, all actuations were complete, and required systems started and functioned successfully with the exception of an indeterminate position indication for the Unit 3 B Inboard Main Steam Isolation Valve. All onsite safe shutdown equipment was available with the exception of the 3B Emergency Diesel Generator (EDG), which was inoperable and unavailable due to planned maintenance. After the event, only one 161-kV line remained available for offsite power - all (seven) 500-kV lines and one (of two) 161-kV line were lost. All three units immediately entered Mode 3 (Hot Shutdown) with their respective 4-kV busses supplied by the onsite EDGs. On April 27, 2011, at 1701 hours, a Notification of Unusual Event (NOUE) was declared due to the loss of normal and alternate supply voltage to all unit-specific 4-kV shutdown boards for greater than 15 minutes and at least two EDGs supplying power to unit-specific 4-kV shutdown boards. On May 2, 2011, at 2050 hours, the NOUE was terminated following restoration of qualified offsite power sources.
259 | 2592013002 | 2013-03-19 | QL7 | Degraded condenser vacuum | [45 empty] | Browns Ferry 1 | B | GE | PO | 80 | On March 19, 2013, at approximately 0402 hours Central Daylight Time, the Browns Ferry Nuclear Plant (BFN), Unit 1, reactor was manually scrammed due to decreasing condenser vacuum caused by a significant leak from the 1C feedwater heater level control line. Condenser vacuum was deteriorating and was approaching the turbine trip setpoint, at which time the reactor was manually scrammed. The main steam isolation valves remained open, reactor pressure was controlled with the main turbine bypass valves, and the reactor feedwater pumps were used to control reactor water level. All systems responded as expected to the scram. All control rods inserted into the core during the scram.<br><br> The root causes for this event were a combination of vibration from the dump valve opening with the vibration in the 4 inch drain line from leaking drain valves, and station personnel did not consistently consider risk when making decisions to replace the BFN, Unit 1, feedwater heater vent and drain valves.<br><br> The corrective actions to prevent recurrence are to design and implement a design change for the feedwater heater vent and drain header piping to provide increased support, and establish initial and continuing training requirements for leaders and craft that support their roles and responsibilities. Also, BFN has implemented a Strategic Performance Management process to reinforce and institutionalize conservative decision making principles.
259 | 2592014003 | 2014-08-26 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 1 | B | GE | PO | 95 | On August 26, 2014, at 1730 Central Daylight Time, Browns Ferry Nuclear Plant (BFN), Unit 1, experienced a turbine trip resulting in an automatic reactor scram. The cause of the turbine trip was a control valve fast closure signal that was generated by a turbine trip on generator neutral over voltage signal from the 1A Generator Neutral Overvoltage relay.<br /><br /> The root cause of the event was the failure of an internal fuse to Generator Circuit Breaker Potential Transformer to clear a fault due to improper fuse size. This was the result of insufficient technical rigor during vendor design and in the Tennessee Valley Authority's review of the vendor design.<br /><br /> The corrective action to prevent recurrence is to develop and implement a design change for all three BFN Units to replace the fuses contained within the Main Generator Circuit Breaker Potential Transformers with a fuse that will coordinate with the Generator Neutral Overvoltage Relay and clear prior to the actuation point of the Generator Neutral Overvoltage Relay during any postulated failure of the Potential Transformers.
259 | 2592018002 | 2018-03-18 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Browns Ferry 1 | B | GE | PO | 100 | On March 18, 2018, at 1158 CDT, the Unit 1 reactor automatically scrammed due to a Reactor Protection System (RPS) signal generated from High Reactor Steam Dome Pressure in response to the Electro-Hydraulic Control (EHC) system clamping the Turbine Control Valves. All control rods fully inserted into the core. Main Steam Isolation Valves (MSIV) remained open with Main Steam Relief Valves operating on the initial transient as expected. Main Turbine Bypass Valves controlled reactor pressure. Reactor Feedwater pumps remained in service to control reactor water level. Primary Containment Isolation System Groups 2, 3, 6, and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. All safety systems operated as expected. <br /><br /> An investigation determined the event was caused by Operations and Engineering Management failing to track and review the aggregate impact of off-normal conditions. There was inadequate procedural guidance to assess operational impacts when equipment failures/faults occurred, prior to entering the work management process. The normal level of review would not have identified the condition leading to the scram. <br /><br /> Both megawatt input transducers were replaced prior to Unit 1 restart from the scram. As an interim action, a Nuclear Operating Experience Report (NOER) was issued for communication to other TVA sites. This NOER stressed the importance of evaluating the full impact of failed digital equipment, which must include software logic inputs. As a corrective action to prevent future recurrence, operator responsibilities for performing operational impact reviews were clarified in procedures. This included developing a tool or checklist for operational impact reviews.
259 | 2592020001 | 2020-07-20 | QL7 | Degraded condenser vacuum | [45 empty] | Browns Ferry 1 | B | GE | PO | 30 | On July 20, 2020, at approximately 0955 Central Daylight Time (CDT), the Unit 1 control room received the traveling screen differential pressure high alarm. Assistant Unit Operators dispatched to the condenser circulating water (CCW) system forebay reported large masses of eel grass. The influx of eel grass resulted in fouling of the trash racks and traveling water screens for all three units which reduced the CCW flows during this event. <br /><br /> As a result of degrading condenser vacuum on Unit 2, operators manually scrammed the reactor at 1325 CDT. On July 21, 2020, as Unit 1 condenser vacuum continued to degrade to the turbine trip setpoint, the Unit 1 operators manually scrammed the reactor at 0435 CDT. <br /><br /> The root cause of the event is that existing permanently installed plant equipment at the BFN forebay was not adequate to mitigate the newly developed threat presented by large scale eel grass accumulation on Wheeler Lake. <br /><br /> The action plan for addressing the root cause of this event has been developed which consists of deciding which equipment upgrades will be the most effective based on studies of river flow and environmental conditions, funding these upgrades, issuing design packages, and implementing the final designs.
260 | 2601991014 | 1991-06-29 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 2 | B | GE | SU | 1 | On June 29, 1991, during performance of power ascension testing the Unit 2 reactor was manually scrammed at 0248 hours from approximately 25 megawatts thermal power due to the bulk suppression pool water temperature exceeding the Technical Specification limit of 110 degrees F. This occurred as a result of suppression pool thermal stratification while operating Reactor Core Isolation Cooling (RCIC). <br /><br /> The root cause of this event was inadequate procedures. Plant procedures did not provide information on the possibility for thermal stratification of suppression pool water which can result from operation of RCIC. Contributing to this event was the location of the temperature elements in the suppression pool, malfunction of the suppression chamber atmospheric temperature recorder (manufactured by Leeds & Northrup) and failure of the Shift Technical Advisor and the General Electric shift advisor to analyze the expected torus water heatup during the plant evolution. <br /><br /> TVA revised the procedure for operating RCIC to note the potential for thermal stratification of the suppression pool, and to require evaluation of the necessity to initiate suppression pool cooling. Other plant procedures will be revised as necessary to add this information. TVA also issued an Operations Standing Order which specifies the expected rate of suppression pool heatup during RCIC and High-Pressure Coolant injection system operation, and when suppression pool cooling should be initiated. Operating crews were trained on the standing order and the details of this event.
260 | 2601991017 | 1991-09-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On September 14, 1991 at 1832 hours, with Unit 2 operating at 100 percent power, an automatic reactor scram occurred on low reactor water level. The low water level was caused by a momentary loss of reactor feedwater. The loss of reactor feedwater was a result of a failed soldered connection on the air supply line to the steam packing exhauster bypass flow control valve (FCV) allowing the FCV to close. The loss of flow condition subsequently caused 'A' and 'B' condensate booster pumps and 'A' and 'B' reactor feed pumps to trip on low suction pressure. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as a condition which resulted in manual or automatic actuation of engineered safety features including the reactor protection system. <br /><br /> The root cause of this event was poor workmanship on the failed air supply line soldered connection. TVA's analysis determined that the bonded area of the failed solder joint was less than 15 percent. <br /><br /> The soldered connection was repaired. Those required soldered connections in air supply lines whose failure could cause a reactor scram will be inspected by visual examination using liquid leak detection solution.
260 | 2601991018 | 1991-10-18 | QR6 | Manual Reactor Trip | [13 empty] | X | [30 empty] | X | Browns Ferry 2 | B | GE | PO | 8 | On October 18, 1991 at 0458 hours, during a controlled shutdown, Browns Ferry Unit 2 reactor was manually scrammed from approximately eight percent thermal power due to unexpected equipment responses.<br /><br /> The root cause of this event was inappropriate personnel action. A plant operator failed to follow the procedure for turbine generator shutdown when he did not open the exciter field breaker after the manual turbine generator trip. This action caused unexpected equipment responses including actuation of the generator reverse power relay and subsequent tripping of the reactor recirculation pumps. <br /><br /> The reverse power relay was tested. The evaluation and testing of the recirculation pump boards was completed. Operations personnel will receive live-time training on the event. TVA will change the plant design to include automatic tripping of the generator field breaker when the turbine generator is tripped. The Browns Ferry simulator will be upgraded to match plant conditions.
260 | 2601991019 | 1991-12-08 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 80 | On December 8, 1991 at 2320 CST, Browns Ferry Unit 2 automatically scrammed from approximately 80 percent power following a turbine trip. In addition, during this event, an unexpected loss of one of the offsite power supplies occurred. <br /><br /> The root cause of this event was an unexpected and unforeseen fuse (Gould-Shawmut) failure. <br /><br /> TVA has replaced the existing 500kV Bus Potential Transformer secondary fuses to minimize the possibility of spurious relay operations. <br /><br /> TVA will evaluate reconfiguring the existing plant design to eliminate the possibility that the loss of the relaying potential from a single bus will result in the loss of the generating unit. In addition, TVA will investigate the spurious trip of Trinity line 1 line during this event and correct any identified deficiencies.
260 | 2601992004 | 1992-04-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On April 27, 1992, at approximately 1432 hours, Unit 2 reactor scrammed on low reactor water level. Engineered safety feature actuations included primary containment isolation system Groups 2, 3, 6, and 8, and actuation of the control room emergency ventilation and standby gas treatment (all trains) as expected. <br /><br /> The low reactor water level was due to the failure of the feedwater level control system. This resulted in the feedwater pumps run back and low flow to the reactor vessel. The operator was unable to regain control of the feed pumps before the reactor scrammed on low water level. <br /><br /> The cause of this event was the master feedwater level controller output failed downscale. The downscale failure was due to an unexpected and random failure of an electrolytic capacitor in the controller.<br /><br /> The following corrective actions have been or will be taken to address this event: 1) The maintenance planning guide has been revised to include testing wet type electrolytic capacitors, 2) TVA will evaluate the power stores procedure on monitoring shelf life of high-risk components in storage, and 3) TVA will evaluate implementation of the Scram Frequency Reduction Committee recommendation to design and install a fault tolerant digital feedwater control system.
260 | 2601992006 | 1992-07-28 | QR8 | Spurious Reactor Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On July 28, 1992, at 1932 hours, during troubleshooting on the Unit 2 Feedwater Level Control (FWLC) System, Browns Ferry Unit 2 experienced an automatic main turbine trip and reactor scram from an indicated high water level spike on two of three level channels. Engineered safety feature actuations included Primary Containment Isolation System Group 2, 3, 6, and 8 logic and all trains of Standby Gas Treatment and Control Room Emergency Ventilation. <br /><br /> The level spike was induced by the replacement of a relay in the control circuit of the FWLC system. Subsequent investigation determined that the relay replacement was not required. The root cause of this event was an inaccurate evaluation and diagnosis of prior feedwater system trouble symptoms, and failure to anticipate the FWLC circuit response to the relay replacement.<br /><br /> Administrative controls will be provided to ensure high risk troubleshooting activities on certain plant systems receive an independent technical review in addition to that already done. TVA will review this event with appropriate personnel.
260 | 2601994004 | 1994-04-15 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On April 15, 1994, at 0219 hours , Unit 2 received a full scram from full power due to a RPS trip signal generated by a low Scram Pilot Air Header pressure signal. This resulted in a low reactor water level which caused isolation of various ESF and RPS system actuation. exception that high temperature alarms were received for the High Pressure Coolant Injection (HPCI) system. Affected ESF and RPS systems were returned to operable status by 0300 hours on April 15, 1994. Operators returned HPCI to service at 0535 hours after no abnormal conditions could be found. <br /><br /> The root cause of this event was inappropriate personnel action during maintenance activity on the Scram Pilot Air Header. The personnel involved deviated from the work order, but did not take the proper actions to ensure that their actions would not adversely affect plant operation. If the work order had been performed as written the scram would not have occurred. <br /><br /> During the unit scram a false high temperature alarm in the HPCI led to isolation of HPCI. This was attributed to a failed module in the temperature detection loop. <br /><br /> This event is reportable per 10 CFR 50.73(a)(2)(iv) due to the ESF and RPS actuation, and 50.73(a)(2)(v) due to the isolation of the HPCI system, which is a single train system. Corrective actions to prevent recurrence include a review of this event by appropriate personnel and tighter controls for those activities which have the potential for ESF actuation.
260 | 2601994005 | 1994-04-18 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Browns Ferry 2 | B | GE | PO | 15 | On April 18, 1994, at approximately 0355 hours CDST, the Unit 2 reactor automatically scrammed from 15 percent power when the Main Steamline Isolation Valves (MSIVs) unexpectedly closed. MSIV closure was caused by low main steam pressure when six main turbine Bypass Valves (BPVs) spuriously opened to their full open position. Engineered Safety Feature (ESF) systems responded as designed. These systems included the automatic isolation or actuation of primary containment isolation system groups 2, 3, 6, and 8. This event is reported in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in the automatic actuation of any ESF, including the reactor protection system. <br /><br /> TVA determined that the most likely cause of the BPVs opening was an Electro-Hydraulic Control (EHC) system malfunction. A defective pressure regulator potentiometer was found in the EHC circuitry. <br /><br /> The defective potentiometer was replaced and satisfactorily tested before the restart of Unit 2. TVA will perform a failure investigation of the defective potentiometer and reevaluate preventive maintenance actions for other sensitive system potientiometers. While there have been a number of previous reactor trips due to EHC/turbine control problems, there were no previous similar reactor scrams caused by multiple BPVs opening unexpectedly.
260 | 2601994013 | 1994-12-02 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 54 | On December 2, 1994 at 0717 hours, Unit 2 received a full automatic scram from 54 percent reactor power. The scram was generated by a main generator turbine trip with the first stage turbine pressure greater than 154 psig. The turbine trip was caused by an invalid loss of main generator stator cooling water signal. The scram resulted in a low reactor water level which caused the isolation/actuation engineered safeguards (ESF) and reactor protection (RPS) systems. The affected ESF and RPS systems were returned to standby readiness by 0729 hours. The root cause of the event was mechanical degradation of the Main Generator Stator Cooling Water system temperature switch. The switch experienced setpoint drift which caused it to prematurely actuate. TVA will issue a procedure for calibration of the stator cooling water temperature switch. Additionally, TVA will evaluate balance of plant devices capable of causing turbine generator trips and ensure that the procedural guidance for calibration is adequate. Finally, TVA will evaluate other balance of plant devices to Bee if due to its age, replacement is required. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv), as any event or condition that resulted in manual or automatic actuation of any ESF including the reactor protection system.
260 | 2601995002 | 1995-02-09 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On February 9, 1995, at 0028 hours, the Unit 2 reactor scrammed due to a turbine trip. This trip was a result of a sensed generator load unbalance condition. The scram then resulted in the automatic actuation of the engineered safety feature (ESF) system. This event is, therefore, reportable in accordance with 10 CFR 50.73 (a)(2)(iv) as a condition responsible for an automatic actuation of the ESF system. The root cause of the event was a degraded subcomponent. Specifically, a leaking cooling water line manifold dripped water on the rectifier circuitry potentially creating a path to ground. Additionally, two generator field rectifier banks had a low-resistance to ground condition. Corrective actions to preclude recurrence are: (1) the leaking cooling water line was replaced, and (2) a determination will be performed for additional corrective actions based on a failure analysis of the leaking cooling water manifold and analytical tests of the rectifier cooling water tubes.
260 | 2601995004 | 1995-03-30 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On March 30, 1995, at 1800 hours, the Unit 2 reactor scrammed during the performance of the Core and Containment Systems Analog Trip Unit Functional Test. During this test, alternate rod insertion solenoid valves opened (i.e., energized) and vented control air from the scram pilot air header, causing a low scram pilot air header pressure condition (less than 53 psig.), which initiated a reactor scram. The scram then resulted in the automatic actuation of the engineered safety feature (ESF) system due to a sensed low reactor water level condition. This event is, therefore, reportable in accordance with 10 CFR 50.73 (a)(2)(iv) as a condition which resulted in an automatic actuation of the ESF system. The root cause of the event was personnel error in that an Instrumentation and Controls technician prematurely repositioned the Anticipated Transient Without Scram mode switch from the 'TEST' to the 'NORMAL' position with a test signal present. Corrective actions involve appropriate personnel corrective actions for the individual in this event.
260 | 2601995007 | 1995-08-19 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Browns Ferry 2 | B | GE | PO | 100 | On August 19, 1995, at 0124 hours, an offgas hold up volume high temperature alarm was received. This condition eventually resulted in isolating the steam jet air ejectors (SJAEs). When the SJAEs isolated, the main condenser began to lose vacuum resulting in a turbine trip. The turbine trip subsequently caused the reactor to scram at 0201 hours. The cause of this event was a faulty power supply resulting in an improper level control of the offgas condenser (OGC). The additional water in the OGC drastically reduced its heat removal capability. This caused the offgas holdup volume temperature to increase. Corrective actions were taken to restore the plant to a safe configuration. Additional corrective actions were to replace the faulty power supply, manually drain the OGC and clean the Raw Cooling Water (RCW) strainers filtering the RCW to the offgas dehumidifier chiller (OGDC). This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as a condition that resulted in an automatic actuation of an Engineered Safety Feature system.
260 | 2601996005 | 1996-05-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On May 10, 1996, at approximately 1024 hours, Browns Ferry Unit 2 was operating at 100 percent power when the unit automatically scrammed on low reactor water level due to a runback of two of the three reactor feed pumps. This occurred while software parameter changes were being made on the newly installed digital feedwater control system. When the software parameter changes were made active (i.e., saved) a reinitialization sequence automatically occurred within the control software "block," which drove the feed pump speed demand signal to zero for a period of a few seconds. This resulted in a low reactor water level which caused various Engineered Safety Feature (ESF) and Reactor Protection System actuations. The cause of this event is inadequate design of the digital feedwater control system software. Specifically, the system will reinitialize its feed pump demand output signal to zero during software parameter changes in the digital feedwater control system in some Of the software blocks provided (5 of 380). This system characteristic was outlined by the vendor as eliminated from the software design and was not known to the BFN plant staff. Plant safety systems responded as expected for this type of event. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as a condition that resulted in manual or automatic actuation of ESFs.<br /><br /> Reactor Core Isolation Cooling (RCIC) topped on high exhaust pressure during its startup transient. A design change implemented during the Unit 2 Cycle 8 refueling outage replaced the turbine exhaust check valve with a model having more reliability and leak tightness repeatability. The valve was also a lift check in lieu of a swing check which resulted in slightly higher operating exhaust pressure. Since the system did not function as required, RCIC was determined to be inoperable since the startup on April 24, 1996. Manual initiation of RCIC would not have resulted in the high exhaust pressure trip due to the different valve alignments and the timing of these manipulations. Therefore, the system was available for manual operation had it been needed. Following the successful completion of a rated-pressure flow test at normal operating pressure, RCIC was declared operable on May 15, 1996. This condition is also reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's technical specifications.
260 | 2601996007 | 1996-10-29 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On October 29, 1996, at approximately 1538 hours, a full reactor scram on control valve fast closure occurred. The Unit 2 main generator field collapsed due to an exciter malfunction, and the resultant voltage and current condition caused the generator backup relays to operate. The associated switchyard breakers opened and the power load imbalance initiated fast closure of the turbine control valves, which resulted in an automatic reactor scram. Automatic Engineered Safeguard Features and automatic isolations or actuations occurred as expected with exception of main steam safety relief valves failing to lift within their Technical Specifications setpoint tolerances. Peak reactor pressure reached approximately 1130 psig. The setpoint on the lowest setpoint MSRV is 1105 + 11 psig. The cause of the exciter malfunction was determined to be personnel error in that the applicable maintenance instruction was inadvertently revised with incorrect guidance on exciter brush replacement. The procedure criteria for replacement of the brushes did not meet the specified vendor guidance. Corrective actions taken were: The collector ring was repaired and brushes were replaced per vendor guidance. The Unit 3 exciter brushes were inspected and three brushes were replaced. The affected procedure was revised. All safety relief valve pilot cartridges were replaced or tested and recertified. The individual involved in the erroneous procedure revision was counseled. <br /><br /> Failure of the main steam safety relief valves to meet Technical Specifications setpoint tolerance requirements will be addressed in LER 260/96008.
260 | 2601997001 | 1997-04-24 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Browns Ferry 2 | B | GE | PO | 100 | On April 24, 1997, at 1814 Central Daylight Time (CDT), Unit 2 scrammed from full power due to a turbine trip caused by a high reactor water level trip signal. The main turbine and all three reactor feedwater pump turbines tripped when a high reactor water level trip signal was generated during the performance of 2-SI-4.2.B-ATU(C), Core and Containment Cooling Systems Analog Trip Unit Functional Test. The initiating high water level signal was caused by personnel error when a volt-ohm meter being used in the test was inadvertently connected across terminals of a companion Channel A relay instead of the intended Channel C relay. When Channel C was tripped per the test instruction with the meter connected to Channel A, the two out of two trip logic for high water level was completed. The Main Steam Isolation Valves (MSIV) subsequently closed from an unexpected high steam flow signal associated with the transient. The closure of the MSIVs in this event was an unexpected response to a turbine trip transient. The most probable cause of the high steam flow signal was instrumentation response to a steam line pressure wave and process noise from Main steam relief valve (MSRV) operation. Reactor water level decreased to -45 inches as a result of the loss of feedwater and the reactor pressure increase from the MSIV closure. Water level was restored and maintained by manual initiation of the Reactor Core Isolation Cooling System and automatic initiation of the High Pressure Coolant Injection System. The MSRVs functioned to control reactor pressure. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv), as any event or condition that resulted in manual or automatic actuation of any engineered safety feature including the reactor protection system. Corrective actions included personnel corrective action. TVA will place supplemental labels on individual relays. In addition, TVA will issue a design change to increase the response time for the main steam line high flow isolation function.
260 | 2601997007 | 1997-10-28 | QR8 | Spurious Reactor Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 70 | On October 28, 1997, at 1509 Central Standard Time (CST), Unit 2 automatically scrammed from approximately 70 percent power while cycling #1 Turbine Control Valve after repair. The scram resulted from an actuation of scram channel B1 caused by a pressure perturbation in the electro-hydraulic control (EHC) system at the turbine control valves. The pressure perturbation was induced by opening #1 turbine control valve. A half scram was previously present in RPS A due to cycling #1 control valve. Subsequent testing showed that the seal-in contact for one of the contactors in scram channel B1 (5A-K14B) exhibited chattering when subjected to reduced voltage. The scram contactor was replaced. Other corrective actions include procedure revisions to mitigate the consequences of pressure perturbation experienced while testing control valves, the installation of orifices in the EHC lines on the turbine control valves, and conducting a failure analysis of the RIPS contactor that was replaced. TVA is reporting this event in accordance with 10 CFR 50.73(a)(2)(iv), as an event that resulted in automatic actuation of an engineered safety feature including the reactor protection system.
260 | 2601998003 | 1998-10-01 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On October 1, 1998, at 0047 CDT, Unit 2 received a full automatic scram from 1 00 percent reactor power. The scram was generated by a main turbine trip which was the result of high generator stator cooling water outlet temperature. The reactor scram caused reactor water level to go below the low level setpoint (level 3) which generated a redundant scram signal and initiated the Primary Containment Isolation System, as expected. The low reactor water level signal also initiated the Standby Gas Treatment and Control Room Emergency Ventilation Systems. All systems responded as expected and all control rods fully inserted. The root cause was failure of a normally open manual isolation valve which blocked the flow of stator cooling water through the associated heat exchangers. The failure resulted from the separation of the valve plug from the valve stem, which allowed the loose plug to be forced against the valve seat by system flow thus blocking the flow path to the heat exchangers. The failed valve was replaced. TVA will initiate preventative maintenance for periodic inspections of the normally open stator cooling water valves. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in an automatic actuation of an engineered safety feature, including the reactor protection system.
260 | 2601999003 | 1999-05-15 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On May 15, 1999, at 1456 CDT, Unit 2 received an automatic scram from 100 percent reactor power due to a turbine trip that occurred during routine turbine overspeed testing. The reactor scram caused reactor water level to go below the low level setpoint (level 3) which generated a redundant scram signal and initiated the Primary Containment Isolation System, as expected. The low reactor water level signal also initiated the Standby Gas Treatment and Control Room Emergency Ventilation Systems. All systems responded as expected and all control rods fully inserted. The cause was of the turbine trip was failure of the mechanical trip cylinder to latch when hydraulically reset. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in an automatic actuation of an engineered safety feature, including the reactor protection system. This report was initially submitted on June 14, 1999, as 50-260/1999001. The number has been corrected and this report is being re-submitted as 50-260/1999003.
260 | 2601999009 | 1999-09-15 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On September 15, 1999, at 1825 CDT, Unit 2 operators manually scrammed the reactor from 54 percent power due to an Electro-Hydraulic Control (EHC) [TG] leak that could not be isolated. The reactor had been at 100 percent power prior to the leak. As expected, the reactor scram caused reactor water level to go below the low level setpoint (level 3) which generated a redundant scram signal and initiated Primary Containment Isolation, Standby Gas Treatment, and Control Room Emergency Ventilation Systems. All systems responded as expected and all control rods fully inserted. The cause of the leak was failure of a stainless steel tubing connection that was installed for the power uprate modification package to measure pressure perturbations in the EHC system. The damaged tubing was removed and the connection plugged. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in a manual actuation of an engineered safety feature, including the reactor protection system.
260 | 2601999010 | 1999-09-17 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 30 | On September 17, 1999, at 1702 Central Daylight Time, during reactor startup operations at 30 percent power, a high water level in main steam moisture separator 2C2 caused a Unit 2 main turbine trip. This resulted in an automatic reactor scram on turbine stop valve closure. Safety systems responded as expected and all control rods fully inserted. The cause of the high level in the moisture separator was a failed high level controller for the 2C2 moisture separator drain reservoir. The 2C2 reservoir level transmitter and relays were replaced and tested satisfactorily. Unit 2 was restarted on September 18, 1999. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in an actuation of an engineered safety feature, including the reactor protection system.
260 | 2602001003 | 2001-07-25 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On July 25, 2001, at 1047 hours Central Daylight Time (CDT) Unit 2 received an automatic scram from 100 percent power due to a main turbine trip from a power-load unbalance that occurred during Combined Intermediate Valve (CIV) testing. Vendor (General Electric Global Services) developed software contained a numerical error that resulted in an inadvertent turbine trip. The reactor scam caused the water level to go below the low level setpoint (level 3) which generated an additional scram signal and initiated Primary Containment Isolation Signals. All systems responded as expected and all control rods fully inserted. The root cause of this event was a weakness in the process for procurement of non-safety related SSCs that potentially impact generation. TVA will review procedures controlling software requisition, and revise as necessary, the requirements for non-safety related software that potentially impacts generation. TVA is reporting this event in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in manual or automatic actuation of any systems listed in paragraph (a)(2)(iv)(B), (i.e., Reactor Protection System (RPS) including reactor scram or reactor trip).
260 | 2602002002 | 2002-07-27 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On July 27, 2002, a Unit 2 main generator trip, main turbine trip, and reactor scram occurred from 100% power. All expected system responses were received, including the automatic opening of four safety-relief valves. Actuation of primary containment isolation system groups 2, 3, 6, and 8 occurred due to the expected temporary lowering of reactor water level. This logic isolates shutdown cooling (if in service), isolates the reactor water cleanup system, isolates the normal reactor building ventilation, initiates the standby gas treatment and the control room emergency ventilation systems, and retracts traversing incore probes (if inserted). The normal heat rejection path for the reactor remained in service. Reactor water level was recovered to the normal operating range by the normal reactor water level control system. Neither the high pressure coolant injection nor reactor core isolation cooling systems were used during this event. The generator tripped due to a ground fault on a main bank transformer bushing, which occurred due to thermal degradation of the paper insulation of the bushing’s internal condenser. Corrective actions included replacement of all of the low-side bushings on the transformer and increased monitoring of generator neutral resistor voltage trends. All new bushings will be installed on Unit 2 and Unit 3 main bank transformers. TVA will re-evaluate the criteria used in determining bushing condenser replacement intervals, and the bushing maintenance practices will be revised accordingly.
260 | 2602008001 | 2002-10-04 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On October 4, 2008 at 2208 hours, Central Day Light Time (CDT) the Unit 2 reactor automatically scrammed following a turbine generator load reject signal. At approximately 2107 hours CDT, just prior to the reactor scram, operations noted the 500 kV Unit Station Service Transformer 2B tap changer operating excessively and the generator was experiencing field voltage, transfer voltage, and phase amperage swings. Operations decided to place the voltage regulator in the manual control mode in accordance with Operating Instruction, 2-OI-47, Turbine-Generator System. However, when Operations transferred the voltage regulator from the auto mode to the manual mode, Unit 2 received a turbine trip and subsequent automatic reactor scram. While placing the voltage regulator in the manual mode, contacts 7 and 8 on the Voltage Regulator Auto/Manual Transfer Relay (43A relay) failed to make-up; thus, causing the turbine to trip. The root cause of this event was a failure of the design change process. The process did not provide a prompt to consider relay contact wetting and signal threshold when selecting a relay for switching low energy control signals. The event was result of the installation of a relay in an application for which it was poorly suited. TVA replaced the 43A relay in main-generator voltage regulator circuit with a relay that is better suited for a low power application. TVA will revise the Technical Evaluation Considerations Checklist to address contact selection for relays installed in low energy circuits.
260 | 2602003003 | 2003-03-26 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 63 | On March 26, 2003, at 0018 hours, the 2A reactor recirculation pump tripped as a result of an invalid output ground fault indication in its variable frequency drive (VFD) . Operations entered into Technical Specification (TS) LCO 3.4.1 Action A. The reactor power was reduced to approximately 63 percent. At 0244 hours, the 2B reactor recirculation pump also tripped as a result of an invalid output ground fault indication in its VFD. Due to an inoperable Oscillation Power Range Monitor (OPRM) function, TS .3 .3 .1 .1-I was in effect at the time of the event . Abnormal Operating Instruction 2-AOI-68-1B implemented the conditions of TS 3.3.1.1-I, and required Operations personnel to manually scram the reactor when both reactor recirculation pumps tripped. The root cause of this event was spiking in the neutral voltage signals in the VFDs . The cause of the spiking has not been determined. Contributing factors were: lack of a pre-trip alarm, and knowledge about the VFD control function was not available to TVA Engineering personnel. Corrective actions include: (1) The ground fault trip function of the VFDs was changed to an alarm function, (2) Ground fault alarm setpoint was increased, (3) Investigation is ongoing to determine the cause of the voltage signal spiking, (4) Single point failure analysis design standard will be revised to address pre-trip alarms, and (5) Procedural guidance for post-modification testing (PMT) will be revised to address expectations of PMTs.
260 | 2602004001 | 2004-07-08 | QR8 | Spurious Reactor Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | While in steady state operation at 100% power, a Unit 2 main turbine trip/reactor scram occurred. All expected system responses were received, including the automatic opening of seven safety-relief valves. Electrical switching was in progress at the time of the scram, and during this switching activity the Unit 2 Unit Preferred System (UPS) 120 VAC Bus was inadvertently de-energized briefly. The reactor scram occurred at this time due to a turbine control valve fast closure/turbine trip condition. The loss of the UPS power would not by itself be expected to result in a turbine trip/reactor scram because of the fault-tolerant design of the main turbine electro-hydraulic control (EHC) system logic. However, it was determined that one of two main generator output current signal channels in the EHC logic had been automatically bypassed previously by the system software during a separate power supply transient on a different plant distribution bus. The subsequent temporary interruption of the UPS bus caused the loss of the second main generator output current signal channel, and the system logic indicated that a power-load unbalance (i.e., main generator load reject) condition existed. The event root cause was the procedure controlling the transfer of the UPS bus contained detail inadequate to prevent interaction between the alternate and normal supplies’ voltage control circuits. A contributing factor was an EHC system software configuration which gave the system an unrecognized single point scram vulnerability. Corrective actions include procedure revisions and improvement in the EHC logic alarm capability.
260 | 2602005007 | 2005-08-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | At 1708 hours Central Daylight Time (CDT) on August 5, 2005, the Unit 2 Reactor automatically scrammed on low reactor water level from 100 percent power following a sequential loss of Reactor Feed Pumps (RFP) 2C and 2B. RFP 2C was lost when the RFP turbine main steam flow control valve (FCV) control linkage failed. RFP 2A and RFP 2B increased flow in an attempt to maintain reactor feedwater level, however; RFP 2B tripped when the thrust bearing wear detector trip actuated. Loss of RFP 2C and RFP 2B resulted in low reactor water level, an automatic runback and trip of the Reactor Recirculation System pumps, and a reactor water level automatic scram. When the reactor water level reached the low low water level, the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems auto initiated recovering reactor water level.The cause of the event was a low reactor water level resulting from the sequential loss of RFP 2Cand RFP 2B. First, the control valve linkage for RFP 2C came disconnected from the low pressure steam admission FCV actuator. The FCV failed closed and RFP 2C stopped. Second, RFP 2B turbine thrust bearing wear detector actuated and tripped the pump turbine. The investigation into the root cause of the main steam control valve linkage failure of for RFP 2C was inadequate installation of a locking device. The investigation into the root cause for RFP 2B turbine trip is ongoing. Oil samples do not indicate any thrust bearing wear and a calibration check of the turbine thrust bearing wear detector indicated satisfactory operation.
260 | 2602007001 | 2007-01-11 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 10 | On January 11, 2007, at 0818 hours Central Standard Time the Unit 2 reactor automatically scrammed on a turbine generator load reject signal during the performance of Operating Instruction 2-OI-47, Main Generator Voltage Control Rheostat Test. Just prior to the reactor scram, with the main generator voltage regulator in the automatic mode, the operations personnel were in the process of performing a rheostat cleaning operation on the generator field voltage manual adjust rheostat (70P) by cycling the rheostat to its upper limit and back to zero. Following this step, per the OI the voltage regulator was placed in the manual mode. After a short time delay, Unit 2 received a turbine trip and subsequent automatic reactor scram. The turbine trip and reactor scram resulted from the failure of a relay in the main generator voltage regulator. During the performance of 2-OI-47, a contact on the regulator mode transfer relay (43A relay) in the auto/manual portion of the main generator voltage regulator control circuit failed. TVA replaced the 43A relay in the main generator voltage regulator circuit.
260 | 2602009001 | 2009-02-16 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On February 16, 2009, at 0513:47 hours Central Standard Time (CST), the Unit 2 reactor was manually scrammed and the turbine tripped in response to excessive stator cooling water temperature and initiation of the automatic turbine trip timer. At 0506 hours CST, operations received a stator cooling water abnormal alarm. Operations dispatched an auxiliary unit operator to the stator cooling water skid to investigate the alarm. At approximately 0512 hours CST, the idle stator cooling water pump was started. At 0513 hours, operations received alarms indicating the stator cooling water outlet temperature had exceeded the high temperature setpoint of 174 degrees F and the automatic turbine trip timer started. As required by Alarm Response Procedure, ARP-9-8A, Operations manually scrammed the reactor and tripped the turbine at 0513:47 hours CST. The root cause of this event was inadequate design of the stator cooling water system. In this event, the temperature controller and TCV-35-54 is a single point failure that led to the manual scram. The stator cooling water temperature control valve, TCV-35-54, is a proportioning valve that directs water flow through the stator cooling water heat exchangers. When the TCV is in the open position, flow bypasses the stator cooling water heat exchangers. In contrast, when the TCV is in the closed position, water flows through the stator cooling water heat exchangers. When the temperature controller failed, TCV-35-54 repositioned to the open position bypassing the heat exchangers. To prevent recurrence of this event, TVA's plans include design and install a temperature controlled solenoid that will vent the actuator air supply to TCV-35-54. Also, install a hand wheel to allow manual control of TCV-35-54.
260 | 2602009007 | 2009-09-29 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | At 2321 hours on September 29, 2009, with Unit 2 at 100 percent power, operators were in the process of removing reactor feedwater pump 2B from service for scheduled maintenance. At the time, condensate pump 2B and condensate booster pump 2C had been previously removed from service for maintenance. When feedwater pump 2B speed was lowered to where flow was below the minimum flow setpoint, the pump 2B minimum flow valve automatically opened. This action increased total condensate flow, which lowered feedwater and condensate booster pump suction pressures. Feedwater pump 2A and condensate booster pump 2A subsequently tripped on low pump suction pressure signals. Feedwater pump 2C automatically increased speed to maintain reactor vessel level and tripped on overspeed. Operators manually scrammed the reactor due to decreasing vessel water level. Decreasing vessel level also resulted in the auto-initiation of High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC). HPCI successfully started and in combination with feedwater pump 2B restored water level to normal. RCIC started, but failed to achieve sufficient speed to inject. A separate LER is being submitted on the RCIC malfunction. The event investigation determined that the operating instructions for removing a feedwater pump from service were inadequate for the operating configuration (with less than a full complement of condensate and condensate booster pumps in operation). The subject operating instructions have been revised to require that feedwater flow be below that needed for 85 percent power prior to removing a feedwater pump from service if a condensate/condensate booster pump is not in service. A new tool for assessing the risk of online activities was implemented. The risk review process for performing online feedwater/condensate system maintenance is also being reviewed.
260 | 2602010003 | 2010-06-09 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Browns Ferry 2 | B | GE | PO | 100 | On June 9, 2010, at approximately 0330 hours Central Daylight Time (CDT), outboard Main Steam Isolation Valve (MSIV) A closed while transferring the Reactor Protection System (RPS) 120 V-AC power from the normal to the alternate power supply in preparation for a planned activity. At approximately 0331 hours CDT Unit 2 received a Primary Containment Isolation Signal (PCIS) Group 1 isolation signal resulting in the closure of all of the MSIVs and automatic reactor scram. During the scram, all automatic functions occurred as expected. All control rods inserted. Operations personnel briefly entered Emergency Operating Instruction, 2-EOI-001, "Reactor Pressure Vessel Control," controlling both reactor vessel pressure and reactor vessel water level. At approximately 0335 hours CDT, Operations personnel reset the PCIS Group 1 Isolation Signal, and by approximately 0341 hours the reactor scram was reset. The root cause for the MSIV closure event is indeterminate. TVA's analysis identified two possible causes: 1) Debris from the control air system in the Direct Current (DC) solenoid plunger area or, 2) DC power system electrical circuitry issues. TVA plans to install a filter in the control air system upstream of the outboard MSIV control air header. TVA also plans to install transient monitoring equipment on the DC solenoid circuit and evaluate the results. If the results of the monitoring change the root cause and corrective actions, TVA will provide a revised report.
260 | 2592011001 | 2011-04-27 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Browns Ferry 2 | B | GE | PO | 75 | On April 27, 2011, severe weather in the Tennessee Valley Service Area caused grid instability and loss of all 500-kV offsite power sources that resulted in automatic scrams of all three units. All three units were in Mode 1 at the time of the event. All scram systems were actuated, all actuations were complete, and required systems started and functioned successfully with the exception of an indeterminate position indication for the Unit 3 B Inboard Main Steam Isolation Valve. All onsite safe shutdown equipment was available with the exception of the 3B Emergency Diesel Generator (EDG), which was inoperable and unavailable due to planned maintenance. After the event, only one 161-kV line remained available for offsite power - all (seven) 500-kV lines and one (of two) 161-kV line were lost. All three units immediately entered Mode 3 (Hot Shutdown) with their respective 4-kV busses supplied by the onsite EDGs. On April 27, 2011, at 1701 hours, a Notification of Unusual Event (NOUE) was declared due to the loss of normal and alternate supply voltage to all unit-specific 4-kV shutdown boards for greater than 15 minutes and at least two EDGs supplying power to unit-specific 4-kV shutdown boards. On May 2, 2011, at 2050 hours, the NOUE was terminated following restoration of qualified offsite power sources.
260 | 2602012006 | 2012-12-22 | QR8 | Spurious Reactor Trip | [45 empty] | Browns Ferry 2 | B | GE | PO | 100 | On December 22, 2012, at 1152 Central Standard Time (CST), the Browns Ferry Nuclear Plant (BFN), Unit 2, reactor automatically scrammed due to actuation of the Reactor Protection System (RPS) from loss of power to both RPS buses. At 1134 CST, the 4kV Shutdown Board D unexpectedly de-energized resulting in the loss of power to the RPS 2B bus. While attempting to re-energize the RPS 2B bus, the RPS 2A bus was inadvertently de-energized resulting in the BFN, Unit 2, automatic reactor scram. During this event the Reactor Core Isolation Cooling system and the High Pressure Coolant Injection system automatically initiated as designed to restore water level above the initiation set point. All affected safety systems responded as expected for the loss of the RPS buses.<br /><br /> The root cause was that Operations' standards for the use of Error Prevention Tools were not understood nor properly applied by Operations personnel during transient plant conditions.<br /><br /> Corrective actions to prevent recurrence are: to develop and deliver training to provide expected behaviors for leaders and craft that support their roles and responsibilities, to perform paired observations between management and direct reports, from the level of department directors to first line supervisors, in order to verify or establish that the standards possessed by the department leaders are adequate and shared uniformly among the group, and to revise the Training Program Description for License Operator Requalification to specify that Operations Management provide training on standards and expectations for the implementation of the requirements of procedure OPDP-1, Conduct of Operations.
260 | 2602019003 | 2019-10-01 | QR8 | Spurious Reactor Trip | [45 empty] | Browns Ferry 2 | B | GE | SU | 0 | On October 1, 2019, at approximately 0307 Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN) Unit 2 received a reactor scram signal from less than 1% power that originated from the Neutron Monitoring System. There were no complications associated with this scram. All required safety systems functioned as designed. The initiating condition was discovered to be a scram signal due to electrical noise induced when the pushbutton was depressed for driving Source Range Monitors (SRMs) C and D out concurrently. <br /><br /> On October 1, 2019, at approximately 0605 CDT, Operations personnel completed Event Notification 54302 to the NRC. <br /><br /> The root cause of this event was that BFN engineering and leadership demonstrated weaknesses in risk perception related to the failure to advocate for and implement a permanent solution to the long standing Intermediate Range Monitor (IRM) noise susceptibility issue. Specifically, the IRM system design is not robust enough to mitigate the effects of noise intrusion. Corrective actions which will reduce or mitigate the probability of recurrence are to implement a process to manage the risk of identified equipment vulnerabilities; to implement time constant modifications to BFN Units 1, 2, and 3 which will make the system more robust against noise spiking; and to revise the Bridging and Mitigation Strategy Development procedure to explicitly require review of OE during bridging or mitigation strategy development.
260 | 2592020001 | 2020-07-20 | QL7 | Degraded condenser vacuum | [45 empty] | Browns Ferry 2 | B | GE | PO | 66 | On July 20, 2020, at approximately 0955 Central Daylight Time (CDT), the Unit 1 control room received the traveling screen differential pressure high alarm. Assistant Unit Operators dispatched to the condenser circulating water (CCW) system forebay reported large masses of eel grass. The influx of eel grass resulted in fouling of the trash racks and traveling water screens for all three units which reduced the CCW flows during this event. <br /><br /> As a result of degrading condenser vacuum on Unit 2, operators manually scrammed the reactor at 1325 CDT. On July 21, 2020, as Unit 1 condenser vacuum continued to degrade to the turbine trip setpoint, the Unit 1 operators manually scrammed the reactor at 0435 CDT. <br /><br /> The root cause of the event is that existing permanently installed plant equipment at the BFN forebay was not adequate to mitigate the newly developed threat presented by large scale eel grass accumulation on Wheeler Lake. <br /><br /> The action plan for addressing the root cause of this event has been developed which consists of deciding which equipment upgrades will be the most effective based on studies of river flow and environmental conditions, funding these upgrades, issuing design packages, and implementing the final designs.
261 | 2611987020 | 1987-07-10 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Robinson 2 | P | WE | PO | 100 | On July 10, 1987, Unit 2 experienced a reactor trip from 100% power on Steam Generator "A" low level coincident with steam/feed flow mismatch due to Main Feedwater Regulating Valve "A" failing closed. On July 16, 1987, Unit 2 experienced a reactor trip from 72% power on Steam Generator "A" low level coincident with steam/feed flow mismatch due to Main Feedwater Regulating Valve "A" not controlling properly. Each trip was caused by the same valve but for two separate and apparently unrelated reasons. The July 10 valve failure was due to an electrical short in a 125 volt DC wire to one of two safeguards solenoids for the valve operator caused by water of undetermined origin entrapped in the solenoid's condulet since some prior time. The July 16 valve problem was caused by impaired operation of the valve positioner. <br /><br />The discrepant conditions were corrected and the other two Main Feedwater Regulating Valves were also examined, with no discrepant conditions noted. In addition, the I/P converter and the positioner for the "A" Main Feedwater Regulating Valve were replaced. <br /><br />Following each event, the reactor was returned to critical and the Unit returned to power operation. Since the last event, the valve has been closely observed and has performed satisfactorily. Maintenance engineering has initiated a review to determine whether additional preventive measures should be established.
261 | 2611987020 | 1987-07-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Robinson 2 | P | WE | PO | 72 | On July 10, 1987, Unit 2 experienced a reactor trip from 100% power on Steam Generator "A" low level coincident with steam/feed flow mismatch due to Main Feedwater Regulating Valve "A" failing closed. On July 16, 1987, Unit 2 experienced a reactor trip from 72% power on Steam Generator "A" low level coincident with steam/feed flow mismatch due to Main Feedwater Regulating Valve "A" not controlling properly. Each trip was caused by the same valve but for two separate and apparently unrelated reasons. The July 10 valve failure was due to an electrical short in a 125 volt DC wire to one of two safeguards solenoids for the valve operator caused by water of undetermined origin entrapped in the solenoid's condulet since some prior time. The July 16 valve problem was caused by impaired operation of the valve positioner. <br /><br />The discrepant conditions were corrected and the other two Main Feedwater Regulating Valves were also examined, with no discrepant conditions noted. In addition, the I/P converter and the positioner for the "A" Main Feedwater Regulating Valve were replaced. <br /><br />Following each event, the reactor was returned to critical and the Unit returned to power operation. Since the last event, the valve has been closely observed and has performed satisfactorily. Maintenance engineering has initiated a review to determine whether additional preventive measures should be established.
261 | 2611987022 | 1987-08-10 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Robinson 2 | P | WE | PO | 8 | On August 10, 1987, at 2334 hours, with Unit No. 2 in startup at about eight percent (%) power, Intermediate Range Channel N-35 initiated a high flux reactor trip. The NRC was notified pursuant to 10CFR50.72(b)(2)(ii). <br /><br />Prior to the event, the reactor coolant average temperature (TAVC) was decreasing as the unit was synchronized, picking up an initial load of about thirty-five megawatts. A utility licensed operator began withdrawing rods to increase TAVC, and received a Rod Stop signal. Reactor power increased due to TAVC decrease, and a high flux reactor trip resulted. <br /><br /> Intermediate Range Detector N-35 had just been replaced, and the high flux trip setpoint had yet to be determined. The setpoint is based on detector current equivalent to 25% of full reactor power as determined by startup testing. The existing setpoint used was that of the old detector, but the new detectors response was significantly higher. Channel N-35 reached the current equivalent to the old detector setpoint before the automatic trip could be bypassed. This resulted in the reactor trip. <br /><br />Following the trip, N-35 was calibrated, and the Plant returned to power operation at approximately 0400 hours on August 11, 1987. <br /><br />Procedures will be revised to ensure that a new Intermediate Range Detector's high flux trip setpoint is bypassed during startup until the proper Intermediate Range setpoint is established.
261 | 2611987025 | 1987-09-28 | QR8 | Spurious Reactor Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | On September 28, 1987, Unit 2 was at 100 percent power when the reactor tripped at 1445 hours due to a cognitive personnel error. A Plant Maintenance Instrumentation & Control Technician performing a scheduled test of the Reactor Protection Logic Train "B" inadvertently tripped the Train "A" reactor trip breaker resulting in a one-out-of-two reactor trip logic. The NRC Senior Resident Inspector for the Plant was notified at 1510 hours. The utility-licensed Shift Foreman notified the NRC at 1618 via the Emergency Notification System pursuant to 10CFR50.72(b)(2)(i). The reactor automatically went to zero percent power and into a safe, stable hot shutdown condition. The trip was cleared, the surveillance test properly completed, and the reactor made critical at 2333 hours, returning on-line at 0047 hours, September 29, 1987. The licensee has disciplined the technician responsible and has reviewed the event to determine whether additional actions are necessary to preclude recurrence. There were no component failures during the event. There are no known prior events similar to this isolated incident. The event is reported pursuant to 10CFR50.73.(a)(2)(i)(A).
261 | 2611988001 | 1988-01-19 | QR5 | Turbine Trip | [45 empty] | Robinson 2 | P | WE | PO | 66 | An automatic reactor trip occurred at 0216 hours, Tuesday, January 19, 1988. The trip was initiated by an automatic turbine trip on a two-out-of-three autostop oil pressure logic. The turbine was under surveillance testing at the time, with the reactor at 66 percent power. Normal operation over a period of years had apparently caused the seat of one of the two autostop oil pressure regulating valves to wear so that the valve was unable to hold pressure. When the trip test lever was returned to the reset position following the turbine overspeed trip test, the backpressure further aggravated the relief and sufficient pressure was lost to cause the turbine trip and, subsequently, the automatic reactor trip. Both regulating valves were replaced with valves of a known higher reliability in accordance with recommendations from the turbine vendor. The reactor and turbine were returned to power operation using standard startup and operating procedures. The licensee notified the NRC Emergency Operations Center via the Emergency Notification System pursuant to 10CFR50.72(b)(2)(ii) for a four-hour nonemergency event. This report is submitted pursuant to 10CFR50.73(a)(2)(iv).
261 | 2611988010 | 1988-05-02 | QR5 | Turbine Trip | [45 empty] | Robinson 2 | P | WE | PO | 60 | On Monday, May 2, 1988, the Plant was placed on line at 0852 hours following a forced outage for repair of a RTD bypass valve packing gland leak. At 1756 hours, with the reactor at 60% power the licensed Control Operator attempted to adjust load swings on the turbine using the Electro-Hydraulic (E-H) control panel. The E-H Controls System malfunctioned causing the four turbine governor valves to shut. At 1758 hours, the turbine tripped from a main generator lockout which resulted in a reactor trip from the reactor/turbine trip logic (i.e., turbine trip with reactor power greater than 10%). All systems responded normally and the reactor was brought to hot shutdown. The E-H malfunction was caused by an intermittent failure of a clock circuit and a loose connection in the governor valve position limiter circuitry. The defects in the E-H system have been repaired and the system has been fully tested by the manufacturer's technical representative using a simulator to ensure the repairs were effective. The licensee notified the NRC Emergency Operations Center via the Emergency Notification System pursuant to 10CFR50.72(b)(2)(ii) for a four-hour non-emergency event. This report is submitted pursuant to 10CFR50.73 (a)(2)(iv).
261 | 2611988011 | 1988-05-12 | QR5 | Turbine Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | On May 12, 1988, at 1129 hours, with the reactor at 60 percent power, the Plant experienced an automatic turbine trip/reactor trip while surveillance testing of the Turbine Redundant Overspeed Trip System (TROTS) was in progress. The turbine trip was caused by a 2 out of 3 TROTS logic. Maintenance had placed one TROTS channel in test when a second channel spuriously actuated due to degraded insulation on its speed probe. The insulation has been repaired and the speed probe replaced. The NRC was notified of the trip pursuant to 10CFR50.72(b)(2)(ii). Subsequently, the licensee found that the periodic TROTS functional test and calibration procedures required by Technical Specifications, Table 4.1-1, Item 28 have omitted the TROTS solenoid valves on the turbine stop and control valves. These solenoid valves were functionally tested on May 14, 1988 and will be tested on a monthly basis. Complete elimination of the TROTS is under evaluation. The reactor was returned to power operation at 0144 hours, May 15, 1988. This LER was originally submitted pursuant to 10CFR50.73(a)(2)(iv).
261 | 2611989004 | 1989-02-27 | QR5 | Turbine Trip | [45 empty] | Robinson 2 | P | WE | PO | 30 | On February 27, 1989, at 1617 hours, Unit 2 received a Safety Injection signal and, subsequently, an automatic reactor trip from 30 percent power when the turbine experienced a momentary loss of load. At the time, Maintenance personnel were investigating a power supply trouble alarm in the turbine control system when a technician inadvertently caused a short circuit, causing the governor valves to close. The steam dump system responded. When the electrical short was corrected, the governor valves reopened, resulting in high steam flow, but the steam dump valves had not modulated closed and a Safety Injection signal was initiated on high steam flow with low steam line pressure/low average reactor coolant temperature. The technician who caused the short found that the multimeter being used was wrongly configured to measure amperage versus voltage. This had apparently created the short in the turbine DC power supply. The licensee declared an Unusual Event at 1618 hours, then terminated the Event at 1651 hours, and Unit 2 was returned to power operations on February 28, 1989. The cause of the event has been attributed to inattentiveness by the maintenance technician to the configuration of the multimeter. Plant safety was maintained throughout the event. The problem of improper steam dump valve modulation was the result of the saturation of the steam dump signal summator. This summator was replaced and tested with satisfactory results. Parts have been ordered and will be installed which will upgrade the circuit by reducing the susceptibility to failure by saturation. This should preclude the occurrence of future problems related to saturation of this signal summator. This Licensee Event Report is submitted in accordance with 10CFR50.73(a)(2)(iv).
261 | 2611989005 | 1989-03-22 | QL5 | Partial Closure of MSIVs | [45 empty] | Robinson 2 | P | WE | PO | 100 | On March 22, 1989, with Unit No. 2 operating at one hundred percent (%) power, a reactor trip occurred due to the inadvertent closure of a Main Steam Isolation Valve (MSIV), which isolated flow from "A" Steam Generator. All plant systems performed as designed throughout the event, and the plant was stabilized using emergency operating procedures. The NRC Operations Center was notified of the event in accordance with 10CFR50.72 at 0256 hours via the ENS. The event is attributed to personnel error on the part of the licensed Control Operator who manipulated the incorrect switch during the performance of a surveillance test. The Control Operator has been disciplined for inattention to detail. Additionally, the human factors aspects associated with the event are being reviewed. This LER is submitted pursuant to 10CFR50.73(a)(2)(iv).
261 | 2611989006 | 1989-03-30 | QR5 | Turbine Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | On March 30, 1989, at 0320 hours, the unit experienced a reactor trip from 100% power. The reactor trip signal was initiated by a turbine trip, which resulted from the loss of both the main and backup +15 volt turbine electro-hydraulic (E-H) control power supplies. Loss of both the main and backup power supplies initiates an automatic turbine trip, which in turn will initiate a reactor trip when the unit is above 10% power. At 0400 hours, the licensee made notification to the NRC of the reactor trip pursuant to 10CFR50.72(b)(2)(ii) via the Emergency Notification System. Subsequent investigation and troubleshooting identified blown fuses in both the main and backup power supplies and five defective or suspect power supply regulating transistors. The power supply fuses and transistors were replaced. Also, adjustments were made to overvoltage protective circuitry settings. Subsequent post-maintenance testing showed all equipment to be operating properly. This Licensee Event Report is submitted pursuant to the requirements of 10CFR50.73(a)(2)(iv)
261 | 2611990002 | 1990-01-17 | QR8 | Spurious Reactor Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | On January 17, 1990, at 2026 hours, a Reactor Protection System (RPS) actuation occurred with the unit at 100% power. The reactor trip occurred during performance of a routine operations surveillance test on the power range nuclear instrumentation channels. The operator performing this test had inadvertently placed the bistables for two independent channels of the overtemperature differential temperature (OT, delta T) reactor trip feature into the tripped position, completing the required logic to initiate the RPS actuation. The primary cause of this event was identified as personnel error, with a possible contributing factor being the format of the test procedure. The operator has been counseled regarding procedure adherence and attention to detail. In addition, the Manager - Operations has communicated to operations personnel the importance of promptly identifying and correcting situations which might later result in a personnel error or injury. Also, a review will be performed to establish and document the aspects of human factors, procedure format, and work practices which may have contributed to the occurrence of this event. The NRC was notified of this event pursuant to 10CFR50.72(b)(2)(ii) at 2105 hours via the Emergency Notification System. This Licensee Event Report is submitted pursuant to 10CFR50.73(a)(2)(iv).
261 | 2611990007 | 1990-05-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Robinson 2 | P | WE | PO | 100 | On May 17, 1990, at 0606 hours, an automatic reactor trip was received from a steam flow-feedwater flow mismatch coincident with a low level in steam generator (SG) B. The cause of the event was an equipment failure in that the SG B feedwater regulating valve (FRV) malfunctioned in a manner which impeded flow to SG B. Disassembly and inspection revealed that a spring pin had sheared which allowed the valve plug to unthread from the valve stem. A possible contributing factor was a procedural deficiency in that the vendor recommended stem-to-plug torque requirement was not provided within the FRV corrective maintenance procedure. The stem and plug were torqued to the required value and a new stem and longer spring pin were installed. The FRVS for SGs A and C were also disassembled and inspected, with precautionary replacement of both spring pins, and replacement of the valve stem for the SG C FRV. A procedure revision has been made to incorporate the recommended torque value. This event was reported via the Emergency Notification System at 0717 hours pursuant to 10CFR50.72 (b)(2)(ii). This Licensee Event Report is submitted pursuant to 10CFR50.73 (a)(2)(iv).
261 | 2611991011 | 1991-08-30 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Robinson 2 | P | WE | PO | 100 | On August 30, 1991, at 0700 hours with Unit No. 2 operating at one hundred percent power, an automatic reactor trip was received from a "C" Steam Generator low level coincident with a steam flow/feed flow mismatch. The cause of this trip is attributed to failure of the "B" Condensate Pump shaft, which resulted in inadequate feedwater flow to the steam generators. The Plant was brought to shutdown conditions using Emergency Operating Procedures, and was stabilized at 0711 hours. The NRC was notified of this event via the ENS at 0830 hours pursuant to 10 CFR 50.72(b)(2)(ii). <br /><br /> Repairs to the "B" Condensate Pump will require use of a pump that has been previously in service, and is awaiting refurbishment. Until this pump can be placed back in service, the Plant will operate at approximately sixty five percent power, which can be achieved with adequate feedwater being supplied with only one condensate pump in operation. <br /><br /> This Licensee Event Report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv).
261 | 2611992017 | 1992-08-22 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Robinson 2 | P | WE | PO | 100 | On Saturday, August 22, 1992, H. B. Robinson Unit No. 2 was operating at one hundred percent power. At 1007 hours a loss of offsite power occurred due to a trip of the Startup Transformer. The loss of the Startup Transformer caused a loss of Emergency Bus E-2 and Instrument Bus 4, causing a turbine runback. At 1009 hours, a high level in "A" Steam Generator caused a turbine trip and a subsequent reactor trip. At 1010 hours the Auxiliary Transformer tried to transfer its load to the Startup Transformer as designed, and a loss of E-1 resulted. At 1012 hours the Emergency Operating Procedures network was entered and immediate actions were begun for response to the reactor trip. In accordance with the Emergency Plan, an Unusual Event was declared at 1025 hours due to loss of offsite power. The plant was stabilized and repairs were initiated on the startup Transformer. <br /><br /> The Startup Transformer trip vas caused by a short circuit in the sudden pressure fault protective relay sensing circuitry. During the event, the plant response performed as expected. There was no threat to public safety since both Emergency Diesel Generators started as required and provided power to the Emergency Busses. Repairs to the Startup Transformer were completed and normal power vas restored to the Emergency Busses at 0050 hours on Sunday, August 23, 1992. The Unusual Event was terminated at 0124 hours. <br /><br /> This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(C) and 10 CFR 50.73(a)(2)(iv).
261 | 2611994006 | 1994-04-03 | QR6 | Manual Reactor Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | On April 3, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit 2 was operating at 100% power. At 2214 hours, the reactor was manually tripped during a load reduction that had been initiated at 2211 hours due to an electro-hydraulic (E-H) oil leak. The leakage, which originated from the #1 turbine governor valve (GV-1), resulted in automatic trips of the B-H oil pumps due to the low oil level in the oil reservoir. Prior to the trips of the E-H oil pumps, a manual load reduction had been initiated due to the leak. Once the pumps tripped, the governor valves started closing, which resulted in a rapid unanticipated load reduction. A manual reactor trip was initiated when the operators determined that an automatic reactor trip was imminent. The Unit was subsequently stabilized at hot shutdown. The leak was caused by a failed O-ring in the blank flange of GV-1 which had been installed during refueling outage 15 (RFO #15). An event evaluation determined the primary root cause of the O-ring failure to be incorrect installation of its associated blank flange. <br /><br /> This event is reported pursuant to 10 CFR 50.73(a)(2)(iv) as a condition that required a manual reactor trip.
261 | 2611994016 | 1994-08-02 | QR6 | Manual Reactor Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | On August 2, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100% power. At 0541 hours, control room operators initiated a manual reactor trip in anticipation of an imminent automatic reactor trip due to rapidly decreasing turbine generator load. During the transient, operators received indication that a pressurizer power operated relief valve (PORV) had not completely reclosed after operating to relieve the pressure transient, and at 0554 hours, an Unusual Event was declared due to this configuration. Following the reactor trip, the plant was placed in normal hot shutdown status, with one PORV block valve shut. The Unusual Event was terminated at 0717 hours following verification that there was no leakage through the block valve. Subsequent investigation revealed that the PORV had, in fact, closed as required.<br /><br /> This event was caused by component failure. A fuse failure occurred in a control circuit that monitors the generator output breaker position, and closes the main turbine governor valves if the generator output breakers open with the unit operating at full load. Following fuse replacement and system testing, the plant was returned to 100 percent power. This report is submitted pursuant to 10 CFR 50.73 (a)(2)(vi) since this condition resulted in a manual reactor trip.
261 | 2611995004 | 1995-06-30 | QL5 | Partial Closure of MSIVs | [45 empty] | Robinson 2 | P | WE | PO | 100 | On June 30, 1995, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100% power. At 1426 hours, a reactor trip occurred as the result of an inadvertent closure of 'B' Main Steam Isolation Valve (MSIV) MS-V1-3B. Upon closure of MS-V1-3B, the Reactor Protection System (RPS) reactor trip signal was received from Low - Low 'B' Steam Generator level. Following the reactor trip, Operations personnel placed the plant in hot shutdown condition in accordance with plant procedures. <br /><br /> This event was caused by component failure. Subsequent investigation found that the MSIV closure was caused by a loose fuse block fuse clip for the fuse that supplies control power to the MSIVs actuator 'open' air supply solenoid valve. The loss of power occurred while Operations personnel were reinstalling a fuse on a nearby circuit of the same fuse block on the same 125 VDC Auxiliary Panel for an unrelated piece of equipment. Following relocation of the two affected circuits that were identified and post maintenance testing, the plant was returned to 100 percent power. <br /><br /> This event is reported pursuant to 10 CFR 50.73(a)(2)(iv) as an RPS actuation.
261 | 2611996004 | 1996-09-07 | QR6 | Manual Reactor Trip | [45 empty] | Robinson 2 | P | WE | PO | 28 | On September 7, 1996, the H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 28 % power. Operations personnel were performing a scheduled shutdown of the plant to begin Refueling Outage (RO) 17. At 2241 hours Eastern Daylight Time (EDT), the High Pressure (HP) Turbine Electro-Hydraulic Control (EHC) System failed in both the automatic and the manual control modes. Because the EHC System failed, HP Turbine Governor Valve (GV)-1 would not close in response to manual or automatic control signals. After operations personnel determined that no immediate repairs could be made that would enable continuation of the plant shutdown, the Reactor Protection System (RPS) was manually initiated and the reactor was tripped at 2313 hours. All reactor control rods fully inserted into the reactor core and affected systems responded as designed, except that Main Feedwater Pump 'A' tripped on low feedwater flow. Following the manual actuation of the RPS, operations personnel placed the plant in a cold shutdown condition. The event was caused by a component failure. A broken wire was found in the EHC housing to valve GV-1. The broken wire was caused by wire fatigue induced by vibration. Also, broken bolts were found on the electro-hydraulic controller housing terminal block and evidence of wire fatigue was determined to be induced from de-termination and re-termination of wires during previous maintenance activities. The broken wire in the governor valve electro-hydraulic controller was repaired, and the electro-hydraulic controller housings of all governor valves are being repaired to eliminate loose and broken bolts, and to eliminate sources of wire fatigue at the terminal blocks. <br /><br /> This event is reported pursuant to 10 CFR 50.73(a)(2)(iv) as a manual actuation of the RPS.
261 | 2611996007 | 1996-10-20 | QP5 | Excessive Feedwater Flow | [45 empty] | Robinson 2 | P | WE | PO | 20 | On October 20, 1996, H.B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was in power ascension following startup from Refueling Outage 17, and was operating at 20 percent reactor power. An automatic reactor trip occurred at 1337 hours following a rapid increase in demand for the 'B' Steam Generator (SG) level and feedwater flow, and a subsequent SG overfeed condition. Plant systems functioned as expected, and plant operators stabilized the reactor at zero percent power and hot shutdown conditions using Emergency Operating Procedures (EOPs). Although the root cause of this event could not be conclusively determined, based on industry data and the maintenance history for the 'B' SG Feedwater Regulating Valve (FRV) manual/automatic control station, equipment aging is the most likely cause of this event. Although the failure of the 'B' SG FRV manual/automatic control station resulted in an automatic actuation of the Reactor Protection System (RPS) and a plant transient, this event has minimal safety significance. The 'B' SG FRV manual/automatic control station was replaced on October 21, 1996, and the plant was placed back on line. Licensed Operators will review this event by December 31, 1996, during Cycle 6 of the Licensed Operator Training program. CFR 50.73(a)(2)(iv).
261 | 2611997011 | 1997-11-16 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Robinson 2 | P | WE | PO | 100 | On November 16, 1997, at 0133 hours, with H. B. Robinson Steam Electric Plant, Unit No. 2 at one hundred percent (100%) power, an automatic actuation of the Reactor Protection System (RPS) occurred causing an automatic reactor trip. The RPS actuation resulted from "C" Steam Generator (SG) low level coincident with feedwater flow less than steam flow. The cause of the reactor trip was reduced feedwater flow to the SG following the failure of the "B" condensate pump stub shaft. The unit was stabilized in MODE 3 using the Emergency Operating Procedures. The NRC Operations Center was notified of this event at 0353 hours on November 16, 1997, in accordance with 10 CFR 50.72(b)(2)(ii). Plant equipment operated as designed with the exception of the intermediate range neutron monitoring system, channel N-35, which prevented the source range neutron monitoring channels from automatically reenergizing and providing indication. A previous similar event occurred in 1991 when the "B" condensate pump stub shaft failed causing a reactor trip that was reported in LER 91-11. An investigation into the event reported in this LER has determined that the cause of the shaft failure was similar to the 1991 event. The cause of this event has been determined to be failure to adequately complete the corrective actions from the 1991 event. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in an automatic actuation of the reactor protection system.
261 | 2611998003 | 1998-04-25 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Robinson 2 | P | WE | PO | 100 | On April 25, 1998, at approximately 1334, an automatic reactor trip resulted from an inadvertent closure of the turbine governor valves. Closure of these valves resulted in an increased steam generator (SG) pressure and subsequent shrink in level below the reactor trip setpoint. The Steam Dump Valves did not open in response to the decrease in first stage pressure and high reactor coolant temperature. The most probable cause of the governor valve closure was attributed to a pressure spike sensed in the impulse pressure control of the turbine control system. During the approximately 7 seconds between receipt of alarms, and reactor trip, the control board operator placed the reactor control rods in manual based on a diagnosis that the event was due to a failed turbine first stage pressure transmitter. The diagnosis of the event was incorrect. However, the action did not significantly affect the event. Subsequent to this event operation of the turbine control system was revised to reduce the vulnerability to turbine first stage pressure transients. In addition the impulse pressure transmitter was replaced, and additional instruments to monitor the turbine control system were temporarily installed. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in a manual or automatic actuation of an engineered safety system, including the reactor protection system.
261 | 2611998005 | 1998-10-17 | QP5 | Excessive Feedwater Flow | [45 empty] | Robinson 2 | P | WE | PO | 100 | On October 17, 1998, at approximately 0208 EDT, during surveillance testing of nuclear instrumentation, a control power fuse blew, causing a turbine runback. During the runback the steam dump valves did not open automatically. The operators selected an alternate control mode to open the steam dump valves. The "C" Steam Generator level increased to the high level trip setpoint causing a turbine trip. An automatic reactor trip resulted from the turbine trip. The investigation of the event identified that a degraded power supply caused the blown fuse that resulted in the turbine runback. The degraded power supply has been replaced. The steam dump system failure was the result of an incorrect bias potentiometer setting on the module that controls the steam dump valves. The bias potentiometer setting has been corrected and the module was re-calibrated. The high steam generator level was the result of the failure of a feedwater regulating valve to adequately control level. The feedwater regulating valve failure was the result of an incorrect gain potentiometer setting on the feedwater regulating valve controller. The gain potentiometer setting has been corrected and applicable calibration data sheets are being revised to include verification of potentiometer settings on selected control modules.
261 | 2612000001 | 2000-06-21 | QR6 | Manual Reactor Trip | [45 empty] | Robinson 2 | P | WE | PO | 68 | On June 21, 2000, at 0257 hours EDST, the H.B. Robinson Steam Electric Plant. Unit No.2 reactor was manually tripped from approximately 68%power. The manual reactor trip was initiated in response to leakage of main turbine system Electro-Hydraulic (EH) control system fluid. At 0210 hours an EH alarm for hi/lo-lo level occurred. Investigation of the alarm revealed an EH oil leak on non-isolable supply tubing to the hydraulic actuator for the Moisture Separator Reheater 2A Reheat Intercept Valve. Investigation of the leak revealed a circumferentially oriented crack in the EH fluid tubing. The tubing failure was caused by corrosion fatigue initiated at a defect on the outer diameter surface of the tube. The failed section of tubing was repaired. Planned corrective actions to prevent recurrence of this type of EH control system tubing failure include weather protection for selected exposed fittings, installation of flexible tubing where appropriate, and changing to a different fitting design on the 14 Main Steam and Main Turbine system valves operated by the EH system. There were no operator errors or procedural deficiencies that contributed to the event.
261 | 2612006001 | 2006-10-25 | QR5 | Turbine Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | At 0247 hours on October 25, 2006, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at 100% power, control room operators responded to alarms received for steam flow greater than feed flow on all three steam generators. Turbine first stage pressure indicated 0 psig. Three of the four turbine governor valves indicated closed, the fourth indicated an intermediate position. The control rods began automatically inserting, as expected. The net megawatt recorder indicated that electrical generation had rapidly reduced from 742 to 0 megawatts. The control room operators diagnosed the event as a 100% load rejection and initiated a manual reactor trip at 0248 hours, 68.8 seconds following the start of the event. The root cause of this event was failure of a turbine governor valve electro-hydraulic control system card. A pressurizer power operated relief valve lifted and reseated during the event. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
261 | 2612007001 | 2007-05-15 | QR5 | Turbine Trip | [45 empty] | Robinson 2 | P | WE | PO | 84 | At 1116 hours EDT on May 15, 2007, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at approximately 84% power, a generator lockout signal tripped the main turbine-generator [TG:TA,TB], which resulted in a reactor trip. The generator lockout signal was caused by an electrical fault in the circuitry for the "C" phase main transformer [XFMR:EL] alarm panel. The root cause of this event was the failure to crimp and inspect the tightness of the lug connecting the current transformer (CT) to the transformer alarm panel, which allowed the wire to disconnect and cause an AC electrical voltage from the "C" main transformer neutral bushing CT to be superimposed on the Train "A" DC system. The Train "A" motor-driven auxiliary feedwater (MDAFW) pump [P:BA] failed to start automatically, but it was started manually within about one minute after the reactor trip by an operator. The cause of the Train "A" MDAFW pump failure was subsequently determined to be a failure of the control switch [HS:BA], which prevented the automatic start signal. The equipment was repaired and the unit was placed back on-line at about 1211 hours on May 17, 2007. Planned corrective actions include procedure changes to verify proper connections in the main transformer equipment during work on that equipment and replacement of the Train "B" MDAFW pump control switch during the next refueling outage. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
261 | 2612008002 | 2008-11-17 | QR6 | Manual Reactor Trip | [45 empty] | Robinson 2 | P | WE | PO | 78 | At 0551 hours EST on November 17, 2008, the H. B. Robinson Steam Electric Plant, Unit No. 2, reactor was manually tripped from approximately 78% power due to high vibrations detected on the main turbine. At 0516 hours EST, the No. 9 bearing vibration was about 13.5 mils and increasing. A power reduction from 100% power was commenced in accordance with Abnormal Operating Procedure, AOP-006. At approximately 0551 hours, with power level at approximately 78%, the No. 9 bearing vibrations reached the AOP-006 trip criterion of 14 mils and the reactor was manually tripped. The auxiliary feedwater system started automatically, as expected, in response to steam generator level changes after the reactor trip. The primary system and steam generator power operated relief valves and safety valves did not actuate during this event. The main feedwater system, main steam system, and condenser remained available during the event and were used for decay heat removal. The root cause investigation for the turbine vibrations determined that the most probable causes were: 1) The size and placement techniques for the shims installed under the exciter base were incorrect, 2) procedure, CM-024, "Exciter Maintenance and Inspection," utilized standard shim placement, which for the new exciter was not adequate, 3) incorrect clearances of the refurbished generator hydrogen seal resulted in a rub condition, and 4) a vendor fabrication error in the exciter gusset plate configuration could have resulted in a soft foot condition. This report is being made in accordance with 10 CFR 50.73(a)(2) (iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
261 | 2612009003 | 2009-11-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Robinson 2 | P | WE | PO | 100 | At 2203 hours EST on November 6, 2009, with H. B. Robinson Steam Electric Plant, Unit No. 2, operating at approximately 100% power, control room operators responded to alarms received for steam flow greater than feed flow and level deviation on 'A' Steam Generator. Feed Regulating Valve, FCV-478, for 'A' Steam Generator indicated closed with controller demand of 0 percent. Control room operators attempted to manually open FCV-478. During this time, an increase in feed flow was noted. The 'A' Steam Generator level continued to lower to approximately 35 percent. The reactor was manually tripped at 2203 as the trip setpoint was approaching. The event was caused by a premature failure of the flow error signal summator power supply for the 'A' Feed Regulating Valve Control Loop FC-478E. The summator power supply has been replaced and the loop was calibrated successfully. The condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
261 | 2612010002 | 2010-03-28 | QR2 | Loss of Primary Flow (RPS Trip) PWR |  |  |  |  | X |  |  | X | [15 empty] | X | [9 empty] | X | [11 empty] | Robinson 2 | P | WE | PO | 99 | At 18:52 EDT on March 28, 2010, with the H. B. Robinson Steam Electric Plant, Unit No. 2, operating in Mode 1 at approximately 99.5% power, a feeder cable failure to 4kV non-vital Bus 5 caused an arc flash and fire. Four kV Bus 5 failed to isolate from non-vital 4kV Bus 4 due to a failure of circuit breaker 52/24 to open, which resulted in reduced power to 'B' Reactor Coolant Pump (RCP) and a subsequent reactor trip on Reactor Coolant System (RCS) loop low flow. Subsequent to the reactor trip, an automatic safety injection occurred due to RCS cooldown. Plant response was complicated by equipment malfunctions and failure of the operating crew to diagnose plant conditions and properly control the plant. During plant restoration a relay was reset, which re-initiated the electrical fault and caused a second fire. The root cause of the event was failure of circuit breaker 52/24 to open due to incorrect evaluation of trip circuit indication. Lack of monitoring of key plant parameters by the operating crew is an additional root cause that contributed to the event. The event described in this Licensee Event Report is reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
261 | 2612010007 | 2010-09-09 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Robinson 2 | P | WE | PO | 100 | At 1437 hours EDT on September 9, 2010, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at approximately 100% power, an automatic reactor trip occurred. The reactor trip signal was based on the Overtemperature DeltaT (OTDeltaT) reactor protection function. Due to the plant transient condition, the three steam generator Power Operated Relief Valves (PORVs) opened and one pressurizer PORV cycled momentarily. This event is being investigated using the HBRSEP, Unit No. 2, Corrective Action Program (CAP) and is being documented in Nuclear Condition Report (NCR) 420936. During investigation of the cause of the transient, a degraded connection on a circuit board (1A08H2) in the electro-hydraulic (EH) control cabinet was found. It has been concluded that this condition caused the loss of the governor valve common signal to the four turbine governor valves. Closure of the governor valves caused pressure and temperature in the Reactor Coolant System (RCS) to change. This resulted in the opening of a pressurizer PORV and the OTDeltaT reactor protection function initiating a reactor trip. The completed corrective action was replacement of the circuit board (1A08H2) found with the degraded connection. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
261 | 2612010009 | 2010-10-07 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Robinson 2 | P | WE | PO | 100 | At 0013 hours EDT on October 7, 2010, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at 100% power, an automatic reactor trip occurred. A motor fault on Reactor Coolant Pump (RCP) 'C' resulted in the Single Loop Low Flow reactor protection function and a subsequent reactor trip. The root cause for the reactor trip was determined to be inadequate end winding bracing of RCP 'C' motor. The failed RCP was replaced with the motor that had been recently removed from 'A' RCP. The removed motor will be rewound using an improved design, followed by the current motor. At approximately 0405 hours EDT on October 7, 2010, the Auxiliary Feedwater (AFW) system actuated due to a trip of Main Feedwater (MFW) Pump 'A' while attempting to start the pump. At approximately 1315 hours EDT on October 7, 2010, the operating crew recognized that action taken at about 1018 hours to place the feedwater isolation key switches in the Override/Reset position in order to start MFW Pump 'A' resulted in the inadvertent disabling of the feedwater isolation function and entry into Technical Specifications Limiting Condition for Operation (LCO) 3.0.3. The root cause for the automatic AFW initiation signal and the inadvertent entry into LCO 3.0.3 was determined to be an inadequate procedure. The procedure was revised to include appropriate guidance for resetting the Feedwater Isolation signal. The conditions described in this Licensee Event Report are reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(iv)(A), and 10 CFR 50.73(a)(2)(v)(D).
261 | 2612011002 | 2011-09-26 | QR8 | Spurious Reactor Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | At 1145 hours EDT on September 26, 2011, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, while in Mode 1 at approximately 100% power, an automatic reactor trip occurred. At the time of the trip, the control room received a "One Loop Low Flow" alarm indicating that Reactor Coolant Pump (RCP) 'C' had shut down. The Reactor Protection System (RPS) tripped the reactor on an input that breaker 52/14, for RCP 'C,' had opened. Verification of plant conditions immediately following the event identified that RCP 'C' was still running and that breaker 52/14 was still closed. The false indication signal, from relay RCP-3-X(B) was the source of the RPS trip signal. This event has been investigated in accordance with the HBRSEP, Unit No. 2, Corrective Action Program (CAP) and is documented in Nuclear Condition Report (NCR) 490203. The investigation concluded that the reactor trip was due to a defective coil lead wire, as supplied by the vendor, on the RCP-3-X(B) relay. Relay RCP-3-X(B) was replaced and post maintenance testing was performed. Relays at risk for a similar failure were also replaced. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
261 | 2612012004 | 2012-03-28 | QP5 | Excessive Feedwater Flow | [45 empty] | Robinson 2 | P | WE | PO | 55 | At 1503 hours EDT on March 28, 2012, with the unit in Mode 1 at 55% power, the H.B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP, Unit No. 2) reactor tripped due to a turbine trip caused by a Feedwater Isolation signal from Steam Generator (SG) 'B' High Level. The Feedwater Regulating Valve FCV-488 had gone 100% percent open causing a Feed Flow greater than Steam Flow alarm and the SG 'B' level to increase rapidly. The operators placed the valve in manual control and attempted to close the valve; however, the feedwater flow could not be brought under control before the SG 'B' high level set point on 2 of the 3 level protection loops initiated a Feedwater Isolation, turbine trip and corresponding reactor trip. The site failed to recognize the need for periodic replacement of low wattage control switches based on the guidance in the Control Switch Preventive Maintenance Basis Template, and the apparent lack of site Operating Experience (OE) indicating the need for preventive replacement. This resulted in no preventive maintenance on the failed switch over an extended period. The most likely cause was determined to be high resistance readings on the contacts that caused the feedwater flow signal to reduce to zero. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any system listed in paragraph (a)(2)(iv)(B); the Reactor Protection System and Auxiliary Feedwater system.
261 | 2612013003 | 2013-11-05 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Robinson 2 | P | WE | PO | 19 | At 1801 hours EST on 11/5/2013, with the Unit in Mode 1 at 19% power, H. B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP2) experienced an automatic reactor trip while operators were transferring loads from the Startup Transformer to the Unit Auxiliary Transformer (UAT), as part of activities associated with coming on line and increasing power following Refueling Outage 28. During the coordinated breaker operation, the reactor tripped when an anomaly occurred that resulted in the actuation of two undervoltage relays associated with the loss of 2 of 3 4KV buses. The 'A' Emergency Diesel Generator (EDG) auto-started and supplied the E-1 emergency bus as a result of the undervoltage transient. The event was reported as a 4 hour Non-Emergency report per 10 CFR 50.72 (b)(2)(iv)(B) due to the valid Reactor Protection System Actuation, and as an 8 hour Non-Emergency report per 10 CFR 50.72(b)(3)(iv)(A) due to the valid actuation of Auxiliary Feed Water and EDG auto-start and subsequent starting of required undervoltage loads, save `A' Service Water Pump.<br /><br /> The investigation into the cause of this event determined that advanced aging/fatigue of the phenolic operating rods of the UAT breaker (52/7) caused the failure of the 'B' phase operating rod, which prevented closure of the 'B' phase of the breaker. The cause of the failure of the 'A' Service Water Pump to sequence onto the E-1 bus during the blackout sequence was attributed to a loose wire termination in the Emergency Control Station (ECS). Immediate corrective actions consisted of assessment of the switchyard and E-1 Bus, inspection of Breaker 52/7, and securing the loose wire termination in the ECS. This event did not impact the health and safety of the public.
261 | 2612014001 | 2014-01-09 | QR5 | Turbine Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | At 2234 hours EST on 1/9/2014, with the Unit in Mode 1 at 100% power, H. B. Robinson Steam Electric Plant, Unit 2 experienced an automatic reactor trip/turbine trip during the performance of Steam Generator (SG) Water Level Protection Channel testing. The 'B' reactor trip breaker opened as a result of its 2/3 SG Lo-Lo Level input logic being satisfied. This occurred when one channel contact was "open" due to foreign material lodged between the contact faces and the second channel contact was opened during channel testing. The opening of the 'B' reactor trip breaker resulted in a turbine trip followed by a reactor trip. Auxiliary Feedwater automatically started as expected. There were no other equipment performance issues.<br /><br /> The cause of this event was degradation of passive components (wire labels) in the Reactor Protection System (RPS) relay rack. Degraded wire labels were the source of the foreign material which became lodged in an RPS relay contact creating an undetected halftrip condition.<br /><br /> The foreign material was removed from the RPS relay contact. Both trains of RPS were tested to verify proper functioning of each RPS relay, and both trains of RPS relay racks were inspected to confirm no foreign material was present which could affect proper operation of the RPS relays.
261 | 2612016004 | 2016-08-24 | QR5 | Turbine Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | At 1338 hours EDT On 08/24/2016, with the Unit in Mode 1 at 100 percent power, H. B. Robinson Steam Electric Plant, Unit 2 (RNP), experienced an automatic turbine trip followed by an automatic reactor trip during the performance of a visual inspection of the Main Turbine Trip Block. Following the reactor trip, the Auxiliary Feedwater System actuated as expected on low steam generator level. There were no other equipment performance issues.<br /><br /> The cause of this event is attributed to the absence of a standard that would govern risk assessment and control of work activities around trip sensitive equipment. The perceived low significance nature of the risk in conjunction with the evolution comprising only a visual inspection and the procedural silence with respect to data gathering activities in the proximity of trip sensitive equipment, taken together gave rise to the unintended turbine trip, and a subsequent reactor trip. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) due to the event resulting in an automatic actuation of the Reactor Protection System (RPS) and Auxiliary Feedwater System (AFW).
261 | 2612016005 | 2016-10-08 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Robinson 2 | P | WE | PO | 100 | At 1302 hours Eastern Daylight Time (EDT) on 10/08/2016 with the plant in Mode 1 at 100 percent power, H. B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP2), experienced a grid perturbation. As a result, HBRSEP2 experienced a reactor trip due to low voltage on the 4kV buses. Plant safety systems responded with the emergency buses separating from offsite power due to emergency bus undervoltage. The emergency diesel generators (EDG) started and powered the 480V emergency buses. 'A' service water pump did not start on the blackout sequencer; however, sufficient service water flow was available from the three operating service water pumps. This failure did not aggravate this event. The site declared an Unusual Event (UE) at 1317 EDT for loss of power to emergency buses. At 0011 EDT on 10/09/16, the UE was terminated. <br /><br /> Once the power grid was stable, plant personnel commenced restoration of offsite power to allow shutdown of the EDGs. During this evolution, at approximately 2323 EDT on 10/08/2016, an automatic actuation of the 'B' auxiliary feedwater (AFW) pump occurred due to improper breaker coordination that satisfied the autostart logic for the AFW system. <br /><br /> The apparent cause of the voltage transient in the HBRSEP2 switchyard is a failed fault detection relay, which prevented the grid fault from being immediately isolated. The failed relay has been replaced.
261 | 2612019001 | 2019-08-11 | QR5 | Turbine Trip | [45 empty] | Robinson 2 | P | WE | PO | 100 | At 0840 hours Eastern Daylight Time (EDT) on 08/11/2019 with the plant in Mode 1 at 100 percent power, H. B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP2), experienced an electrical fault within the main generator exciter. The exciter field breaker tripped due to a loss of generator field excitation, causing a main generator lockout. As a result, HBRSEP2 experienced an automatic turbine trip and subsequent reactor trip. Plant safety systems operated as designed. Auxiliary Feedwater Pumps started as expected. The plant was stabilized in Mode 3 and subsequently cooled to Mode 4. <br /><br /> The exciter was removed and shipped from HBRSEP2 to a vendor where it was disassembled, tested and inspected. This inspection identified extensive exciter damage. Due to the extensive damage, the precise failure cause is indeterminate. <br /><br /> Actions taken to correct the condition were to reinstall a refurbished exciter. HBRSEP2 returned to power operation on 09/03/2019. There was no impact to the health and safety of the public as a result of this event.
263 | 2631987004 | 1987-01-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Monticello | B | GE | PO | 100 | The event was initiated by a trip of the #11 reactor feedwater pump (RFP) (P-2A) due to a low oil pressure trip switch (PS-1735) actuation by a painter who was working in the area. Power was reduced and the tripped RFP returned to service. Vessel level increased rapidly to the high water level setpoint, tripping both RFPs and the main turbine giving a load reject scram. Vessel level then dropped to the low level setpoint, causing a reactor building isolation, a group II and a group III primary containment isolation and an automatic start of the standby gas treatment system. Reactor vessel level was recovered by manually initiating HPCI and restoring the feedwater system to normal. Plant conditions were stabilized using normal scram recovery procedures. <br /><br /> The #11 RFP oil pressure switch gauge glass was found loose. The housing cover plate was replaced and the trip setpoint of the switch verified correct. The procedure for recovery from loss of one RFP was revised to give better guidance on the immediate actions to be taken. A procedure was prepared for painting activities. Feedwater level control was verified to be operating properly.
263 | 2631987006 | 1987-02-16 | QC4 | Loss of ac Instrumentation and Control Bus. | [13 empty] | X | [30 empty] | X | Monticello | B | GE | PO | 100 | Electrical disturbance on the division I uninterruptible power supply, UPS, initially caused lockup of feedwater regulating valves, and transfer of the division I UPS to its alternate source. Two minutes later a second electrical disturbance resulted in trip of the division I reactor protection system level instrumentation initiating a reactor scram, primary containment isolations, automatic initiation of the Standby Gas Treatment System and trip of both reactor recirculation pumps. Following reactor scram, reactor building vent Channel A wide range gas monitor, WRGM, failed. Reactor pressure was automatically controlled by the low-low set actuation of one safety relief valve. Plant conditions were stabilized using normal scram recovery procedures. <br /><br />A failed feedback control transformer and blown fuse were discovered on the division I UPS inverter and are thought to be the root cause of the event. A failed metal oxide varistor, processor unit and blown fuse were found in the Channel A WRGM following the event. <br /><br />The failed components were replaced and functional testing of all affected systems was satisfactorily performed. <br /><br />The power sources for the reactor water level instrumentation will be changed to prevent a reactor scram and primary containment isolations due to a loss of one UPS division.
263 | 2631987009 | 1987-04-03 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Monticello | B | GE | PO | 100 | While obtaining required data during pump testing in accordance with ASME B&PV Code, Section XI, jarring of the protective relays in the door of the 4KV Circuit Breaker for the #11 Condensate Pump caused the pump to trip. This resulted in a trip of both reactor feedwater pumps on low suction pressure and a plant scram on low water level. Secondary containment isolation and Standby Gas Treatment System initiation occurred. The low low level trip setpoint was reached which caused an Emergency Core Cooling System initiation, diesel generator start, primary containment isolation and a recirculation pump trip. The high pressure coolant injection and reactor core isolation cooling systems restored water level. Plant conditions were stabilized using normal scram recovery procedures. The root cause of the event was personnel error, when the test engineer failed to heed a warning statement on the door of the circuit breaker and jarred the protective relays for the breaker while closing the door of the breaker cubicle. There were no safety system equipment malfunctions associated with the event.
263 | 2631987014 | 1987-07-16 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Monticello | B | GE | PO | 100 | A substation transformer phase conductor broke free, caused a phase to phase fault and a plant undervoltage condition which resulted in tripping the reactor recirculation pumps, circulating water pumps, and a cooling tower pump. The undervoltage condition also caused a transfer to the emergency mode of the emergency filtration train, an Engineered Safety Feature (ESF) system. Condenser low vacuum, which resulted from the circulating water pump trips, initiated a reactor scram. The fault cleared automatically and plant bus voltages immediately returned to normal. Plant operators restarted the required pumps and stabilized plant conditions. The transformer bus/phase conductor connection was not designed with sufficient strength to withstand the loads imposed on this connection. To correct the deficiency, the transformer bus was redesigned to strengthen the connection point. A task force was established to investigate steps for avoiding similar plant trips.
263 | 2631988007 | 1988-12-16 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Monticello | B | GE | PO | 100 | A momentary false high level signal during calibration of a reactor protection system reactor level transmitter resulted in a feedwater pump and turbine trip that caused a reactor scram. Plant conditions were stabilized using normal scram recovery procedures. Cause of the event was degradation of the level transmitter pressurizing valve. The valve was replaced and additional guidance was provided to the instrument and control technicians to minimize the potential of recurrence in the event of a degraded valve.
263 | 2631989009 | 1989-06-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Monticello | B | GE | PO | 59 | During the shutdown of a Reactor Feed Pump (RFP), the discharge check valve, FW 67-2, failed to seat. This provided a recirculation path for the operating RFP and caused reactor water level to decrease to the SCRAM set point. Reactor water level was restored with the operating RFP and normal procedures were used to recover from the scram. <br /><br /> Excessive component wear which would allow the top of the valve disc to wedge under the lip of the seating surface is presumed to be the failure mode. If excessive clearances had been recognized during a 1987 inspection of FW 67-2, repairs could have prevented this event. The root cause of this event was inadequate acceptance criteria for valve inspection. <br /><br /> Check valve parts were replaced or rebuilt. Other similar valves were tested. <br /><br /> The RFP shut down procedure was changed to include closing the RFP discharge valve to help assure no back flow through the pump. Future actions include developing acceptance criteria for check valve inspections, minimizing operation at critical system flow rates, and investigating a check valve modification.
263 | 2631989038 | 1989-11-15 | QR8 | Spurious Reactor Trip | [45 empty] | Monticello | B | GE | PO | 100 | A reactor scram occurred from 100% power. Channel A of the reactor pressure system was tripped for routine surveillance. A spurious, momentary high reactor pressure signal tripped channel B of the reactor protection system. All testing verified the calibration and operability of the pressure switch. Computer event logs indicated a momentary trip signal with characteristics resembling a bump to the switch. Although no individual could be located who was aware of having bumped the switch, this remains the probable cause of this event. The switch was replaced in kind. Bench testing of the removed switch verified proper operation. This event will be added to general employee training to raise awareness of the consequences of bumping plant instruments. Technical Specification changes will be pursued to reduce the total time half scrams are required during maintenance and testing. The clarity and visibility of posted warnings to plant personnel in the area of these switches will be improved.
263 | 2631990017 | 1990-10-29 | QR8 | Spurious Reactor Trip | [45 empty] | Monticello | B | GE | PO | 100 | A reactor scram occurred from 100% power due to a spurious reactor high pressure signal which activated both channels of the reactor protection system high pressure scram logic. Subsequent investigation revealed that workers had been moving scaffolding in the immediate area of the A safeguards sensing line which is common to the activated switches. Follow-up testing demonstrated that a relatively small external impact on the sensing line at the work location creates a hydraulic shock in the sensing line sufficient to trip the pressure switches. The cause of this event was failure to recognize and identify the sensitivity of the sensing line to bumping. Work in the area of both A and B sensing lines was restricted by placing signs on the sensing line and installing physical barriers. Scaffolding and other equipment was removed from the sensing line areas prior to startup. Painting in the areas was postponed until the next scheduled refueling outage and painting and scaffolding procedures were revised to identify sensitive instrument lines.
263 | 2631991014 | 1991-06-05 | QR8 | Spurious Reactor Trip | [45 empty] | Monticello | B | GE | PO | 100 | A reactor scram occurred from 100% power due to a spurious Main Steam isolation signal occurring in the A channel while the B channel was tripped in accordance with an approved surveillance procedure which was in progress at the time. Normal post-scram recovery procedures were followed. Investigative efforts to determine the source of the signal did not identify the root cause. After the safety aspects of the occurrence were examined and found to be acceptable, the plant was restarted with data gathering instrumentation in place to give better resolution in the event of a recurrence. Plant Instrument and Control personnel were reminded that passive preparation work should never go beyond the channel that is currently tripped. A Technical Specification revision is being pursued which will minimize the time channels are tripped during surveillance procedures. Improvements are being considered for the sensor relay inputs to the plant computer.
263 | 2631991019 | 1991-08-25 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Monticello | B | GE | PO | 100 | At 0609 hours on August 25, 1991 while operating at 100% power, an interruption in off-site power resulted in a reactor scram and actuated several Engineered Safety Feature systems. The cause of the event was a failed insulator on the 115KV line supplying the Station Reserve Transformer. The event occurred during a lightning storm and it is suspected that the insulator failure was caused by a lightning strike. The failed insulator caused a lock-out of the Station Reserve Transformer, resulting in an interruption of normal electrical power to all plant 4KV busses and a reactor scram. The essential busses were automatically reenergized from the Auxiliary Reserve Transformer in about 5 seconds as designed. All Engineered Safety Features operated as designed. Procedures were used to place the plant in a stable condition. The plant was restarted after all insulators on the affected 115KV tower were replaced, insulators on remaining 115KV towers were inspected, and protective relaying was functionally checked.
263 | 2631993006 | 1993-03-23 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Monticello | B | GE | PO | 10 | During startup from a refueling outage a Reactor Protection System trip from high reactor pressure occurred. The trip occurred while performing the main turbine Stop Valve tightness test. The cause of the event was an inadequate procedure. Contributing factors were inadequate knowledge by the individuals involved in the procedure revision, incorrect simulator modeling and an inadequate vender technical manual procedure. During the event one control rod scram solenoid failed to operate resulting in a slow rod insertion time. The Turbine Stop and Control Valve Tightness Test procedure has been revised. The plant simulator was modeled to reflect actual operation. The failed scram solenoid pilot valve was replaced and all scram solenoid pilot valves were verified to function properly. This event and the lessons learned from the event will be presented in Engineering Technical Staff Continuing Training and License Operator Requalification training. The vendor technical manual on pressure control will be revised.
263 | 2631993008 | 1993-07-31 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Monticello | B | GE | PO | 100 | During normal full power operation a Reactor Protection System trip from low reactor water level occurred. The Standby Gas Treatment System and several containment isolation groups were also initiated on low reactor level. Normal post trip procedures were followed to restore stable conditions. One condensate and one feedwater pump remained in operation during the event. Level remained well above the ECCS initiation setpoint. There were no failures or other complications. The immediate cause was a reduction in reactor feedwater flow due to a ground fault relay trip of a main condensate pump. motor stator. The motor will be rewound or scrapped.
263 | 2631994003 | 1994-04-15 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Monticello | B | GE | PO | 100 | A transmission system electrical fault on the 345 kV system (originating at a nearby generating plant) caused protective relaying to trip plant equipment. The tripping of the Circulating Water Pumps caused the loss of the condenser vacuum, which caused a reactor scram. The electrical fault caused a decrease in voltage to approximately 55% for 2 to 3 cycles. A modification will be initiated to reduce the likelihood of similar substation transients initiating a reactor scram.
263 | 2631994004 | 1994-06-04 | QL7 | Degraded condenser vacuum | [45 empty] | Monticello | B | GE | PO | 100 | An electrical storm caused the loss of the Offgas Recombiner system resulting in loss of condenser vacuum causing a reactor scram. A second storm caused a false upscale trip on the Fuel Pool Monitor causing a Containment Isolation. be made to make the affected instrumentation less sensitive to electrical storms.
263 | 2631996006 | 1996-06-09 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Monticello | B | GE | PO | 100 | The 'A' stator water cooling pump tripped and the 'B' stator water cooling pump automatically started as designed. Several hours later, the 'B' stator water cooling pump failed. This left no operable stator water cooling pumps and led to a turbine trip and subsequent reactor trip. <br /><br /> The root cause of the stator water cooling pump failures is believed to be caused by electrical discharge through the thrust bearing. The reactor was shut down by the automatic scram and operators properly responded maintaining the reactor in a safe condition at all times. <br /><br /> The pumps were rebuilt and the oilers were placed with a different type device. A grounding strap/brush was installed on both stator water cooling pumps.
263 | 2631996007 | 1996-06-15 | QR5 | Turbine Trip | [45 empty] | Monticello | B | GE | PO | 55 | While investigating a suspected faulty light bulb, an operator shorted the 120 VAC bulb lead to ground. This fault was not isolated locally but isolated by an upstream fuse which de-energized additional equipment, including a protective relay in the turbine runback circuitry. This initiated a turbine runback. Operators properly reduced power, but a turbine trip occurred, followed by a reactor scram. The local fuse did not isolate the fault due to a wiring error during installation. The wiring error was corrected.
263 | 2631996011 | 1996-11-12 | QR6 | Manual Reactor Trip | [45 empty] | Monticello | B | GE | PO | 100 | During a new surveillance procedure, a jumper was installed on the wrong relay. This caused the tripping of both reactor recirculation pumps. The operators inserted a manual reactor scram in accordance with abnormal operations procedures. The jumper was installed by a licensed operator and witnessed by the engineer who had written the test. The geometry of the relay location and inadequate labeling caused the wrong relay to be independently selected by the operator and the engineer. The surveillance procedure was revised to select a more accessible location for jumper installation. Labeling improvements will be made.
263 | 2631997013 | 1997-11-25 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Monticello | B | GE | PO | 100 | Control room operators received alarms from the tripping of two 480V load center breakers. Each breaker fed one division of the Offgas Recombiners and the Offgas Compressors plus associated equipment. Loss of the Condenser Offgas System, specifically the recombiners, caused condenser vacuum to decrease. Control Room operators decreased reactor power to reduce the rate of loss of condenser vacuum. Engineering and operations personnel determined that the breakers had tripped on short circuit. Since it would not be possible to re-energize the offgas recombiners, condenser vacuum would continue to decrease. Control room operators conservatively manually scrammed the reactor (inserting the control rods). A cross-divisional cable fault caused the two 480V load center breakers to trip. Temporary cables were installed primarily above ground. The temporary cables feeding the Offgas Storage Building will be replaced with permanent underground cables. An evaluation of the action necessary to ensure the proper functioning of existing plant underground cables will be conducted.
263 | 2631998004 | 1998-09-09 | L2 | Loss of Condenser Vacuum | [7 empty] | X |  |  | X | [22 empty] | X | [6 empty] | X |  |  |  |  | Monticello | B | GE | PO | 100 | A rapid recombination of hydrogen and oxygen in the Offgas System caused a pressure transient that closed the isolation valves between the main condenser and the air eject recombiners tripped at the same time. With no apparent offgas removal means, operations personnel reduced power and subsequently manually scrammed the reactor. The rapid recombination of hydrogen and oxygen was caused by a high temperature in an Offgas System valve. The high temperature was caused by valve seat leakage which self-ignited the hydrogen and oxygen. The burning of hydrogen and oxygen on the low pressure side of the valve caused a rise in the temperature of the valve body, which initiated the rapid recombination of hydrogen and oxygen on the high pressure side of the valve seat. The valve seat was replaced, as was the valve seat of the similar valve on the other train. Several operating procedures were changed; temporary instrumentation was added; and extensive testing was performed. Training will be provided on the importance of performing thorough investigations should symptoms of a potential problem be identified. During subsequent piping inspections, no damage was found from the pressure transient.
263 | 2631999004 | 1999-04-22 | QP2 | Partial Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Monticello | B | GE | PO | 100 | Failure of a digital feedwater control system (DFCS) power supply caused one feedwater regulating valve to close and the other to lock-up in its pre-existing condition. Attempts to manually control reactor water level failed due to the DFCS failure, resulting in an automatic reactor low water level scram. Subsequently, steam lines for the main steam system, High Pressure Coolant Injection system (HPCI) and Reactor Core Isolation Cooling system (RCIC) were overfilled, causing HPCI and RCIC to become inoperable for about 1/2 hour. Water level was restored to shutdown normal conditions approximately one hour later. The DFCS power supply failure was due to an oxidized connection in a plus 5 volt power supply. The overfill was caused by the failed level indications and misleading Safety Parameter Display System (SPDS) indications. Concern about using reactor water level indications led to bypassing the Reactor Feedwater Pump (RFP) high water level trip. Three power supplies were replaced and all associated connections cleaned. Several operating procedures were revised, temporary monitoring instrumentation was added and extensive testing was performed. Operator training was provided on several topics.
263 | 2631999005 | 1999-05-08 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [28 empty] | X | X |  |  |  |  | Monticello | B | GE | PO | 100 | A rapid recombination of hydrogen and oxygen in the Off-gas system caused a pressure transient that initiated an isolation of valves between the main condenser and the air ejectors. With no means of removing off-gas, operations personnel reduced power and manually scrammed the reactor. Following the reactor scram, low steam line pressure caused a Group 1 containment isolation which closed the main steam isolation valves. Three safety relief valve openings occurred while the main steam isolation valves were closed. The main steam isolation valves were reopened, and the plant was placed in cold shutdown. The rapid recombination of hydrogen and oxygen was caused by recombiner catalyst migration. The Group 1 containment isolation was caused by the reactor mode switch being in RUN when the steam line pressure decreased to the Group 1 low pressure set point. All safety systems performed as designed. Catalyst has been removed from the off-gas piping up to the recombiner. A time delay was added to the high pressure trip for the air ejector suction isolation valves. Training was provided to all licensed operators.
263 | 2632001011 | 2001-10-23 | QR8 | Spurious Reactor Trip | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Monticello | B | GE | PO | 98 | While in coastdown for refueling, at 1712 on October 23, 2001, a human performance error caused a reactor scram. The scram was a result of inadvertent contact of a support brace attached to a sensitive instrument rack by an individual performing work in the area. The primary cause of the event was determined to be inadequate work practices. Although the worker was aware of the sensitive nature of the instrumentation on the rack in the area in which he was working, the worker elected to transport heavy barrier stanchions through the narrow pathway immediately adjacent to a sensitive instrument rack. The worker lost his balance and bumped a support brace for the instrument rack.
263 | 2632002001 | 2002-01-21 | QR5 | Turbine Trip | [45 empty] | Monticello | B | GE | PO | 100 | While operating at 100% power at 1735 on January 21, 2002, a turbine control valve fast closure (load rejection) signal resulted in a reactor scram. All rods fully inserted and all safety systems functioned as designed. The primary cause of the scram was failure of the main turbine pressure control system. A detailed review of plant computer data revealed that the mechanical pressure regulator (MPR) had been behaving erratically for several days prior to the scram. This erratic behavior eventually caused the MPR to take control from the electric pressure regulator. This initiated rapid cycling of the turbine control and bypass valves which tripped both protection system sub channels on reduced hydraulic oil pressure at the control valve acceleration relay. Investigation determined that failure of the MPR was caused by a damaged rate feedback bellows. Following repair of the MPR, and completion of other unrelated maintenance, the unit was returned to service at 1327 on January 27, 2002.
263 | 2632007001 | 2007-01-10 | QR1 | RCS Low Pressure (RPS Trip) PWR | [10 empty] | X | [28 empty] | X | [5 empty] | Monticello | B | GE | PO | 88 | On January 10, 2007, the turbine control valves [JJ] ramped from approximately 50 percent open to 100 percent open in two seconds without a demand from the pressure control system. A Group 1 isolation and automatic scram ensued. Review of plant conditions immediately after the scram disclosed that the main turbine [TRB] control valves [SCV] did not close following the scram. During a post scram plant walk down it was identified that the supports for the turbine control valve enclosure [SPT] had failed, allowing the enclosure to transition downward approximately six inches. The root cause of this event was determined to be latent shortcomings in the design and construction of the turbine control valve enclosure support system during initial construction. Corrective actions include modifying and strengthening the enclosure support system, performing inspections of associated piping and systems, and performing an extent of condition review.
263 | 2632008005 | 2008-09-11 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Monticello | B | GE | PO | 100 | On September 11, 2008 at 2248 hours, the site experienced a lockout of the primary auxiliary transformer with the reserve transformer isolated for planned maintenance. This resulted in a Loss of Normal Off-site Power (LONOP) and an associated SCRAM. The cause of the event was the A and B phase conductors supplying power to the primary auxiliary transformer faulted to ground. Corrective actions taken or planned are: the faulted cable was repaired, repaired other degraded cable splices identified by the extent of condition, and improvements in the cable condition monitoring program.
263 | 2632011008 | 2011-10-21 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Monticello | B | GE | PO | 100 | At 1250 on October 21, 2011, at the Monticello Nuclear Generating Plant, a 2R Auxiliary Transformer lockout unexpectedly occurred causing off-site power to automatically transfer to the 1R Auxiliary Transformer, which resulted in a reactor scram. One cable of the "A" phase conductor, supplying power from 2RS to 2R Transformer, faulted to ground, resulting in the 3N4 breaker opening, as designed, to protect 2RS Transformer and other equipment from fault current damage. Subsequent testing indicates the cable suffered from environmental and age-related degradation. Implementation efforts to replace the cables between 2R Transformer and 2RS Transformer were in progress at the time of the event. A portion of the new raceway was under construction. The cables were replaced entirely employing a route designed to avoid cable submergence in water. Subsequent to installation, cables were successfully tested and returned to service.
263 | 2632011009 | 2011-11-19 | QR5 | Turbine Trip | [45 empty] | Monticello | B | GE | PO | 90 | On November 19, 2011, at approximately 2312 CST, during performance of regularly scheduled Turbine-Generator Quarterly Surveillance, an unplanned reactor scram occurred. Following the reactor scram, reactor water level lowered below the Group II isolation initiation setpoint (+9") and an actuation of Primary Containment Isolation System occurred. The direct cause of the scram was the actuation of the Main Turbine acceleration relay (load rejection) pressure switches. The root cause was ineffective management of Turbine Lube Oil (TLO) Tank Vacuum which resulted in oil build up on the turbine shaft resulting in fouled grounding braids. The shaft grounding device is intended to prevent damage to turbine generator components caused by circulating currents. Resulting circulating currents degraded the speed governor drive gear which resulted in governor oscillations ("bobble") that manifested itself during speed load changer testing and caused pressure oscillations at the acceleration relay (load rejection) pressure switches. Corrective actions include replacing the TLO Tank Vacuum Indicator with High Accuracy Device, and updating the operator round sheet to reflect new control bands as required. Repairs were also made to the speed governor gear drive components and main shaft oil pump components which were damaged by electrolysis and a modification was performed to install a more robust grounding apparatus.
263 | 2632012003 | 2012-09-25 | QP5 | Excessive Feedwater Flow | [45 empty] | Monticello | B | GE | PO | 100 | On September 25, 2012 at the Monticello Nuclear Generating Plant, during maintenance on 4160V 12-Bus ammeter switch, a 12-Bus lockout occurred removing power from 12-Reactor Feed Pump and 12-Reactor Recirculation pump. With both Main Feed Regulating Valves in auto, the level transient reached the Reactor Water Level Hi Hi setpoint (+48 inches). The Main Turbine and 11-Reactor Feed Pump tripped as designed and a Reactor scram occurred. The root cause for the 12-Bus lockout was determined to be that fleet work management guidance does not require the appropriate level of detail needed to expose the potential impact when injecting energy into plant structures, systems, and components. Additionally, a second root cause focused on the level transient determined that the Digital Feedwater Control System (DFCS) was not designed to control reactor pressure vessel level below +48 inches on a 12-Bus lockout from 100% power. The organization had a mind-set based on procedure bases and training that DFCS in automatic would maintain reactor level below +48 inches following a 12-Bus lockout. Immediate corrective actions were to remove the test equipment and reset the 12-Bus lockout. Long-term corrective actions include revising the work management guidance to require the appropriate level of detail. Classroom and simulator training for all licensed operators will be performed on this event and will include changes to the abnormal operating procedures to address DFCS.
263 | 2632015006 | 2015-11-23 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Monticello | B | GE | PO | 100 | On November 23, 2015, a trip of the # 11 Reactor Recirculation Pump occurred, followed by a Group 1 isolation which resulted in a reactor scram. A post scram troubleshooting investigation determined a large spike in differential pressure occurred in the 'C' main steam flow instrumentation line at the time of the Group 1 initiation event. <br /><br /> The root cause of this event was determined to be legacy foreign material present in the 'C' main steam flow instrumentation line. This foreign material obstructed the instrumentation line and resulted in the momentary sensed high steam flow. The sensed high steam flow was not due to an actual high steam flow condition in the 'C' main steam line. <br /><br /> Since the presence of foreign material in the instrument line is a legacy issue, the corrective action for the root cause was to remove the foreign material. The corrective action for the trip of the reactor recirculation pump, will be to revise the fleet procedure to require verification of torque on accessible electrical connections for critical components which are bench tested and also to ensure that accessible soldered and crimped electrical terminations are inspected for signs of degradation during bench testing.
265 | 2651987005 | 1987-03-21 | QR5 | Turbine Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | On March 21, 1987, Quad Cities Unit Two was in the RUN mode operating at approximately 100 percent power. At 0143 hours, the Unit Two main generator tripped due to an actuation of the main transformer sudden pressure relay. This resulted in a reactor scram due to a turbine/generator load mismatch. A normal scram recovery followed. <br /><br />Testing by the Operational Analysis Department (OAD) revealed no problems with the main transformer, the sudden pressure relay or its associated inhibit relay. Both relays were replaced like for like and Unit Two startup was initiated at 2148 hours on March 21, 1987. No problems were encountered and the Unit Two generator was synchronized at 1150 hours on March 22, 1987. Commonwealth Edison's Technical Center is continuing to analyze and test the relays involved with this event in an effort to discover the root cause for the relay actuation. This report is submitted to comply with 10CFR50.73(a)(2)(iv).
265 | 2651987009 | 1987-08-01 | QR5 | Turbine Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | On August 1, 1987, Quad Cities Unit Two was in the RUN mode operating at 100 percent core thermal power. At 1422 hours, a reactor RCT! scram JC! occurred from a turbine generator (TG) TG!TA! load mismatch which was caused by a generator GEN! trip. The generator trip occurred as a result of an electrical fault in the main transformer XFMR! "C" phase windings. Following the generator trip, the auxiliary power automatically transferred as designed; however, 30 seconds later buses (BU! 21 and 22 tripped from an undervoltage signal. This resulted in loss of power to the reactor feed pumps P!SJ!. The Reactor Core Isolation Cooling (RCIC) BN! System was used to inject water into the vessel RPV! until auxiliary power was restored and a reactor feed pump was started at 1433 hours. <br /><br />The main transformer was replaced with a spare. It was found to have faulted due to thermal deterioration caused by high leakage flux heating. The cause of the buses tripping was due to a loose termination causing relays to sense an undervoltage condition and trip the bus feed breaker. <br /><br /> This report is submitted in accordance with the requirements of 10CFR50.73(a)(2)(iv).
265 | 2651987011 | 1987-09-17 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Quad Cities 2 | B | GE | PO | 93 | On September 17, 1987, Quad Cities Unit Two was in the RUN mode at 93 percent of core thermal power. While Instrument Maintenance (IM) personnel were performing QIS 11-2 (Low low reactor water level functional test), a reactor scram and other related engineered safety feature (ESF) actuations occurred due to an indicated low reactor water level. This was a result of personnel error because the IM failed to prepressurize level instrument LIS 2-263-72C before reopening its isolation valve. This caused a pressure transient that actuated level switches LIS 2-263-57A and B which caused the reactor scram and associated ESF actuations. NRC notification per 10 CFR 50.72 was completed at 0717 hours. <br /><br />Disciplinary action was administered to the IM involved. Additionally, this event has been discussed with all IM personnel. QIS 11-2 is to be revised to include notes and caution statements and the associated checklist will be revised to add a signoff step for prepressurization. All similar procedures will be reviewed and revised as necessary if they lack adequate cautions an signoffs. This report is provided to comply with 10 CFR 50.73 (a)(2)(iv).
265 | 2651987013 | 1987-10-19 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Quad Cities 2 | B | GE | PO | 90 | On October 19, 1987, Quad Cities Unit Two was in the RUN mode at approximately 90 percent of reactor thermal power. At 1959 hours, an Equipment Operator (EO) incorrectly attempted to rack out of service an energized 4 kV circuit breaker on Bus 23. As the breaker was withdrawn, the shutter in the breaker cubicle, which was lowered in the racking out process, came in close contact with the energized breaker stabs and flashed to ground. Bus 23 tripped on overcurrent. As a result, a reactor scram and Emergency Core Cooling System (ECCS) initiations and related actuations occurred at 2000 hours. All systems responded as designed except for two minor discrepancies relating to the High Pressure Coolant Injection (HPCI) system. Reactor water level dropped to approximately -60 inches but was quickly restored. A normal scram recovery then followed. NRC notification of this event was completed at 2117 hours. <br /><br />The cause for this event was personnel error. Disciplinary action was administered. Other corrective actions include: 1. procedure revisions, 2. training sessions, 3. circuit breaker inspections, 4. HPCI system special tests, 5. development of a new training module addressing 4 kV breakers, and 6. creation of a Emergency Planning position in the Training Department. This report is provided to satisfy the requirements of 10 CFR 50.73(a)(2)(iv).
265 | 2651987020 | 1987-12-10 | QR5 | Turbine Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | On December 10, 1987, Quad Cities Unit Two was in the RUN mode at 100 percent thermal power. At 0118 hours, a reactor scram occurred due to a Turbine/Generator load mismatch. This occurred after a problem was identified while the Operating Department was performing weekly Turbine/Generator testing. NRC notification was completed at 0330 hours to comply with 10 CFR 50.72. <br /><br />An investigation revealed that the cause for this event was component failure. The B pilot solenoid valve of the turbine master trip solenoid valve failed, ultimately causing a pressure reduction in the hydraulic trip system, which caused the turbine to trip. The failed solenoid was replaced and no further corrective action is deemed necessary. The pilot solenoids are currently tested weekly. This report is provided to satisfy 10 CFR 50.73 (a)(2)(iv).
265 | 2651988001 | 1988-01-11 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Quad Cities 2 | B | GE | PO | 100 | On January 11, 1988, Quad Cities Unit Two was in the RUN mode at 100 percent thermal power. At 1055 hours, a reactor scram occured due to a turbine/generator load reject signal. This generator trip resulted from a ground detected by the generator 18 kV ground detection system. All safety feature actuations occurred as designed based on low reactor water level which resulted from the collapse of voids in the reactor core. A normal scram recovery followed. Two overvoltage relays were found tripped. NRC notification of this event was completed at 1120 hours to satisfy the requirements of 10 CFR 50.72. <br /><br />The cause of this event was not determined. Station Electrical Maintenance and the Operational Analysis Department (OAD) performed extensive tests but no grounding problem was identified. The only problem identified was a blown fuse which could explain why one overvoltage relay was tripped, but could not have caused the other relay to trip. <br /><br />Unit Two generator was put on-line at 0300 hours on January 16, 1988. No problems have been observed since that time. This report is provided to comply with 10 CFR 50.73(a)(2)(iv).
265 | 2651988005 | 1988-03-20 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Quad Cities 2 | B | GE | PO | 45 | On March 20, 1988, Quad-Cities Unit Two was in the RUN mode at 45 percent thermal power. At 0123 hours, a reactor scram (and related Engineered Safety Feature actuations) occurred due to a spurious turbine trip caused by a packing leak on 2B Feedwater Regulating Valve (FRV). The leakage caused a short across terminal contacts in Busses 21 and 22 that cause the turbine to trip. A group I isolation also occurred during this event. NRC notification via the Emergency Notification System was completed at 0215 hours per 10 CFR 50.72. <br /><br />The cause of this event is attributed to component failure (packing on 2B FRV). Contributing to this event is the lack of administrative controls to ensure valve packing is replaced prior to failure. <br /><br />Corrective actions included repairs and inspection of both FRVs and moisture removal and inspection of affected equipment. Additional corrective actions include: 1) Disassembly and repair of the 2B FRV during the Refuel outage, 2) vibration isolator installation on Group I instrument racks, 3) development of guidelines for packing replacement, 4) evaluation of area floor drain system and area cable pan covers, and 5) round sheets revision to ensure once/shift inspection of FRV. This report is supplied per 10 CFR 50.73 (a)(2)(iv).
265 | 2651988026 | 1988-10-15 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Quad Cities 2 | B | GE | PO | 96 | On October 15, 1988, Quad Cities Unit Two was operating in Economic Generating Control (EGC) with a range of 725 to 800 MWe. At 0040 hours, the Unit Two Instrument Air Compressor Dryer "B" Prefilter and the "A" Afterfilter were being returned to service, when the service air back-up to the instrument air system was inadvertently isolated. The scram air header pressure decreased to 44 psig. The reactor was manually scrammed at 0047 hours as directed by the Shift Engineer. NRC notification of this event was completed at 0144 hours to comply with the requirements of 10CFR50.72. <br /><br />This event was caused by performing the RTS in the wrong sequence. Contributing factors are a misunderstanding of sequencing, lack of knowledge concerning instrument air, and the incorrect installation of a dryer blowdown valve. <br /><br />Immediate corrective actions taken include tailgate sessions with each operating crew covering sequencing and the instrument air system as it relates to the service air system, and the correct installation of the blowdown valve. Corrective actions include a new OOS training program for all operators as well as plant training for non-licensed operators on instrument air, revision of the instrument air lesson plans, training for the work analysts concerning reliability-related work, a revision to the OOS procedure (QAP 300-14), and a study by the Station's Instrument Air Task Force to evaluate the Station's current instrument air system design. <br /><br />This report is provided to comply with the requirements of 10CFR50.73(a)(2)(iv).
265 | 2651989001 | 1989-04-06 | QR5 | Turbine Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 80 | On April 6, 1989, Quad Cities Unit Two was in the RUN mode at 80 percent of rated core thermal power. At 0332 hours, a reactor scram occurred due to a Turbine Stop Valve Closure. This occurred while the Operating Department was performing weekly Turbine/Generator testing. NRC notification was completed at 0404 hours to comply with 10 CFR 50.72. <br /><br /> An investigation revealed that the cause for this event was component failure. The A pilot solenoid valve of the turbine master trip solenoid valve failed in the de-energized condition. Due to a stuck limit switch, the light indication continued to show the pilot solenoid valve energized. Thus, when the B master trip solenoid was tested, a turbine trip occurred. The failed solenoid was rebuilt and the coil and limit switch were replaced. The pilot solenoids are tested weekly. This report is provided to satisfy 10 CFR 50.73(a)(2)(iv).
265 | 2651989005 | 1989-10-12 | QR5 | Turbine Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 55 | On October 12, 1989, Quad Cities Unit Two was in the RUN mode at 55 percent of rated core thermal power. At 0140 hours, a reactor RCT! scram JC! occurred due to Turbine TRB! Stop Valve SHV! closure. This occurred when the station's Electrical Maintenance Department was removing a Limit Switch ZIS! from the number two Main Stop Valve SHV!(MSV). NRC notification was completed at 0227 hours to comply with 10CFR50.72(b)(2)(ii).<br /><br /> An investigation revealed that the cause for this event was personnel error. The Work Analyst, while developing the electrical work packages, overlooked the removal of two connections CON! on the MSV Limit Switch. This caused the number 1, 3, and 4 Turbine Main Stop Valves to close and subsequently the reactor scram.<br /><br /> The maintenance workers were immediately counseled. Further corrective actions will involve training, a procedure revision, issuance of an Operating Memo, and a training lesson plan revision. <br /><br /> This report is provided to satisfy 10CFR50.739a)(2)(iv).
265 | 2651990010 | 1990-10-15 | QR5 | Turbine Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | On October 15, 1990, Quad Cities Unit Two was in the RUN mode at 100 percent of rated core thermal power. At 1210 hours, a reactor scram occurred due to turbine stop valve closure. The turbine stop valve closure was a result of a turbine trip caused by moisture separator high level. All safety feature actuations occurred as designed. Emergency Notification System (ENS) notification was completed at 1530 hours on October 15, 1990, to comply with the requirements of 10CFR50.72(b)(2)(ii). <br /><br /> An investigation revealed the cause of this event was due to a partially blocked drain line on the 2C moisture separator level switch. Because water was not draining properly from the level switch chamber, the level in the chamber increased to the high level setpoint. This resulted in a turbine trip. <br /><br /> The level switches for the moisture separator have been added to a Preventative Maintenance program.<br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(iv). VR 140
265 | 2651991012 | 1991-10-07 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Quad Cities 2 | B | GE | SU | 1 | At 0223 hours on October 7th, 1991, Unit Two was in the Startup mode at 1 percent rated reactor core thermal power. When the reactor RCT! RPV! reached approximately 63 psig, a spurious actuation of Electromatic Relief Valve (ERV) RV! 2-203-3C occurred. At 0253 hours, Unit Two was manually scrammed and cooldown was initiated. Later, when a Drywell entry was made, the pilot valve V! for the 2-203-3C was found stuck open. <br /><br /> The cause of this event was binding of the pilot valve for the 2-203-3C ERV. The Mechanical Maintenance Department replaced the pilot valve internals for each ERV as a precautionary measure. On October 7th 1991, at 1912 hours, the ERV's were stroked manually and tested successfully. Unit Two startup was initiated at 2054 hours on October 7th, 1991. QCOS 203-3, Main Steam Valves Operability Test, was performed on October 8th, 1991 at 1020 hours, and the ERV declared operable. <br /><br /> This report is being submitted in accordance with 10CFR50.73(a)(2)(iv).
265 | 2651992001 | 1992-01-01 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Quad Cities 2 | B | GE | PO | 24 | On January 1, 1992, Quad Cities Unit Two was in the RUN mode at 24 percent of rated core thermal power. Special Test Procedure 2-104, Turbine Trip Main Steam Line Low Pressure Test, was in progress in an attempt to discover the cause for historical Group I Primary Containment Isolations (PCI) following turbine trips. At 0014 hours, the Unit Two Main Turbine was manually tripped from 200 MWe. Within 0.5 seconds of the turbine trip, a Group I PCI occurred. A reactor scram then occurred upon ten percent closure of the Main Steam Isolation Valves (MSIV). All safety feature actuations occurred as designed. An Emergency Notification System (ENS) notification was completed at 0223 hours on January 1, 1992.<br /><br /> Test data obtained revealed the cause of the Group I PCI to be main steam line (MSL) pressure wave and instrument line resonance due to Turbine Stop Valve fast closure. This caused large pressure fluctuations at the location of the MSL Low Pressure Switches. This fluctuation was large enough to actuate all four switches and cause the Group I PCI. General Electric has been contracted to evaluate the test results and provide recommended corrective actions.
265 | 2651993001 | 1993-01-07 | QL5 | Partial Closure of MSIVs | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | On January 7, 1993, Quad Cities Unit Two was in the Run mode at 100 percent of rated core thermal power. At 1008 hours, Reactor Protection System (RPS) Bus B was being transferred to its alternate power supply in preparation for the semi-annual testing of the RPS Electrical Protection assemblies (EPA) units. When the breaker for the RPS Bus B was opened the 2-203-2A Main Steam Isolation Valve (MSIV) closed causeing the reactor flux and pressure to exceed the scram setpoints. All safety feature actuations occurred as designed. An Emergency Notification System (ENS) notification was completed at 1205 hours on January 7, 1993. <br /><br /> The cause of the 2 -203-2A MISV closing during the transfer of the B RPS Bus is attributed to the failure of the DC solenoid coil on the MSIV manifold assembly. Corrective actions will include proposed changes to the Technical Specifications and changes to QOP 7000-1, Reactor Protection System MG Sets. <br /><br /> This reports is being submitted to comply with 10CFR50.73(a)(s)(iv).
265 | 2651993005 | 1993-01-29 | QR8 | Spurious Reactor Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | At 1340 hours on January 29, 1993, Unit Two was in the RUN Mode when a full SCRAM occurred. <br /><br /> The SCRAM was initiated by a spurious high reactor pressure signal. The indicated reactor pressure was normal for plant operations. The apparent cause is due to a contractor accidentally bumping the reactor high pressure switches' common sensing line while performing the Reactor Vessel Water Level Indicating System modification work. <br /><br /> This event will be tailgated with groups performing work in the plant to enhance personnel awareness of the sensitivity of the reactor high pressure switches and their associated sensing lines.
265 | 2651993006 | 1993-03-06 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Quad Cities 2 | B | GE | PO | 71 | On March 6, 1993, Unit Two was in the RUN mode at 71% of rated core thermal power. At 2019 hours, the 2-203-3E Electromatic Relief Valve (ERV) [RV] failed to close during routine testing. At 2021 hours, the reactor [RCT] was manually scrammed per procedure and the relief valve reseated on its own at 193 psig reactor pressure. The Unit was in cold SHUTDOWN at 0112 hours on March 7, 1993. During a Drywell inspection it was discovered that the leakoff line from the 2-203-3E ERV was sheared off where it attaches to the 8 inch discharge header. NRC notification was completed at 2156 hours on March 6, 1993 per 10 CFR 50.72(b)(2)(ii). <br /><br /> Investigation revealed that the cause of the event was component failure. The pilot valve seat bushing had severe steam cutting. The fractured leakoff line piping is being sent off site for failure analysis. This ERV will be replaced with an overhauled valve during the current refuel outage and it will be tested along with all of the other relief valves during reactor startup.<br /><br /> This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv).
265 | 2651993013 | 1993-06-13 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Quad Cities 2 | B | GE | PO | 57 | On June 13, 1993 at approximately 0624 hours, Unit 2 was in the RUN mode at 57% power when an internal electrical fault within the Unit 2 Main Power Transformer resulted in an automatic generator trip. The Main Turbine tripped and caused a reactor scram due to turbine stop valve closure. All safety features functioned as designed, however an unexpected Group I isolation occurred immediately following the turbine trip. An Emergency Notification System (ENS) call was completed at 0726(CST) on June 13, 1993, to comply with the requirements of 10CFR50.72(b)(2)(ii). <br /><br /> The transformer was determined to be damaged beyond repair and was determined to be damaged beyond repair and was replaced with a new ABB transformer. The Group I isolation was determined to be caused by pressure fluctuations caused by the rapid closure of the main stop valves following the turbine trip. A modification to eliminate the spurious Group I has been designed and is scheduled to be implemented during Q2R13 and Q1R14.
265 | 2651993024 | 1993-12-02 | QR8 | Spurious Reactor Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 97 | On December 2, 1993, two Instrument Maintenance (IM) Technicians were performing Quad Cities Instrument Surveillance (QCIS) 200-1. Quarterly Reactor (Rx) High Pressure SCRAM Calibration and Functional Test on Unit 2 High Rx pressure switch (PS) 63! 2-263-55A. The Control Room received a Unit 2 Rx Low Level SCRAM. It was believed at that time that the SCRAM was caused due to a leaky isolation valve ISV!. <br /><br /> The valve was removed and disassemble for inspection. The inspection revealed stainless steel particles inside the valve. These particles are assumed to have wedged in between the valve seat and disc which caused the valve to remain partially open when the valve was initially closed. The SCRAM appears to have been due to pressure wave propagation in the common tapped instrument sensing lines. <br /><br /> Immediate corrective actions taken were as follows: The Unit 2 Rx was brought to a cold shutdown condition. The Operations Department withheld the performance of this surveillance test on the rest of the pressure switches on both units, until the preliminary investigation was completed. The IM Department along with the Operations Department developed a method for performing surveillances, involving pre-pressurization valves, to determine if the instrument isolation valve was leaking by. This method was documented in IM memorandum #25. The IM Department is also backflushing all instrument lines on both units that have the same valve design configuration. <br /><br /> Recommended corrective actions include the review and possible re-design of the isolation valve configuration and the review and possible inclusion of these valves into a preventive maintenance schedule for backflushing. .
265 | 2651994005 | 1994-06-21 | QR6 | Manual Reactor Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 95 | On June 21, 1994, Unit 2 was in the RUN mode at approximately 95% power. An Equipment Operator reported that the Electro Hydraulic Control (EHC) fluid reservoir level was rapidly decreasing. At 1405 the Reactor was manually scrammed and the main turbine was manually tripped due to anticipation of low EHC control oil pressure. <br /><br /> The source of the EHC fluid leak was discovered on a one inch EHC line to turbine control valve #2. It appears that the EHC line failure was due to high cycle fatigue crack propagation at the radius of the tube flare. The exact source of the cycle stresses responsible for the fatigue crack initiation and propagation could not be determined. A likely cause is that the stresses were induced by vibration on the EHC line caused by oscillations of the #2 turbine control valve. <br /><br /> The Causal Factors (C/F) for this event are attributed to Equipment Specification, Manufacture, Construction and Plant/System Operation. <br /><br /> Corrective actions that have been completed include: replacement of the EHC lines to the #2 control valve, liquid penetrant examination of the EHC lines to the #1, 3 & 4 control valves, replacement of the #2 control valve servo valve and circuit boards and recalibration of the #2 control valve controller loop. <br /><br /> Corrective actions to be completed include: analysis of the cracked tubing, evaluating the replacement of the flared fittings, and liquid penetrant examination of the EHC lines to the Unit 1 control valves.
265 | 2651994006 | 1994-08-23 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Quad Cities 2 | B | GE | PO | 99 | On August 23, 1994, Unit 2 was in the RUN mode at approximately 99% power. Contractor Instrument Maintenance (IM) personnel had received permission to calibrate the 2B Reactor Recirculation pump seal pressure transmitter located on an instrument rack immediately adjacent to one of the two Main Steamline (MSL) high flow instrument racks. At 0827 a Group I primary containment isolation (PCI) was received from a main steamline high flow signal. A Reactor Scram followed from Main Steam Isolation Valves not being full open while in the Run mode. <br /><br /> The root cause of this event was inadvertent vibrational disturbance to the MSL high flow instruments by contractor IM personnel working at the rack. This vibration resulted in the trip of the MSL high flow switches. A full Group I PCI and Reactor Scram then occurred. The Causal Factors for this event are attributed to Lack of awareness of the need for concern and Design configuration. Corrective actions that have been completed include: installation of vibration dampening pads, construction of an additional temporary barrier and placement of 'CAUTION Sensitive Equipment' signs around the instrument racks. <br /><br /> Corrective actions to be completed include: review current training requirements and consider additional training for all work groups at the station reiterating the sensitivity of the MSL high flow instrument racks and other racks identified as vibration sensitive, improving the permanent rack barriers and investigating a method to reduce the vibrational sensitivity of the MSL high flow actuation switches.
265 | 2651995005 | 1995-08-25 | QR5 | Turbine Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 60 | On August 25, 1995, Quad Cities Unit 2 was operating at 60 percent of rated core thermal power. At 0848 hours, Unit Two experienced an automatic reactor [RCT] scram during an Electro Hydraulic Control (EHC) pressure regulator [RG] fail-over test. <br /><br /> The apparent cause of the event was attributed to the failure of General Electric (GE) and ComEd personnel to recognize that a pressure regulator failure would be a worse reactor transient than a 10 psig pressure step change at Quad Cities Station. Inadequate EHC system pressure regulator setpoint bias and small lag time constant settings were also contributors to the scram. <br /><br /> Corrective actions that have been completed include: adjustment of the EHC system pressure setpoint bias and time lag constants to obtain a smooth output curve that represents a small transient on the system when a pressure regulator fails. <br /><br /> Corrective actions to be completed include: revisions to the EHC lineup instructions for setting up the 3 psig 'effective' pressure setpoint bias and inclusion of the correct minor lag time constant on the Steam Line Resonance Compensator circuit boards.
265 | 2651998003 | 1998-06-28 | QR5 | Turbine Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | On 06/28/1998, at 0223, Unit 2 was in Power Operation at 100% power. A Unit 2 Main Generator trip and subsequent Reactor Scram occurred. A walkdown of the relay targets associated with the Unit 2 Main Generator was performed. A differential protective relay on the "C" phase for the Main Generator was found actuated. Simultaneously, a 345 KV line tripped on a "B to C" phase fault. The fault was indicated on the line protective relays and the digital fault recorder located in the 345 KV switchyard. A line crew found a static line that had fallen down 9-10 miles outside of Quad Cities Station caused by severe weather related conditions in the area. The Operational Analysis Department (OAD), System Engineering and Electrical Maintenance were called to investigate the cause for the Unit 2 Main Generator trip. A loose electrical connection was found in a junction box on a lead off a Current Transformer under the Main Generator. The loose connection along with the indicated line fault caused the protective relay to trip which in turn tripped the Main Generator. Immediate corrective actions included stabilizing Unit 2, placing the Unit in Hot Shutdown and initiating Work Request's to troubleshoot and repair problems found. Also, a method of verifying the integrity of the generator circuits in high vibration areas will be developed. The safety significance to the health and safety of the onsite personnel and to the public was minimal. All expected ESF actuation's occurred as designed to bring the reactor to a safe shutdown condition.
265 | 2652000006 | 2000-05-05 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Quad Cities 2 | B | GE | PO | 100 | On May 5, 2000, at 0940 hours, a Group I Primary Coolant isolation and a reactor trip were received on Unit 2 during calibration of Main Steam Line High Flow switches. The individual performing the calibration adjusted a switch other than the one that was isolated and prepared for calibration. The root causes of this event were inadequate individual performance on the part of the Instrument Maintenance Technician in the field, failure to adequately enforce management expectations concerning established human performance initiatives, insufficient barriers considering the risk associated with testing Group I isolation instruments, and a lack of oversight and communication. Additionally, previous corrective actions were inadequate. The safety significance of this event was minimal. No mitigating equipment was degraded, and all Emergency Core Cooling Systems were operable throughout the event Several immediate corrective actions were taken commensurate with the seriousness of the event. Corrective actions that remain to be taken include divisionalization of Instrument Maintenance (IM) procedures with the potential to cause a unit trip or derating.
265 | 2652000007 | 2000-05-22 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | On May 22, 2000, at 2159 hours, the Unit 2 reactor scrammed on a high flux signal during a return to service for an electro-hydraulic control (EHC) solenoid replacement on a turbine control valve (CV). The high flux was due to an unanticipated response of the CVs, most likely from air entrapped in the EHC system. The root cause of this event was inadequate risk assessment. Corrective actions include improving the risk assessment process to ensure .available options are explored and independently reviewed, and strengthening the questioning attitude at the station. On May 22, 2000, at 2229 hours, a reactor water cleanup system isolation occurred on low reactor water level (RWL). The actuation occurred when operators delayed the start of a reactor feed pump while awaiting an in-plant check. The root cause of the isolation was inadequate decision-making regarding restart of components. Corrective actions to prevent recurrence include updated dynamic simulator training focusing on RWL control. The safety significance of these events was minimal. The only mitigating equipment that was not fully operable was the "D" residual heat removal service water pump. The unit was shut down using normal operating equipment. Although feedwater flow was not fully restored prior to receiving the low level isolation, the restoration was in progress and the low level signal was cleared within three minutes.
265 | 2652000008 | 2000-07-18 | QR5 | Turbine Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | At 0548 hours on July 18, 2000, Unit 2 automatically scrammed from full load due to a C-phase generator differential relay operation. The Unit 2 trip was concurrent with an insulator fault on the C-phase of a 345kV line. Equipment on Unit 2 responded to the scram as expected to shut the unit down. Approximately ten seconds after the Unit 2 scram an attempted automatic reclosure of a 345kV breaker in the switchyard caused a 345kV differential relay to operate. The result of this was a loss of power to the Reserve Auxiliary Transformer (RAT), which provides normal offsite power to one division of Unit 1. The loads normally supplied by the RAT automatically transferred to the Unit Auxiliary Transformer (UAT), which normally provides power from the Unit 1 generator to one division of Unit 1. Unit 1 continued to operate for about ten hours with power supplied to both Unit 1 divisions by the UAT, after which the RAT was reenergized and the loads transferred back. The root causes of this event included current transformer mismatch, an inappropriate breaker reclose scheme, and inadequate consideration of CT mismatch during implementation of distribution yard design changes. The safety significance of this event was minimal. On Unit 2, all control rods inserted, and reactor water level and pressure were controlled using the normal coolant supply and heat removal systems. On Unit 1, the UAT supplied power during the event, with offsite power available from the Unit 2 RAT, as designed.
265 | 2652001001 | 2001-08-02 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Quad Cities 2 | B | GE | PO | 100 | On August 2, 2001, at 0813 hours, lightning struck a 345 kV line that connected to the Quad Cities switchyard. This resulted in failure of the Unit 2 Main Power Transformer (MPT), an automatic reactor scram on Unit 2 and loss of normal offsite power to Unit 2. An Unusual Event was declared, the Unit 2 and 1/2 Emergency Diesel Generators started, and the Reactor Core Isolation Cooling system and the Safe Shutdown Makeup Pump were manually started to maintain reactor vessel level. The MPT fire was extinguished at 0845 hours and normal offsite power was restored to Unit 2 at 1047 hours. The safety significance of this event was minimal. All safety systems operated as designed to shut the Unit 2 reactor down and maintain it in a safe shutdown condition. Offsite power was available to Unit 2 from the Unit 1 Reserve Auxiliary Transformer through the emergency bus crosstie throughout the event. The root cause of the MPT failure was mechanical failure of the bus bar clamps due to original equipment manufacturer design and construction errors. The root cause of the loss of normal offsite power was age degradation in a Static Breaker Failure (SBF) relay. The SBF relay was replaced and the preventive maintenance program has been upgraded concerning local breaker backup schemes. The MPT Specification Development Lessons Learned Review Checklist has been upgraded and a comprehensive transformer monitoring strategy will be implemented.
265 | 2652002002 | 2002-04-05 | QR6 | Manual Reactor Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | On April 5, 2002, at 1028 hours, a manual scram was inserted on Unit 2 in response to increasing reactor level. The increase in reactor level was due to a blown fuse in the Digital Feedwater Level Control (DFWLC) system, caused by the inadvertent grounding of test leads during an instrument surveillance. Although the DFWLC logic is intended to be able to respond to a blown fuse without causing a level transient, the indicating fuse holder provided a circuit that inhibited recognition of the blown fuse by the DFWLC logic. The root cause of the Unit 2 reactor scram was a design deficiency involving the installation of indicating fuse holders. The inadvertent grounding of the test leads was a contributing cause. Also, although the operator actions were in accordance with procedure, different actions may have mitigated this event. The safety significance of this event was minimal. Adequate makeup to the vessel was available at all times from the feedwater system, as well as from the ECCS systems. Corrective actions include removal of the indicating fuse holders, actions to minimize the potential for grounding test leads, and review of the default operator actions for a level transient.
265 | 2652003002 | 2003-04-16 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Quad Cities 2 | B | GE | PO | 100 | On April 16, 2003, at 1322 hours, the Unit 2 3B Main Steam Relief Valve (RV) selfactuated. The operators initiated the appropriate procedures for an open RV, including initiation of suppression pool cooling, a manual reactor scram, removal of the control power fuses to the 3B RV, and closure of the main steam isolation valves to slow the reactor cooldown rate. At 1359 hours, the suppression pool temperature reached 110F and an Alert was declared in accordance with the Exelon Emergency Plan. The Alert was exited at 2251 hours. The safety significance of this event was minimal. The opening of the 3B RV did not affect the capability of the relief valves to protect against high reactor pressure. At the time of the event, the Emergency Diesel Generator was out of service for planned maintenance. All other mitigating systems were available. Therefore, both emergency and non-emergency sources of injection to the vessel were available to make up for the coolant being relieved through the RV to the suppression pool. The root cause was excessive leakage past the 3B RV pilot valve seat, which allowed the RV closure force to diminish and the RV to open. Corrective actions included replacement of the 3B RV, improvements in RV tailpipe temperature monitoring, and removal of the requirement to perform on-line test actuations of the RV.
265 | 2652004003 | 2004-03-30 | QR5 | Turbine Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 72 | On March 30, 2004, at 0740 hours, during testing of the Thrust Bearing Wear Detector (TBWD), the main turbine tripped and a Reactor Protection System trip signal was received from the closure of the main turbine stop valves. All control rods fully inserted, and the unit was taken to shutdown. The cause of this event was the inappropriate use of a surveillance procedure with a known single-point vulnerability, in lieu of a calibration procedure. This was caused by an implementation practice that did not require performance of all three TBWD calibration procedures following turbine maintenance. The safety significance of this event was minimal. All plant systems operated as designed to shut the unit down. Corrective actions include the revision of the operations turbine test of the TBWD to provide a positive means of inhibiting a turbine trip during TBWD testing, a review of the implementation of Instrument Maintenance procedures for other situations in which the procedures are used interactively with procedures from another department, and the revision of the work frequency codes that determine when the local adjustment procedures are performed such that the procedures are appropriately performed at the end of an outage.
265 | 2652007001 | 2007-02-28 | QL7 | Degraded condenser vacuum | [45 empty] | Quad Cities 2 | B | GE | PO | 30 | On February 27, 2007 at 2300 hours, control room operators commenced a power reduction on Unit 2 to 725 MWe to effect repairs on the 2C Reactor Feed Pump (RFP) due to a seal leak. At approximately 2352 hours, a pressure controller malfunction in the auxiliary steam supply to the 2A offgas train caused a reduction in its noncondensible gas removal efficiency. This malfunction impacted the 2A Offgas Preheater, Unit 2 steam dilution, and the 2A steam jet air ejector (SJAE) operation, and caused increased condenser back pressure. On February 28, 2007, at 0120 hours, Quad Cities Station Unit 2 Reactor was manually scrammed due to increasing condenser back pressure. This event was caused by a blockage of the pressure sensing line to pressure controller (PC) 2-3041-3A with fine sized corrosion products. The increase in demand of PC 2-3041-3A caused relief valve (RV) 2-3099-129 to open, which ultimately caused a reduction in 2A SJAE efficiency and an increase in condenser back pressure. The safety significance of this event was minimal. While this event required action to diagnose and initiate a manual scram, the reactor, turbine, condenser, and supporting systems performed as expected and within Technical Specifications and UFSAR limits. All safety systems remained fully functional during this event.
265 | 2652010002 | 2010-08-17 | QR6 | Manual Reactor Trip | [45 empty] | Quad Cities 2 | B | GE | PO | 100 | On August 17, 2010, Quad Cities Unit 2 performed a scheduled adjustable speed drive [DRIV] (ASD) programmable logic controller [DCC] (PLC) restoration activity. During the evolution, the ASD was unable to control the reactor [RCT] recirculation (recirc) pump [P] speed and resulted in a trip of the 2B recirc pump. The 2B feedwater [SJ] regulating valve [FCV] (FRV) was also in manual control mode at this time, and reactor pressure vessel (RPV) water level increased. Operators transferred the 2B FRV controls from manual to automatic, RPV water level continued to rise, manual scram criteria was met at 44 inches RPV water level, and subsequently Operators were required to manually scram the reactor via the reactor protection system [JD] (RPS). There were no complications during the reactor scram, and all systems functioned as required. Forced outage, Q2F65, was initiated to investigate and performs repairs. The reactor and all systems responded as designed. When in automatic operation the 2B FRV responded unexpectedly to Operators, however, the FRV operated as designed. Operators had not been informed of the valve position recovery time delay involved when transferring the 2B FRV from manual to automatic position control in this scenario. The root cause of this event is management's failure to recognize and effectively challenge critical assumptions used in authorizing work activities for performing the ASD resynchronization, and for determining risk in controlling the 2B FRV. Both process reviews failed to adequately assess and manage risk prior to performing these activities. Corrective actions include enhancements in technical rigor used in the identification and evaluation of plant decisions involving risk, associated operating procedure revisions, enhanced training, and additional considerations to perform simulator testing. The safety significance of this event was minimal. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram or reactor trip.
265 | 2652012003 | 2012-04-18 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Quad Cities 2 | B | GE | PO | 21 | On April 18, 2012, at 1511 hrs, while at low power conditions after refueling outage Q2R21, an automatic reactor scram occurred on Unit 2 due to high reactor pressure. The pressure increase occurred during post-modification testing on the main generator automatic voltage regulator (AVR) which had been upgraded during refueling outage Q2R21. The testing included a generator load reject, which was in progress when the pressure transient occurred. There were no complications during the reactor scram and subsequent turbine trip, and all systems functioned as required. Operators performed required actions safely and in accordance with procedures and training. The cause of the automatic scram was due to high reactor pressure created by the load rejection associated with the main generator voltage regulator testing, coincident with unresponsive opening demand of turbine control valves (TCVs) that impacted the turbine bypass valves (TBVs) ability to control reactor pressure. Since the digital electro hydraulic control (DEHC) system design lacked the required Intercept (IV) EHC shutoff valves, this resulted in low EHC pressure and caused the TCVs to be unresponsive. Unit 1 was unaffected by the event and remained at 100% power. Corrective actions included evaluating the impact of the event on the operability of the TBVs, and applying a Minimum Critical Power Ratio (MCPR) Operating Penalty (TS 3.7.7) when reactor power is between 25% and 50%. Future corrective actions include development of a hardware/software modification to the DEHC system to correct the design deficiency. The safety significance of this event was minimal. This event is reportable (Unit 2) per 10 CFR 50.73(a)(2)(iv)(A), which requires the reporting of any event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram; (Units 1 and 2) 10 CFR 50.73(a)(2)(i)(B), which requires the reporting of any operation or condition which was prohibited by the plant's Technical Specifications; and (Units 1 and 2) 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems needed to control the release of radioactive material.
265 | 2652014002 | 2014-04-02 | QR6 | Manual Reactor Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Quad Cities 2 | B | GE | PO | 8 | On April 2, 2014, at 1228 hours, a Fire Alarm System (FAS) alarm was received for the Unit 2 D heater bay area. Although entry into the room at the time identified only a steam leak, subsequently various spurious alarms and electrical system anomalies occurred.<br /><br /> At 1303 hours, Unit 2 was manually scrammed, the turbine was tripped, and the main steam isolation valves (MSIVs) were closed to ensure the steam leak was isolated. A fire was identified to have occurred in the D heater bay (an area of the plant containing the high pressure (final stage) D feedwater heaters, and several Unit 2 cable trays and risers). The fire was extinguished by the automatic wet pipe sprinkler fire suppression system.<br /><br /> At 1340 hours, due to the manual de-energizing of safety-related motor control center (MCC) 29-1 in the reactor building in response to notification that smoke had been observed, an ALERT level Emergency Action Level classification was declared as HA3 (fire in a vital area affecting safety system equipment). The emergency was terminated at 2132 hours.<br /><br /> The cause of the event was an existing cable flaw that was caused by cable routing that exceeded the required minimum static bend radius.<br /><br /> Corrective actions included repairing impacted cables, replacing the failed steam seal expansion joint, operating procedure revisions, and additional inspections/tests.<br /><br /> The safety significance of this event was minimal. Given the impact on multiple systems, this report is submitted in accordance with 10 CFR 50.73 (a)(2)(iv)(A) for manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B); in accordance with 10 CFR 50.73 (a)(2)(v)(D) for an event that could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident; and in accordance with 10 CFR 50.73(a)(2)(i)(A), for the completion of a nuclear plant shutdown required by the plant's Technical Specifications.
266 | 2661987005 | 1987-11-21 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | Point Beach 1 | P | WE | PO | 100 | On November 21, 1987, at 0305 hours, Unit 1 reactor coolant pressure began decreasing and the reactor tripped due to low pressurizer pressure. Reactor coolant pressure continued to decrease until safety injection initiated flow to the reactor coolant system. Pressure was lost when a pressurizer spray valve stuck open. An unusual event was declared at approximately 0331 hours and was terminated at 0457 hours. <br /><br />An inspection of the pressurizer pressure control equipment revealed two failures, a broken solder joint in a pressurizer spray valve controller and a stuck pilot valve in the associated pressurizer spray valve positioner resulted in the spray valve being maintained in the full open position. The minimum pressure reached while the spray valve was stuck open was 1378 psig. The maximum pressure reached after the pressurizer was filled with water was approximately 2077 psig. <br /><br />The controller and pilot stem were repaired and returned to service. The unit was then returned to full power operation.
266 | 2661991005 | 1991-05-30 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Point Beach 1 | P | WE | PO | 100 | On May 30, 1991, the Point Beach Nuclear Plant Unit 1 was operating at 100% power. At 1146, power to the Unit 1 red instrument bus was lost due to the failure of the inverter (1DY01) supplying the bus. This resulted in a reactor trip. However, loss of power to the bus does not directly cause a trip. The Plant Process Computer System (PPCS) sequence of event recorder did not indicate the exact cause of the trip. Start-up tests were performed and all results were satisfactory. <br /><br /> The instrument bus was transferred to the spare inverter and Unit 1 was started up and returned on line at 0047 on May 31, 1991. 1DY01 was subsequently repaired, tested, and returned to service supplying the Unit 1 red instrument bus.
266 | 2661991008 | 1991-06-29 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Point Beach 1 | P | WE | PO | 100 | On June 29, 1991, while operating at 100% power, an automatic reactor trip occurred on Unit 1 at 6:38 P.M. The reactor trip was caused by the loss of power from 1DY03, the inverter supplying power to the "white" instrument bus. The loss of power to this bus resulted in a steam flow to feed flow mismatch coincident with a low steam generator water level on the "B" steam generator, resulting in a reactor trip. <br /><br /> The instrument bus was transferred to the spare inverter, DY0C, and Unit 1 was started up and returned to service at 11:52 a.m. on June 30, 1991. Full power was achieved at 2:15 a.m. on July 1, 1991. Currently, power to the "white" instrument bus is being supplied by the spare inverter.
266 | 2661992008 | 1992-10-05 | QL5 | Partial Closure of MSIVs | [45 empty] | Point Beach 1 | P | WE | PO | 100 | On October 5, 1992, at 3:34 a.m., with Unit 1 operating at 100% reactor power, 1MS-2018, the Unit 1 'A' steam generator main steam isolation valve (MSIV), shut during the performance of Periodic Check (PC)-11, Part 2, 'MSIV Solenoid Valve Trip Test (Quarterly). ' This resulted in an automatic turbine trip and a reactor trip. The MSIV shut when 1MS-2018D-S, the associated 'B' train solenoid vent valve, opened, venting instrument air from the valve operator. This vent valve was replaced and retested satisfactorily. Unit 1 was subsequently returned to service at 1:59 a.m. on October 6, 1992.
266 | 2661995006 | 1995-07-14 | QR5 | Turbine Trip | [45 empty] | Point Beach 1 | P | WE | PO | 100 | At 1010 on July 14, 1995, the Point Beach Nuclear Plant (PBNP) Unit 1 main generator tripped. The generator trip caused a turbine trip, which resulted in a reactor trip from 100% power. The generator trip was initiated by a 'Unit Lockout' signal from a loss of generator excitation. Inspection of the exciter revealed that water had condensed inside the exciter housing. The condensation caused shorting and failure of the exciter. The exciter was repaired and Unit 1 was placed back on-line at 1405 hours on July 18, 1995. The condensation in the exciter was caused by a period of extremely hot and humid weather coupled with the cold exciter cooler water supply. Corrective actions for this event include; mitigation of this problem in Unit 2, increasing the exciter-cooler outlet temperature by reducing cooling water flow, and development of appropriate guidance to initiate the necessary actions when exciter-cooler condensation could cause problems. Unit 1 safety equipment responded as required and the health and safety of the public and plant personnel were not impacted by this event.
266 | 2661999005 | 1999-05-14 | K1 | Steam Line Break Outside Containment | [9 empty] | X | [26 empty] | X | [8 empty] | Point Beach 1 | P | WE | PO | 100 | On May 14, 1999, with the Unit 1 operating at full power, Point Beach Nuclear Plant (PBNP) experienced a steam leak from the rupture of the shell side of the #4B feedwater heater. In response to this incident, the Unit 1 reactor was manually tripped and the steam to the #4B feedwater heater was secured. In response to a decreasing pressurizer level, a manual safety injection signal was initiated. The pressurizer level was restored with no need for actual ECCS injection. Plant systems operated as anticipated in response to the incident. There were no personnel injuries or significant incidental equipment damage. An inspection of the Unit 1 #4 feedwater heaters revealed shell wall thinning in the vicinity of the inlet nozzle deflector plates. The apparent cause of the rupture and wall thinning was a combination of steam impingement and flow accelerated corrosion. Inspection of the Unit 2 heaters revealed no comparable wall thinning. Following repair of the feedwater heaters, Unit 1 was returned to operation after nine days.
266 | 2662000001 | 2000-01-21 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Point Beach 1 | P | WE | PO | 41 | Unit 1 reactor and turbine were manually tripped from approximately 41% reactor power, at 0239 on January 21, 2000, in accordance with AOP-13A, "Circulating Water System Malfunction" upon the circulating water system pump bay water level having decrease d to -11 feet from reference. A rapid load reduction had been initiated in accordance with AOP-17A at 0210 with the pump bay level at -10.5 feet. Circulating water intake crib ice blockage was the cause for the level decrease. With three minor equipment performance exceptions, all equipment operated per design during and following the trip. Initial NRC event notifications were made in accordance with 10 CFR 50.72(b)(1) for a TS required shutdown. A subsequent notification was made for 10 CF R 50.72(b)(2)(ii) for the manual reactor protection system actuation. After inspections to verify structural integrity of the circulating water intake structure and testing to assure operability of the system with two circulating pump operation, Unit 1 was restarted on January 22, 2000, and returned to full power operations at 1930 on January 24, 2000.
266 | 2662000010 | 2000-10-27 | QR6 | Manual Reactor Trip | [45 empty] | Point Beach 1 | P | WE | PO | 100 | On October 27, 2000, the Point Beach Nuclear Plant Unit 1 reactor was manually tripped, while operating at full power, due to concerns for the safety and welfare of contract divers who were conducting underwater inspections of the common circulating water pump house. Unit 2 was shut down and defueled at the time. The divers were inspecting the Unit 2 piping from the condensers to the outlet seal well when communications with one of the two underwater divers was lost. When the second diver was initially unsuccessful in pulling the first diver from the pipe using his safety tether, the decision was made to manually trip the operating unit and secure the Unit 1 circulating water pumps. The divers were subsequently removed from the water, examined by medical personnel and determined to be unharmed. Following the unit trip, systems and equipment operated as expected. An incident investigation and post trip review was completed in accordance with procedures and the unit was returned to full power operation on October 30, 2000. A root cause evaluation of the event is underway.
266 | 2662003002 | 2003-07-15 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Point Beach 1 | P | WE | PO | 100 | On July 15, 2003, at approximately 1340 CDT, Point Beach Nuclear Plant (PBNP) Unit 1 experienced an automatic reactor trip from full power followed by a loss of Feedwater/Turbine Trip due to the reactor trip and main feedwater regulating valve closure. The cause of the trip was a failure of the 1G-06 Control Rod Drive Motor Generator set. The first out indication for the trip was an over temperature delta T signal. This trip also resulted in an automatic actuation of the Auxiliary Feedwater System. An operator was dispatched to the Unit 1 Rod Drive Room and identified smoke coming from the Voltage Regulator cabinets. Actions were taken to de-energize both Rod Drive Motor Generator (MG) Sets. Operators continued with follow-up actions to stabilize the unit in Mode 3. An event notification (EN# 39996) was made to the NRC at 1429 CDT. An investigation concluded that the voltage regulator failure was caused by the failure of a surge suppresser component in the power and feedback circuit. The 1G-06 MG set was repaired and a modification to the circuitry to improve voltage regulator reliability was completed in both the 1G-06 and 1G-07 motor generator sets. Systems and equipment necessary to mitigate the consequences of this equipment failure and subsequent reactor trip functioned as designed and the plant was maintained in a stable hot shutdown condition during the troubleshooting and repair of 1G-06. The safety and welfare of the public and the plant staff was not impacted by this event and the safety significance was minimal.
266 | 2662005008 | 2005-12-13 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [28 empty] | X | X |  |  |  |  | Point Beach 1 | P | WE | PO | 100 | This report describes the December 13, 2005, manual reactor trip due to a loss of main condenser vacuum caused by a mechanical failure of the operating circulating water pump. Major plant systems responded normally, including an auxiliary feedwater actuation due to the resultant low steam generator level. This condition was reported to the NRC via the Emergency Notification System on December 13, 2005 (EN# 42199).
266 | 2662007004 | 2007-06-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Point Beach 1 | P | WE | PO | 100 | On June 5, 2007, Unit 1 was operating in Mode 1 at 100% power. At 1512 hours water level in B steam generator was observed to be cycling between 70% and 78%. Abnormal Operating Procedure (AOP) 2B, Feedwater System Malfunction, was entered. An immediate in-plant inspection of main feedwater regulating valve 1 CS-476 B identified the positioner feedback arm was disconnected, with the connecting bolt nut located on the insulation covering the valve. Due to the inability to control steam generator level, operators initiated a manual reactor trip at 1517 hours and entered Emergency Operating Procedure (EOP) 0. An unexpected electrical lockout of 345 kV switchyard Bus Section 2 occurred. One moisture separator reheater drain valve failed to automatically shut and was manually shut. One turbine bearing oil lift pump failed to automatically start and was manually started. Reactor trip response was not negatively impacted by the unexpected conditions. After the reactor trip steam generator water levels were controlled using the feedwater regulating valve bypass valves. The plant was stabilized in Mode 3. A root cause evaluation is in progress and initial indications are that less than adequate maintenance procedure guidance caused the loss of the positioner arm nut. Vendor guidance had not been included in maintenance procedures. Changes to the maintenance procedure will be tracked via the site's corrective action program. A safety function review has determined there was no safety impact from this event because the position controllers have no safety function.
266 | 2662010002 | 2010-07-26 | QL7 | Degraded condenser vacuum | [45 empty] | Point Beach 1 | P | WE | PO | 19 | On 7/26/2010 at 2001 CDT, operations personnel initiated a manual reactor trip of Unit 1 from approximately 19% reactor power. Unit 1 was off-line to support main generator repair. The generator breaker had just been opened and steam load was transferred to the condenser steam dumps when condenser vacuum lowered. The reactor was manually tripped in accordance with plant procedures due to a lowering of main condenser vacuum prior to an automatic trip of the reactor. All safety systems functioned as expected. All control rods fully inserted. The lowering of condenser vacuum and subsequent manual reactor trip was caused by the improper application and adherence to human performance (HU) tool standards for self-checking. The failure to perform the self-check resulted in an incorrect status report for the turbine crossover steam dump motor operated valves, 1MOV-1 and 1MOV-2.
266 | 2662012004 | 2012-08-14 | QR6 | Manual Reactor Trip | [45 empty] | Point Beach 1 | P | WE | PO | 100 | On August 14, 2012 at 2031, a Point Beach Nuclear Plant (PBNP) Unit 1 manual reactor trip was actuated due to indications of a loss of load to the main turbine. At approximately 2031 alarms were received in the control room indicating reduced PBNP Unit 1 turbine first stage pressure and generator megawatts, indicative of a reduction in turbine load. Control rods were responding as designed by inserting into the reactor to reduce reactor power. Based on these indications, the Shift Manager directed that the reactor be shutdown by manually actuating the reactor protection system. No automatic reactor protection setpoints were exceeded and an automatic shutdown was not actuated or required. Based on troubleshooting, NextEra determined that the loss of turbine load was due to a failure of the main speed channel card in the electro-hydraulic (EH) system. The speed channel card was replaced. Pursuant to 10 CFR 50.73 (a)(2)(iv)(A), the event is reportable as an event or condition that resulted in manual actuation of the reactor protection system.
266 | 2662015002 | 2014-12-02 | QR6 | Manual Reactor Trip | [45 empty] | Point Beach 1 | P | WE | PO | 62 | On December 2, 2014, operators commenced a rapid power reduction of Unit 1 due to noted degradation of Unit 1B Condensate Pump. At 2050 on December 2, 2014, with Unit 1 in Mode 1 at 62% power, operators initiated a manual reactor trip of Unit 1 following securing of the Unit 1B Condensate Pump due to imminent failure. The Auxiliary Feedwater Pumps started as expected on low steam generator level experienced due to the reduced steam demand from the turbine trip in response to the reactor trip. All other plant systems functioned as required.<br /><br /> After the reactor trip, feedwater pump suction pressure remained low. The decision was made to secure both Main Steam Generator Feedwater Pumps. The Main Steam Generator Feedwater Pump A was manually secured. Prior to securing the Main Steam Generator Feedwater Pump B, it automatically tripped. All control rods fully inserted in the core due to the manual trip. There was no Emergency Core Cooling System actuation. Offsite power was maintained throughout the event. The Main Steam Generator Feedwater Pumps were available to be restarted due to the recovered feedwater suction pressure from the running Condensate Pump A.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) for both the manual RPS actuation and also for the automatic initiation of Auxiliary Feedwater.
266 | 2662015006 | 2015-11-28 | QR5 | Turbine Trip | [45 empty] | Point Beach 1 | P | WE | PO | 100 | On November 28, 2015 with Unit 1 in MODE 1 at full power, an automatic reactor trip was actuated as the result of a failure of the main generator automatic voltage regulator (AVR). All control rods fully inserted into the core. The Auxiliary Feedwater Pumps started as expected on low steam generator level. The Auxiliary Feedwater system was secured and decay heat removal was provided by the Condenser Steam Dumps utilizing the Main Feedwater system.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) for the automatic actuation of the reactor protection system and auxiliary feedwater system.
266 | 2662019001 | 2018-12-05 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Point Beach 1 | P | WE | PO | 100 | At 1539 on December 5, 2018, with Unit 1 operating in MODE 1 at full power, Operators removed Unit 1 from service by manually tripping the reactor when operators identified decaying main condenser vacuum conditions. All control rods fully inserted in the core due to the manual trip. The auxiliary feedwater system started as expected when a valid system actuation occurred after the reactor trip. There was no emergency core cooling system actuation and offsite power was maintained throughout the event. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) for both the manual RPS actuation and also for the automatic initiation of Auxiliary Feedwater.
266 | 2662021001 | 2021-07-31 | QP2 | Partial Loss of Feedwater Flow | [10 empty] | X | [29 empty] | X |  |  |  |  | Point Beach 1 | P | WE | PO | 100 | At 1646 on July 31, 2021, with Unit 1 operating in MODE 1 at full power, Operators removed Unit 1 from service by manually tripping the reactor when operators identified control board indications warranting prompt removal of the reactor from service. <br /><br /> All control rods fully inserted into the core due to the manual trip. The auxiliary feedwater system started as expected when a valid system actuation occurred after the reactor trip. There was no emergency core cooling system actuation and offsite power was maintained throughout the event. After the reactor trip, equipment anomalies occurred for which the operators effectively responded. <br /><br /> The cause of the condition requiring the manual reactor trip was a failure of the main steam generator feedwater pump B motor. Corrective actions included replacement of the main steam generator feedwater pump B motor and additional maintenance activities for anomalies identified during the reactor trip. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A).
269 | 2691988009 | 1988-07-05 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Oconee 1 | P | BW | PO | 100 | On July 5, 1988, at 0827 hours while operating at 100% full power, Unit 1 experienced an anticipatory reactor trip due to the loss of both Main Feedwater Pumps. The trip was initiated when an Instrument and Electrical (I&E) Technician was preparing to calibrate a Unit 1 Turbine Header Pressure transmitter. The I&E Technician used an instrument which was in the current-measuring mode rather than in the voltage-measuring mode to obtain a pressure transmitter output reading. Use of the current-measuring mode caused a false high pressure indication to be fed into the Integrated Control System (ICS). When the ICS began adjusting plant parameters, a valve in the secondary system failed to open. The combination of the personnel error and of the valve failure resulted in the Unit 1 trip. <br /><br />The immediate corrective action was to stabilize the unit at hot shutdown. The supplemental corrective actions included determining the causes of the unit trip, calibrating the turbine header pressure transmitters, providing disciplinary action to personnel involved, and repairing the valve that failed.
269 | 2691989001 | 1989-01-02 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 1 | P | BW | PO | 100 | On January 2, 1989, at 1523 hours, Unit 1 experienced a reactor trip from 100% full power. Investigation revealed that the cause of the trip was personnel error due to the tripping of two Reactor Protective System (RPS) channels during the performance of a RPS calibration procedure. A contributing cause to the event was procedural incompleteness. At the time of the trip, several Integrated Control System (ICS) stations, including the Feedwater Masters, were in manual control. This condition contributed to an overfeed situation in the steam generators causing a trip of the Main Feedwater Pumps. However, no overcooling condition was experienced from this overfeed due to the high decay heat load. The immediate corrective action was to stabilize the unit at hot shutdown conditions. Other significant corrective actions included: the replacement of failed components in the ICS BTU Limit and Emergency Feedwater circuitry, the counseling of Control Room Operators involved in the incident and the counseling and administering of disciplinary actions to I&E Technicians involved in the incident.
269 | 2691989002 | 1989-01-03 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Oconee 1 | P | BW | PO | 26 | On January 3, 1989 with Unit 1 at 26% power during power escalation after a previous trip, a fire occurred in 1TA switchgear. The switchgear fire resulted in the tripping of two Reactor Coolant Pumps (RCP) fed from the 1TA switchgear. An Unusual Event was declared. The Reactor was manually tripped and the two remaining RCPs were secured in preparation for using water to extinguish the switchgear fire. Cooldown rates specified by Technical Specifications were violated as a result of overfeeding the SGs while mitigating a RCS pressure increase. After the fire was distinguished, the RCS was not operated within the Thermal Shock Operating Region(TSOR). The root cause of the switchgear fire was Equipment Failure of unknown cause. The root cause of the vessel overcooling was Personnel Error. The root cause of the RCS not being operated in the TSOR region for the required time period is Management Deficiency. The root cause of the TS violation for exceeding the temperature differential between the pressurizer water and the spray fluid was Management Deficiency. The subsequent corrective actions were to provide additional guidance to the operators on entering the TSOR region and when it was necessary to do so. In addition, an analysis of the pressurizer spray nozzles steam generator and the reactor vessel was performed to evaluate the impact of the temperature transients throughout the event, adequate core subcooling margin was maintained and fuel integrity was not threatened. In addition, the primary system integrity was not breached and a release of radioactivity did not occur. The health and safety of the public were not affected.
269 | 2691989013 | 1989-08-10 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 1 | P | BW | PO | 40 | On August 10, 1989, at 1541 hours, Unit 1 tripped due to an inadvertently induced Reactor Protective System (RPS) actuation. At the time of the trip, Unit 1 was at 40% Full Power due to a previous power reduction to add oil to the 1A2 Reactor Coolant Pump motor. During this reduced power operation with three pumps, the steady state quadrant power tilt limit was exceeded in one core quadrant. As required by Technical Specifications, actions were initiated to both reduce the quadrant power tilt within limits and to reduce the overpower trip setpoints based on flux and flux/flow/imbalance. While performing the procedure to lower the overpower trip setpoints, an Instrumentation and Electrical technician incorrectly positioned a flow test circuit selector switch. Since another RPS channel was tripped per procedure, a reactor trip was initiated when the channel was returned to service with the incorrectly positioned switch. The root cause of this event is classified as Inappropriate Action, failure to follow procedure. The immediate corrective action was to stabilize the unit at hot shutdown conditions.
269 | 2691990013 | 1990-08-28 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Oconee 1 | P | BW | PO | 100 | On August 28, 1990, at 14:27:26 hours, while operating at 100% Power, the Unit 1 Reactor tripped due to high Reactor Coolant System (RCS) pressure. The unit was operating at a steady state prior to the trip. All four Reactor Protective System (RPS) Channels actuated on high RCS pressure due to the loss of the "B" Condensate Booster Pump (CBP) and the subsequent trip of the "A" Feedwater Pump. The Unit was brought safely to hot shutdown. The "B" CBP trip was caused by a "not open" signal from the pump's discharge valve 1C-84. Preventive maintenance had been completed on the valve less than five minutes prior to receiving the "not open" signal. The reason for the "not open" signal could not be determined, therefore, the root cause of this event is classified as "Unknown". Additionally, at the time of the "B" CBP trip, the "A" CBP was in standby and aligned for automatic start. The "A" CBP failed to start due to faulty bearing oil pressure instrumentation. Therefore, a contributing cause of this trip is "Equipment Failure/Malfunction" due to the malfunction of the bearing oil pressure instrumentation which prevented the standby CBP from starting.
269 | 2691991006 | 1991-05-16 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 1 | P | BW | PO | 100 | On May 16, 1991, at 1507 hours, Unit 1 tripped from 100 % Full Power, during a thunderstorm. The unit Events Recorder failed immediately prior to the trip, so it is unknown which trip signal was received first. Computer and Chart Recorder outputs indicated that an Instrument and Electrical (I&E) Technician may have erroneously opened the high pressure impulse line isolation valve instead of the low pressure valve on a non-safety related Reactor Coolant System flow transmitter following calibration. This may have caused a momentary dip in the pressure signal to four channels of Reactor Protective System flow instruments which share the impulse lines from the flow element. The pressure dip would have caused a trip on Flux/Flow/Imbalance. Alternatively, the trip could have occurred due to a switchyard transient. Operators took immediate action to stabilize the unit following the trip. The root cause is Unknown, Possible Inappropriate Action. Additional investigation performed during a subsequent Unit 1 refueling outage failed to clarify the cause.
269 | 2691991011 | 1991-10-02 | QR5 | Turbine Trip | [45 empty] | Oconee 1 | P | BW | PO | 73 | On October 2, 1991, Unit 1 reactor tripped from 73 percent full power on a Reactor Protective System turbine anticipatory trip signal due to a generator lockout. The lockout occurred when a protective relay circuit spuriously actuated. Investigation found that the relay circuitry was interrupted when either a terminal wire or a connector became loose. The root cause was assigned equipment failure in the 41MXa circuitry. Posttrip operator response stabilized the plant. After the trip, the Emergency Feedwater System was actuated due to low feedwater pump discharge pressure during a condensate-feedwater pressure oscillation. One main feedwater pump was manually secured. The second main feedwater pump tripped due to high pressure at the pump discharge. Corrective actions include tightening connections, evaluating the need for a preventive maintenance program on electrical connectors near vibrating equipment, and investigation into low demand feedwater oscillations.
269 | 2691992003 | 1992-05-07 | QR5 | Turbine Trip | [45 empty] | Oconee 1 | P | BW | PO | 100 | On May 7, 1992, at 1355 hours, Unit 1 reactor tripped from 100 percent full power on a Reactor Protective System turbine anticipatory trip signal due to a generator lockout. The lockout occurred when a protective relay circuit (41MXa) spuriously actuated. An investigation found that the control power to the relay circuitry was interrupted due to a loose connector pin. The root cause of the event was equipment failure in the 41MXa circuitry. Post-trip operator response stabilized the plant. Corrective action was to bypass the defective pin connector and hard wire to the appropriate terminal.
269 | 2691992004 | 1992-05-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Oconee 1 | P | BW | PO | 14 | On May 8, 1992 at 0342:23 hours, Unit 1 reactor tripped from 14 percent full power on a Reactor Protective System anticipatory trip signal due to low discharge pressure on the Main Feedwater Pump (MFDWP). The low discharge pressure occurred when operators were attempting to decrease a high hotwell level, which diverted flow from the suction of the MFDWP. After the trip, the Emergency Feedwater (EFDW) System actuated due to the low MFDWP discharge pressure. Once the MFDWP was verified to be operating, the EFDW Pumps were secured. The two root causes identified for this event were management deficiency, less than adequate training given and lack of a task specific procedure. Corrective actions include Operator training to inform Operators of the hotwell level oscillations, correct methods of reducing hotwell level, and development of a task specific procedure.
269 | 2691992015 | 1992-10-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Oconee 1 | P | BW | PO | 8 | On October 3, 1992 at 0810 hours, Unit 1 tripped from 7.5 percent power on a Reactor Protective System Main Feedwater Pump (MFDWP) low discharge pressure anticipatory trip signal. The trip occurred during an attempt to restore the 1B MFDWP to service following minor maintenance. When the 1B MFDWP suction valve was opened it tied the unpressurized train to the operating 1A MFDWP train causing a momentary discharge pressure drop. This condition was the result of the controlling procedure's step to fill the pump casing not identifying the need to pressurize the system. This deficiency led the Operating team to determine this step not applicable, as the steps to drain the pump had not been performed. Immediately upon opening the suction valve, various Control Room alarms indicated that the Unit had tripped. The root cause for this event was defective procedure.<br /><br /> A contributing cause for this event was design deficiency. Immediate corrective action included safely controlling the reactor shutdown. Further corrective action will include procedure changes.
269 | 2691993008 | 1993-08-23 | QR5 | Turbine Trip | [45 empty] | Oconee 1 | P | BW | PO | 100 | On August 23, 1993 at 1117 hours, with Unit 1 operating at 100% Full Power, a breaker was opened to allow for a peak inverse voltage test on the DC power system diodes. Upon opening the breaker, one of the unit's AC and DC Instrumentation and Control Power Panelboards was lost. The supply breaker input leads in the alternate power path were found rolled, causing the loss. The loss of these power panelboards resulted in the loss of the 125v DC Electro-Hydraulic Control circuit, tripping the Main Turbine and causing an anticipatory reactor trip. Main Feedwater system responded to the reactor trip; however, due to an inappropriately installed Output Limiter card in the Integrated Control System, Main Feedwater Pump speed was limited. This resulted in the initiation of the 'Dryout Protection' circuit, automatically starting both Motor Driven Emergency Feedwater Pumps. The root causes of this event are inappropriate Actions (Improper Action, Lack of Attention to Detail, and Failure to Follow Procedures) with contributing cause of Management Deficiency (Policy or Directive). Corrective actions include procedure changes, directive enhancements and personnel training.
269 | 2691993010 | 1993-11-03 | QL5 | Partial Closure of MSIVs | [45 empty] | Oconee 1 | P | BW | PO | 13 | On November 3, 1993, Unit 1 was operating at approximately 88% Full Power due to a feedwater heater drain pump being out of service. A manual reactor trip at 13% Full Power was initiated at 0100 hours after a plant transient. This transient resulted from a momentary circuit interruption due to a broken wire termination lug in the terminal box on Main Steam Stop Valve (MSV) 2 causing MSV 2 to partially close. The other three MSV's closed due to an interlock. The circuit interruption then cleared and MSV 2 began to open. The other three MSV's received a signal to reopens however, only MSV 1 reopened. Two MSV'S, associated with the A Main Steam line, remained closed due to stuck test solenoid valves. This condition resulted in only the B Steam Generator (SG) supplying steam to the Main Turbine and A SG isolated with its' Main Steam Relief Valves open. This ultimately lowered SG B pressure and water level to a point where the reactor was manually tripped by the Control Room Operator in accordance with Operations Management Procedures. Emergency Feedwater initiated to restore SG level and other systems responded as expected to stabilize the unit. The root cause of the event is Equipment Failure. Corrective actions include repairing the wire lug in the control cabinet, inspecting and cleaning the test solenoid valves, and evaluating the need to require a manual reactor trip on low SG pressure.
269 | 2691994002 | 1994-02-26 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Oconee 1 | P | BW | PO | 100 | On February 26, 1994, at 0657 hours, Oconee Unit 1 tripped on loss of both Main Feedwater (MFDW) pumps, while operating at 100% Full Power. An Instrument and Electrical Supervisor (IES) was removing power from an Integrated Control System power supply that had failed and was smoking. The IES removed a neutral wire that is daisy chained with other devices. When the neutral (daisy chained) terminal was loosened, the 1B Steam Generator high level circuits were de-energized. This condition resulted in a trip of the Main Turbine/Reactor, of both MFDW pumps, and the initiation of the Emergency Feedwater system. The Unit was stabilized at Hot Shutdown conditions. The root cause of the Unit trip was Inappropriate action; Improper action (Response chosen was proper but proper execution failed because; a human factors deficiency existed). A contributing cause is Equipment Failure. Corrective actions included replacing the defective power supply and removing the daisy chain associated with this circuit.
269 | 2691996004 | 1996-02-28 | QP3 | Loss of Condensate Flow | [45 empty] | Oconee 1 | P | BW | PO | 100 | On February 28, 1996, at approximately 2102 hours, while operating at 100% full power, Unit 1 experienced a Feedwater transient. Operators observed Reactor Coolant System pressure and average temperature increasing. The Integrated Control System (ICS) was taken to manual in an attempt to stabilize the unit during the transient. The Reactor tripped from approximately 95% full power at approximately 2103 hours due to the loss of both Main Feedwater pumps on low suction pressure. The Emergency Feedwater pumps started and maintained Steam Generator levels. The unit was stabilized at hot shutdown conditions. Investigations indicated the cause of the initiating Feedwater transient was a failed multiplier card in the ICS and the cause of the Reactor trip was a failed positioner relay on a valve in the Condensate system. The root cause of the event is an equipment failure as the result of a degraded subcomponent. Corrective actions included replacing the ICS multiplier card and the positioner relay on the Condensate system valve.
269 | 2691999005 | 1999-07-07 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Oconee 1 | P | BW | SU | 15 | On July 7, 1999, Oconee Unit 1 was in Mode 1 at 15 percent Full Power preparing to place the Turbine-Generator on line following a refueling outage. Operations secured and isolated the 1B Main Feedwater Pump (MFP) at 0110 hours. Due to misrouted instrument lines on non-safety related pump suction pressure switches, the 1A MFP tripped which caused the Reactor Protective System to trip the reactor on loss of feedwater. Operators stabilized the reactor in Mode 3. The root cause of the trip was inadequate procedural guidance such that personnel did not maintain adequate configuration control when disconnecting and reconnecting instrument lines during a modification in 1996. A contributing cause was deficient post-modification testing (PMT). The PMT did not identify that the pump suction pressure sensing lines were connected to the wrong pumps. Corrective actions include connecting the instrument lines to the correct pumps, and revisions to processes and procedures. The health and safety of the public was not compromised by this event.
269 | 2691999006 | 1999-08-18 | QR3 | Reactivity Control Imbalance | [45 empty] | Oconee 1 | P | BW | PO | 100 | On August 18, 1999, Oconee Unit 1 was in Mode 1 at 100 percent Full Power, when at approximately 1956 hours Unit 1 tripped. Operators stabilized the reactor in hot standby condition (mode 3). The unit post trip response was normal. The events recorder indicated that group 5 control rods had dropped into the core. Approximately three seconds later the Reactor tripped on a Reactor Protective System variable low pressure/temperature trip. There was no testing or maintenance being performed at the time of the trip. The root cause of the trip was equipment malfunction of the rod group 5 programmer. Corrective actions include replacing the programmer and sending the suspect programmer offsite for further testing and evaluation. The health and safety of the public was not compromised by this event.
269 | 2692001002 | 2001-09-12 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Oconee 1 | P | BW | PO | 100 | On September 12, 2001, Oconee Unit 1 was operating in Mode 1 at 100% power. At approximately 1813 hours Unit 1 tripped due to problems with the Isolated Phase Bus disconnect switch. During the plant trip, due to difficulties with the Z phase of the Isolated Phase Bus, an indication of a loss of power (as monitored on Z phase) actuated the 4kV switchgear undervoltage relays. This resulted in the loss of the Hotwell and Condensate Booster Pumps, which in turn caused the Main Feedwater (MFW) Pumps to trip. The Emergency Feedwater System actuated on loss of both Main Feedwater pumps. Steam Generator levels were correctly maintained by the Emergency Feedwater System. The unit post trip response was normal except for the MFW not being available. The plant was maintained in Mode 3. Investigation determined that the electrical generator disconnect switch on the "Z" phase had failed. Corrective actions to prevent recurrence were to replace the damaged disconnect switch and to improve the performance of the Isolated Phase Bus cooler. The health and safety of the public was not compromised by this event.
269 | 2692007001 | 2007-02-15 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Oconee 1 | P | BW | PO | 100 | On February 15, 2007 at 1654 hours, a breaker failure occurred in the Jocassee Hydro Station switchyard, causing one phase to fault to ground. The phase-to-ground fault was isolated at the Oconee 230 KV switchyard, but the resulting prolonged (less than 1 second) grid disturbance led to a trip of Oconee Units 1 and 2. A wiring design error on the loss-of-excitation relays caused a generator lock-out, turbine trip, and bus transfer from normal to startup sources on Oconee Units 1 and 2. Both reactors were subsequently tripped by the reactor coolant pump power monitors, which correctly sensed the voltage transient and resultant power sag. Incorrect settings on the auxiliary switch fast contacts of the normal main feeder bus breakers caused a slow bus transfer of 4160 volt loads on Oconee Unit 1, leading to a loss of normal feedwater flow. This necessitated cooldown to Mode 4, which was accomplished by procedure with emergency feedwater and atmospheric dump valves. Unit 2 secondary systems performed as expected. Appropriate post-trip reviews were performed and recovery actions completed per station procedures. Unit 2 was returned to power operation on February 18, 2007 and Unit 1 returned to service on February 23, 2007. This event is considered to have no significance with respect to the health and safety of the public.
269 | 2692010002 | 2010-08-07 | QR6 | Manual Reactor Trip | [45 empty] | Oconee 1 | P | BW | PO | 100 | On August 7, 2010, at 1130 hours, while operating at 100%, Oconee Nuclear Station (ONS) Unit 1 received statalarm 1SA-9-D2 (Reactor Coolant Pump Vibration High). Operators entered the applicable response procedure to reduce Unit 1 power. Vibration readings continued to increase. At 1451 hours, with power at 17%, Control Room Operators manually tripped Unit 1 when the indicated vibration readings reached procedural limits. The post-trip response was normal, with all major operating parameters remaining within expected limits. Operators took appropriate action to stabilize the unit in Mode 3 (hot standby). While the operators were controlling Pressurizer and Letdown Storage Tank Level per procedure, the standby 1B High Pressure Injection (HPI) pump auto started due to low Reactor Coolant Pump Seal Flow. Investigation revealed that a false high Reactor Coolant Pump (RCP) vibration indication occurred because the active power supply (Power Supply No. 2) had failed within the control module. Corrective Actions included replacement of the Unit 1 control module (Indikon 500-IM22) and positioning the RCP vibration equipment Power Supply Selector switches to "Auto". This event is considered to have no significance with respect to the health and safety of the public.
269 | 2692016001 | 2016-03-06 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | Oconee 1 | P | BW | PO | 100 | At 1512 on March 6, 2016, Oconee Nuclear Station (ONS) Unit 1 experienced a Reactor Trip, initiated by an electrical bushing failure on the Unit 1 Main Step-up Transformer that resulted in a transformer fire. The plant response to the trip was evaluated, and was found to be acceptable. The reactor trip is a RPS actuation and requires an LER per 10 CFR 50.73(a)(2)(iv)(A). <br /><br /> Due to the transformer fire a "Notification Of Unusual Event" was declared at 1520. The fire eventually led to a transformer overhead line failure that caused a switchyard bus lockout and the loss of one emergency power path for the site. The second emergency power path and multiple offsite sources remained operable during the event. The emergency classification was upgraded to an "Alert" condition at 1658, upon determining that the fire had an impact on safety related equipment.<br /><br /> The 4-hour notification related to this reactor trip was bounded by the notifications made for the Emergency Classifications described above (See Event Notification 51770). <br /><br /> Post trip conditions and Emergency event conditions were controlled and maintained within the allowances of Technical Specifications with no personnel injuries or challenges to other safety system actuations. The transformer deluge system activation along with the response of onsite and offsite fire teams promptly contained the fire.
269 | 2692018001 | 2018-04-13 | QR6 | Manual Reactor Trip | [45 empty] | Oconee 1 | P | BW | PO | 24 | On April 13, 2018 at 0227 hours, Oconee Unit 1 was manually tripped from 24% power. At the time of the trip, Unit 1 was in the process of a planned shutdown to repair a rod control cable connector and recover a dropped rod. The turbine was offline. While reducing power, problems were encountered such that power would no longer decrease. The main feedwater control valves (MFCVs) would not respond to automatic or manual control to close the MFCVs. An investigation revealed that the MFCVs would not go fully closed with a full closed demand signal from the Integrated Control System (ICS). The valves were subsequently tested and their electric to pneumatic (E/P) converters were found to be failed on the low end of calibration. The E/P converters failing in this manner caused the MFCVs to not go full closed despite the full closed demand signal from ICS. <br /><br /> This event was reported as a 4-hour notification to the NRC on April 13, 2018, in Event Notification (EN) number 53329 under 10 CFR 50.72(b)(2)(iv)(B) - Reactor Protection System (RPS) Actuation - Critical. The event is also reportable under 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the RPS.
269 | 2692018002 | 2018-10-19 | QL7 | Degraded condenser vacuum | [45 empty] | Oconee 1 | P | BW | PO | 25 | On October 19, 2018, Oconee Unit 1 was in the process of shutting down to begin a scheduled refueling outage when auxiliary steam control valve 1AS-10 failed to open. At the time this occurred Unit 1 was at approximately 19% Rated Thermal Power (RTP) with the turbine-generator online. The failure of 1AS-10 caused a loss of Steam Seal Header (SSH) pressure which resulted in a decrease in condenser vacuum and a subsequent automatic turbine trip. Operators anticipated a loss of the operating Main Feedwater (MFW) pump and manually started both Motor Driven Emergency Feedwater (EFW) pumps (MDEFWPs). The cooler EFW flow entering both steam generators led to a 5.8% increase in reactor power. Operators manually tripped the reactor at approximately 25% RTP based on approaching the automatic trip of the last MFW pump at 19" Hg condenser vacuum which would have resulted in an automatic reactor trip.<br /><br /> The event was reported on October 19, 2018, via NRC Event Number 53677. This Licensee Event Report (LER) is required pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a valid actuation of the Reactor Protection System (RPS) and EFW. <br /><br /> 1AS-10 failed to open because of age-related degradation of the positioner relay. It was determined that the Preventive Maintenance (PM) scope was inadequate. The positioner relay was replaced to correct the failure.
270 | 2701987001 | 1987-01-18 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 20 | On January 18, 1987, at 2024 hours, the Oconee Unit 2 main turbine tripped at 1500 RPM due to low oil pressure. After main turbine oil pressure returned to acceptable levels, the turbine was reset and unit startup was continued using the same copy of the TurbineGenerator Startup procedure in use at the time of the turbine trip. The main turbine trip contact buffers in the reactor protective system cabinets were not reset per this procedure following the main turbine trip at 2024 hours. <br /><br />At 2223 hours during restart, power reached 20%, the setpoint for the turbine/generator to reactor anticipatory trip circuit, and the unit tripped as designed. Immediate corrective action was to stabilize the unit at hot shutdown conditions and determine the cause of the trip. <br /><br /> The root cause of this event was personnel error as the anticipatory trip contact buffers were not reset as required by procedure. Contributory errors were the lack of direction for re-use of a procedure without prescribing acceptable methodology. <br /><br />The Reactor Protective System reacted in accordance with design features, no Technical Specification limits were exceeded, and there was no release of radioactivity. Therefore, the health and safety of the public were not affected.
270 | 2701987002 | 1987-03-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Oconee 2 | P | BW | PO | 96 | On March 26, 1987 at 2333 hours, Unit 2 tripped from 96% Full Power on high Reactor Coolant System (RCS) pressure. An open connection in the "A" loop BTU limit section of the Integrated Control System (ICS) caused the ICS to respond by decreasing feedwater flow to the Steam Generators. This decrease in feedwater flow caused a decrease in the heat transfer rate, leading to an increase in RCS temperature and pressure. The unit tripped on high RCS pressure. <br /><br />The immediate corrective action was to stabilize the unit at hot shutdown conditions. The supplemental corrective action was to investigate the cause of the transient. <br /><br /> The root cause of this event was an intermittent poor connection in the ICS BTU limit loop "A" circuitry. <br /><br />No Technical Specification limits were exceeded, and there was no release of radioactivity. As such, the health and safety of the public was not affected.
270 | 2701987004 | 1987-04-20 | QP5 | Excessive Feedwater Flow | [45 empty] | Oconee 2 | P | BW | PO | 87 | On April 20, 1987 at 0533 hours, Unit 2 tripped from 87% Full Power on high Steam Generator level. This trip was due to a failed module in the "A" loop BTU limit section of the Integrated Control System (ICS). The ICS responded by decreasing Feedwater (FDW) flow to the "2A" Once Through Steam Generator (OTSG) and increasing flow to the "2B" OTSG. When the "2B" OTSG level reached 96% on the operating range level indication, the Main Feedwater Pumps (MFDWP) and the Main Turbine (MT) tripped. The reactor tripped on the Turbine/Reactor anticipatory trip. <br /><br />The immediate corrective action was to stabilize the unit at hot shutdown conditions. The supplemental corrective actions included investigating the cause of the transient, identifying the failed ICS multiplier module, and replacing it. <br /><br />The root cause of this event was the failure of the ICS multiplier module in the ICS BTU limit loop "A" circuitry. <br /><br />No technical specification limits were exceeded, and there was no release of radioactivity. As such, the health and safety of the public was not affected.
270 | 2701988003 | 1988-08-26 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 100 | On August 26, 1988, at 1557 hours while operating at 100% Reactor Power, the Unit 2 Main Turbine (MT) tripped resulting in an anticipatory Reactor trip. The MT trip was initiated by a false high water level indi-cation in the "2A2" Moisture Separator Reheater (MSRH). The false high water level trip indication occurred because conductors associated with the "2A2" MSRH high water level trip switch "short-circuited" against the switch housing. The "short circuit" occurred because brittle insulation separated from the conductors, allowing them to make contact with the switch housing. <br /><br />The immediate corrective action was to stabilize the unit at hot shutdown. The supplemental corrective actions included determining the cause of the unit trip and repairing the degraded conductors. The root cause of this unit trip was the shorted circuit in the MSRH high level trip switch, which was caused by the failure of the conductor insulation in the circuit.
270 | 2701989002 | 1989-02-03 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 100 | On February 3, 1989 at 1545 hours while operating at 100% Reactor Power, the Unit 2 Main Turbine (MT) tripped resulting in an anticipatory Reactor trip. The MT trip was initiated by a loss of 125 VDC power to the Electro Hydraulic Control (EHC) system. The loss of DC power occurred due to the incorrect wiring of a circuit during implementation of a Nuclear Station Modification (NSM). This combined with a pre-existing ground on a conductor supplying power from the EHC to the "2A2" Moisture Separator Reheater high water level switch, caused a loss of 125 VDC power to the EHC. The immediate corrective action was to stabilize the unit at hot shutdown. Supplemental corrective actions included determining the cause of the trip, correcting the wiring problem, and repairing the degraded conductor. The root causes of this trip were: a management deficiency of not properly implementing the independent verification program and of assigning an unqualified person to perform a task; and an equipment failure.
270 | 2701989003 | 1989-02-05 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 100 | On February 5, 1989, at 0023 hours while operating at 100% full power, the Unit 2 Main Turbine (MT) tripped resulting in an anticipatory reactor trip. The MT tripped immediately following the performance of step 2.2 of procedure PT/2/B/290/05 (Secondary Systems Protection Test), which placed the Master Trip Solenoid test lever in the trip "A" position. A work request was written to investigate the Master Trip Solenoid test switch. However, investigation into the incident did not identify the cause of the MT trip. The immediate corrective action was to stabilize the unit at hot shutdown. The supplemental corrective actions included troubleshooting the Electro Hydraulic Control System and replacing the Master Trip Solenoid test switch as a precautionary measure. The root cause of the unit trip could not be determined because the scenario was not repeatable. Therefore, this incident is classified as unknown.
270 | 2701989004 | 1989-04-03 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Oconee 2 | P | BW | PO | 100 | On April 3, 1989, at 1007 hours, Oconee Unit 2 tripped from 100% Full Power. Plant response to the trip was normal, with no radiological releases or Engineered Safeguards actuations. The trip resulted from a falling object striking the Condensate Booster Pump (CBP) Emergency Low Suction Pressure pressure switch. The impact shifted the instrument setpoint resulting in a trip of CBPs followed by Main Feedwater Pump trip and anticipatory Reactor trip. Emergency Feedwater actuated and maintained decay heat removal. The root cause is MANAGEMENT DEFICIENCY, poor housekeeping.
270 | 2701992004 | 1992-10-19 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Oconee 2 | P | BW | PO | 100 | On October 19, 1992, at 2121 hours, Oconee Unit 2 experienced a Loss of Offsite Power, a generator load rejection, and a trip from 100 % Full Power. A battery charger was placed in service without a connected battery. it produced excessive voltages which caused a series of spurious breaker failure relay actuations, locking out both buses in the 230 KV Switchyard. The relays had been identified as susceptible to spurious operation due to excessive voltages in 1980 but were not modified. Also, during recovery actions, shutdown of one emergency generator, after the emergency start signal had been reset, resulted in the unanticipated trip of the operating emergency generator leading to a second loss of power on Oconee Unit 2. The root cause of the event was determined to be Management Deficiency, (Deficient Program, less than adequate corrective action). Corrective actions included several modifications, procedure changes, and equipment reviews.
270 | 2701993005 | 1993-08-25 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 100 | On August 25, 1993, at 2330 hours, Unit 2 reactor tripped from 100% full power on a Reactor Protective System turbine anticipatory trip signal due to a generator lockout following an indicated loss of load. The loss of load indication occurred when an operator pulled generator metering, relay and regulating equipment drawers to the disconnect position on the Unit 2 generator instead of Unit 1. The operator was supposed to perform the work in preparation for returning Unit 1 generator to service. Post trip operator response stabilized the plant. The root cause of the event is Inappropriate Action (Improper action; the action chosen was incorrect because of a lack of attention to detail). Corrective actions include reemphasizing the Stop, Think, Act, Review (STAR) process, adding Unit specific labeling and repairing locks on the equipment.
270 | 2701993007 | 1993-10-24 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 2 | P | BW | PO | 100 | On October 24, 1993, at 0634 hours, Unit 2 tripped from 100 % full power on a flux/flow/imbalance trip of the Reactor Protective System (RPS). The flux/flow/imbalance trip occurred when transmitters monitoring flow in both loops of the Reactor Coolant System (RCS) simultaneously indicated that flow spiked low. Post trip operator response stabilized the unit. An investigation revealed that the method used to calibrate the RCS flow inputs to the RPS flux/flow/imbalance trip introduced an error which reduced the operating margin associated with the trip function. Also, it was found that an error was made while performing the last completed calibration procedure, which further reduced the margin. Therefore, the root causes of this event are considered to be Deficient Procedure (technical deficiency) and an Inappropriate Action (failure to follow procedure, improperly followed the correct procedure) in conjunction with an indicated low RCS flow spike. Corrective actions included reanalyzing core operating limit calculations to increase the operating margin, revising the calibration procedure, and reviewing this event with personnel involved in the procedure error.
270 | 2701994002 | 1994-04-06 | QP2 | Partial Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Oconee 2 | P | BW | PO | 54 | On April 6, 1994, Unit 2 was operating at 100% Full Power (FP) when the 2B Main Feedwater Pump (MFDWP) tripped on low oil pressure at 1047 hours. The Integrated-Control System (ICS) automatically ran back reactor power to approximately 54% FP as designed. Automatic control of the 2A MFDWP was erratic, resulting in feedwater oscillations. As operators were taking ICS stations to manual to control the feedwater swings, the 2A MFDWP tripped on high discharge pressure. This resulted in an Anticipatory Reactor Trip at 1108 hours, due to the loss of both MFDWPs. The response of operators and .automatic systems brought the unit to stable hot shutdown conditions. An investigation into the cause of the 2A and 2B MFDWP trips revealed a set screw on the 2A MFDWP's Motor Gear Unit was loose and the Main Shaft Oil Pump gear's on 2B MFDWP had failed. The root cause was Equipment Failure with a contributing cause of Defective Procedure (technical deficiency). Corrective actions included revising the MFDWP's preventive maintenance procedure, replacing the set screw, and the repair of 2B MFDWP.
270 | 2701994005 | 1994-12-08 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Oconee 2 | P | BW | PO | 100 | On December 8, 1994, at 1425 hours, Unit 2 Reactor tripped from 100% full power. The Reactor tripped when a breaker that supplies 'auto' power to the Integrated Control System (ICS) tripped. The loss of 'auto' power caused a relay to deenergize (by design) that introduced a false high Steam Generator (S/G) level that tripped the Main Feedwater Pumps and the Main Turbine. The trip of the Main Feedwater Pumps and Main Turbine resulted in an anticipatory trip of the Reactor Protective System. Emergency Feedwater automatically actuated with all three pumps starting and feeding the S/Gs as expected. The Unit was then stabilized at Hot Shutdown condition with decay heat removal via the S/Gs. No major problems were noted as a result of the trip. Investigation revealed a loose lug on the load side of the breaker that generated sufficient heat to trip the breaker on thermal overload. The root cause of the event is equipment failure possibly due to thermal cycling. Corrective actions included the changeout of the power supply breaker and review of breaker preventive maintenance program.
270 | 2701995002 | 1995-04-14 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 100 | On April 14, 1995, at 09:59:24 hours, Unit 2 reactor tripped from 100% full power on a Reactor Protective System turbine anticipatory trip signal due to a generator lockout. A generator protective relay circuit actuated due to a fault that occurred on the system grid, followed by a breaker failure located in an offsite substation. Post trip response was normal. An investigation revealed that a timer on the protective relay had been incorrectly set for .8 seconds instead of 10 to 60 seconds as recommended by the manufacturer. The root cause of this event was determined to be Design Deficiency, functional design deficiency, electrical. Corrective action includes the design and implementation of a modification for all three units to replace the timer on the protective relay and setting the timer between 10 and 60 seconds.
270 | 2701996004 | 1996-09-24 | K1 | Steam Line Break Outside Containment | [9 empty] | X | [26 empty] | X | [8 empty] | Oconee 2 | P | BW | PO | 60 | On September 24, 1996, at approximately 1642 hours, while operating at 60% full power, Unit 2 experienced a drain pipe rupture on the secondary side of the plant. At 1643 hours, the resulting steam release from the pipe rupture was isolated by closing the Main Steam supply block valves to the Second Stage Reheat system and manually tripping the reactor. The pipe rupture was due to a water hammer which was a result of the following three root causes: 1) A lack of a general understanding of the potential consequences of the water hammers experienced in the past resulted in untimely development and implementation of modifications necessary to prevent water hammers, 2) Failure to revise the Moisture Separator Reheater procedure to provide the information and instructions necessary to successfully perform the required task, and 3) A human error of inadequate verbal communication resulted in incomplete and inaccurate instructions being provided to perform the required task. Planned corrective actions include installation of modifications, procedure changes, and personnel training to prevent recurrence of water hammer events.
270 | 2701997002 | 1997-07-06 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 100 | On July 6, 1997 at 0652 hours, Oconee Unit 2 was operating at 100% full power when a system grid disturbance initiated a Generator protective relay actuation that resulted in all four reactor coolant pump/power monitor channels of the Reactor Protective System tripping. The operators placed the Unit in a stable, hot shutdown condition. The grid disturbance was created by a switching problem at Jocassee Hydro Station, located approximately 15 miles away from Oconee. The voltage regulator on Unit 2 did not respond as expected to the grid disturbance and maintain bus voltage within acceptable ranges. The root cause of this event is a manufacturing deficiency, inadequate installation instructions. Corrective action included calibration of the voltage regulator. This event is not considered to have an impact on the health and safety of the public.
270 | 2701998003 | 1998-06-03 | QL7 | Degraded condenser vacuum | [45 empty] | Oconee 2 | P | BW | PO | 83 | On June 3, 1998, Oconee Unit 2 was returning to full power following a refueling outage. Units 1 and 3 were at 100% full power. At 1609 hours, Unit 2 automatically tripped from approximately 83% full power while holding for repair of a heater drain pump. The Reactor trip occurred on an anticipatory trip signal when Main Condenser vacuum decreased below the Main Turbine trip set point. Repair work on an Auxiliary Steam (AS) System de-superheater created an air in-leakage pathway to the Condenser. The de-superheater was being repaired as part of a planned AS header outage for all three units. The work package for the repair of the de- superheater had been cleared for work and released to the field without proper isolation. After the trip, the vacuum leak was identified, isolated, and vacuum was restored to normal values. The plant's post trip response was normal. The root cause of this event is inadequate work clearance process. A contributing cause is an improper action. Corrective actions include revising the method for preparing, planning, reviewing, and approving block tagouts (including non-outage block tagouts).
270 | 2701998007 | 1998-11-03 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 100 | On November 3, 1998, at approximately 1015 hours, Unit 2 tripped from 100 percent power on an anticipatory reactor trip due to a trip of the main turbine-generator (MT) and both main feedwater (MFW) pumps which was initiated by a spurious high steam generator (SG) level. Immediately prior to the reactor trip, vital 125 VDC positive to ground indications had been received. Actual SG levels remained at normal operating levels until after the trip. All three emergency feedwater pumps started and maintained post-trip SG levels per design. The unit was stabilized at Hot Shutdown per procedure. All systems operated as designed to maintain the unit within acceptable limits. Investigations determined that the MT and MFW pump trip occurred when a metal nail used in repair of fire barrier penetrations grounded the cable for the 125 VDC positive supply conductor. Immediately thereafter, the signal conductor for the MT and MFW pump trip circuit also grounded thereby tripping the MT and MFW pump. Nails are used to hold fiberboard over the outside of fire barrier sealant material for repairs. Corrective actions to prevent recurrence include planned modifications to the electrical fire barrier penetration repair methodology, and improved training and supervision. This event is considered of no significance to public health and safety.
270 | 2701999001 | 1999-02-28 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 98 | On February 28, 1999, at 1544 hours, Unit 2 was at 100% power. A small Reactor transient occurred when Electro Hydraulic Control (EHC) System normal electrical power was lost and a swap over to backup power occurred. The loss of EHC system normal electrical power was due to the failure of a fuse. Reactor power stabilized at 98% following the transfer of EHC electrical power. At approximately 2040 hours, during troubleshooting and root cause investigation, there was a spurious reapplication of power through the failed fuse. The reaction of the EHC system caused Unit 2 Turbine control valves to close and the Reactor tripped on high Reactor Coolant System pressure. All primary and secondary parameters responded as expected and operations personnel appropriately stabilized the unit at hot shutdown conditions. The root cause of the reactor trip is equipment failure. The fuse failed due to an internal open circuit fault at one end of the fuse rather than an overcurrent condition. A detailed laboratory analysis of the failed fuse is being performed. Corrective action includes replacing the failed fuse, having the failed fuse analyzed, and revising maintenance processes as required. This event is considered of no significance with respect to the health and safety of the public.
270 | 2701999002 | 1999-06-19 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 66 | On June 19, 1999, Oconee Unit 2 was operating in Mode 1 at 66 percent Full Power. At 1015:14 hours, the Unit 2 Reactor tripped on an anticipatory trip following a Main Turbine trip. Operators took immediate action to stabilize the unit in Mode 3. No significant problems were encountered. The trip was due to a spurious trip signal caused by two concurrent electrical ground faults in the Moisture Separator Reheater high level switches. The root cause of one ground was a manufacturing deficiency that allowed a wire to chafe against a sharp edge. The second ground was due to missing adhesive that allowed a Mercury switch vial to move in its retaining bracket until a conductor contacted the metal bracket. The investigation determined the adhesive may have degraded over time. Corrective actions included inspecting all similar switches, moving wires away from the sharp edge, and installing new adhesive, as necessary. The switch manufacturer is being consulted for additional possible corrective actions. The health and safety of the public was not compromised by this event.
270 | 2701999005 | 1999-12-21 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Oconee 2 | P | BW | PO | 100 | On December 21, 1999, Oconee Unit 2 was in Mode 1 at 100 percent Full Power, when at approximately 1852 hours Unit 2 tripped due to spurious closure of the Math Turbine Intercept and Control Valves The unit post trip response was normal. The plant tripped on a valid trip signal. The root cause investigation for the closing of the Main Turbine Intercept and Control valves found no specific problems, because of an intermittent ground. Corrective actions included replacing two suspect Power Load Unbalance (PLU) circuit cards. On December 24, 1999, Oconee Unit 2 had returned to mode 1 at 77 percent power, when at approximately 0207 hours, Unit 2 tripped due to spurious closure of the Main Turbine Intercept and Control Valves. The unit post trip response was normal. The root cause of the Main Turbine Intercept valves closing was an intermittent short circuit fault to the Linear Variable Differential Transformer (LVDT) signal cable for Intercept Valve 2MS-120. The corrective action was to repair the cable. This root cause was also determined to be the cause of the closure of the Main Turbine valves on December 21, 1999, causing the Unit 2 trip. The health and safety of the public was not compromised by this event.
270 | 2701999005 | 1999-12-24 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 100 | On December 21, 1999, Oconee Unit 2 was in Mode 1 at 100 percent Full Power, when at approximately 1852 hours Unit 2 tripped due to spurious closure of the Math Turbine Intercept and Control Valves The unit post trip response was normal. The plant tripped on a valid trip signal. The root cause investigation for the closing of the Main Turbine Intercept and Control valves found no specific problems, because of an intermittent ground. Corrective actions included replacing two suspect Power Load Unbalance (PLU) circuit cards. On December 24, 1999, Oconee Unit 2 had returned to mode 1 at 77 percent power, when at approximately 0207 hours, Unit 2 tripped due to spurious closure of the Main Turbine Intercept and Control Valves. The unit post trip response was normal. The root cause of the Main Turbine Intercept valves closing was an intermittent short circuit fault to the Linear Variable Differential Transformer (LVDT) signal cable for Intercept Valve 2MS-120. The corrective action was to repair the cable. This root cause was also determined to be the cause of the closure of the Main Turbine valves on December 21, 1999, causing the Unit 2 trip. The health and safety of the public was not compromised by this event.
270 | 2702006001 | 2006-04-12 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Oconee 2 | P | BW | PO | 100 | On April 12, 2006, while operating at 100% in Mode 1, Oconee Nuclear Station Unit 2 experienced a reactor trip. The post trip response was normal, with all major operating parameters remaining within expected limits. Operators took appropriate action to stabilize the unit in Mode 3. The cause of the event was determined to be a trip of a reactor coolant pump during testing of a pump power transducer. The pump trip occurred due to a loss of isolation between the power transducer being tested and the operating circuit while connected to the test equipment. Corrective actions address changes to restrict use of this procedure on critical equipment while operating. This event is considered to have no significance with respect to the health and safety of the public.
270 | 2692007001 | 2007-02-15 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Oconee 2 | P | BW | PO | 100 | On February 15, 2007 at 1654 hours, a breaker failure occurred in the Jocassee Hydro Station switchyard, causing one phase to fault to ground. The phase-to-ground fault was isolated at the Oconee 230 KV switchyard, but the resulting prolonged (less than 1 second) grid disturbance led to a trip of Oconee Units 1 and 2. A wiring design error on the loss-of-excitation relays caused a generator lock-out, turbine trip, and bus transfer from normal to startup sources on Oconee Units 1 and 2. Both reactors were subsequently tripped by the reactor coolant pump power monitors, which correctly sensed the voltage transient and resultant power sag. Incorrect settings on the auxiliary switch fast contacts of the normal main feeder bus breakers caused a slow bus transfer of 4160 volt loads on Oconee Unit 1, leading to a loss of normal feedwater flow. This necessitated cooldown to Mode 4, which was accomplished by procedure with emergency feedwater and atmospheric dump valves. Unit 2 secondary systems performed as expected. Appropriate post-trip reviews were performed and recovery actions completed per station procedures. Unit 2 was returned to power operation on February 18, 2007 and Unit 1 returned to service on February 23, 2007. This event is considered to have no significance with respect to the health and safety of the public.
270 | 2702008001 | 2008-03-31 | QR5 | Turbine Trip | [45 empty] | Oconee 2 | P | BW | PO | 100 | At 1352 hours, on March 31, 2008, while operating at 100%, Oconee Nuclear Station, Unit 2 experienced an indicated loss of condenser [SG] vacuum. The most probable cause for the loss of condenser vacuum indication was a combination of obstruction (corrosion or foreign material) in the impulse line to the vacuum instrumentation and leakage of the 23 condenser pressure isolation valve(s). The obstruction and leakage produced an indication of loss of vacuum that resulted in the trip of Unit 2 main turbine. The trip of the main turbine caused the Unit 2 reactor to trip. The post trip response was normal, with all major operating parameters remaining within expected limits. Operators took appropriate action to stabilize the unit in Mode 3. Corrective actions address changes to procedures to restrict maintenance activities on vacuum and absolute pressure instruments while operating and also prevent the usage of B-6P4T Swagelok plug valve(s) for isolation in this particular application. This event is considered to have no significance with respect to the health and safety of the public.
270 | 2702021005 | 2021-12-10 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 2 | P | BW | PO | 73 | On December 10, 2021 at 0049 EST, with Unit 2 in MODE 1 at 73% power, an automatic reactor trip occurred. At the time of the trip, Unit 2 was in the process of power ascension following a refueling outage. The reactor trip was uncomplicated. Post-trip plant response was normal and plant conditions were controlled and maintained within the allowances of Technical Specifications with no safety system actuations. <br /><br /> Subsequent analysis determined the reactor tripped due to the 2B Reactor Protective System (RPS) channel being placed in “trip” via the Manual Trip Keyswitch during the performance of planned maintenance per procedure IP/2/A/0315/018B (TXS RPS Ch B Statalarm and Event Recorder Test and Manual Trip Keyswitch Test), and a concurrent momentary trip signal being received in the 2A RPS channel, thus satisfying the 2/4 trip logic. The momentary trip signal received in the 2A RPS Channel was determined to be caused by a short duration signal spike (200ms) on the 2NI-5 detector causing a Flux/Flow/Imbalance function trip in RPS Channel 2A. <br /><br /> This event was reported to the NRC on December 10, 2021, in Event Notification (EN) number 55638, as an 8-hour notification under 10 CFR 50.72(b)(2)(iv)(B) - Reactor Protection System (RPS) Actuation – Critical (Automatic Reactor Trip). The event is also reportable under 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the RPS.
271 | 2711987005 | 1987-08-07 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Vermont Yankee | B | GE | PO | 7 | On 8/7/87 at 2159, in the process of shutting down for a scheduled refueling outage with the Main Generator off-line and Turbine in coast-down, a Reactor SCRAM occurred as a result of reactor vessel high pressure. The reactor vessel pressure transient was the result of a malfunction in the Turbine Control System (JJ)* that caused the by-pass valves to close. <br /><br />Prior to this event, pressure control was being performed by the Electrical Pressure Regulator (EPR). Soon after switching to the Mechanical Pressure Regulator (MPR) for control (2155), the by-pass valves shut resulting in a Reactor SCRAM from high reactor vessel pressure. <br /><br />The inability of the MPR to control pressure was caused by a clogged sensing line valve (JJ)* which prevented the MPR from responding to pressure changes. <br /><br />To correct the control system problem, the sensing line valve will be replaced. <br /><br />*Energy Industry Identification System (EIIS) System Component Identifier
271 | 2711987015 | 1987-10-03 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Vermont Yankee | B | GE | PO | 18 | On 10/03/87 at 1356, with reactor at 18% power, while bringing the Turbine up to speed in preparation for placing the generator in service, a SCRAM occurred as a result of a turbine control valves' rapid opening and subsequent fast closure. The turbine control valves were not operating properly due to a suspected problem in the Turbine Control Oil System (TG*). <br /><br />When oil pressure control switched from the Auxiliary Oil Pump to the Shaft Driven Oil Pump, an oil pressure transient caused the control valves to quickly open to the load limiter position. The subsequent short-term increase in steam flow through the Turbine was equal to approximately 50%, as determined by turbine first stage pressure. This rapid increase in turbine first stage pressure, above 30%, removed the automatic SCRAM bypass for the Turbine Control Valve Fast-Closure logic. Since the Control Valve Fast-Closure SCRAM signal cannot be reset (armed) until oil pressure is being supplied by the shaft driven pump, this previously bypassed SCRAM signal caused the reactor to SCRAM at approximately 1356. <br /><br /> Vermont Yankee's investigation revealed that the pressure transient was caused by a flow imbalance in the Turbine Control Oil System. The turbine startup procedure was revised to ensure that the appropriate system balance is established during turbine startup. No similar events have been reported in the last 5 years. <br /><br />*Energy Industry Identification System EIIS Identifier.
271 | 2711987017 | 1987-11-08 | QP5 | Excessive Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Vermont Yankee | B | GE | PO | 88 | On 11-8-87, at 0124, during a plant power reduction from 100% to 80% in preparation for surveillance testing, the two Feedwater Regulating valves (EIIS=FCV) failed to throttle closed as required by decreased Feedwater flow demand. This was due to a mechanical restriction of the manual operators on these valves that was added approximately three weeks earlier to temporarily repair the operators. When installed, it was not recognized that future full stroke valve motion would be restricted by the repair. <br /><br />The failure of these valves to close as required created a high Reactor Water Level and subsequent Turbine trip and Reactor SCRAM at 0126. All automatic actions occurred as required. All systems were stabilized and returned to normal within two minutes. <br /><br />An unexpected Primary Containment Isolation System (PCIS) actuation of the Main Steam Isolation Valves (MSIV's) occurred during operator SCRAM response as a result of the Reactor Mode Switch being moved from RUN. This switch movement was done prior to Main Steam flow instrumentation resetting from decreased steam flow from the SCRAM. PCIS isolations were promptly reset. <br /><br />Valve operator restrictions were removed and repaired and full stroke of the valves was verified. Plant personnel will be further trained in the proper operation of these valves. A procedure change has been made to preclude the inadvertent Reactor Mode Switch initiated PCIS isolation.
271 | 2711988007 | 1988-06-18 | QP5 | Excessive Feedwater Flow | [45 empty] | Vermont Yankee | B | GE | PO | 100 | On 6-18-88 with the Reactor at 100% power in three element control a Reactor SCRAM occurred due to a turbine trip on High Reactor Water Level at 1737 hours. The High Reactor Water Level was caused by a failed component in the feedwater flow integrator (EIIS=CTR). The Feedwater Control System (JB) responded to the failure by increasing feedwater flow to maximum thus resulting in the high water level. <br /><br />The reactor water level reached the high setpoint level in approximately 20 seconds and tripped the turbine before operators could reduce feedwater flow. Following the scram operators secured the C Feedwater Pump and returned Reactor level to normal. <br /><br />An investigation determined that the cause of the failure was a failed bearing in the integrator counter drive motor. The failed bearing created a short circuit between the armature and motor windings. This short circuit resulted in a false zero flow indication to the flow controller resulting in maximum flow. <br /><br />The failed feedwater integrator was replaced with a spare. VY personnel are investigating the possible removal of the integrator from the feedwater control system with General Electric Company. The root cause of the failure was determined to be end of life.
271 | 2711988008 | 1988-06-24 | QR5 | Turbine Trip | [45 empty] | Vermont Yankee | B | GE | PO | 100 | On 6/24/88 at 1546, with the Reactor at 100% power, the Main Turbine (TA) tripped which resulted in a Reactor SCRAM and Primary Containment Isolation System (PCIS) (JM) trip (Groups 2, 3 and 5). The turbine trip resulted from an erroneous high vibration signal from the No. 10 Turbine Bearing Vibration Probe (EIIS=VT). Vibration at the turbine bearings is monitored by the Turbine Supervisory Instrument System (JJ) which utilizes vibration probes located at each bearing. This system also sends a trip signal to the Main Trip Solenoid (MTS #1) when excessive vibration is sensed on any of the monitored bearings. The Main Trip Solenoid, in turn, causes the Turbine Stop and Control Valves to close and a Reactor SCRAM signal to be generated with a subsequent SCRAM of the Reactor. <br /><br />The Reactor SCRAM along with the fast closure of the turbine valves caused the Reactor water level to shrink to the low water level trip point which subsequently caused the trip of the Containment Isolation System valves. <br /><br />On 6/24/88 at 1550, the SCRAM and isolations were reset. <br /><br />The immediate cause of the turbine trip is attributed to a failure of the vibration probe coil in the No. 10 turbine bearing. <br /><br />The exact root cause of the coil failure could not be readily determined but is suspected to be aging. <br /><br />The probe was subsequently replaced by the Instrument and Control Department on 6/29/88 and the system placed back in service.
271 | 2711988009 | 1988-07-03 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Vermont Yankee | B | GE | SU | 1 | On 7-3-88, with the Plant operating at 58% power, a shutdown was commenced to allow repair of a steam leak. At 13:45, approximately 30 minutes after the Main Turbine was taken offline, operators observed a Reactor pressure decrease from 930 PSIG to 872 PSIG over a five minute period with no operator action at a power level of approximately 5%. <br /><br /> Operators then used various modes of the Mechanical Hydraulic Control (MHC) (EIIS=JI) System, which controls and stabilizes Reactor pressure. MHC was found to operate eratically in all modes. Attempts to control pressure by positioning Main Steam Bypass Valves resulted in large valve position changes and subsequent Reactor pressure/water level oscillations. At 14:11, during a high level oscillation, the single operating Feedwater (EIIS=SJ) pump tripped. A standby Feedwater pump was started at 14:15 to maintain water level. The resulting introduction of relatively cold water into the Reactor vessel caused a rapid neutron flux/power increase which resulted in a high Intermediate Range Monitor (IRM)(EIIS=IG) flux scram from less than 1% power at 14:16. All safety systems responded as designed. <br /><br />The root cause of this event is suspected as being a malfunction of the MHC hydraulic control oil system most probably caused by dirt/grit being lodged in a control oil pressure control valve. <br /><br />Corrective action consisted of extensive MHC testing while shutdown, testing for proper operation of MHC during the subsequent startup, and plans for further MHC maintenance during the next refueling outage. <br /><br />(Note: If additional pertinent information concerning the MHC malfunction is discovered during the upcoming refueling outage, a supplemental LER will be provided.)
271 | 2711990004 | 1990-03-21 | QR0 | RCS High Pressure (RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Vermont Yankee | B | GE | PO | 25 | On 03/21/90 at 2248, with reactor at approximately 25% power, while bringing the TUrbine (EIIS=TA) up to speed in preparation for placing generator in service, a SCRAM occurred due to exceeding the reactor high pressure set point. The SCRAM was followed by a Primary Containment Isolation System (PCIS, EIIS=JE) Group I Isolation at 2250. The SCRAM and the isolation were the result of a failure of the Pressure Control System (EIIS=JI) to control reactor pressure. Based on results of followup testing, the root cause appears to be a lack of response of the #1 Turbine Control Valve at low hydraulic oil pressure. The root cause of the Group I isolation was the failure of the #1 Bypass Valve to go completely closed. <br /><br /> The immediate corrective actions were to increase the differential pressure across the Control Valve actuator and lubricate the linkage for all the Bypass Valves. Upon initiating these immediate corrective actions the turbine-generator was successfully brought back on line.
271 | 2711990009 | 1990-06-01 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Vermont Yankee | B | GE | PO | 100 | On 06/01/90, at 1353 hours, with the Reactor at 100% power, a contract electrician working on a normal/emergency lighting panel allowed a ground wire to come in contact with a live bus. The resulting short circuit caused the Vital AC Motor Generator Set (EIIS=EF) to lose the field excitation and subsequently a loss of generator output. On the loss of generator output, the Vital AC bus transferred to its alternate source. This caused a pressure transient in the reactor coolant system due to the transfer from the Electric Pressure Regulator to the Mechanical Pressure Regulator, resulting in a Reactor Scram. On 06/03/90, at 0103 hours, the Reactor Mode Switch was returned to the RUN position and the Main Generator phased to the grid. <br /><br /> The root cause of this event was personnel error due to a lack of mental attention. <br /><br /> Corrective actions will include electrical contractor retraining and increased emphasis on safety and attention to detail. An evaluation will be performed of the Vital AC MG set to determine if collapse of the generator field as a result of the fault was the appropriate equipment response. A Plant Operational Review Sub-Committee will evaluate the need for a formal guideline governing work in energized electrical equipment.<br /><br /> No other incidents involving a fault on the Vital AC causing a Reactor Scram have occurred in the last five years.
271 | 2711990015 | 1990-11-04 | QR5 | Turbine Trip | [45 empty] | Vermont Yankee | B | GE | PO | 94 | On 11/4/90 at 0120 hours, with reactor power at 94%, while performing weekly testing of the Turbine Emergency Governor (JC*), a reactor scram occurred as a result of a turbine control valve fast closure signal. The turbine control valve fast closure signal was generated by the acceleration relay after operators removed a trip lockout from the Emergency Trip Valve. This operator action was taken based on Emergency Trip Valve position information later identified as erroneous due to a missing set screw on a collar in the turbine front standard linkage. Since the collar was not attached to the linkage, a spring was not able to act upon the linkage and the Emergency Trip Valve limit switch did not change state as the valve moved. <br /><br /> The plant was stabilized without incident following the transient and the turbine (TA) was placed on the turning gear at 0241 hours. The turbine vendor (GE) assisted plant personnel in repairing and testing the malfunctioning linkage prior to restoring the turbine control system (TG*) to service. The reactor was returned to critical on 11/4/90 at 2222 hours. A procedure is being revised to provide additional operator actions to be taken if light indications are abnormal. Turbine outage maintenance is being expanded to include an inspection of similar locking collars and position indicating. <br /><br /> *Energy Information Identification System (EIIS) Component Identifier
271 | 2711991005 | 1991-03-13 | QR5 | Turbine Trip | [45 empty] | Vermont Yankee | B | GE | PO | 100 | On 3/13/91 at 2228 hours, with reactor power at 100%, a Reactor scram occurred due to a generator/turbine trip as a result of the failure of an 80 ft. vertical section of 345KV Switchyard Bus (B Phase) between the Main Transformer aerial T1 disconnect switch and the horizontal bus bar spanning the 1T-11 and 81-1T-2 disconnect switches. The cause of the bus failure is attributed to a broken insulator stack which secured the bus to the tower. The plant was subsequently stablized by resetting Primary Containment isolations, restarting Reactor Water Cleanup and establishing level control using the 10% Feedwater Regulator valve. Shutdown Cooling was later employed at 0504 hours on 3/14/91 and maintained until the necessary repairs and testing were completed. The reactor was returned to critical on 3/18/91 at 0055 hours. The need to expand present Switchyard system maintenance is being evaluated.
271 | 2711991009 | 1991-04-23 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Vermont Yankee | B | GE | PO | 100 | On 04/23/91 at 1448 hours, during normal operation with Reactor power at 100%, a Reactor Scram occurred as a result of a Generator/Turbine trip on Generator Load Reject due to the receipt of a 345KV Breaker Failure Signal. The Failure Signal was the result of Breaker Failure Interlock (BFI) signals that occurred simultaneously in the 345KV and 115KV Breaker control circuitry during the restoration of a battery bank to Switchyard Bus DC 4A. The cumulative effects of both (BFI) signals resulted in a total loss of 345KV and 115KV off-site power. An Unusual Event was declared at 1507 hours. Both Emergency Diesel Generators provided power for essential safety related systems during the LNP until approximately 0430 hours on 04/24/91 at which point off-site 345KV power was restored and backfed through the Station Auxiliary Transformer. During the event, Torus Water volume exceeded the Technical Specification limit of 70,000 cubic ft. The Unusual Event was terminated at 1950 hours on 04/24/91. The reactor reached Cold Shutdown at 0357 hours on 04/25/91 and was returned to critical at 0300 hours on 04/30/91.<br /><br /> The Root Cause of this event is failure of the repair department personnel to recognize the consequences of operating a DC bus without a connected battery bank. <br /><br /> Corrective actions to prevent reoccurrence are outlined within this report.
271 | 2711991014 | 1991-06-15 | QR5 | Turbine Trip | [45 empty] | Vermont Yankee | B | GE | PO | 100 | On 06/15/91 at 2224 hours, during normal operation with Reactor power at 100%, a Reactor Scram occurred due to a Turbine Control Valve Fast Closure on Generator Load Reject resulting from a loss of the 345KV North Switchyard Bus. The event was initiated during a thunderstorm in which a lightning strike occurred on the "B" phase of the 381 transmission line between Vermont Yankee and Northfield. The fault resulted in the opening of all 345KV Air Trip Breakers (ATBs). During the event, a subsequent Reactor Scram and corresponding Primary Containment Isolation Signals (PCIS)(*JM) Groups 2 and 3 were received due to Low Reactor Water level. The Reactor was stabilized in Hot Standby using the Main Condenser, Condensate, and Feedwater systems. At 2100 hours on 06/16/91, after Reactor depressurization was completed, Shutdown Cooling using the "D" RHR pump on the "B" loop was initiated. The reactor reached Cold Shutdown at 0500 hours on 06/17/91. The reactor was returned to critical at 1413 hours on 06/20/91. The Root Cause of this event is a defective (shorted) transistor in offsite (Scobie Pond) Protective Relaying System Carrier equipment. The need to perform additional testing of Carrier systems is being evaluated. <br /><br /> *Energy Information Identification System (EIIS) Component Identifier
271 | 2711994004 | 1994-04-10 | QR5 | Turbine Trip | [45 empty] | Vermont Yankee | B | GE | PO | 99 | On 4/10/94, at 0122 hours with the reactor at 98.5 % power, a reactor scram occurred from a Turbine Control Valve (TCV) Fast Closure scram signal due to a high level in the 'C' Moisture Separator (MS). The event was initiated during turbine testing when the level transmitter for the Normal Level Control valve failed to sense an increasing level in the MS Drain Tank due to a shift in calibration of the transmitter. This allowed the level in the MS Drain Tank to increase to the Emergency Dump Valve opening setpoint. The Emergency Dump Valve Level Transmitter sent an open signal to the Emergency Dump Valve Level Controller but the controller failed to bleed the air off the Emergency Dump Valve diaphragm which allows the valve to open. Consequently, the high MS level trip point was reached and tripped the turbine which resulted in the TCV Fast Closure scram. <br /><br /> During this event, a subsequent reactor scram and corresponding Primary Containment Isolation signals for Groups 2,3 and 5 were received due to low reactor water level. The reactor was stabilized in Hot Standby, the Primary Containment Isolations were reset, Reactor Water Cleanup was restarted and normal water level was re-established using the 10% Feedwater Regulator valve. <br /><br /> The apparent cause of this event is inadequate preventive maintenance of the Emergency Dump Valve level controller. The failure mode of the controller could not be determined as the controller was checked and recalibrated, in an effort to correct the problem, prior to being sent to the manufacturer for analysis. A contributing cause of this event is a calibration shift of the normal water level transmitter. Corrective Actions include replacement and calibration of the level instruments and controllers in the MS drain system.
271 | 2711995021 | 1995-12-08 | QP5 | Excessive Feedwater Flow | [45 empty] | Vermont Yankee | B | GE | PO | 79 | On 12/8/95 at 1114 an automatic plant shutdown occurred. The plant shutdown was the result of a turbine trip caused by high reactor water level due to a failure of the 'A' Feedwater Regulating Valve (FCV-6-12A). Power had been reduced to 79% and FCV-6-12A had been pinned in manual due to problems with the valve oscillation. When FCV-6-12A was placed in manual the tapered pin used to couple the manual operator to the valve stem could not be fully inserted. Due to asbestos contamination concerns in the area the operators were ordered out of the area until cleanup could be completed. Vibration of FCV-6-12A subsequently caused the tapered pin to come out allowing the valve to open. The failure of the FCV-6-12A operator was due to an unthreading of the connection between the upper and middle operator shafts. The torque on the connection is thought to have been disturbed during a prior maintenance activity and vibration during operation resulted in the two shafts becoming disconnected. The valve was repaired and retested satisfactory. The valve overhaul procedure is being revised to incorporate manufacturers recommendations, and improved I&C Technician training on these specific valve operators is being pursued. The availability of limited asbestos worker training for Auxiliary operators to allow them to enter contaminated areas if required to operate equipment is being pursued.
271 | 2711997008 | 1997-04-24 | QR8 | Spurious Reactor Trip | [45 empty] | Vermont Yankee | B | GE | PO | 100 | On 04/24/97 an Automatic Reactor Scram occurred as a result of personnel errors made during calibration of the Local Power Range Monitor (LPRM) detectors. Average Power Range Monitor (APRM) channels "A" and "D" were removed from service to block test signals to the Reactor Protection System (RPS). Failure to properly perform a procedural step resulted in the mode selector switches for APRM channels "A" and "D" remaining in the "Zero" vice "Operate" position. Following the calibration of the LPRM detectors, the procedure directed that the affected APRM output be adjusted to indicate core thermal power. Having omitted the restoration of the APRM mode switches the Reactor Engineer (RE) was unable to adjust APRM output. Without resolving this discrepancy, the RE proceeded with the testing activity. The RE then requested the Licensed Operator to restore APRM channels "A" and "D" to service. The rapidity with which the Licensed Operator restored both APRM channels to service did not allow for proper verification of system response. A reactor scram occurred and went to completion. The Operators followed plant procedures for a reactor scram and the plant was stablized. A post trip report and cause analysis were conducted. Lessons learned were presented to all Licensed Operators. The need for procedural compliance and communication of problems as they occur were reinforced to Site personnel. The quality and ownership of affected procedures are being reviewed and improvements are being made as necessary. This event is not considered to have presented an increased threat to public health or safety.
271 | 2711997023 | 1997-11-25 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Vermont Yankee | B | GE | PO | 85 | On November 25, 1997 a plant trip occurred at Vermont Yankee. The cause of the trip was the failure of a protective device in the Main Generator protective circuitry. Errors made in the switchyard motor operated disconnect operating sequence, performed in support of transmission grid maintenance activities, resulted in a perturbation in the 345 kV transmission system, which in turn caused an initiation of an automatic reduction in steam admitted to the Main Generator turbine. The ramped power reduction should not have exceeded the approximate 0.1 seconds of the perturbation, resulting in minimal impact upon plant operation. However, a comparator/relay failure in the generator protection circuit prevented the circuit from responding to the resumption of normal comparator inputs, causing the automatic generator load reduction to continue. The operating crew performed the actions prescribed by plant procedures in response to the runback. The adequacy of those procedures are being verified. The automatic reduction in steam to the turbine results in a marked reduction in feedwater heating, and a resulting positive reactivity addition, ultimately leading to a flow-biased scram. The comparator initiated runback has since been removed from the circuit under the VY temporary modification process. Because the conditions which occurred in this event were bounded by the current analysis of record, and the analysis of record demonstrates that all safety design limits for abnormal operational transients were met, this event presented no increased risk to public health or safety.
271 | 2711998016 | 1998-06-09 | QP5 | Excessive Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Vermont Yankee | B | GE | PO | 65 | On 6/9/98 at 0132 hours, during power reduction in preparation for single loop operation in response to a Recirculating Pump motor-generator (MG) high bearing oil temperature, the reactor scrammed due to a turbine trip on high water level. The "A" feedwater level control valve would not close to accommodate the reduced power due to foreign material, a cap screw, being lodged in the valve. The valve could not close beyond approximately 42% from its fully open position. The running Feedwater Pumps tripped on high water level and reactor water level decreased to the low level setpoint such that Primary Containment Isolation System Groups 2, 3 and 5 were actuated. Approximately fifty minutes after the scram, the "C" Feedwater Pump was started but tripped on low indicated minimum flow. Following the trip of the "C" Feedwater Pump, the "A" and "B" Feedwater Pumps attempted to simultaneously auto-start which caused an overcurrent condition on 4KV bus 1 and subsequently tripped the supply breaker to 4KV bus 1 as well as the feeder breaker to 4KV bus 3. This resulted in a loss of 4KV power to the "A" and "B" Feedwater Pumps, the "A" Condensate Pump and the "A" Recirculation Pump plus 480VAC station busses 6, 8, and 11. Due to the loss of power, the "B" Diesel Generator started and assumed the loads on 4KV bus 3 and 480VAC bus B. When power was restored, bus 6 was cross-tied to bus 7, the turbine bypass valves ramped open which caused a high steam flow scram signal and Group I PCIS isolation. Level control was maintained through the use of the Reactor Core Isolation Cooling system and Torus cooling was in effect. The plant was restarted on 6/13/98 following removal of the cap screw from the feedwater valve and repair of the MG set bearing. The root cause of this event is attributed to foreign material in the feedwater system. All safety systems performed as designed and, therefore, there was no increased threat to public health and safety.
271 | 2712000004 | 2000-09-13 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Vermont Yankee | B | GE | PO | 100 | On 9/13/00, a licensed operator replaced a position indicating light bulb for a steam jet air ejector (SJAE) inlet steam supply valve. The SJAE's are part of a balance of plant, non-nuclear safety system. During the bulb replacement a momentary electrical short was created and caused a protective fuse to blow in the valve control circuit. Although the valve was not in service while the bulb was being replaced, the affected control circuitry shares a common power supply fuse with the redundant (in-service) SJAE steam supply valves. Therefore, the fuse also disconnected power from the in-service SJAE steam supply valves, closing the valves. This caused a lowering main condenser vacuum. The operating crew followed plant procedures for the lowering condenser vacuum while seeking a replacement fuse. Approximately four minutes later, in response to the lowering condenser vacuum, the Station Shift Supervisor directed a manual trip of the reactor. The operating crew brought the plant to a stable shutdown condition following the plant trip. Investigation revealed that the short was caused by the use of an incorrect model bulb extraction tool. The short led to a plant trip because of the design of the associated valve control circuitry. The incorrect model tools were collected and removed from service. The correct model tools were made available. Training on this event was provided to appropriate plant personnel and included the use of the correct extraction tool. An assessment is ongoing to determine if a better extraction tool is available. A review of the adequacy of the affected valve control power circuit design will be performed. All plant safety systems functioned as required to bring the plant to a safe, stable shutdown condition. Therefore, this event presented no significant increase in risk to public health and safety.
271 | 2712001001 | 2001-03-19 | QR8 | Spurious Reactor Trip | [45 empty] | Vermont Yankee | B | GE | PO | 100 | On 3/19/01, Instrument and Control Technicians were performing an Average Power Range Monitoring (APRM) System Functional Test. Per the procedure, the technicians had placed the "A" APRM (APRM-A) logic in the "bypass" condition, 'blocking any associated protective signals from the Reactor Protection System (RPS). The balance of in-service APRM's provide the required protection system outputs during testing. When required by the test procedure, a licensed operator restored the APRM-A bypass switch to "normal" to allow the APRM-A to deliver a trip signal to the RPS. This step is intended to verify proper circuit operation by actuating half of the logic necessary to insert an automatic shutdown. Restoration of the APRM-A bypass switch resulted in an automatic insertion of all control rods. Upon observing the insertion of control rods, the licensed operator initiated a manual plant trip. The cause of the trip was a worn auxiliary contact plunger in the "B" trip system circuitry that had remained in the tripped condition following previous testing. The half trip signal inserted by the APRM-A testing, combined with the closed "B” trip system contact, opened one of the backup scram valves, initiating an automatic insertion of all control rods. The worn auxiliary contact has been replaced. A temporary modification has been installed to verify that the affected auxiliary contact in the "B" trip system (as well as similar auxiliary contacts in the "A" and "B" trip systems) reset properly following future actuations. VY management has established a requirement to use the temporary modification to monitor the contacts for proper operation. Permanent configuration/process changes are being considered. The worn contact failed in the safe condition (initiating a protective action), plant safety systems operated as designed, and the operating crew operated plant systems in accordance with procedures bringing the plant to a stable shutdown condition. Therefore, this event caused no significant increase in risk to public health and safety.
271 | 2712004003 | 2004-06-18 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Vermont Yankee | B | GE | PO | 100 | On 06/18/04 at 0640, with the plant at full power, a turbine load reject scram occurred due to a two phase electrical fault to ground on the 22 kV iso-phase bus. All safety systems responded as designed and the reactor was shutdown without incident. Off-site power transmission lines and station emergency power sources were available throughout the event. Arcing and heat generated during the fault damaged an area around the iso-phase bus ducts and Main Transformer low voltage bushings. The electrical faults disrupted an oil line flange between the Main Transformer oil conservator (expansion tank) and the "C" phase low voltage bushing box, and the leaking oil ignited. Fire suppression systems activated automatically. An Unusual Event was declared at 0650 for a fire lasting greater than 10 minutes. The VY Fire brigade and local community fire departments declared the fire under control at 0717. At 1245, the Unusual Event was terminated. The electrical grounds that initiated the event were caused by loose material in the "B" iso-phase bus duct as a result of the failure of a flexible connector. The grounds raised the voltage on the "A" and "C" iso-phase busses contributing to the failure of the "A" phase surge arrester. The root causes of the event were determined to be the result of a flexible connector fabrication deficiency and preventative maintenance not being performed on the surge arresters located in the Main Generator Potential Transformer (PT) Cabinet. There was no release of radioactivity, breach of secondary containment or personnel injury during this event.
271 | 2712005001 | 2005-07-25 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Vermont Yankee | B | GE | PO | 100 | On July 25, 2005 at 1525, with the reactor at full power, a generator load reject trip and subsequent reactor trip occurred as a result of an electrical transient that originated in the 345 kV Switchyard. The electrical transient was due to a failure of the 345 kV Motor Operated Disconnect (MOD) Switch, T-1, "C" phase that was caused by the failure of an electrical insulator. An off-site laboratory performed an examination of the porcelain insulator revealing that the failure was caused by a manufacturing defect. The appropriate NRC 4-hour notifications were completed at 1735 in accordance with 10 CFR 50.72(b) as NRC Event Number 41868. This event is being reported as an LER pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of systems listed within 10 CFR 50.73(a)(2)(iv)(B). Plant equipment and operator response to the event was as expected, and the reactor was shutdown with no complications. No release of radioactivity or personnel injury occurred as a result of this event. Therefore, this event did not increase the risk to the health and safety of the public.
271 | 2712007003 | 2007-08-30 | QR5 | Turbine Trip | [45 empty] | Vermont Yankee | B | GE | PO | 62 | On 08/30/07, with the reactor at approximately 62 percent power, a reactor trip occurred due to at least three of the four Turbine Stop Valves (TSV) going greater than 10% closed. This condition actuated the Reactor Protection System (RPS) logic which shutdown the reactor as designed. The reactor trip was attributed to the lack of preventative maintenance on the number 2 TSV Bell Crank Mechanism. Binding in the Bell Crank Mechanism resulted in the number 2 TSV failing to open after a closure test. When the mechanism was freed, the valve opened rapidly causing a rapid pressure change in the TSV actuator hydraulic oil system that resulted in all four TSVs going closed. The appropriate initial NRC notifications were made per 10CFR50.72 (b)(2)(iv)(B) and 10CFR50.72 (b)(3)(iv)(A). Plant safety system response was as expected and the plant automatically shutdown. No release of radioactivity or personnel injury occurred as a result of this event. No similar events have occurred in the last 5 years. This event is reportable as a Licensee Event Report per 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of systems identified in 10CFR50.73(a)(2)(iv)(B).
271 | 2712010001 | 2010-05-26 | QR5 | Turbine Trip | [45 empty] | Vermont Yankee | B | GE | PO | 72 | On May 26, 2010, at approximately 1526 hours, a generator lockout and automatic reactor trip occurred on differential current between a current transformer (CT) installed in the newly commissioned switchyard and a CT installed in the plant. During startup, when the plant reached 72% power, both channels of the reactor protection system (RPS) actuated and all control rods inserted. Following the reactor trip reactor vessel level decreased causing primary containment isolation system (PCIS) actuation for groups 2, 3, 4, and 5. All associated valves functioned correctly. Additionally, both trains of standby gas treatment system actuated. Immediate plant actions included entering appropriate trip response procedures. The operators stabilized the plant and reset both RPS and PCIS. During RFO 28, Vermont Yankee (VY) and the Vermont Electric Power Company (VELCO) commissioned a new 345kV switchyard. The direct cause of the trip was that VELCO changed the CT ratio settings within the 345kV Switchyard and failed to communicate the new ratio setting to VY. As power was increased, the differential current caused by the difference in CT ratio settings resulted in the generator lockout. Corrective actions include adjustment of the VY CT to the correct settings and establishment of the necessary programmatic controls to preclude recurrence. This event is reportable as a licensee event report (LER) per 10CFR50.73(a)(2)(iv)(A) as an event or condition that resulted in actuation of the any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B), which includes RPS and PCIS.
272 | 2721987007 | 1987-06-02 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 100 | On June 2, 1987 at 0928 hours, Unit 1 experienced a Turbine Trip/Reactor Trip from 100% power. The trip was caused by a lightning strike in the vicinity of the Deans Switching Station which caused the momentary loss of the 5021 500KV Transmission Line actuating the Salem/Deans "Cross Trip Scheme" for "Generator Protection". On March 1, 1987 several towers supporting the Hope Creek - Keeney 500KV transmission line were damaged due to a navigational accident in the Delaware River. The loss of this transmission line led to a stability concern during simultaneous full power operation of Hope Creek, Salem Unit 1, and Salem Unit 2 Generating Stations. The Salem/5021 Deans 500KV Transmission Line Cross Trip Scheme was established to protect against potential generator instability. The "Cross Trip Scheme" will be removed upon return to service of the Hope Creek-Keeney 500KV transmission line which is expected by December 1987.
272 | 2721988003 | 1988-02-24 | QR8 | Spurious Reactor Trip | [45 empty] | Salem 1 | P | WE | SU | 4 | On February 24, 1988 at 0436 hours, a reactor trip occurred from 4% power. The "first out" annunciation, indicating the cause of the trip, was "IR High Flux". The Unit was involved in a reactor startup following the completion of a refueling outage. The root cause of this trip has been attributed to personnel error. A Maintenance-I&C technician after successful completion of N35 Intermediate Range channel adjustment was requested by Operations personnel to repeat the procedure to determine if a correlation between a No. 13 Tavg channel spike and the N35 channel adjustment existed. Upon repeating the procedure, the technician performed the procedure out of sequence. The output trip signal was not bypassed prior to pulling the channel fuses. The technician involved in this event was counseled. A Human Performance Evaluation System (HPES) review of this event will be conducted to preclude future occurrences. In addition, this event and the results of the HPES recommendations will be evaluated by the PSE&G Nuclear Training Center for incorporation into appropriate training programs.
272 | 2721988009 | 1988-03-30 | QR6 | Manual Reactor Trip | [45 empty] | Salem 1 | P | WE | PO | 100 | On March 30, 1988, at 1143 hours, No. 12 EH (JJ) Pump tripped and No. 11 EH Pump failed to automatically start. With the loss of the EH pumps, and decreasing pressure in the control oil system, the Turbine Governor Valves (JJ) began to drift shut. The Reactor (AC) was subsequently manually tripped due to increasing Tavg. Prior to this occurrence, leakage of EH control oil had been noted issuing from the 12 and 13 MS29 Valves (JJ) and the EH reservoir had been refilled several times by the EOs. During this occurrence the mechanical level indicator had apparently malfunctioned as it continued to indicate a normal to high level although the actual sump level had reached the EH pump low level lockout setpoint. The apparent "root cause" of this occurrence has been attributed to poor communication resulting in not adequately investigating the cause of the constant EH high/low reservoir level alarm in conjunction with equipment failure.
272 | 2721988015 | 1988-08-31 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 100 | On August 31, 1988 at 0509 hours, a Reactor Trip/Turbine Trip occurred due to low Auto Stop Oil System (TG) pressure. The apparent cause of this event has been attributed to an equipment problem. It has been determined that a pressure reducing 1/32" orifice probably clogged during functional testing of the turbine trip mechanisms. The functional testing of the turbine trip mechanisms was subsequently completed satisfactorily. The functional testing procedure has been modified to include a step to closely monitor auto stop oil pressure during performance of testing. The two pressure reduction orifices in the Auto Stop Oil System were cleaned. Preventive maintenance requirements for the Auto Stop Oil System will be expanded to include thorough cleaning of the system and will be scheduled during refueling outages. The overhead annunciation for Low Auto Stop Oil Pressure will be modified to alert Operations personnel of decreasing auto stop oil pressure. Presently the alarm is set to annunciate upon auto stop oil pressure decreasing to the trip setpoint.
272 | 2721989007 | 1989-02-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 1 | P | WE | PO | 100 | On February 6, 1989 at 1055 hours, during routine power operation, the Unit experienced a Reactor Trip on No. 14 Steam Generator (S/G) Low Level concurrent with Steam Flow/Feed Flow mismatch. At the time of the event, No. 14 S/G steam pressure channel I functional surveillance was in progress. The root cause of this event has been attributed to personnel error. Post trip data indicates that the Nuclear Control Operator (NCO) did not select the correct channel during performance of I&C procedure 1PD-2.6.060, "Channel Functional Test - 1PT-544 #14 Steam Generator Steam Pressure Protection Channel I". Pressure compensation for determining steam flow is eliminated when the channel test switch is placed in the test position as per procedure. This causes Steam Flow indication to drop radically causing a signal to initiate closure of the 14BF19 Feedwater Control Valve thereby decreasing feed flow. With the wrong channel apparently chosen as the controlling channel, the 14BF19 valve began closing. Once S/G level dropped to 25% the reactor trip occurred since the signal for Steam Flow/Feed Flow mismatch was proceduraly previously actuated. This event has been reviewed by Operations management. Appropriate corrective disciplinary action has been taken. This event will be reviewed by the Nuclear Training Center for incorporation into applicable training programs. Operations Department will review this event with applicable Operations Department personnel.
272 | 2721989027 | 1989-06-19 | QL5 | Partial Closure of MSIVs | [45 empty] | Salem 1 | P | WE | PO | 45 | On 6/19/89 at 2100 hours, a Reactor Trip on No. 13 Steam Generator (S/G) "Low-Low Level" occurred. The No. 13 main steamline isolation valve, 13MS167, had closed. Prior to the event, reactor power was being increased 3% per hour. At the time of the event, a post maintenance surveillance for the 12MS18 Main Steamline Bypass Stop Valve was in progress. The root cause of this event has been attributed to inadequate design of the continuity check circuitry for the MS167 valves. Surveillance testing of valve 12MS18 was in progress prior to the event. When the Solid State Protection System (SSPS) Train "A" output interface cabinet switch was turned to "operate output", the 13MS167 valve closed followed by the trip. The "operate output" function causes closure of the MS18 valve while checking continuity of the MS167 valve closure circuit. This design can cause inadvertent closure of the MS167 valves as occurred during this event and a similar Unit 2 event on 4/11/89 (ref. LER 311/89-008-00). A design change has been implemented which corrects the circuit design concern by adding a contact which prevents the 74-3A relay from resetting during the testing of the MS18 valves. This contact does not prevent the MS167 valves from functioning in the event of a valid main steam isolation signal. A similar Unit 2 design change will be implemented during the next outage of sufficient duration. In the interim, a new procedure will be issued which addresses the surveillance testing of the MS18 valves. The Unit 1 74-3A relay was replaced and will be sent to the vendor for evaluation.
272 | 2721990012 | 1990-04-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 1 | P | WE | PO | 90 | On 4/9/90 at 1433 hours, during normal power operations, a reactor trip on No. 12 Steam Generator (S/G) Low-Low Level occurred. Prior to the trip, at 1430 hours, after noting that No. 12 Steam Generator Feedwater Pump (SGFP) was idling, a turbine runback was initiated at 200%/min then was reduced to 15%/min once steam flow and feed flow were matched. Upon reaching 60% power, the runback stopped. However, No. 12 S/G level continued to decrease. A second runback to 50% power (at 8%/min) was initiated, however, prior to its completion, the Low-Low Level trip setpoint (16%) was reached. The Unit was stabilized in Mode 3. The root cause of this event is equipment failure. Flow from the No. 12 SGFP had ceased upon failure of the governor valve control linkage. The pilot rod that diverts oil flow to position the servo motor piston had dropped off. The loss of the pilot rod prevented the Woodward Governor from controlling the turbine. The No. 12 SGFP governor valve linkage was repaired and No. 11 SGFP governor valve linkage inspected with no related problems noted. Additional corrective action include: 1) Maintenance procedure M24A will be revised to incorporate more detailed instructions for linkage installation and adjustment; 2) a procedure, to define preventive maintenance requirements will be prepared; 3) recurring tasks will be established as applicable; and 4) a review of similar pump governor linkage arrangements with no additional problems identified.
272 | 2721990029 | 1990-08-17 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Salem 1 | P | WE | PO | 25 | On 8/17/90, during power ascension, the reactor tripped due to No. 14 Steam Generator (S/G) Low-Low Level. The trip occurred during the transfer of the four Group Busses from the Station Power Transformer (SPT) to the Auxiliary Power Transformer (APT). After successfully transferring the 1H and 1E Group Busses, 1G Group Bus was being transferred. The operator initiated closure of the 1BGGD circuit breaker (APT side). The 12GSD breaker opened; however, the 1BGGD breaker failed to close resulting in deenergization of the 1G Group Bus. Consequently the No. 14 Reactor Coolant Pump (RCP) circuit breaker opened on undervoltage. The reactor subsequently tripped on No. 14 S/G Low-Low S/G Level. The root cause of this event is attributed to equipment failure. The 1BGGD circuit breaker failed to close during transfer due to its positive interlock switch not closing thereby preventing energization of the breaker close coil. The positive interlock assembly was found to be out of adjustment/worn preventing the required closing of the breaker's positive interlock switch after the breaker was racked into its normal operating position. The 1BGGD circuit breaker enclosure positive interlock assembly deficiencies were corrected. Subsequently, the 1BGGD breaker was successfully functionally checked. All 4KV and 13KV circuit breakers and enclosures were inspected on both Unit 1 and Unit 2. A review assessing the feasibility of adding supervisory relays across the closing contacts of critical circuit breakers will be conducted.
272 | 2721990030 | 1990-09-10 | QK4 | Steam or Feed Leakage | [45 empty] | Salem 1 | P | WE | PO | 79 | On 9/10/90 at 1201 hours a reactor trip on No. 13 Steam Generator (S/G) Low-Low Level occurred. Prior to the event, the pipe between the No. 11TD900 valve and the main steam line sheared providing a steam flow path to atmosphere. To reduce the steam flow, the No. 11MS29 valve (MS Governor Valve) was closed. At 80% power, the 14MS29 valve is closed ("Partial arc control scheme"). Both the Nos. 11&14MS29 valves direct steam to the upper half of the Turbine. Therefore, with both valves closed, a significant dp across the HP Turbine developed. Contributing to this dp was opening the 11TD4 valve which resulted in bleeding steam away from the upper half of the HP Turbine. The Turbine shaft deflected creating an elliptical oscillation resulting in destruction of the Aux. speed sensor which generated an overspeed signal causing closure of the MS29 valves. Closure of the MS29 valves led to the trip on No. 13 S/G Low-Low Level. The root cause of this event is attributed to personnel error. Ops. Dep't. management did not layout an approved plan of action in addressing the pipe break associated with the 11TD900 valve. Contributing factors were procedural inadequacy and inadequate training. This event has been reviewed by senior management. Those individuals involved in this event have been held accountable. Procedures have been revised to clearly identify the concerns with Turbine Valve Testing below 85% power. Operations Directive procedure OD-15 will be revised. An Operations Department "troubleshooting" procedure will be prepared. Damaged equipment was replaced. This event will be reviewed by the Nuclear Training Center for incorporation of lessons learned.
272 | 2721991024 | 1991-06-16 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 100 | On June 16, 1991, at 1940 hours, during normal full power operation, Salem Unit 1 experienced a Reactor Trip/Turbine Trip. The first out overhead annunciation was "4KV Group Bus Undervoltage". At the time of the event a severe thunderstorm was in progress. Investigation revealed that lightning had struck in the vicinity of the phase B Generator Step-Up (GSU) transformer (EL). Evidence of the lightning strike included carbonization of the high voltage bushing, damage to the corona rings and lightning arrestor and eyewitness accounts. The root cause of the reactor trip event is attributed to an act of nature; i.e., a lightning strike in the vicinity of the phase B GSU transformer, resulted in a 4KV Group Bus Undervoltage and subsequent reactor trip. Lightning protection was assessed by engineering and found to be appropriate. The damage to the Phase B GSU transformer was repaired. Subsequently, on June 24, 1991, the Unit 1 was returned to service. Also as a result of the lightning strike, 500 KV breaker flashover protection was initiated due to sufficient current through the transformer neutral. This resulted in the loss of the No. 2 Station Power Transformer and subsequent de-energization of the 1F and 1G Group Busses. An engineering review has been initiated to prevent flashover protection actuation from a coasting generator. Design changes will be implemented as appropriate.
272 | 2721993002 | 1993-01-16 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Salem 1 | P | WE | PO | 16 | On 1/16/93, during shutdown to Mode 3 (Hot Standby) for maintenance, a manual reactor trip was initiated when 12 Steam Generator Feedwater Pump (SGFP) tripped (11 SGFP was cleared and tagged) due to a turbine trip/feedwater isolation signal (from a 13 Steam Generator (S/G) High-High Level signal). Prior to the turbine trip, Turbine Bypass System control was being transferred from 'T sub ave' to 'Steam Pressure'. During this evolution, Turbine Bypass Valves went full open causing a S/G 'swell'. 13 S/G swelled to the high-high level alarm setpoint resulting in the turbine trip/feedwater isolation signal, an Engineered Safety Feature (ESF). Per design, the 20 valves which provide steam from the S/Gs to the Turbine-Generator isolated and the operating SGFP tripped. Following this, the Turbine Bypass System valves were closed and a manual Reactor trip was initiated. Plant response was as expected following the reactor trip including the degree of Reactor Coolant System cooldown (as has occurred after prior plant trips). Per procedure, a Main Steamline Isolation (an ESF) was initiated stopping the cooldown. The plant was stabilized in Mode 3. The root cause of this event is equipment failure. The Turbine Bypass Pressure Controller and the associated servo potentiometer module of the Turbine Bypass Control System failed causing the controlling station setpoint to go from approximately 1040 psi to 196 psi in approximately 5 seconds. This caused the Turbine Bypass Valves to fully open. The faulty Turbine Bypass System components were replaced. The Unit was returned to service 1/24.
272 | 2721993004 | 1993-02-16 | QR8 | Spurious Reactor Trip | [45 empty] | Salem 1 | P | WE | PO | 100 | At 1656 hours on 2/16/93, an automatic reactor Overtemperature Delta Temperature (OTDT) signal (2/4 channels) occurred due to tripping the OTDT Loop 11 Channel I bistables while the Loop 13 bistables were already tripped for ongoing Nuclear Instrumentation channel calibration. The unit was stabilized in Hot Standby. The root cause of this event is failure of the gain selector switch of Loop 11 OTDT input module QM-411B due to intermittent high contact resistance. This resulted in the Loop 11 OTDT setpoint decreasing to the point of actuating the loop bistables. A large spurious spike on the input to the Loop 11 OTDT setpoint calculator drove it down which provided the necessary coincident logic to trip the loop bistables. Testing showed the QM-411B flux module output would trip high erratically with heat or minimal physical agitation. The 1QM411B module output gain selector switch, as well as the gain selector switches of the OTDT input modules for the balance of the unit's loops, were cleaned and exercised prior to the subsequent Reactor startup. Preventive Maintenance (PM) requirements for the subject modules (Westinghouse-Hagan) are being assessed to identify required changes to help ensure module service reliablity.
272 | 2721993011 | 1993-06-08 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Salem 1 | P | WE | PO | 100 | On 6/8/93, at 1745 hours, an automatic reactor trip from 85% power occurred due to a Main Turbine trip from low condenser vacuum and P-9 trip permissive (i.e. reactor trip on turbine trip > 50% power). This occurred during diver cleaning of the unit Circulating Water System (CWS) trash racks. Prior to this event a turbine load reduction had been initiated and a subsequent order had been given, at 1744 hours, to manually trip the reactor in response to decreasing condenser vacuum. However, before the trip was initiated, the automatic reactor trip occurred. The vacuum decrease resulted from manual tripping of 13A CWS pump and automatic tripping of 12A, 11B, and 11A CWS pumps due to high differential pressure across the pumps' traveling screens. The unit was stabilized in MoDE 3 (Hot Standby). The root cause of this event is 'Management/Quality Assurance Deficiency' with a contributing causal factor of 'External'. specific contributing factors include trash rack debris removal, maintenance of the trash rake which limited its ability to adequately clean the trash racks, and not implementing a past corrective action to modify the trash rake. Unit 1 CWS trash rack cleaning was completed prior to subsequent Unit startup. The circulating water intake structure was dredged. The CWS trash rack rake will be overhauled or replaced. The practice of using divers to clean CWS trash racks will be evaluated to help reduce risks associated with this type activity. Administrative controls will be developed and implemented, as appropriate, to address operation of the CWS trash racks' rake.
272 | 2721993013 | 1993-07-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 1 | P | WE | PO | 97 | On 7/11/93, at 2038 hours, the Unit experienced a reactor/turbine trip signal due to steam flow/feed flow mismatch coincident with low level in 14 Steam Generator (SG). This trip resulted from closure of 14 SG Feedwater Regulating Valve, 14BF19. Shutdown had been in progress per Tech. Spec. 3.3.2.1 Action 13, due to inoperability of part of the Solid State Protection System (SSPS). It was determined that relay BD601 was inoperable requiring its removal. During relay removal, the 125 VDC lead to the component normal actuation circuit was removed causing associated components (solenoid valves for the 14BF19 valve and its bypass valve, 14BF40) to deenergize. The 14BF19 valve closed per design (14BF40 was already closed) causing the trip. The root cause is personnel error. Due to inattention to detail, the maintenance supervisor did not fully assess the affect of disconnecting the BD601 wiring. Corrective discipline has been taken with the supervisor. This event will be reviewed with applicable personnel. Relay BD601 was replaced. On 8/5/93, management review of the reactor trip event investigation determined that the SSPS slave relay operability determination was not diagnosed accurately on 7/11/93, at 0530 hours, and that expeditious troubleshooting was not initiated as appropriate. The cause of this event is personnel error. Appropriate corrective discipline will be taken with the operations personnel involved. This event will be reviewed with all licensed operator personnel.
272 | 2721994003 | 1994-01-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 1 | P | WE | PO | 9 | On 1/2 94, at 2034 hours, during startup following the eleventh refueling outage, a Reactor trip on No. 14 Steam Generator (S/G) low-low level occurred from 9% power. When placed in automatic, the 14BF19/40 level demand signal periodically failed to zero. To compensate, the Nuclear Control Operator (NCO) controlled S/G level by returning the controller to manual and allowing demand signal to return to the program value. During one attempt, the NCO anticipating automatic control circuit recovery of S/G level, delayed transferring control to manual. The automatic control circuit did not recover level and when the NCO transferred to manual, S/G feedwater flow increased causing a level shrink to the 16% low-low setpoint. Emergency Operating Procedure- TRIP-1, 'Reactor Trip Or Safety Injection' was entered and the Unit stabilized and placed in Mode 3. The primary root cause of this event is equipment failure of three circuit cards in 14BF19/40 controller. A contributing factor was buildup of sediment in the sensing line to the 14 S/G feedwater flow transmitter. The failed controller circuit cards were replaced and the controller returned to service. Satisfactory channel calibrations were performed on the S/G level control circuits. The sensing lines to the S/G feedwater flow transmitters were blown down and vented to remove sediment and air. A root cause evaluation of the failed components will be performed.
272 | 2721994005 | 1994-02-10 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 99 | On 2/10/94, hours, at 1258 hours, a control power failure of the turbine Electro-Hydraulic Control (EHC) System occurred causing a turbine/reactor trip. The Unit was stabilized in Mode 3, at approximately 1315 hours (same day). Insufficient margin between the EHC overvoltage protection setpoints and normal EHC power supply voltage allowed a variation in voltage to actuate the overvoltage protection circuitry. The margin resulted from design/installation of the EHC power supplies and use of a 17.3VDC setpoint. A contributor was EHC procedures that did not record power supply voltages in a manner that would reveal a reduced margin to trip. No component failures were identified as contributors to this event. EHC power supplies were monitored and no problems or transients/pulses were recorded. The overvoltage protection circuits were replaced and the circuits, setpoints were reset to 17.9 +/-.1 VDC, and the EHC +15 VDC bus wiring was reworked. Procedure changes have been implemented to ensure adequate margin below the overvoltage protection setpoint. The A +15VDC power supply was replaced and additional testing will be conducted to evaluate transient effects. During the next Unit 2 outage, voltage readings of the Unit 2 EHC 15VDC power supply will be taken to verify adequacy of the overvoltage protection margin to trip setpoint.
272 | 2721994007 | 1994-04-07 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 73 | At 1050 hours on 4/7/94, an automatic Reactor trip occurred, was immediately followed by an Emergency Core Cooling System (ECCS) Safety Injection (SI) and, at 1100 hours an Unusual Event was declared. At 1105 hours, the SI signal was reset and ECCS flow reduction began. Reactor Coolant System temperature increased, Pressurizer level increased to >100%, steam generator pressure increased and main steam safety valves lifted, and at 1128 hours, a second automatic SI occurred. At 1316 hours, a precautionary ALERT was declared. HOT SHUTDOWN was achieved at 0106 hours on 4/8/94, and at 1124 hours (same day), COLD SHUTDOWN was achieved. The trip resulted from assigning inappropriate priority of actions and improperly monitoring reactor power while withdrawing rods. The first SI resulted from inadequate control of primary loop temperature, concurrent with a false high steam flow signal. The second SI resulted from low Pressurizer pressure due to lifting a steam generator safety valve. Involved personnel will complete remedial training and evaluation. Operating procedures have been revised, as appropriate. Component testing, repairs, and modifications have been made, as required.
272 | 2721994009 | 1994-06-10 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 97 | On 6/10/94, at 1434 hours, a turbine/reactor trip turbine trip signal while above the P-9 reactor power interlock setpoint of >/= 50% reactor power. The turbine trip was initiated by a main generator ground fault protection relay, CV-8, actuation. Emergency operating procedures were entered and Main Steam was isolated to limit cooldown of the Reactor Coolant System (RCS). The Unit was stabilized in Mode 3. This event occurred due to an internal ground fault on the primary high voltage winding of the phase 1 potential transformer feeding the main generator voltage regulator and relay circuits, which caused CV-8 to actuate. The PT and a blown PT primary fuse were replaced. Electrical tests were performed, which verified integrity of all main generator PTs and PT fuses. The PT insulators and cubicles were cleaned, as a preventive measure. Additional investigation will be conducted to determine the failure mechanism of the phase 1 PT failure and appropriate action will be taken. Engineering is continuing to investigate RCS cooldown following trips and potential corrective actions are being assessed.
272 | 2721994011 | 1994-07-14 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Salem 1 | P | WE | PO | 100 | On July 14, 1994, at 2132 hours, during full power operation, a Unit 1 manual reactor trip was initiated due to loss of all CW pumps caused by the undervoltage (UV) tripping of the Circulating Water (CW) System 4KV bus infeed/load breakers. The UV condition resulted from a lightning- induced voltage drop of the 500KV Hope Creek - New Freedom line that transferred to Salem's switchyard via the Salem - Hope Creek tie line. Emergency Operating Procedures were entered and at 2139 hours Main Steam was isolated to limit cooldown of the Reactor Coolant System. The root cause of the event is attributed to Design, Manufacturing, Construction/ Installation. The Unit 1 circulating water bus UV protection, installed as part of a switchyard upgrade design change in 1993, included new switchgear containing instantaneous relays. A time delay, which would have precluded UV relay actuation, was not used. Time delay relays with a 700 millisecond setting have now been installed. The protective relaying technical standard will be revised to provide overall guidance on the selection of UV protective relaying schemes. In addition, specific reference to the CW 4KV bus system will be provided. The Unit 2 switchyard upgrade DCP (which includes CW bus UV protection) will be reviewed and a suitable UV time delay scheme will be incorporated.
272 | 2721999001 | 1999-02-28 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 60 | At 1:38 AM, on February 28, 1999, the Salem Unit 1 Reactor was automatically shut down due to a Low Oil Pressure Trip of the Main Turbine. The unit was operating at 60% power prior to the shutdown and was being maintained at this power level to allow maintenance troubleshooting activities. Preparations were also being made to allow maintenance to repair a leaking Main Turbine Lube Oil Cooler. While adjusting the cooler isolation valve, the operators inadvertently positioned the valve off of its closed seat, allowing oil from the in service cooler to enter the partially drained out-of-service cooler. This diverted flow caused a momentary drop in the turbine oil pressure and resulted in the automatic shutdown of the Main Turbine and Reactor. A root cause investigation determined that the cause of this event was personnel error. This event is being reported pursuant to 50.73(a)(2)(iv) Licensees shall report "any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor m RPS ."
272 | 2721999004 | 1999-05-20 | QR3 | Reactivity Control Imbalance | [45 empty] | Salem 1 | P | WE | PO | 100 | On 5/20/99, at approximately 2137 hours, the reactor tripped from 100% power due to a negative flux trip signal from the nuclear instrumentation. The negative flux rate resulted from a dropped control rod which was caused by a loss of power to the stationery gripper coil. The loss of power was determined to be the result of a blown fuse. Investigation identified a low insulation resistance pathway on the control cable at the containment penetration seal. The junction box for this seal was found to have an accumulation of rust on the lower panel area with some warpage of the side plates, possibly resulting from a previous service water leak which may have impinged on the junction box. The cable in question was rerouted through a spare cable "feedthrough" in the penetration assembly and returned to service. The penetration seal continues to serve the mechanical sealing function without degradation. All systems functioned as designed in response to the trip. The fuse functioned properly to protect the penetration. The root cause of the cable failure has not been determined. A report was made to the NRC as required by the plant's Emergency Classification Guide and 10CFR50.72(b)(2)(ii). This report is being made in accordance with 10CFR50.73(a)(2)(iv) Licensees shall report "any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS)".
272 | 2722000001 | 2000-01-06 | QP2 | Partial Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Salem 1 | P | WE | PO | 100 | At 1611, on January 6,2000,a manual reactor trip was initiated at Salem Unit I due to loss of the 12 Steam Generator Feedpump (SGFP)and degraded SGFP suction pressure as a result of the isolation of condensate flow to the SGFPs. Immediately following the reactor trip, the 11 SGFP also tripped. The safety systems performed as required except for the 12 Auxiliary Feedwater (AFW) pump, which started but failed to inject flow and the N31 Source Range Detector. The redundant source range detector operated properly throughout the shutdown. The cause of the loss of condensate flow is attributed to radio frequency interference (RFI).Based on the troubleshooting performed, the feedwater heater level instrumentation was determined to be susceptible to RFI. Use of radios within the vicinity of the feedwater heater level instrumentation would cause the feedwater heater isolation valves (CN27s) to close. Radio use in the vicinity of the feedwater heater level instruments has been restricted. The feedwater heaters level instrumentation is currently installed in RFI vulnerable enclosures. The enclosures will either be shielded or replaced with enclosures less vulnerable to RFI. This event is reportable in accordance with 10CFR50.73(a)(2)(iv), “any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF),including the reactor protection system (RPS)...".
272 | 2722000002 | 2000-04-11 | QR6 | Manual Reactor Trip | [45 empty] | Salem 1 | P | WE | PO | 100 | At 1054, on April 12, 2000, a manual reactor trip was initiated at Salem Unit 1 due to a rapidly decreasing main generator electrical output, while a circuit card in the Valve Position Limiter (VPL) portion of the Electrohydraulic Control (EHC) system was being replaced. This card replacement was being performed as an Infrequently Performed Test and Evolution (IPTE) utilizing procedure SC.IC-GP.EHC.0002 (Z), General Troubleshooting for Main Turbine EHC System. The EHC card was being replaced to correct a previously identified slow downward drifting of the VPL. The apparent cause of the initial drifting of the VPL is attributed to induced signal noise being picked up by the EHC VPL circuitry. This noise was determined to be picked up by two unused wires within the control console push-button, which appeared to have been behaving as an antenna for noise. The cause of the reactor trip is attributed to the proper response by the licensed control room operator to the unexpected load drop following the replacement of the card. The apparent cause of the unexpected load drop has been attributed to a momentary power decrease on the Up/Down converter card while installing the 3QO2E2 card. Corrective actions taken to correct the initial drifting problem and the sudden power decrease included the elimination of the two unused wires within the control console push-button, and the replacement of 3 EHC cards.
272 | 2722000003 | 2000-08-09 | QR3 | Reactivity Control Imbalance | [45 empty] | Salem 1 | P | WE | PO | 100 | At 1751, on August 9, 2000 an automatic reactor trip occurred on Salem Unit 1 in response to negative flux rate trip signals from Power Range Channels 2 and 3 in the Nuclear Instrument System. The negative flux rate trip signals were initiated in response to the insertion of Control Rods in Group B. All systems performed as designed to safely shutdown the reactor and maintain the reactor in a safe shutdown condition. The insertion of the Group B Control Rods was caused by the failure of a voltage regulation circuit card used to regulate power to the control rod drive mechanisms' stationary gripper coils. The defective voltage regulation circuit card was replaced and the Control Rod Drive System was satisfactorily retested. The failed circuit card was returned to the manufacturer for further analysis to determine the cause of failure.
272 | 2722000005 | 2000-12-08 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Salem 1 | P | WE | PO | 100 | At approximately 0630, on December 8, 2000, Salem Unit 1 Operators received an overhead alarm "Rx Trip -Low Tavern”. Immediate investigation determined that the Steam Generator levels were falling and the Operator initiated a manual trip. Post trip review determined that an automatic reactor trip occurred, one second prior to the manual trip, in response to low low level in the 13 steam generator. The level in the steam generator fell as result of the feedwater regulating valves going closed due to an invalid signal from the Solid State Protection System. All safety systems performed as designed in response to the trip. Auxiliary feedwater started as designed and steam generator level was returned to proper levels. Post trip investigation determined that an output driver circuit card in the Solid State Protection System had failed, causing the feedwater regulating valves to go closed. The defective circuit card was replaced and the Solid State Protection System was satisfactorily retested and the unit was returned to service on December 10, 2000. The failed circuit card will be returned to the manufacturer for further analysis to determine the cause of failure.
272 | 2722001006 | 2001-05-22 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 100 | At approximately 0616 hours on May 22, 2001, Salem Unit 1 automatically tripped from full power. The direct cause of the reactor trip was the generator lockout relay operation resulting from a main generator phase "A" differential current relay trip. Extensive troubleshooting determined that there was a degraded termination associated with the field wiring to the "A" phase main generator neutral current transformer. The affected field wiring was replaced. Follow-up testing determined the current transformer itself was also degraded. A modification was installed to rewire the protective relaying and metering circuits to alternate current transformers. The unit was returned to power operation (synchronized to the grid) on May 26, 2001.
272 | 2722001008 | 2001-09-24 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Salem 1 | P | WE | PO | 100 | At 2351, on September 24, 2001 a manual reactor trip was initiated in accordance with operating procedures due to the loss of condenser vacuum. At approximately 2243 hours on September 24, 2001 the number 2 Station Power Transformer {XFMR} (SPT) in the Salem Switchyard experienced an electrical fault on one of its associated surge arresters {LAR}. The electrical transient initiated by the fault resulted in the loss of the # 2 station power transformer, and for Salem Unit 1, in the loss of three of the six condenser circulating {NN} water pumps {PMP}, the loss of its circulating water traveling screens {SCN}, as well as the sensing instrumentation for the differential pressure across the traveling screens. With only three of six circulating water pumps operating per unit, both Salem units reduced electrical load to maintain main condenser vacuum. Following the restoration of electrical power to the circulating water bus, one of the remaining Salem 1 circulating water pumps tripped on high differential pressure. As condenser vacuum could not be maintained, Salem Unit 1 licensed control room operators manually tripped the reactor per the guidance of the abnormal operating procedure. The loss of the SPT is attributed to a failed arrester. Some of the corrective actions taken were: (1) The failed arrester was replaced, and (2) Similar arresters in other transformers were also replaced. This condition is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv).
272 | 2722002004 | 2002-11-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 1 | P | WE | PO | 100 | On November 12, 2002, Salem Unit 1 was manually tripped due to a Steam Generator Feedwater Pump (SGFP) runback resulting from voltage decrease in the control power to its governor. The undervoltage occurred when a technician inadvertently grounded the power circuit for a valve limit switch during troubleshooting. The runback was not annunciated in the control room; a level alarm was received several minutes later. Operators initiated main turbine runback and reduced reactor power. As level continued to decrease to the trip setpoint, operators initiated a manual reactor trip. Auxiliary feedwater (AFW) pumps started automatically as expected, and plant shutdown was achieved without complications. The root causes are silent SGFP runback that requires manual operator action, inadequate error prevention while taking voltage readings, and lack of recognition of the risk of troubleshooting. Corrective actions include design changes to minimize and improve plant response to SGFP runbacks, review of the human performance aspects of the root causes and procedural improvements for managing risk of work activities. Operator actions were in accordance with procedures and the plant responded as designed to the manual reactor trip. There were no safety consequences associated with this event. This event is reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to reactor trip and AFW system actuation.
272 | 2722003002 | 2003-07-29 | QC5 | Loss of Non-safety-Related Bus |  | X | [13 empty] | X | [29 empty] | Salem 1 | P | WE | PO | 100 | On July 29, 2003 at 1329 Salem Unit 1 reactor tripped automatically due to generator protection and turbine trip. The cause of this event was an indicated ground fault on the 500KV 1-5 breaker which caused protective relaying to actuate which resulted in isolating the Unit 1 generator causing a generator and turbine trip which lead to a reactor trip. In addition, loss of bus section 1 caused the loss of the 14 station power transformer (SPT) which was feeding the 1B and 1C vital busses. The 1B and 1C vital busses transferred as designed to the 13 SPT, which was feeding the 1A vital bus. In addition, three of the Circulating Water (CW) pumps transferred to the 13 SPT as designed. As a result of the event, the 4KV vital bus voltages dropped below the second level undervoltage setting of 95.1%. Voltage on the Salem Unit 1 4KV vital busses did not recover to the reset setpoint before the relay timeout caused the relay logic to separate the vital busses from offsite power. The Emergency Diesel Generators (EDG) started and loaded as expected and all systems responded as designed. Salem Unit 2 responded as expected throughout the transient. An Unusual Event (UE) was declared at 1401 due to a loss of offsite power for greater than 15 minutes to the vital busses. The UE was exited at 2201 after restoring normal power to the Unit 1 vital busses. Troubleshooting of the 1-5 breaker "Breaker Failure Scheme" circuitry found a shorted cable. The "Breaker Failure Scheme" circuitry was repaired using spare conductors to restore the 1-5 breaker to service. The automatic transfer of Circulating Water busses was temporarily disabled to permit plant restart.
272 | 2722006001 | 2006-03-08 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Salem 1 | P | WE | PO | 100 | On March 8, 2006 at 1109, with Salem Unit 1 at 100 % power, a turbine trip signal was received in the main control room with an immediate reactor trip. The reactor trip actions and plant recovery were performed without complications. Analysis of computer data indicated that the turbine over speed circuit initiated an overspeed signal at 103% and tripped the main turbine as designed. Turbine speed was a constant 1800-rpm as controlled by the electric grid with the generator synchronized to it. The most probable cause of the turbine trip reactor trip was Radio Frequency Interference (RFI) or Electro Magnetic Interference (EMI) by an unknown source. Some of the corrective actions taken were the following: (1) prohibiting the use of electric tools, radios, cellular phones, portable radios, arc flash welders and other equipment that could result in EMI or RFI in relay rooms and (2) posting warning signs in the effected areas. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B."
272 | 2722007002 | 2007-04-24 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Salem 1 | P | WE | PO | 40 | On April 24, 2007 at approximately 2248, a manual reactor trip was initiated with reactor power level at approximately 40%. The manual reactor trip was initiated in response to a degraded Circulating Water System (CWS) and in accordance with operating procedures. The degradation of the CWS was due to extremely heavy river debris loadings that affected the ability of plant equipment to operate under the condition. The unit was returned to service on April 26, 2007 at 1236 following the cleaning of the condenser water boxes and lowering river debris conditions. On April 30, 2007, at approximately 1502, with the unit at approximately 80% power a sudden localized high amount of river water debris again affected the CWS intake resulting in the loss of four (4) circulating water pumps due to high screen differential levels, and a manual reactor trip. The cause of manual reactor trips is attributed to unusual and severe external environmental conditions resulting in record high amounts of river debris loadings, which challenged the design of the CWS. Following cleaning and inspection of the Circulating Water Traveling Screens, condenser water boxes, and lowering river debris conditions the unit was returned to service on May 3, 2007 at 0310. A root cause investigation has been initiated to improve the plant operation and to minimize challenges to the CWS design by: (a) Improving predictive tools and actions on high river debris conditions, and (b)Improving the availability and reliability of the Circulating Water System. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)...."
272 | 2722007002 | 2007-04-30 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Salem 1 | P | WE | PO | 80 | On April 24, 2007 at approximately 2248, a manual reactor trip was initiated with reactor power level at approximately 40%. The manual reactor trip was initiated in response to a degraded Circulating Water System (CWS) and in accordance with operating procedures. The degradation of the CWS was due to extremely heavy river debris loadings that affected the ability of plant equipment to operate under the condition. The unit was returned to service on April 26, 2007 at 1236 following the cleaning of the condenser water boxes and lowering river debris conditions. On April 30, 2007, at approximately 1502, with the unit at approximately 80% power a sudden localized high amount of river water debris again affected the CWS intake resulting in the loss of four (4) circulating water pumps due to high screen differential levels, and a manual reactor trip. The cause of manual reactor trips is attributed to unusual and severe external environmental conditions resulting in record high amounts of river debris loadings, which challenged the design of the CWS. Following cleaning and inspection of the Circulating Water Traveling Screens, condenser water boxes, and lowering river debris conditions the unit was returned to service on May 3, 2007 at 0310. A root cause investigation has been initiated to improve the plant operation and to minimize challenges to the CWS design by: (a) Improving predictive tools and actions on high river debris conditions, and (b)Improving the availability and reliability of the Circulating Water System. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)...."
272 | 2722007003 | 2007-12-28 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Salem 1 | P | WE | PO | 100 | At 1754 on December 28, 2007, Salem Unit 1 experienced an automatic reactor trip due to low Reactor Coolant System loop flow when the 12 Station Power Transformer (SPT) failed. The loss of the 12 SPT resulted in a loss of power to the 1 "F" and 1 "G" Group Busses and associated 13 and 14 Reactor Coolant Pumps causing a subsequent reactor trip on low Reactor Coolant System loop flow. Inadequate scope of maintenance procedures performed on 12 SPT Load Tap Changer (LTC) internal components and insufficient performance monitoring of degrading LTC conditions resulted in the failure of the collector rings and stationary and moving contacts on the LTC. There were no complications associated with the unit trip. The failed components were replaced, the transformer was tested satisfactorily and the unit was returned to service on December 31, 2007. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)...."
272 | 2722010002 | 2010-07-07 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Salem 1 | P | WE | PO | 100 | On July 7, 2010, at approximately 1118, an automatic reactor trip was initiated due to a turbine trip above 50% reactor power. The turbine trip was the result of the actuation of the regular and back-up phase B-C differential relays in the main generator protection scheme. This actuation was the result of an arc flash across the "B" phase main power transformer bushing following an inadvertent actuation of the transformer fire protection deluge system. The deluge system was actuated by one of the 18 air-pilot sprinkler heads that fused due to the transformer's heat, unusually high ambient temperatures, direct sunlight and restricted ventilation caused by concrete walls that surround three sides of the main power transformer "B" phase. Mist from the deluge system actuation rose above the main power transformer "B" phase bushing, driven by the transformer operating fans, heat rising from the transformer and the close proximity of the concrete wall enclosure, which resulted in the observed arc flash and bushing failure. Corrective actions included replacing the main power transformer deluge system air-pilot sprinkler heads with sprinkler heads that have a higher temperature setpoint. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)….”
272 | 2722010005 | 2010-10-15 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 100 | On October 15, 2010, at approximately 2312, Salem Unit 1 experienced an automatic reactor trip. The automatic reactor trip was the result of a turbine trip. The cause of the turbine trip was the actuation of the loss of field relay, which provides the regular (primary) protection for loss of excitation for the main generator. The exact cause for the loss of excitation has not yet been determined; a root cause evaluation is in progress. The most likely cause for the actuation of the loss of field relay is a defective Automatic Digital Regulator computer (WDR 2000). Corrective actions included: Repairing the main generator potential transformer spring loaded detent drawer locking mechanism and replacing the fuses. Unit 1 was returned to service with the voltage regulator in manual control. The unit 1 voltage regulator will be replaced during the next scheduled refueling outage. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).…”
272 | 2722011003 | 2011-04-21 | QL7 | Degraded condenser vacuum | [45 empty] | Salem 1 | P | WE | PO | 89 | This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(A...." On April 21, 2011, at approximately 16:00, a manual reactor trip was initiated with reactor power level at approximately 89%. The manual reactor trip was initiated in response to a degraded Circulating Water (CW) system and in accordance with abnormal operating procedures. The CW system degradation was due to heavy detritus loading that affected the ability of CW traveling water screens (TWS) to operate, and the resultant loss of circulating water pumps. The unit was returned to service on April 23, 2011, at 05:19 after the debris was cleared from the screens, condenser water boxes were cleaned and the established management criteria developed in the Operational and Technical Decision Making Process were met.
272 | 2722012001 | 2012-04-30 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Salem 1 | P | WE | PO | 100 | On April 30th, 2012, at 1003 hours. Salem Unit 1 experienced an invalid Train A Safety Injection, Reactor Trip, Main Steam Line Isolation, Emergency Diesel Generator start, Phase A Isolation, and start of the Auxiliary Feedwater Pumps. Technical Specification 3.0.3 was entered due to both trains of Safety Injection actuation logic being blocked after actuation per system design. The plant exited Technical Specification 3.0.3 at 1428 hrs. when Train B of the Solid State Protection System was reset. The operating crew however, failed to recognize all Technical Specification Action Statements associated with inoperability of a single train of the Solid State Protection System and did not meet the requirement for entry into Mode 4. On May 1st at 0802 hours operators identified the applicable Action Statement and commenced a plant cooldown. The plant entered Mode 4 at 1739 hrs. and entered Mode 5 at 2129 hours. The Safety Injection was caused by invalid actuation of Train A of the Solid State Protection System. The apparent cause of the failure to recognize entry into Technical Specification Action Statements was a lack of procedural adherence. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) for actuation of the Reactor Protection and Safety Injection systems and under 10 CFR50.73(a)(2)(i)(B) for conditions which were prohibited by the plant's Technical Specifications.
272 | 2722012004 | 2012-10-30 | QL7 | Degraded condenser vacuum | [45 empty] | Salem 1 | P | WE | PO | 100 | On October 30, 2012, Salem Unit 1 was in Mode 1, operating at 100% power when its Circulating Water Intake structure was subjected to heavy river debris from Hurricane Sandy. At 0109 hours, the reactor was manually tripped in accordance with operating procedures due to a loss of four of its six Circulating Water Pumps (CWP) {KE/P}. An automatic start of the Auxiliary Feedwater system occurred as expected on unit trip due to low Steam Generator water levels. By 0118 hours, the two remaining CWPs had been tripped due to continuing heavy debris buildup on the Circulating Water (CW) Traveling Screens {KE/SCN}. The unit was stabilized in Mode 3, Hot Standby conditions and operators transitioned from emergency response to normal operating procedures at 0141 hours. A Main Steam Line Isolation was manually initiated at 0513 hours in response to a loss of condenser vacuum. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A), for actuation of the Reactor Protection, Auxiliary Feedwater and Main Steam Line Isolation systems.
272 | 2722012005 | 2012-12-21 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 100 | On December 21, 2012, at 0527 hours, Salem Unit 1 was in Mode 1 operating at 100% rated thermal power when it experienced an automatic reactor trip due to a turbine trip. The turbine trip was the result of a Main Generator trip due to a Main Power Transformer overexcitation signal. An automatic start of the Auxiliary Feedwater system occurred as expected on unit trip due to low Steam Generator water levels. The unit was stabilized in Mode 3, Hot Standby conditions and operators transitioned to normal operating procedures at 0621 hours. The cause of this event is attributed to setpoint drift of the Main Power Transformer General Electric type STV Overexcitation trip relay. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A), for actuation of the Reactor Protection and Auxiliary Feedwater systems.
272 | 2722014002 | 2014-04-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 1 | P | WE | PO | 100 | On April 8, 2014 at 2112, Salem Unit 1 control room operators received an alarm indicating failure of the 12 Essential Controls Inverter. At 2113, operators observed indications of a trip of the 11 Steam Generator Feedwater Pump (SGFP). Operators manually initiated a Main Turbine automatic runback by manually tripping the 11 SGFP in accordance with procedures. At 2114, operators manually tripped the reactor due to a low level in the 13 Steam Generator (SG). All control rods fully inserted on the trip. All three Auxiliary Feedwater (AFW) pumps started as expected in response to low SG levels and decay heat was removed by the steam dumps to the main condenser. Operators entered the emergency procedures for the plant trip and stabilized the plant in Mode 3 (HOT STANDBY).<br /><br /> The cause of this event was due to a loss of power to the 11 SGFP speed probes. A ground on the electrical bus providing power to the speed probes was repaired.<br /><br /> This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)" for a manual reactor trip and automatic actuation of the AFW system.
272 | 2722014003 | 2014-04-13 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Salem 1 | P | WE | PO | 100 | On April 13, 2014 at 2113, Salem Unit 1 experienced an automatic reactor trip. The direct cause of the reactor trip was a generator lockout resulting from a main generator transformer overall differential relay trip. All control rods fully inserted on the trip. All three Auxiliary Feedwater (AFW) pumps started as expected in response to low steam generator levels and decay heat was removed by the steam dumps to the main condenser. Operators entered the emergency procedures for the plant trip and stabilized the plant in Mode 3 (HOT STANDBY).<br /><br /> The Main Generator Overall Differential Relay tripped due to a failed wiring termination on the C Phase Neutral Generator Current Transformer. The failed wiring termination was repaired.<br /><br /> This report is made in accordance with 10 CFR 50.73 (a)(2)(iv)(A), "...any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2Xiv)(B)..." due to an automatic reactor trip and actuation of the AFW system.
272 | 2722014004 | 2014-05-07 | QR5 | Turbine Trip | [45 empty] | Salem 1 | P | WE | PO | 97 | On May 7, 2014 at 0456, Salem Unit 1 experienced an automatic reactor trip. The direct cause of the reactor trip was a generator lockout resulting from a main generator differential relay trip. All control rods fully inserted on the trip. All three Auxiliary Feedwater (AFW) pumps started as expected in response to low steam generator levels and decay heat was removed by the steam dumps to the main condenser. Operators entered the emergency procedures for the plant trip and stabilized the plant in Mode 3 (HOT STANDBY).<br /><br /> The Main Generator Differential Relay tripped due to a failed wiring termination on the A Phase Neutral Generator Current Transformer (CT). The failed wiring termination was repaired.<br /><br /> This report is made in accordance with 10 CFR 50.73 (a)(2)(iv)(A), " ... any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) ... " due to an automatic reactor trip and actuation of the AFW system.
272 | 2722014006 | 2014-10-19 | QR6 | Manual Reactor Trip | [45 empty] | Salem 1 | P | WE | PO | 20 | On October 19, 2014, at 2051, while performing a unit shutdown in preparation for its twenty-third refueling outage, Salem unit 1 control room operators initiated a manual reactor trip at approximately 20 percent reactor power. The manual reactor trip was inserted due to concerns with the 1B Main Power Transformer, which had been in service with identified oil leakage. All control rods fully inserted on the trip. The auxiliary feedwater system actuated as designed in response to low steam generator levels. Decay heat removal was via the steam dumps to the main condenser. The plant was stabilized in Hot Standby.<br /><br /> Operators failed to recognize parameters on 1B Main Power Transformer which would have required them to enter an Adverse Condition Monitoring Plan. Entry into the plan would have required them to perform a fast load reduction and remove the main turbine from service at 40 percent power. Salem Generating Station will fully integrate procedure use and adherence principles and behaviors throughout Operations.<br /><br /> This report is made in accordance with 10 CFR 50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) ... "for a manual reactor trip and for automatic actuation of the auxiliary feedwater system.
272 | 2722020001 | 2020-03-25 | QR3 | Reactivity Control Imbalance | [45 empty] | Salem 1 | P | WE | PO | 17 | At 0056 on 3/25/2020, with Unit 1 at 17 percent power during a plant return from a scheduled refueling outage, the reactor was manually tripped due to a failure of the 11 Rod Control Motor Generator due to a malfunction of its associated Voltage Regulator. All systems responded normally post-trip. An actuation of the Auxiliary Feedwater system occurred following the manual reactor trip as expected due to low level in the steam generators. The unit was stabilized in Mode 3. <br /><br /> The failed equipment was repaired. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A).
275 | 2751987001 | 1987-01-05 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 33 | On January 5, 1987, at 2235 PST, with the unit in Mode 1 (Power Operation), a unit trip, turbine trip, and subsequent reactor trip occurred while the unit was being ramped down in power because of low electrohydraulic (EH) control fluid level. The appropriate emergency procedures were followed and the unit was stabilized in Mode 3 (Hot Standby) at 2247 PST. <br /><br />The low EH control fluid level was caused by leakage from a fitting on a turbine stop valve, FCV 143. The fitting most likely was disturbed during fire fighting and cleanup after a minor loose insulation fire several days earlier. <br /><br />The significant event notification required by 10 CFR 50.72 was made at 2311 PST, January 5, 1987. <br /><br /> The EH reservoir was filled and the leaking fitting was inspected. There was no damage to the fitting, and it was returned to service. The entire EH system was walked down, and all fittings were checked for proper installation and tightness; no discrepancies were found. The system was then pressure checked, and no leakage was found.
275 | 2751987002 | 1987-02-22 | QP5 | Excessive Feedwater Flow | [45 empty] | Diablo Canyon 1 | P | WE | PO | 30 | On February 22, 1987 at approximately 0840 PST, with Unit 1 in Mode 1 (Power Operation) at 30 percent power, licensed operators were preparing to return to 100 percent power following a power reduction. <br /><br />With the steam generator feedwater control system in automatic at this power level, the level control system was not performing satisfactorily. Several attempts to control steam generator water level by assuming manual control of feedwater regulating valve position and main feedwater pump speed were not effective in maintaining proper steam generator water levels. At 0900 PST, February 22, 1987, the Unit 1 turbine generator tripped on high steam generator 1-4 water level, resulting in a subsequent reactor trip. All safety systems responded as designed, and the unit was stabilized in Mode 3 (Hot Standby). <br /><br />The difficulties experienced in controlling steam generator water level resulted from a calibration drift of the electrical current to pressure (I/P) converter on one of the feedwater regulating valves and a steam generator water level control system with characteristic high sensitivity to operator responses at lower power levels. <br /><br />The I/P converter was recalibrated and returned to service. An Engineering and Operations Task Force has been formed to investigate steam generator water level control system performance problems. This event was reviewed with appropriate operations personnel.
275 | 2751987004 | 1987-03-15 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On March 15, 1987, at 1933 PST, with Unit 1 in Mode 1 (Power Operation), a reactor trip occurred when an airplane crashed into the Diablo Canyon-Gates 500 kV transmission line approximately 50 miles from the plant site. <br /><br />When the airplane collided with the 500 kV transmission line, a three phase to ground electrical fault occurred, which caused a large 500 kV system current and voltage transient. The transient created a low voltage condition on the plant auxiliary power system and caused a reactor trip due to reactor coolant pump bus undervoltage relay actuation. <br /><br />At the time of the event, Unit 1 main generator voltage regulation was in manual control, awaiting adjustments to eliminate undesirable system fluctuations observed earlier while in automatic control. <br /><br /> A significant event was declared in accordance with 10 CFR 50.72 at 1933 PST, and terminated at 1933 PST. The unit was stabilized in Mode 3 (Hot Standby) at 1948 PST. <br /><br /> The root cause of the reactor trip is the inability of the unit to withstand a major 500 kV voltage transient with the main generator voltage regulation in manual control. <br /><br />Due to the circumstances of the event, no corrective action was deemed necessary.
275 | 2751987006 | 1987-05-11 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 43 | On May 11, 1987, at 0608 PDT, with the unit in Mode 1 (Power Operation) at 43 percent power, a main transformer bank line pilot wire differential relay signal caused a unit trip, turbine trip, and subsequent reactor trip. The appropriate emergency procedures were followed, and the unit was stabilized in Mode 3 (Hot Standby) at 0623 PDT. <br /><br />The nonemergency four-hour notification required by 10 CFR 50.72 was made at 0708 PDT, May 11, 1987. <br /><br /> The pilot wire differential relay incorrectly tripped during a fault (phase-to-phase) on a 500 kV electrical reactor near the Midway Substation. To prevent recurrence, the unit trip signal provided by the pilot wire differential relay has been removed from service. The existing electro-mechanical differential relays and pilot wires for both units will be replaced with solid state relays and fiber-optic cable. Upon replacement, the unit trip signal will be returned to service.
275 | 2751987023 | 1987-12-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On December 13, 1987, at 0325 PST, with the unit in Mode 1 (Power Operation) at 100 percent power, a low-low steam generator level reactor trip occurred following a trip of main feedwater pump (MFWP) 1-1. All automatic safety functions responded as required. The unit was stabilized in Mode 3 (Hot Standby) by 0500 PST. The 4-hour nonemergency report required by 10 CFR 50.72 was made at 0411 PST. <br /><br />The MFWP trip occurred during continuity tests in the safeguards test panel for the solid state protection system (SSPS) MFWP trip circuit. Investigation determined that the current limiting resistor that allowed the performance of the continuity test was not sufficient to prevent the solenoid from operating when the test circuit was actuated. The original 2.5 K ohm current limiting resistor has being replaced with a 3.0 K ohm current limiting resistor to ensure that the solenoid does not operate when the test circuit is actuated.
275 | 2751988002 | 1988-01-08 | QR8 | Spurious Reactor Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On January 8, 1988, at 1011 PST, with the unit in mode 1 (Power operation) at 100 percent power, a reactor trip and subsequent turbine trip occurred due to a low reactor coolant system flow signal. All automatic safety systems responded and the unit was stabilized in Mode 3 (Hot Standby) in accordance with plant procedures. The 4-hour nonemergency report required by 10 CFR 50.72 was made at 1341 PST. <br /><br /> A plant technician was refilling the sensing line for a reactor coolant flow transmitter for the loop 3 reactor coolant low flow trip logic when, due to inadequate procedural guidance, he inadvertently depressurized the common high side pressure tap. The depressurization of the high side common tap produced low reactor coolant flow signals on the redundant loop 3 flow channels which, coincident with the loss of flow permissive P-8 (the loss of flow permissive actuates when reactor power is above 35 percent), produced the required reactor trip logic. <br /><br />To prevent recurrence of this event, STP I-8B5 was revised to include detailed guidance and controls for returning RCS flow channel transmitters to operation as well as precautions to be observed during work on these transmitters when the reactor trip breakers are closed. A tailboard was conducted on this event for I&C technicians. This event is being added to the I&C quarterly training seminar.
275 | 2751988020 | 1988-07-10 | QR8 | Spurious Reactor Trip | [45 empty] | Diablo Canyon 1 | P | WE | SU | 2 | On July 10, 1988, at 1544 PDT, a reactor trip was initiated from the two out of four coincidence logic for the over temperature delta temperature (OTDT) reactor protection system. The unit was stabilized in Mode 3 (Hot Standby) and the 4-hour nonemergency report required by 10 CFR 50.72(b)(2)(ii) was made at 1653 PDT. <br /><br />The cause of the event was determined to be personnel error (cognitive) by an Instrumentation and Control (I&C) technician performing Surveillance Test Procedure I-2B, "Nuclear Power Range Channel Analog Channel Operational Test," who inadvertently adjusted Detector A test signal to greater than 50 percent instead of the procedurally required Detector B test signal. <br /><br />To prevent recurrence the I&C technician involved has been counseled, and all I&C technicians will receive training regarding the requirements for self verification and procedure compliance. Additionally, plant operators will review the Operations Incident Summary and receive training regarding scaling considerations for the delta flux penalties for the OTDT protection channels.
275 | 2751988021 | 1988-07-12 | QP5 | Excessive Feedwater Flow | [45 empty] | Diablo Canyon 1 | P | WE | PO | 18 | On July 12, 1988, at 1729 PDT, a reactor trip was initiated as a result of a steam generator high-high level during the performance of Operating Procedure (OP) L-3, "Secondary Plant Startup". The unit was stabilized in Mode 3 (Hot Standby) and the 4-hour nonemergency report required by 10 CFR 50.72(b)(2)(ii) was made at 1749 PDT. <br /><br />The event was determined to have been caused by an inadequate OP L-3, which required the automatic control of main feedwater regulating valves prior to paralleling the turbine to the electrical power grid and establishing heated feedwater from the feedwater heater train. This method resulted in an inherently unstable steam generator level control that resulted in diverging control system oscillations. <br /><br />To prevent recurrence, procedure OP L-3 has been revised to require paralleling the generator to the grid and establishing heated feedwater prior to automatic operation of the feedwater regulating valves.
275 | 2751988025 | 1988-08-30 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Diablo Canyon 1 | P | WE | PO | 99 | On August 30, 1988, at 2042 PDT. a Unit 1 reactor trip occurred following the trip of main feedwater pump (MFWP) 1-2. The Unit was stabilized in Mode 3 (Hot Standby), and the 4-hour non-emergency report required by 10 CFR 50.72(b)(2)(ii) was made on August 30, 1988, at 2142 PDT. <br /><br />MFWP 1-2 tripped on overspeed when the feed pump turbine governor valves fully opened due to a pressure build-up in the signal air line to the MFWP control valve positioners. The pressure build-up resulted from leakage into the isolated manual regulator line. The line was isolated due to a closed isolation valve in the line between the high select and the manual regulator. This valve had been installed by the vendor as a vendor field change prior to installation of the MFWP control system in Unit 1. The root causes were determined to be both the failure of the vendor to document a change of design, and failure of the PG&E organization requesting the change to document that request and verify appropriate document revision. <br /><br />Personnel awareness regarding plant configuration change requirements has been heightened through revision and enhancement of procedures which govern initiation and implementation of design changes.
275 | 2751988026 | 1988-09-01 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 13 | On September 1, 1988 at 2016 PDT, at approximately 13 percent power during restart, Unit 1 experienced a unit trip/turbine trip initiated by the anti-motoring relay, and subsequent reactor trip. The unit was stabilized in Mode 3 (Hot Standby) and the 4-hour nonemergency report required by 10 CFR 50.72(b)(2)(ii) was made at 2110 PDT. <br /><br />The event was caused by the root isolation valve on the low side of differential pressure switch PS-30 being in the closed position. Safety systems responded as designed. <br /><br />An investigation led to the conclusion that the valve was closed between July 13, 1988 (the previous Unit 1 startup in which no abnormal behavior was noted) and August 9, 1988 (when the valve was noted to be in a closed position). Records search and personnel inquiries did not provide any information on the reason or the precise time when the valve was closed. <br /><br /> To reduce the probability of recurrence, administrative procedures were issued on September 8, 1988 to provide better instruction on the authorization needed to operate plant components and to provide better documentation of component status. <br /><br />Procedures, OP C-5; I, "Moisture Separator/Reheater-Make Available" and OP C-2, I. "Main Steam and Steam Dump System Alignment Check List" have been revised to include the PS-30 root valves.
275 | 2751989009 | 1989-10-06 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On October 6, 1989, at 1302 PDT, with Unit 1 in Mode 1 (power operation) at 100 percent power, an automatic safety injection/reactor trip was actuated from a steam line differential pressure signal. At 1321 PDT, a 1-hour emergency report was made in accordance with 10 CFR 50.72(a)(1)(i). <br /><br /> During the removal from service process for calibration of a pressure transmitter for an atmospheric steam dump valve (ADV) control, pressure oscillations were created in the common sensing line with a protection set steam generator pressure transmitter. This caused repeated actuations of a steam line differential pressure bistable. The bistable actuation, combined with a previously tripped steam pressure bistable, satisfied the 2/3 coincidence logic to generate a steam line differential pressure SI signal.<br /><br /> The I&C removal from service/calibration procedure was inadequate in that it did not verify the condition of other channel bistables to ensure that coincident logic could not be satisfied. I&C procedures were revised to assure that work on equipment sharing a common process tap is not performed if any of the shared instrumentation is in a configuration that produces a protection actuation or control function. Actions for associated events included developing a policy for guidance on tripped bistables, developing a procedure to control non-TS equipment called upon in emergency conditions, developing training on the characteristics of ADVs, issuing an operations order for normal operation of the steam space sample line, and revising testing to include the dynamic properties of PORVs.
275 | 2751990002 | 1990-02-20 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Diablo Canyon 1 | P | WE | PO | 100 | On February 20, 1990, at 0530 PST, with Unit 1 operating at 100% power, plant operators initiated a manual reactor trip after both main feedwater pumps (MFPs) had tripped. Plant operators initiated actions per plant procedures and stabilized the unit in Mode 3 (Hot Standby) at 0600 PST. <br /><br /> A detailed investigation was performed using information from all event recorders and interviews with personnel involved. This investigation concluded that the immediate cause of the event was all main feedwater control valves tripping shut which caused both MFPs to trip on high discharge pressure. The investigation concluded that the most probable cause of the valves tripping closed was either a non-repeatable Solid State Protection System (SSPS) card failure or an inadvertent actuation caused by Instrumentation and Controls (I&C) technicians working in the SSPS racks.<br /><br /> Immediate corrective actions included extensive testing and inspection of the SSPS to determine the root cause, replacement of the two suspect SSPS cards and a cautionary tailboard of I&C technicians regarding the potential hazards associated with SSPS testing.
275 | 2751990005 | 1990-06-14 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On June 14, 1990, at 1555 PDT, with Unit 1 in Mode 1 (Power Operation), Unit 1 experienced a reactor trip on power range high positive rate during a load rejection from 100 percent power. The load rejection occurred due to an offsite 500 kV transmission system transient. Unit 1 reactor tripped due to increasing reactor coolant pump (RCP) speed and reactor coolant flow which resulted in lower coolant temperatures in the upper regions of the core. The increase in RCP speed was caused by an increased 12 kV bus frequency that was caused by main turbine speedup from load loss. The RCPs tripped on underfrequency as the generator frequency decreased after the turbine trip, placing the reactor into natural circulation. <br /><br /> A four-hour, non-emergency report was made in accordance with 10 CFR 50.72(b)(2)(ii) on June 14, 1990, at 1756 PDT. <br /><br /> The root cause of this event was a false relay operation at Midway Substation which caused the opening of the Unit 1 output breaker causing the load rejection and the subsequent reactor trip. The Unit 1 second output breaker had been cleared for 500 kV switchyard maintenance. The misoperating relay was found and isolated. The relay will be investigated and returned to service, and a memorandum has been sent to Power Control advising them of conditions which may put the plant at high risk of tripping if certain switchyard work is performed.
275 | 2751990014 | 1990-12-05 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 53 | On December 5, 1990, at 2204 PST, with Unit 1 in Mode 1 (Power Operation) at 53 percent power, the unit experienced a reactor trip due to a turbine trip with reactor power greater than 50 percent. A four-hour, non-emergency report was made in accordance with 10 CFR 50.72 (b)(2)(ii) on December 6, 1990, at 0020 PST.<br /><br /> The turbine tripped as a result of a runback initiated by a false indication of a low stator cooling water flow condition. The indicated low stator cooling water flow condition resulted when a flow switch stuck in the low flow position after starting the standby stator cooling water pump. The runback failed to reduce the generator load to below the setpoint of the unit runback check relay, 51RU. This resulted in a generator trip, followed by a turbine trip and subsequent reactor trip.<br /><br /> During the event, circulating water pump 1-2 failed to restart on auto transfer to the start-up bus. <br /><br /> The root cause of the event was determined to be inadequate evaluation of the runback limit for the digital electro-hydraulic controller (DEHC). The runback limit was not sufficiently low to assure that the turbine would runback to a point below the reset point of the 51RU relay. Corrective actions for the event include: (1) upgrading the stator cooling water flow switches; (2) initiating a work request to modify the setpoint for the turbine valve position software; (3) issuing a maintenance bulletin; and (4) developing a preventive maintenance test for circulating water pump auto transfer relays.
275 | 2751990017 | 1990-12-24 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | Diablo Canyon 1 | P | WE | PO | 88 | On December 24, 1990, at 0318 PST, with Unit 1 in Mode 1 (Power operation) at 88 percent power, a reactor trip and safety injection occurred due to low pressurizer pressure. During the recovery from the trip, reactor coolant system (RCS) cooldown exceeded the allowable rate of 100 degrees Fahrenheit per hour of Technical Specification 3.4.9. An Unusual Event was declared at 0320 PST. A one-hour emergency report required by 10 CFR 50.72 (a)(1)(i) was made on December 24, 1990, at 0342 PST. On December 24, 1990, an Event Investigation Team was formed to investigate the event. <br /><br /> The cause of the trip was a pressurizer spray valve that failed open due to its feedback linkage becoming disconnected because the locking device for the screw holding the linkage to the valve stem had not been installed. The major contributor to the overcooling of the RCS was the failure of a condenser steam dump valve pilot stem due to sticking, which resulted in bending of the main stem and thus holding open the valve. <br /><br /> Corrective actions for the event include revising Maintenance Procedure I-2.25-1 to address the use of appropriate locking devices on feedback linkages, revising Abnormal Operating Procedure AP-13 to provide additional guidance for dealing with failed open pressurizer spray valves, revising Emergency Procedure E-0 to provide guidance on closing the main steam isolation valves during cooldown transients, revising design drawings to clarify the installation of the feedback linkage, sending a letter to the vendor describing the feedback linkage problem and asking them to review the documentation used for the linkage assembly for adequacy. Also, the seating angles of the condenser steam dump valves were modified to alleviate sticking.
275 | 2751991002 | 1991-02-01 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Diablo Canyon 1 | P | WE | PO | 90 | On February 1, 1991, at 0909 PST, with Unit 1 operating at approximately 90 percent power, a Unit 1 reactor trip occurred due to Steam Generator (SG) 1-4 low level coincident with a steam flow/feedwater flow mismatch. A four-hour, non-emergency report was made in accordance with 10 CFR 50.72 (b)(2)(ii) on February 1, 1991, at 1149 PST. <br /><br /> The root cause of the event was determined to be personnel error (cognitive). Personnel erecting scaffolding in the area of feedwater regulating valve FCV-530 inadvertently closed valve AIR-I-1-1041, which isolated instrument air supply to feedwater regulating and bypass valves FW-1-FCV-530, 540, 1530, and 1540. The regulating and bypass valves failed closed on loss of instrument air, isolating feedwater flow to two SGs. SG levels decreased and the unit tripped. <br /><br /> The corrective actions include: (1) issuance of a procedure to secure sensitive air valves against accidental closure; (2) issuance of a maintenance policy requiring that all work to be performed prior to the outage must be on the approved daily schedule; (3) issuance of a Work Planning policy on marking work packages; and (4) revision of Administrative Procedure (AP) C-59, "Elevated Work Structures," to clarify responsibilities and restrictions for erection and removal of scaffolding.
275 | 2751991007 | 1991-04-23 | QP5 | Excessive Feedwater Flow | [45 empty] | Diablo Canyon 1 | P | WE | PO | 50 | On April 23, 1991, at 0846 PDT, with Unit 1 in Mode 1 (Power Operation) at approximately 50 percent power, the unit experienced a reactor trip due to a turbine trip caused by high steam generator (SG) 1-3 level (P-14). <br /><br /> Preceeding the trip, all main feedwater (MFW) control components were in automatic except SG 1-3 feedwater regulating valve (FCV-530) which was in manual control mode with feedwater regulating bypass valve (FCV-1530) in automatic control mode. At 0834 PDT, MFW pump 1-1 speed had increased by approximately 1000 rpm, initiating a feedwater control transient. <br /><br /> On April 23, 1991, at 0849 PDT, following the turbine trip and reactor trip, plant operators manually closed the main steam isolation valves to terminate an unanticipated cooldown. At 0903 PDT, the unit was stabilized in Mode 3 at normal reactor coolant temperature and pressure. The 4-hour non-emergency report required by 10 CFR 50.72(b)(2)(ii) was made at 1015 PDT. <br /><br /> The root cause of the initiating feedwater transient was determined to be a random component failure of an operational amplifier in the MFW pump 1-1 speed controller "track and hold" board. The component was replaced and the plant was returned to operation. No corrective actions to prevent recurrence are required. As a prudent action, an operations incident summary will be prepared for review by all plant operators to aid in identifying and responding to abnormal feedwater control occurrences.
275 | 2751991008 | 1991-04-24 | QR3 | Reactivity Control Imbalance | [45 empty] | Diablo Canyon 1 | P | WE | SU | 2 | On April 24, 1991, at 1827 PDT, with Unit 1 in Mode 2 (Startup) at 2 percent power, a plant operator manually tripped the reactor due to inability to manually move control rods into the core due to a rod control urgent failure alarm condition.<br /><br /> Immediately preceeding the trip, on April 24, 1991, at 1819 PDT, the unit had been taken critical and reactor power stabilized for plant testing. Following initial data collection, the plant operator stepped control rods out to increase power to approximately 2.0 percent reactor thermal power (RTP) for further testing. At 1822 PDT, a rod control urgent failure alarm was received in the control room. Plant operators confirmed that manual rod control was inhibited, confirmed locally that rod control power cabinet PN1AC had an urgent failure, and initiated a manual reactor trip to terminate the power increase at approximately 2.5 percent RTP. On April 24, 1991, at 2054 PDT, a four-hour, non-emergency notification was made in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The root cause of this event is unknown. However, based on investigations of possible causes, PG&E believes that the most probable root cause is personnel error. Due to misleading information contained in a 1989 work order, a contract electrician had replaced the power supply fuses in the wrong electrical cabinet thereby inadvertently leaving low reliability fuses in the system. Corrective actions to prevent recurrence include labeling of the fused disconnect panels for the rod control system and tailboarding of maintenance personnel.
275 | 2751991009 | 1991-05-17 | QR8 | Spurious Reactor Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On May 17, 1991, at 0624 PDT, with Unit 1 operating at 100 percent power, a reactor trip occurred due to nuclear instrumentation power range two-out-of-four channels high flux at high setpoint signals: At 0625 PDT, a safety injection occurred due to two-out-of-four low pressurizer pressure signals. During the event, reactor coolant system cooldown exceeded the allowable rate of 100 degrees Fahrenheit per hour of Technical Specification 3.4.9.1.b. An Unusual Event was declared at 0625 PDT on May 17, 1991. A one-hour emergency report required by 10 CFR 50.72(a)(1)(i) was made on May 17, 1991, at 0633 PDT.<br /><br /> The cause of the reactor trip was determined to be personnel error. An I&C technician inadvertently deenergized a second nuclear instrumentation power range channel (N42) while performing surveillance testing on another power range channel (N41). The cause of the safety injection was steam dump valves that failed open and overcooled the reactor coolant system. <br /><br /> Corrective actions for the event included: (1) temporary stoppage of all I&C work until I&C personnel were tailboarded on the necessity of self-verification; and (2) installation of switch and fuse covers on each channel to act as a physical barrier to prevent inadvertent actions. <br /><br /> Corrective actions for the steam dump valves will be discussed in Licensee Event Report 1-90-017-01.
275 | 2751992002 | 1992-03-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On March 6, 1992, at 1032 PST with Unit 1 in Mode 1 (Power Operation) at 100 percent power, a low-low steam generator water level reactor trip was initiated following the trip of a main feedwater pump (MFP). Plant operators initiated actions in accordance with plant procedures and stabilized the unit in Mode 3 (Hot Standby). <br /><br /> A four-hour, non-emergency report was made to the NRC on March 6, 1992, at 1213 PST, in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> A detailed investigation was performed and interviews were conducted with personnel involved. The investigation concluded that the immediate cause of this event was failure of the nonsafety-related inverter power supply for the speed sensing probes on MFP 1-1, which resulted in the tripping of MFP 1-1 and a subsequent low-low steam generator water level reactor trip. The failure of the inverter was due to poor manufacturing and design.<br /><br /> The immediate corrective actions included replacement of the existing inverter and testing and inspection of the other MFP inverters and their transfer circuitry. <br /><br /> To prevent recurrence, a new design change has been implemented that provides for a separate power supply to each of the two speed probes on each MFP.
275 | 2751992004 | 1992-04-25 | QL7 | Degraded condenser vacuum | [45 empty] | Diablo Canyon 1 | P | WE | PO | 50 | On April 25, 1992, at 0408 PDT, with Unit 1 in Mode 1 (Power Operation) at 50 percent power, Unit 1 experienced a low vacuum turbine trip and subsequent reactor trip. The unit was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. <br /><br /> The turbine trip occurred during the removal of the Main Feedwater Pump (MFP) 1-1 turbine from service to allow troubleshooting and repair of the turbine trip oil system. Problems that occurred during MFP turbine isolation caused degrading condenser vacuum. The root cause for this event is programmatic deficiency. Inadequate instructions were available for the task. In addition, the condenser vacuum pump suction line check valve leaked excessively.<br /><br /> The operating procedure for removing an MFP from service was revised to add precautions about removing the pump from service when the condenser may have degraded air removal capacity. In addition, the condenser vacuum pump suction line check valve for each unit shall be inspected and repaired as necessary before the end of the next refueling outage for each unit.
275 | 2751993011 | 1993-12-26 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On December 26, 1993, at 1423 PST, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Unit 1 experienced a turbine trip and subsequent reactor trip. The unit was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A four-hour, nonemergency report was made in accordance with 10 CFR 50.72(b)(2)(ii) at 1455 PST. <br /><br /> The event was due to a failed excitation system isolation transducer combined with a fault on the Midway-Kern #1 and #2 230 kV lines. The fault, combined with the excitation protection system transducer failure, resulted in a unit trip. <br /><br /> The operators manually closed the main steam isolation valves (MSIVs) in response to a reactor coolant system (RCS) pressure and temperature decrease. This action was successful in stopping the cooldown. The RCS pressure was recovered and the MSIVs were reopened. An investigation concluded that the cooldown was due to a combination of auxiliary feedwater (AFW) flow and the additional steam flow to the Moisture Separator Reheater (MSR) 1-2A.<br /><br /> The generator excitation protection transducer was replaced. The other two Unit 1 DC-DC isolation transducers were verified to be within tolerances. The Unit 2 generator isolation transducers will be inspected during the next outage of sufficient duration.
275 | 2751994020 | 1994-12-14 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On December 14, 1994, at 0026 PST, with Unit 1 and Unit 2 in Mode 1 (Power Operation) at 100 percent power, both units experienced reactor trips. Both units were stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A four-hour, non-emergency report was made at 0131 PST in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The reactor trips were due to an undervoltage on the auxiliary power bus that provides power to the reactor coolant pumps. The undervoltage condition was due to a system disturbance external to the PG&E system. <br /><br /> Due to the circumstances of the event, no corrective actions were deemed necessary. However, the Western System Coordinating Council, a utility coordination group composed of the eleven western states and British Columbia that are interconnected through the 500 kV Pacific Intertie, will study the transient and a formal report should be available in several months. If PG&E determines that any corrective actions are necessary as a result of this final report, a supplement to this LER will be issued.
275 | 2751995009 | 1995-09-06 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On September 6, 1995, at 1555 PDT, with Unit 1 in Mode 1 (Power Operation), at approximately 100 percent power, a turbine trip and subsequent reactor trip occurred due to loss of auto stop oil pressure. Plant operators stabilized the plant in Mode 3 (Hot Standby) in accordance with emergency operating procedures. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on September 6, 1995, at 1836 PDT. <br /><br /> The cause of the event was vendor substitution of pilot valve seat material in a replacement backup trip solenoid valve in the auto stop oil system. <br /><br /> Corrective actions included replacing the solenoid valve with one having the correct seat material, allowing only inspected valves to be issued from the warehouse, and placing the defective valve on the restricted equipment list for the plant.
275 | 2751995015 | 1995-11-28 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Diablo Canyon 1 | P | WE | PO | 50 | On November 28, 1995, at 2215 PST, with Unit 1 in Mode 1 (Power Operation) at approximately 50 percent power, plant operators initiated a manual Unit 1 reactor trip. The trip was initiated when feedwater flow was lost. The in-service main feedwater pump (MFP) had tripped on high discharge pressure. Unit 1 was stabilized in Mode 3 (Hot Standby) in accordance with emergency operating procedures. A 4-hour non-emergency report was made to the NRC on November 29, 1995, at 0035 PST, in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> PG&E determined the root cause to be a design deficiency in the speed probe cabling for the MFP speed controller that resulted in the signal wire grounding inside the conduit coupling. PG&E determined a contributing cause to be the maintenance practice of storing the excess wire for the probe inside the conduit near the coupling. <br /><br /> Corrective actions included replacing the failed speed probe and inspecting the remaining speed probes on both Unit 1 and Unit 2 main feedwater pumps. PG&E will design and install connectors for the speed probes to facilitate maintenance. PG&E is reviewing this event with maintenance personnel through group meetings and will include the event in the next quarterly maintenance training program.
275 | 2751995017 | 1995-12-13 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Diablo Canyon 1 | P | WE | PO | 50 | On December 13, 1995, at 1033 PST, with Unit 1 in Mode 1 (Power Operation) at approximately 50 percent power, plant operators initiated a manual reactor trip of Unit 1 as required by OP AP-7, 'Degraded Condenser,' following debris loading of the traveling screens due to heavy swells from a major Pacific storm. The unit was stabilized in Mode 3 (Hot Standby) in accordance with emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1248 PST in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> Plant operators decreased power on Unit 2, separated the turbine generator from the grid, and stabilized the unit in Mode 2 (Start-up), at 1346 PST, to prevent damage to the traveling screens from heavy kelp loading.<br /><br /> Additional screen rakes are being added to the screens to improve the efficiency of debris removal. Simulator training has been provided to all five operating crews dealing with the loss of circulating water system screen functions. <br /><br /> The above actions are near term actions designed to reduce overall plant impact and damage to equipment. However, PG&E can not entirely eliminate the potential need to expedite manual reactor trips when high seas and dislodged plant life from the ocean bottom result in heavy debris loading on the traveling screens.
275 | 2751996008 | 1996-06-10 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Diablo Canyon 1 | P | WE | PO | 100 | On June 10, 1996, at 0106 PDT, with Unit 1 in Mode 1 (Power Operation) a manual reactor trip was initiated due to a loss of normal feedwater. On June 10, 1996, at 0203 PDT, a 4-hour non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The loss of normal feedwater was caused by a loss of both main feedwater (MFW) pumps during recovery from a MFW and condensate system flow transient due to a load transient bypass (LTB) signal actuation. The LTB actuation occurred when a plant protection system loop calculation processor (LCP) failed and was reset. <br /><br /> The root cause of this event was personnel error (cognitive) in that licensed plant operators failed to place the LTB control system in manual prior to reset of the Rack 8 LCP. <br /><br /> Plant operator and technical maintenance training will be revised regarding removing equipment from service for maintenance. Plant operating procedures will be revised regarding LTB recovery.
275 | 2751996012 | 1996-08-10 | QR7 | Other Reactor Trip (Valid RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On August 10, 1996, at 1549 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, a major disturbance on the western transmission grid resulted in reactor trips on both units. Both units were stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1842 PDT in accordance with 10 CFR 50.72 (b)(2)(ii). <br /><br /> Undervoltage and underfrequency conditions were experienced on both the auxiliary and startup systems due to a disturbance on the 500 kV system external to the PG&E system. Unit 1 experienced a reactor trip due to a 12 kV auxiliary power system reactor coolant pump (RCP) feeder bus undervoltage and Unit 2 experienced a reactor trip due to two of four RCP breakers open. <br /><br /> The Unit 1 RCPs and the circulating water pumps remained running throughout the event. Since the Unit 2 RCPs were not running, control room operators closed the Unit 2 main steam isolation valves to prevent excessive cooldown. One RCP was restarted 69 minutes after the pumps tripped off the line; thus Unit 2 was on natural circulation for 69 minutes. <br /><br /> The Western System Coordinating Council study of the transient did not provide any recommendations applicable to Diablo Canyon Power Plant. PG&E determined that no additional corrective actions were necessary.
275 | 2751996017 | 1996-11-22 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On November 22, 1996, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, an electrical fault in the 12 kV bus fed from Auxiliary Transformer 1-1 resulted in automatic reactor trip. Unit 1 was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1339 PST in accordance with 10 CFR 50.72 (b)(2)(ii). <br /><br /> The cause of the electrical fault was determined to be degradation of the 12 kV electrical bus polyvinyl chloride (PVC) insulating material (boots). Degradation of the PVC boots caused deterioration of bus duct materials, corrosion, and contamination of insulators that led to an electrical arc damaging the circuit. <br /><br /> Immediate corrective action included replacement of all suspect PVC boots with Raychem tape for Unit 1 and evaluation of the 4 kV and 12 kV bus ducts for Unit 2. <br /><br /> Corrective action to prevent recurrence includes analysis of the failed components, evaluation of PVC boots as an insulation material for electrical buses, and planned inspections of suspect 4 kV and 12 kV buses.
275 | 2751999006 | 1999-09-22 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On September 22, 1999, at 0932 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, the unit experienced a full load rejection after the 500 kV supply breakers opened. Approximately 9 seconds later, the reactor tripped automatically. Unit 1 was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. During the transient, two power operated relief valves opened for less than 1 second each. A 4-hour non-emergency report was made to the NRC at 1150 PDT in accordance with 10 CFR 50.72 (b)(2)(ii). The full load rejection was caused by a lightning strike which actuated a 500 kV overvoltage relay and opened the 500 kV breakers for Unit 1. The reactor trip was initiated by a valid OT delta T signal. Walkdowns of the affected areas were completed with no equipment damage indicated. PG&E is evaluating the design of the lightning protection system and the relay protection scheme for enhancements.
275 | 2751999009 | 1999-10-28 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Diablo Canyon 1 | P | WE | PO | 50 | On October 28, 1999, at 1359 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 30 percent power, and at 1400 PDT, with Unit 1 in Mode 1 at 50 percent power, plant operators initiated manual reactor trips as required by Operating Procedure AP-7, "Degraded Condenser." The trips were required when differential pressure across the intake water traveling screens exceeded limits due to sudden heavy debris loading from a major Pacific Ocean storm. The units were stabilized in Mode 3 (Hot Standby) in accordance with emergency procedures. A 4-hour, non-emergency report was made to the NRC, in accordance with 10 CFR 50.72(b)(2)(ii), at 1520 PDT. PG&E previously added screen rakes and debris grinders to the seawater cooling system to improve debris removal. Operator training was enhanced regarding loss of circulating water system screen functions. PG&E cannot entirely eliminate the potential need to expedite manual reactor trips when high seas and dislodged plant life from the ocean bottom result in heavy debris loading on the traveling screens. PG&E will designate an operations management team to focus on lessons learned and streamline the coping strategy decision making process during storm warning conditions.
275 | 2752000004 | 2000-05-15 | B1 | Loss of Offsite Power (LOOP) |  | X | [5 empty] | X | [7 empty] | X | [17 empty] | X | [11 empty] | Diablo Canyon 1 | P | WE | PO | 100 | On May 15, 2000, at 0025 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Unit 1 experienced a unit trip, followed immediately by a turbine trip and automatic reactor trip. The cause of the unit trip was an electrical phase-to-phase fault on the 12 kV bus supplied by Auxiliary Transformer 1-1.The 12 kV electrical fault created electrical arcing (fire) which damaged a nearby 4 kV startup bus resulting in loss of both offsite sources of power to all 4 kV loads. All three onsite emergency diesel generators (EDGs) started, and vital loads automatically sequenced onto the EDGs as designed. In response to the fire and loss of both sources of offsite power to vital loads, an Unusual Event (UE) was declared at 0043 PDT. The onsite fire brigade extinguished the small fire with carbon dioxide. After clearing the room of smoke, the fire was declared out at 0143 PDT. On May 16, 2000, at 0959 PDT, after offsite power was restored and electrical loads were transferred from emergency diesel generators, the UE was terminated. On May 17, 2000, at 2000 PDT, the unit entered Mode 5 (Cold Shutdown). The cause of the electrical fault could not be conclusively determined but is believed to be associated with long-term degradation, and/or inadequate preventive maintenance (PM) exacerbated by a marginal design. Corrective actions include a new PM program and upgrades to the 4 kV and 12 kV nonsegregated buses on both units.
275 | 2752000011 | 2000-11-05 | QR6 | Manual Reactor Trip | [45 empty] | Diablo Canyon 1 | P | WE | SU | 1 | On November 5, 2000, at 1707 PST with Unit 1 in Mode 2 (Startup), at 6E-9 amperes, the shift foreman ordered a manual trip of the reactor due to a failure in the rod control system. At 1744 PST, operators made a 4-hour, nonemergency notification in accordance with 10 CFR 50.72(b)(2)(ii). The root cause of the rod control failure was a faulty buffer memory card. The card was replaced and personnel performed the required maintenance verification testing.
275 | 2752000012 | 2000-11-20 | QR8 | Spurious Reactor Trip | [45 empty] | Diablo Canyon 1 | P | WE | PO | 46 | On November 20, 2000, at 0352 PST, with Unit 1 in Mode 1 (Power Operation) at approximately 46 percent power, plant operators experienced an automatic reactor trip. Incore flux map testing was in progress when an intermittent electrical short circuit in test equipment attached to Nuclear Instrumentation (NI)-44, concurrent with a preexisting tripped condition associated with NI-41, provided a two out of four coincidence resulting in a reactor trip. This event is an engineered safety feature and reactor protection system actuation. On November 20, 2000, at 0445 PST, a 4-hour nonemergency report was made in accordance with 10 CFR 50.72(b)(2)(ii). Corrective actions to preclude recurrence include revising procedures, providing a case study regarding this event and expected test prerequisites to appropriate plant personnel.
275 | 2752002004 | 2002-06-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Diablo Canyon 1 | P | WE | PO | 86 | On June 3, 2002, at 1302 PDT, while Unit 1 was in Mode 1 (power operation) at 86 percent power, Unit 1 experienced an automatic reactor trip due to low-low steam generator (SG) water level in SG 1-1. Feedwater flow was terminated to SG 1-1 when the feedwater flow control valve, FCV-510, failed closed. The valve failed closed, as designed, on loss of air when a valve-mounted air test connection broke off after contacting structural steel during thermal expansion of the feedwater piping. The test connection was reinstalled in a configuration to prevent contact with structural steel during thermal expansion. Similar installations were visually inspected during the subsequent power ascension to assure there were no other problems resulting from thermal movement of piping. The root cause of the event was a deficiency in the design-change and work-control processes to consider configuration control of trip-sensitive instruments that are mounted on plant piping subject to thermal expansion during power ascension. As corrective action to prevent recurrence, PG&E will identify trip-sensitive components on thermally expanding piping and include provisions in the design change and work-control processes to consider their configuration during modification and maintenance.
277 | 2771989012 | 1989-05-19 | QP5 | Excessive Feedwater Flow | [45 empty] | Peach Bottom 2 | B | GE | PO | 24 | At 0721 on 5/19/89 with Unit 2 at 24% thermal power the FeedWater Level Control System was transferred from single element to three element control. Immediately, the "REACTOR HI-LO LEVEL" alarm annunciated, followed by both "B" and "C" Reactor Feed Pumps (RFP) tripping simultaneously. Feedwater level control was returned to single element and a restart of "C" RFP attempted. Before feed flow could be re-established, level decreased below 0 inches resulting in an automatic scram and Group II and III isolations. The "C" RFP was restarted and level decrease stopped above -48 inches. At this level, Alternate Rod Insertion backup scram initiated and both Reactor Recirculation pumps tripped. The High Pressure Coolant Injection and Reactor Core Isolation cooling systems also receive initiation signals at this level, but did not actuate as the logic was not Satisfied. Reactor water level was restored to greater than 0 inches and the unit stabilized in the hot shutdown condition. The scram and Group II and III isolations were reset and essential systems returned to service. The root cause of this event was failure of the Feedwater Level Control Selector switch. No actual Safety consequences occurred as a result of this event. The failed switch Was replaced, feedwater control amplifiers were calibrated and procedures were enhanced. This event will be reviewed with the appropriate plant personnel. Three previous similar LERs were identified.
277 | 2771989015 | 1989-07-21 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Peach Bottom 2 | B | GE | PO | 79 | At 2231 on 7/21/89 with Unit 2 at 79% thermal power, an attempt was made to remove a malfunctioning Reactor Pressure Vessel (RPV) Pressure Regulator Set from the electronic portion of the Main Turbine (MT) Electro-Hydraulic Control (EHC) Pressure Regulating System. Immediately, the MT Bypass and Control Valves opened, causing main steam line pressure to decrease to approximately 480 psig. At 850 psig main steam line pressure a Group I Isolation occurred causing the Main Steam Isolation Valves (MSIV) to close. As a result, a full reactor scram occurred. RPV level decrease due to shrink following MSIV closure resulted in a Group II and III isolation as level decreased below 0 inches. Two Main Steam Relief Valves (MSRV) lifted once automatically, followed by manual Operator cycling of MSRVs to control RPV pressure between 930 psig and 1060 psig. The High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems were placed in operation to control RPV pressure and level. The root cause of this event was a malfunction of the electronic portion of the "A" RPV Pressure Regulator Set. No actual safety consequences occurred as a result of this event. The majority of the "A" Regulator electronic components were replaced. This event has been reviewed with appropriate plant personnel. One previous similar LER was identified.
277 | 2771989023 | 1989-10-05 | QL5 | Partial Closure of MSIVs | [45 empty] | Peach Bottom 2 | B | GE | PO | 100 | At 1806 hours on 10/5/89, with Unit 2 at 99.5% thermal power, ST 1.3A-2 "PCIS Group I Logic System Functional Test" was in progress. As part of the test, the Outboard Main Steam Isolation Valve (MSIV) AC solenoid pilot valves were de-energized, which resulted in the unexpected closure of the "D" outboard MSIV. Subsequently, an automatic reactor scram occurred at 1806 hours due to an APRM High Flux Signal upon the resultant rapid increase in reactor pressure. A reactor Water clean up isolation occurred shortly after the scram. Other safety systems operated as designed. The cause of the "D" MSIV closure was the binding of its DC solenoid pilot valve plunger in the vented position thus allowing the MSIV to close when the AC solenoid valve was de-energized. The root cause of the failure was incomplete technical guidance supplied by the solenoid manufacturer for the installation of the plunger spring in the solenoid valve. The correct technical information has been received from the manufacturer and the maintenance procedure used to install these solenoid valves on the MSIV's will be revised to reflect this information. The "D" DC solenoid valve was replaced. ST 1.3A-2 was completed satisfactorily prior to returning Unit 2 to service. The Unit 3 solenoid valves will be inspected prior to Unit 3 restart.
277 | 2771989033 | 1989-12-20 | QR8 | Spurious Reactor Trip | [13 empty] | X | [30 empty] | X | Peach Bottom 2 | B | GE | PO | 100 | On 12/20/89 at 1752 hours with Unit 2 operating at 100% power, a full scram signal was received when a technician performing a surveillance on Average Power Range Monitor (APRM) "D" inadvertently operated a switch on APRM "A" (APRM "D" actuates a "B" channel half scram signal while APRM "A" actuates an "A" channel half scram signal). The reactor feedwater pumps (RFP) tripped following the scram. The High Pressure Coolant Injection (HPCI) and the Reactor Core Isolation Cooling (RCIC) systems actuated as designed to maintain reactor water level, other safety systems operated as designed. Control Rod 38-39 settled to position 02 shortly following the scram and was later re-inserted. The root cause of the event has been attributed to procedural deficiencies and inattention to detail by the technician performing the surveillance. The technician involved in this event was counseled and disciplined. APRM Surveillance procedures which test APRM channels adjacent to other APRM channels have been revised to provide physical barriers between APRM channels during testing and to instruct operators to bypass adjacent APRM channels when permissible. Current panel labeling will be evaluated and improved as appropriate. There was one previous similar event.
277 | 2771991022 | 1991-06-27 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Peach Bottom 2 | B | GE | PO | 100 | On 6/27/91 at 1052 hours, an Offgas Recombiner isolation occurred causing main condenser vacuum to begin decreasing. A fast reactor power reduction was initiated in accordance with the procedure for a loss of main condenser vacuum. At 1106 hours, a manual scram was initiated by placing the mode switch in shutdown following the receipt of a reactor auto half scram signal. A Group II and III isolation occurred as a result of the manual scram. The cause of the event has been determined to be a defective relief valve and the lack of complete guidance for restoring the isolated system. The event has been discussed with the involved individuals and the pertinent information will be provided to Operations and other members of the technical Staff. The operating procedure for recovery will be revised to prevent future recurrences. No actual safety consequences occurred as a result of this event. There were two previous similar events.
277 | 2771991028 | 1991-08-05 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 98 | On 8/5/91 at 1432 hours, a trip of an emergency bus breaker caused an automatic 4 KV fast transfer which resulted in a Primary Containment Isolation System (PCIS) half Group 1, Group II, and Group III isolations. At 1510 hours, a reactor scram occurred due to a turbine trip from moisture separator high level which resulted in PCIS Group II/III isolations. The scram and isolations were reset and the affected systems were restored to normal. The cause of the event has been determined to be that an Electrician pulled an incorrect fuse during Preventive Maintenance activities. The 'D' moisture separator dump valve failed closed due to a positioner failure. The event has been discussed with the involved individuals and the pertinent information has been provided to the appropriate personnel. The failed components have been repaired and the Preventive Maintenance activities have been reviewed and revised as necessary. No actual safety consequences occurred as a result of this event. One previous similar LER was identified.
277 | 2771992006 | 1992-04-07 | QR6 | Manual Reactor Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 43 | On 4/7/92 at 0935 hours, the Floor Foreman reported a weld leak on a one inch vent line and that it could not be isolated during current plant conditions. At 0955 hours, the one inch vent line weld broke and a rapid shutdown was commenced in accordance with General Procedure GP-9-2 "FAST REACTOR POWER REDUCTION". At 1014 hours, a reactor scram was initiated during a fast power reduction at 43% power when the mode switch as placed in the "SHUTDOWN" position. A Primary Containment Isolation System (PCIS) Group II/III isolation occurred as expected due to the level decrease following the scram. The cause of the event has been determined to be the failure of a one inch vent line weld on a six inch condensate line. Metallurgical analysis showed that the weld failure was the result of metal fatigue due to high frequency vibration. Following the event, the scram and PCIS Group II/III isolation logics were reset. Affected systems were restored to appropriate conditions as necessary. The failed one inch weld was repaired. An evaluation is being performed on similar drain and vent line configurations in this high vibration area on both units. No actual safety consequences occurred as a result of this event. One previous similar event has been identified.
277 | 2771992009 | 1992-05-20 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 99 | On 5/20/92 at 2115 hours, during the performance of a Routine Test (RT)-0-001-408-2 "Cycling of Combined Intermediate Valves", a reactor scram occurred when two Main Turbine Combined Intermediate Valves (CIV) closed simultaneously causing a power load unbalance trip signal. The power load unbalance circuitry caused a Main Turbine Control Valve fast ClOSure which resulted in a reactor scram. The cause of the event has been determined to be an unexpected closure of the #2 Intercept Valve (IV) during testing of the #3 CIV. The investigation was unable to recreate the inadvertent closure of the #2 IV. However, a faulty test solenoid on the #2 IV was discovered which may have been a contributing factor to this event. Following the event, the scram and isolations were reset and the affected systems were restored to normal. Two CIV test logic relays and a circuit board in the test logic were replaced as a preventive measure. The faulty test solenoid will be sent offsite for failure analysis and corrective actions will be reviewed and implemented as appropriate. No actual safety consequences occurred as a result of this event. No previous similar events have been identified.
277 | 2771992010 | 1992-07-04 | C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) |  |  | X | [7 empty] | X | [5 empty] | X | [23 empty] | X |  |  |  |  | Peach Bottom 2 | B | GE | PO | 95 | On 7/4/92 at 0119 hours, the #1 Auto Transformer failed and the #3 Startup feed was lost when its breaker (3435) tripped open. The loss of the #3 Startup feed resulted in a Unit 2 Primary Containment Isolation System (PCIS) Group II/III isolation during a Unit 2 4KV fast transfer. At the same time, the E-13 4KV bus on Unit 3 failed to automatically transfer to the other Startup feed and the E-1 Emergency Diesel Generator (EGD) did not start. Loss of the E-13 4KV bus voltage de-energized the 30Y033 electrical distribution panel which caused several Steam Jet Air Ejector (SJAE) valves to fail open. This resulted in a Offgas Recombiner isolation. At 0127 hours, a Unit 3 scram occurred during the fast power reduction due to Main Turbine Condenser low vacuum. The cause of the PCIS isolations and scram has been determined to be the loss of the #3 Startup feed in conjunction with the defective E-313 breaker control switch. The defective control switch resulted in loss of the SJAE system and Main Turbine Condenser vacuum. The transformer and disconnect will be repaired or replaced as needed. The defective control switch has been replaced and tested. No actual safety consequences occurred as a result of this event. One previous similar LER has been identified.
277 | 2771992012 | 1992-07-17 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 95 | On 7/17/92 at 1903 hours, a reactor scram occurred on Unit 2 when the Main Generator output breaker tripped open and caused a Main Generator power load unbalance trip signal. This trip signal occurred during a severe thunder storm. Primary Containment Isolation System Group II/III isolations occurred as expected due to the reactor water level decrease after the scram. The cause of the scram has been determined to be a lightning strike. The scram and isolations were reset and systems were returned to normal. No actual safety consequences occurred as a result of this event. Four previous similar LERs have been identified.
277 | 2771992015 | 1992-08-17 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 97 | On 8/17/92 at 0712 hours, during the application of a Substation Load Dispatcher (LD) permit on Circuit Breaker (CB-205), a reactor scram occurred following a Main Generator Lock Out. PCIS Group II/III isolations occurred as expected. The cause of the event has been determined to be less than adequate generation and approval of a Substation LD permit. Following the event, the scram and isolations were reset and the affected systems were restored to normal. As an interim corrective action, Substation LD permits will be reviewed by Station personnel for reliability. Approved blocking sequences will then be generated for Substation equipment. No actual safety consequences occurred as a result of this event. No previous similar events have been identified.
277 | 2771993004 | 1993-03-02 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Peach Bottom 2 | B | GE | PO | 70 | On 03/02/93, the 'C' Condensate Pump breaker tripped open and caused the 'A' and 'C' RFPs to trip on low pump suction pressure. The Reactor water level decreased to the scram setpoint. The High Pressure Coolant Injection (HPCI) and the Reactor Core isolation Coolant (RCIC) systems started on low Reactor water level. The HPCI and RCIC systems continued to restore Reactor water level until the 'C' RFP was returned to service. An Unusual Event was declared due to the HPCI injection to the reactor from a valid initiation signal. The Unusual Event was terminated at 1908 hours. The cause of the scram has been determined to be an unexpected trip of the 'C' Condensate Pump. An investigation was conducted to inspect the relays and components which could have caused the 'C' Condensate Pump trip and no equipment problems could be reproduced. <br /><br /> Therefore, it has been concluded that the trip was not due to equipment failure. An investigation did identify a human factors issue with the location of the control switches. After HPCI had completed its function, it was discovered that the HPCI Auxiliary Oil Pump (AOP) would not start. The cause of the HPCI AOP failure has been determined to be a spurious failure of a time delay relay to properly operate. The relay coil has been replaced and setup. An evaluation will be performed on this event and previous similar type relay problems to identify additional corrective actions.
277 | 2771994003 | 1994-05-15 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Peach Bottom 2 | B | GE | PO | 100 | On 5/15/94, the '2A' Reactor Recirculating (RECIRC) Pump experienced an unexpected speed increase. This caused a reactor power spike which reached the Average Power Range Monitor (APRM) High Neutron Flux Scram Setpoint. It was determined that the '2A' RECIRC Pump speed increase was due to a mismatch between the Blind Controller and the Linear Variable Differential Transformer (LVDT) output signals. Troubleshooting concluded that the decrease in the LVDT output signal was caused by a spurious problem with either the LVDT or its demodulator. A spare LVDT and demodulator was installed and calibrated to control the '2A' RECIRC Scoop Tube Positioner over the full range of motion. The inputs to the strip chart recorder installed on this pump to monitor RECIRC M/G set control system performance have been modified to include a channel to monitor the status of the electrical power supply to the Scoop Tube Positioner. An evaluation will be performed to identify what actions can be taken to mitigate the effects of a future similar failure. The RECIRC M/G Sets are scheduled to be replaced with improved Adjustable Speed Drive units during the next Refueling Outages. The components which malfunctioned will be eliminated as part of this modification. No previous similar events have been identified.
277 | 2771996010 | 1996-10-06 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 88 | This LER is being submitted to report two automatic reactor shutdowns which occurred on 10/6/96 and 10/15/96 as a result of a main generator trip and lockout due to the actuation of the negative sequence current protective relay. No evidence of an actual main generator negative sequence current event was identified. During testing of the negative sequence relay instrumentation circuitry, all electrical connections were checked. Loose connections on the current transformer were identified and corrected which were believed to have caused the relay to actuate. No other potential causes were identified. Subsequently, on 10/15/96, Unit 2 automatically shutdown again as a result of a main generator trip and lockout due to the actuation of the negative sequence current protective relay. The negative sequence relay was replaced with a newer design, the trip function was defeated based on an engineering analysis, and additional monitoring equipment was installed. Unit 2 was subsequently returned to service on 10/18/96 with no anomalies identified per the monitoring program. The investigation into the cause of the actuation of the negative sequence relay is continuing. The negative sequence relay has been sent to General Electric Co. for a detailed analysis. No actual safety consequences occurred as a result of these events. both events. No previous similar LERs were identified
277 | 2771996010 | 1996-10-15 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 88 | This LER is being submitted to report two automatic reactor shutdowns which occurred on 10/6/96 and 10/15/96 as a result of a main generator trip and lockout due to the actuation of the negative sequence current protective relay. No evidence of an actual main generator negative sequence current event was identified. During testing of the negative sequence relay instrumentation circuitry, all electrical connections were checked. Loose connections on the current transformer were identified and corrected which were believed to have caused the relay to actuate. No other potential causes were identified. Subsequently, on 10/15/96, Unit 2 automatically shutdown again as a result of a main generator trip and lockout due to the actuation of the negative sequence current protective relay. The negative sequence relay was replaced with a newer design, the trip function was defeated based on an engineering analysis, and additional monitoring equipment was installed. Unit 2 was subsequently returned to service on 10/18/96 with no anomalies identified per the monitoring program. The investigation into the cause of the actuation of the negative sequence relay is continuing. The negative sequence relay has been sent to General Electric Co. for a detailed analysis. No actual safety consequences occurred as a result of these events. both events. No previous similar LERs were identified
277 | 2771997009 | 1997-11-09 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 100 | On November 9, 1997, with unit 2 at 100 percent power, a generator lockout and subsequent turbine trip occurred that resulted in a reactor scram. The turbine trip caused an expected high reactor pressure condition resulting in a main steam relief valve lifting and Alternate Rod Insertion (ARI) to initiation. The generator lockout resulted from problems caused during activities that swapped the 2AD003 battery charger from charger #1 to charger #2 when an equipment operator failed to appropriately follow procedure. No safety consequences occurred as a result of the scram and all safety systems were available. Corrective actions for the personnel error/procedure non-compliance were taken by the Senior Manager of Operations and reinforced with operations shift personnel. Additionally, during post-scram recovery activities, the 2A reactor feedpump turbine (RFPT) failed to trip on demand from the control room and at the local trip station. Corrective actions for the RFPT included repair, reinstallation and testing of the trip device, and an on-going analysis of the anomalies associated with the trip oil system.
277 | 2771999006 | 1999-09-30 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 100 | On Thursday, September 30, 1999 at approximately 19:06 hours, with Unit 2 operating at 100 percent power, a generator lockout and subsequent turbine trip, occurred that resulted in a reactor SCRAM. The turbine trip caused a high reactor pressure condition resulting in three Main Steam Relief Valves (MSRV) lifting and an Alternate Rod Insertion (ARI) initiation. Additionally, Primary Containment Isolation System (PCIS) Group II and Group III isolations occurred due to low reactor water level following the SCRAM. The generator lockout occurred when the Generator Over Frequency relay actuated the Accidental Energization Protection generator lockout relay. The Generator Over Frequency relay was actuated by a transient ground on the DC Power System. On Saturday, October 2, 1999, at approximately 04:20 hours, with Unit 2 in Mode 3, the Reactor Recirculation System piping experienced a heatup rate of approximately 170° F within 45 minutes. This exceeded the 100° F/hr heatup rate as specified In Tech. Spec. Section 3.4.9. This occurred while flushing the Residual Heat Removal (RHR) system to equalize temperatures in the 2A Reactor Recirculation piping prior to restarting the 2A recirculation pump. These activities were being performed as part of the SCRAM recovery activities. There were no safety consequences from these events and all safely systems were available. The ARI initiation, the lifting of MSRVs, and the PCIS isolations are reportable per 10 CFR 50.73 (a)(2)(iv). Exceeding the heatup rate of the recirculation line specified in Tech. Spec. Section 3.4.9 Is reportable per 10CFR 50.73 (a)(2)(i)(B).
277 | 2772000003 | 2000-09-15 | QR6 | Manual Reactor Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 16 | On September 15, 2000 at 1505 hours, with Unit 2 operating at approximately 16% power in preparation for the 13th refueling outage, an unplanned manual reactor scram was inserted. The unplanned manual reactor scram was inserted as a result of the unplanned trip of the 2B Reactor Recirculation pump due to improper tag-out coordination in conjunction with the planned trip of the main turbine. As expected, Primary Containment Isolation System (PCIS) Group 2 and Group 3 isolations, and Secondary Containment isolation also initiated. RPS, PCIS, and Secondary Containment are Engineered Safety Features (ESF). This LER is being submitted pursuant to the requirements of 10 CFR 50.73(a)(2)(iv) for the unplanned manual scram as a result of the 2B Reactor Recirculation pump trip.
277 | 2772001002 | 2001-07-01 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 100 | On June 30, 2001 at approximately 1900, the operating crew noticed erratic indications on the main turbine control valve servos, pressure set, and various EHC indicators. I&C was contacted and a troubleshooting plan was developed to determine the cause of the fluctuations. On July 1, 2001, at approximately 0206 hours, an EHC power supply failed and the Unit 2 Main Turbine tripped causing the reactor to automatically scram on a turbine control valve fast closure signal. As a result of the main turbine trip and reactor scram, reactor pressure increased to approximately 1140 psig and reactor water level decreased to approximately -13 inches. This resulted in four safety relief valves lifting to control reactor pressure and PCIS group II and III isolations occurring, as expected. Additionally, both Reactor Recirculation pumps received a trip signal when reactor pressure exceeded 1106 psig. No Emergency Core Cooling System actuations occurred due to this event. The operating crew stabilized the plant per applicable procedures.
277 | 2772001004 | 2001-10-23 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 90 | On 10/23/01, at approximately 1102 hours, an automatic reactor scram occurred as a result of a main turbine trip caused by a generator lockout. As expected when the turbine tripped, reactor pressure increased resulting in five safety relief valves lifting initially to control reactor pressure. Reactor water level decreased resulting in expected containment isolations and a standby gas treatment start. There were no actual safety consequences as a result of this event. Plant equipment responded as designed to the event. It was discovered that the Main Generator A phase isophase bus ventilation damper became detached from the bus compartment and fell onto the Main Generator A phase conductor resulting in a ground fault. The investigation into the cause of this event determined that tapped holes in the ductwork were stripped during previous maintenance. The isophase bus ductwork damper was repaired. Other similar dampers on Unit 2 were inspected and no similar concerns were noted. Similar dampers on Unit 3 will be inspected during an outage of sufficient duration to permit inspections. Maintenance procedures will be upgraded. There were no previous similar events identified.
277 | 2772002001 | 2002-12-21 | L3 | Turbine Bypass Unavailable | [10 empty] | X | [30 empty] | X |  |  |  | Peach Bottom 2 | B | GE | PO | 100 | At approximately 2035 on 12/21/02, Unit 2 automatically scrammed as a result of Main Steam Line Isolation Valve closure due to a Group I Primary Containment Isolation System (PCIS) actuation. The Group I PCIS actuation was a result of low main steam line pressure caused by the opening of Main Steam Line Bypass Valves due to an Electro-Hydraulic Control (EHC) circuit malfunction. PCIS Group II/III isolations were received as expected. A secondary containment isolation damper did not initially close due to a sticking solenoid valve. The redundant damper closed as designed. The High Pressure Coolant Injection and Reactor Core Isolation Cooling (RCIC) systems automatically started and injected water into the reactor vessel. RCIC was used to control reactor water level although the flow controller operated erratically which was subsequently determined to have caused RCIC to be inoperable resulting in a condition prohibited by Technical Specifications. Additionally, the reactor cool down rate of 100°F/hr was exceeded at 2205 hours on the reactor bottom head resulting in a Technical Specification Required Action entry. The Required Action entry was exited upon conclusion of a satisfactory thermal cycles analysis. The EHC control circuit malfunction was due to a component failure on a circuit card. Corrective actions include replacing the defective circuit card, replacing the secondary containment isolation damper solenoid valve, readjusting the RCIC flow controller, and reinforcing the monitoring of cool down rates to licensed operators.
277 | 2772003001 | 2003-04-12 | QL5 | Partial Closure of MSIVs | [45 empty] | Peach Bottom 2 | B | GE | PO | 100 | At 1847 hours on 4/12/03, Unit 2 scrammed as a result of a high reactor pressure condition. The high pressure condition resulted from the closure of the 'D' Outboard Main Steam Isolation Valve (MSIV). The MSIV closed as a result of a failed instrument air line that provides control air to the valve control manifold. Primary Containment Isolation System (PCIS) Group II and III isolations were received, as expected, as a result of reaching the Level 3 reactor water level set point. There were no significant equipment issues that adversely affected Operations personnel response to the event. The plant was maintained in the hot shutdown condition (Mode 3) until the mode switch was placed in the Startup position (Mode 2) on 4/13/03 at 1545 hours. Analysis of this event determined that the event was not risk significant. The cause of the broken air line is primarily due to less than adequate supporting of the instrument air line that allowed the instrument air line to experience a fatigue failure. The instrument air line was replaced and additional supports were added to the line. Supports for other similar instrument lines on other Outboard MSIVs were upgraded. Similar instrument lines on Unit 3 Outboard MSIVs are planned to be upgraded. Other pneumatic lines will be inspected for enhancements. There were no previous similar events.
277 | 2772003003 | 2003-07-22 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Peach Bottom 2 | B | GE | PO | 100 | At approximately 1345 on 7/22/03, Unit 2 automatically scrammed as a result of a fast closure of the Main Turbine Control Valves. This was a result of a Main Generator lockout due to a generator neutral high voltage ground fault. Control rods fully inserted and Primary Containment Isolation System (PCIS) Group II / III isolations were received, as expected. At approximately 1358 hours, a Main Steam Line Isolation valve closure occurred due to a Group I PCIS actuation. The actuation was a result of high area temperatures in the vicinity of the main steam lines caused by a loss of normal ventilation due to the Group II / III isolations. A reactor scram signal was also received as a result of the Group I isolation. The Reactor Core Isolation Cooling (RCIC) system controller was observed to have an inappropriate response while controlling reactor water level in that the RCIC system flow was oscillating (a condition that was subsequently determined to be a Technical Specification inoperable condition). A reactor scram occurred at approximately 1615 hours during transition to reactor level control using the feedwater / condensate system. The generator bus fault occurred when foreign material in the isophase bus duct came in contact with a bus conductor. This foreign material was identified as remnants of failed isophase bus cooling fan belts that had previously failed. The foreign material was removed, thereby resolving the bus ground. Design changes are in progress to add isophase bus fan belt debris guards.
277 | 2772003004 | 2003-09-15 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Peach Bottom 2 | B | GE | PO | 100 | At approximately 0132.on 9/15/03, Units 2 and 3 automatically scrammed and received Primary Containment Isolations as a result of an interruption of power to the Reactor Protection System (RPS) and the Primary Containment Isolation System (PCIS) logic circuits. This interruption of power was caused by a brief loss of two, of the three PBAPS off-site power sources caused by an electrical grid disturbance approximately 35 miles away from the site. The disturbance was the result of failure of off-site protective relaying during a lightning storm. The Emergency Diesel Generators (EDGs) started and provided on-site power. On Unit 3, one Safety Relief Valve (SRV) remained Open, after actuation. It subsequently closed, when reactor pressure was reduced. At approximately 0235 hours, the E-2 EDG tripped on low, jacket coolant pressure. A discretionary Unusual Event was declared by the Shift Manager as a result of the E-2 EDG trip combined with the off-site grid concerns. The High Pressure Coolant Injection and Reactor Core Isolation Cooling systems were used to provide reactor water level control. Safety Relief Valves were used for reactor pressure control. The Suppression Pool cooling system was used for containment heat removal. Normal power was restored to the on-site emergency busses and the Unusual Event was terminated at 1046 hours. The cause of the event was due to less than adequate maintenance and testing on protective relaying on the off-site electrical distribution system. Appropriate maintenance, testing and other upgrades are being pursued.
277 | 2772004001 | 2004-02-22 | QL7 | Degraded condenser vacuum | [45 empty] | Peach Bottom 2 | B | GE | PO | 43 | Peach Bottom Unit 2 was manually scrammed at approximately 1510 hours on 2/22/04 as a result of decreasing Main Condenser vacuum. Prior to the event, at 1424 hours, an increase in the air in-leakage into the condenser occurred. This prompted entry into the Operational Transient (OT) procedure for low condenser vacuum. Condenser vacuum was 27.1" Hg at the time the OT procedure was entered. A power reduction was performed to approximately 43% power with a resultant condenser vacuum of approximately 25.5" Hg. A briefing was conducted and the reactor was manually scrammed in accordance with the OT procedural direction since Condenser vacuum was not restored to above the procedurally required 26.2" Hg value for the current plant condition. As a result of the manual scram, reactor water level decreased, as expected, to below the reactor water level-three (lo-level) set point resulting in Primary Containment Isolation System Group II and III isolations. The cause of the event was due to a leaking Reactor Feed pump Turbine Exhaust expansion joint. The expansion joint was repaired. There were no safety consequences as a result of this event.
277 | 2772004003 | 2004-12-22 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Peach Bottom 2 | B | GE | PO | 100 | On 12/22/04 at approximately 0455 hours, a Unit 2 Reactor scram occurred as a result of a Primary Containment Isolation System (PCIS) Group I isolation. The Group I PCIS isolation was a result of low main steam line pressure caused by the opening of Main Turbine Bypass Valves due to an Electro-Hydraulic Control (EHC) circuit malfunction. The PCIS Group I isolation resulted in the closure of the Main Steam Isolation Valves (MSIVs). As would be expected for a PCIS Group I isolation, Reactor water level decreased to the Level 2 set point resulting in the actuation of the High Pressure Coolant Injection (HPCI), Reactor Core Isolation Cooling (RCIC) and the Alternate Rod Injection (ARI) / Recirculation Pump Trip systems. PCIS Group II and IlI isolations also occurred as Reactor water level passed through the Level 3 set point. The cause of the EHC system malfunction was due to a failed 'A' Pressure Regulator circuit card. The card was found to have a manufacturing defect involving excess solder. The defective card was replaced and the EHC system tested to verify proper operation. The EHC system was placed in service and has been appropriately controlling Reactor pressure since this event. Similar installed circuit cards on Unit 2 were inspected and no similar solder deficiencies were observed. Additional evaluations and corrective actions are being performed in accordance with the corrective action program. This event was not considered to be risk significant.
277 | 2772005001 | 2005-07-10 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 2 | B | GE | PO | 100 | On 7/10/05, at approximately 0318 hours, a Unit 2 automatic scram occurred as a result of a Main Turbine Stop Valve closure signal. The Main Turbine Stop valves had closed as a result of a Main Turbine trip signal generated during performance of the weekly Main Turbine Mechanical Trip Valve routine test. The Main Turbine trip signal was generated when a failed test was being aborted and did not reflect any actual adverse Main Turbine condition that required the Main Turbine to be tripped. As a result of the automatic scram, the Reactor Vessel water level 3 set point was reached as expected. This resulted in Primary Containment Isolation System (PCIS) Group II and III isolations. Also, a Reactor Vessel high pressure condition occurred resulting in automatic operation of the C, D, and E Main Steam Safety Relief Valves. There were no actual safety consequences associated with this event. The Main Turbine trip was caused by incorrect assumptions concerning the status of the Main Turbine trip system and not involving additional personnel while aborting the routine test. Corrective actions include remediation and re-evaluation of involved personnel and reinforcing management expectations regarding human performance practices.
277 | 2772021003 | 2021-11-14 | QL7 | Degraded condenser vacuum | [45 empty] | Peach Bottom 2 | B | GE | PO | 79 | On 11/14/2021 at 05:25 EST, a manual reactor scram was inserted on Unit 2 from 79 percent power due to degrading Main Condenser (EIIS: SG) vacuum. The loss of vacuum occurred due to an isolation of the Offgas System (EIIS: WF) on high Steam Jet Air Ejector discharge pressure and high Jet Compressor suction pressure. The manual reactor scram occurred with no complications and plant systems responded as expected. Unit 3 was unaffected. The scram resulted in an automatic Primary Containment Isolation System (PCIS)(EIIS: JM) Group II/III isolation. Upon initial investigation, it was identified that the valve positioner for the Jet Compressor Bypass Valve (EIIS: PCV) had a significant air leak which prevented the valve from closing. The root cause of the positioner failure was determined to be the use of low temperature soft parts in a high temperature environment. The soft parts within the failed positioner were replaced with higher-temperature rated components. Actions are in place to replace other low temperature soft parts within the Offgas System. <br /><br /> There were no safety consequences as a result of the event. This report is made pursuant to 10CFR50.73(a)(2)(iv)(A) for manual actuation of the Reactor Protection System (scram) (EIIS: JC) and automatic actuation of the PCIS which affected containment isolation valves in more than one system.
278 | 2781987001 | 1987-03-17 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Peach Bottom 3 | B | GE | PO | 85 | On March 17, 1987 at 0254 hours, Unit 3 scrammed from 85% power on high neutron flux signals from the neutron monitoring system. The unplanned activation of an engineered safety feature makes this event reportable. The high flux resulted from an increase in reactor coolant system pressure caused by turbine control valve fluctuations. Investigation indicated that circuitry in the Electrohydraulic Control System (EHC) was affected by spurious electrical noise believed to have been caused by malfunctioning cabinet cooling fans. Philadelphia Electric Company investigations have determined that operators were inattentive to instrumentation indications during the hours preceding the scram. Five fans were electrically disconnected, 4 fans were replaced, and 4 EHC cards were replaced. To prevent recurrence, the cooling fans in all 6 EHC electronics bays will be replaced, as part of the preventive maintenance program, during every other refueling outage. The operators on duty during this event received counseling regarding the importance of attentiveness. The operations staff received a letter from plant management, emphasizing the need to monitor various plant parameters and respond to deviations from normal conditions. Other than the unit shutdown transient, there were no adverse consequences of this event.
278 | 2781987002 | 1987-03-25 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Peach Bottom 3 | B | GE | SU | 1 | On March 25, 1987, with Unit 3 at less than 1% power, troubleshooting of the Main Turbine Electrohydraulic Control (EHC) System Circuitry led to a reactor scram. The unplanned activation of an engineered safety feature makes this event reportable. The lifting of a lead in the EHC circuitry has been identified as the cause of the scram. The electrical lead, TB702-14, was reconnected, thereby returning the EHC system to normal. To prevent recurrence, future troubleshooting activities will be reviewed to ensure that personnel with the necessary expertise are present. Other than the unit shutdown transient from 1%, there were no adverse consequences of this event.
278 | 2781990002 | 1990-01-28 | QR6 | Manual Reactor Trip | [45 empty] | Peach Bottom 3 | B | GE | PO | 100 | On January 28, 1990 the Unit 3 reactor was manually scrammed due to a leak of Electrohydraulic Control System (EHC) fluid at the number one main turbine control valve. Reactor coolant level fluctuations following the scram resulted in three Group II and III Primary Containment Isolation System (PCIS) actuations. The cause of the EHC fluid leak was failure of an O-ring on the fluid inlet port to the servo valve which controls the number one main turbine control valve. The reactor level fluctuations were aggravated by the need for rapid depressurization via the main turbine bypass valves, inability to restart the 'C' reactor feedwater pump (RFP) and the subsequent batch feeding of reactor coolant via the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems. Inability to reset the 'C' RFP was due to a RFP turbine hydraulic control problem. The cause of this problem was the lock nut on the RFP interlock dump valve setting adjustment bolt becoming unsecured due to system vibration. No actual safety consequences occurred as a result of this event. The EHC fluid leak was stopped and the leaking servo valve was replaced. Investigation into the servo valve O-ring failure could not determine a plausible root cause. This failure is considered an isolated occurrence and not systematically recurring in nature. The RFP interlock dump valve lock nuts on both units will be mechanically secured. No previous similar LERs were identified.
278 | 2781990003 | 1990-03-06 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 3 | B | GE | PO | 100 | On March 6, 1990 at 0250 hours with Unit 3 operating at 100% power a reactor scram occurred due to a main turbine trip. The 'A' stator cooling pump tripped. The turbine tripped when the main generator loss of stator cooling runback trip timer timed out prematurely. The stator cooling pump tripped due to a sharp corner of the pump motor power lead lug wearing through its tape insulation and arcing from the pump motor power lead to ground. The trip timer had an improper setting due to a deficient test procedure. <br /><br /> During reactor cooldown on March 7, the bottom head drain and recirculation loop temperatures were not logged as required by Technical Specifications because the bottom head drain and recirculation loop temperature indications were not considered to be representative of actual reactor coolant temperatures. Based on later reviews of thermocouple indications, reactor vessel pressure and temperature limits of Technical Specifications were not exceeded. No actual safety consequences occurred as a result of this event. The stator cooling pumps have been repaired. The loss of Stator Coolant trip timer has been properly set. Procedure RT 5.40 was revised. An investigation of the bottom head drain flow problem was performed resulting in a highly successful cleaning effort during the cycle 8 refueling outage. No previous similar events were identified.
278 | 2781990008 | 1990-07-27 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Peach Bottom 3 | B | GE | PO | 80 | On 7/27/90 at 0350 hours, with Unit 3 operating at 100% power, an offgas recombiner isolation occurred causing the main condenser vacuum to begin decreasing. A fast reactor power reduction was initiated in accordance with the procedure for a loss of main condenser vacuum. At 0403 hours, with Unit 3 at approximately 80% power, a manual scram was initiated by placing the mode switch in shutdown following the receipt of an 'A' channel reactor auto half scram signal. A Group II and Ill isolation occurred as d result of the manual scram. Other safety systems performed as designed. An offsite radioactive gaseous release amounting to 23.5% of Technical Specification limits occurred during post scram recovery. There were no adverse health threats to onsite personnel or the general public. The cause of the failure appears to be a component/system failure in the offgas recombiner condensate cooling water pressure control system. The design of the system will be evaluated to determine the exact cause of the failure and the appropriate measures required to correct the problem. There was one previous similar event.
278 | 2781991001 | 1991-01-16 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 3 | B | GE | PO | 58 | On 1/16/91 at 1238 hours a reactor scram occurred on Unit 3 due to Turbine Control Valve fast closure on a Main Generator Load Reject signal caused by a Main Transformer sudden pressure lockout signal. A Primary Containment Isolation System (PCIS) Group II/III isolation occurred as expected due to the Reactor Water level decrease following the scram. The load reject was initiated by actuation of the sudden pressure trip device on the '3A' Main Transformer when the fire system deluge was manually actuated in an attempt to cool down the overheating transformer. The transformer was overheating due to a loss of power to its cooling system. During performance of the procedure for resetting a scram, a second scram occurred as a result of procedural non-compliance. The cause of the first event was component failure and inadequate equipment design. The adequacy of the cooling system power supply circuit design is being evaluated. Information on this event will be included in Plant Operator and Licensed Operator training. The Operator involved in the second scram was coached by the Shift Manager and the Superintendent of Operations with regard to following procedures. No previous similar LERs have been identified.
278 | 2781991010 | 1991-07-07 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 3 | B | GE | PO | 97 | On 7/7/91 at 2312 hours, a reactor scram occurred on Unit 3 due to Turbine Control Valve fast closure on a Main Generator Load Reject trip signal. This trip was caused when the Generator output breaker position indication relays received a false signal due to a ground in a block switch. A Primary Containment Isolation System Group II/III isolation occurred as expected due to the reactor water level decrease after the scram. The cause of the event has been determined to be the result of lightning. The scram and isolations were reset, systems were returned to normal, and the damaged components were replaced. Engineering will evaluate the possibility of block switch removal, upgrade, or provisions to protect the Generator output breaker position indication relays from lightning strikes. Three previous similar LERs have been identified.
278 | 2781992003 | 1992-05-04 | QR8 | Spurious Reactor Trip | [45 empty] | Peach Bottom 3 | B | GE | SU | 1 | On 5/5/92 at 1230 hours, the Reactor Protection System (RPS) initiated a full reactor scram signal. The full reactor scram was a result of a "B" RPS channel half scram signal in conjunction with a "A" RPS channel half scram signal already inserted. The "B" RPS channel half scram signal was a result of a "B" Intermediate Range Monitor (IRM) failed upscale. The "A" RPS channel half scram was previously inserted due to having two IRMs in the "A" RPS channel inoperable. The cause of the "B" IRM channel spiking was low insulation resistance in the signal channel which was traceable to foreign material in the undervessel cable connector. Current-Voltage and Time Domain Reflectometry measurements were performed on all defective IRM channels. A quality improvement team had been formed to address chronic Nuclear Instrumentation failures. No actual safety consequences occurred as a result of this event. No previous similar LERs have been identified.
278 | 2781992005 | 1992-07-24 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Peach Bottom 3 | B | GE | PO | 55 | On 7/14/92 at approximately 1150 hours, an Offgas Recombiner low flow condition caused main condenser vacuum to begin decreasing. A fast reactor power reduction was initiated in accordance with the procedure for a loss of main condenser vacuum. At 1155 hours, a manual scram was initiated by placing the mode switch in shutdown following the receipt of a reactor auto half scram signal. A Group II and III isolation occurred as a result of the manual scram. The cause of the event has been determined to be a loose Pressure Control Valve (PCV) feedback linkage. The Steam Jet Air Ejector PCV feedback linkages on both units have been replaced with an improved design. No actual safety consequences occurred as a result of this event. There are no previous similar LERs.
278 | 2781992008 | 1992-10-15 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Peach Bottom 3 | B | GE | PO | 100 | On 10/15/92 at 2112 hours, a full Primary Containment Isolation System (PCIS) Group I actuation occurred which caused a reactor scram. PCIS Group II/III isolations occurred as expected. At 2316 hours, a second reactor scram occurred on a reactor high pressure condition. This occurred after the HPCI and RCIC systems tripped on a high reactor water level condition which prevented them from being used for reactor pressure control. The cause of the first scram has been determined to be an unexpected actuation of very sensitive PCIS Group I isolation pressure switches. The cause of the second scram has been determined to be less than adequate command and control during the shift turnover process. The cause of the pressure - temperature violation has been determined to be stratification of reactor coolant in the bottom head region. After each scram occurred, the appropriate PCIS and scram logics were reset and the affected systems were restored to the appropriate configuration. The events have been discussed with the involved individuals. Corrective actions will be implemented as appropriate for each event. No actual safety consequences occurred as a result of this event. Several previous similar events have been identified.
278 | 2781993002 | 1993-03-07 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Peach Bottom 3 | B | GE | PO | 23 | On 03/07/93 at 23% rated power, the 'C' Reactor Feed Pump (RFP) tripped and the 'B' RFP failed to respond. This caused the Reactor water level to decrease to the low level scram setpoint. Primary Containment Isolation System (PCIS) Group II/III isolations also occurred when the Reactor water level decreased. The 'A' RFP was placed in-service to restore Reactor water level. The PCIS and the Reactor Protection System (RPS) scram logics were reset. The cause of the scram has been determined to be an unexpected trip of the 'C' RFP on a high vibration condition. An investigation has been performed and concluded that a damaged vibration element in conjunction with a rough turbine shaft caused the false high vibration indication and the 'C' RFP trip. A defective controller in the 'B' RFP control logic caused the pump to fail to respond during the transient. The vibration element on the 'C' RFP was replaced and the lubrication spray nozzle was repositioned. Similar elements on the other RFPs were inspected and found to be satisfactory. The shaft roughness on the 'C' RFP will be addressed during a future outage. The defective controller on the 'B' RFP was replaced and setup. An evaluation will be performed on the defective controller to identify if additional corrective actions are necessary for other similar type controllers. This corrective actions will be based on the cause of the 'B' RFP controller failure. No previous similar events have been identified.
278 | 2781993004 | 1993-07-30 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Peach Bottom 3 | B | GE | PO | 72 | On 7/30/93, after venting the Off Gas Recombiner (OGR) steam flow condensing chambers using a Special Procedure (SP-1438), a simulated low steam flow signal to the Recombiner initiated an isolation signal to the OGR. This caused Main Condenser vacuum to begin decreasing. At 0327 hours, with the Reactor at 72% power, a auto half scram signal was received due to low main condenser vacuum. Therefore, the unit was manually scrammed. An investigation has determined that the cause of the OGR isolation was the combination of a previously failed fuse from unknown causes in the 'B' OGR steam flow isolation logic and the blowing of a fuse in the 'A' OGR steam flow isolation logic due to grounding of a jumper being removed during the performance of SP-1438. Following the event, the scram and isolation logics were reset. Affected systems were restored to appropriate conditions and the blown fuses were replaced. <br /><br /> SP-1438 has been revised to ensure that fuse status is monitored. An investigation is currently underway to identify the cause of the fuse failure in the 'B' OGR logic and to determine if terminal point modifications are necessary. Design changes and/or corrective actions will be implemented as necessary. No actual safety consequences occurred as a result of this event. No previous similar LERs have been identified.
278 | 2781994002 | 1994-02-03 | QR6 | Manual Reactor Trip | [45 empty] | Peach Bottom 3 | B | GE | PO | 45 | On 2/03/94, a Main Generator Ground Fault alarm was received in the Control Room. A Nuclear Plant Operator (NPO) discovered that the Main Generator Ground Relay status light was out, which is indicative of a field ground, but the relay flag was not up. While troubleshooting the Main Generator ground condition, the Outside Shift Supervisor (SSV) discovered a problem in the Main Generator Exciter cabinet. The Alterex Field Collapsing Circuit resistor was overheating. A rapid reactor shutdown was commenced to enable the Main Generator to be removed from service without having to scram the reactor. The NPO and SSV returned to the Main Generator cabinet and found control wiring melted and wiring insulation discolored above the resistor. Shift Management made the decision to scram the reactor. At 1914 hours, at approximately 45% power, the unit was manually scrammed. An investigation has revealed that an internal 'rack out' tab was not installed on the Alterex Field Breaker during recent maintenance activities. The Maintenance procedures used to overhaul-this breaker did not provide guidance to ensure that the rack out tab was properly installed. The damaged components were repaired and the breaker was replaced with a spare. The procedure used to overhaul the Alterex Field Breaker has been temporarily changed and will be permanently revised. No previous similar events have been identified.
278 | 2781994005 | 1994-10-11 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Peach Bottom 3 | B | GE | PO | 100 | On 10/11/94, the 'A' & 'C' Reactor Feed Pumps (RFP) locked up and both Recirculating (Recirc) Pumps ran back. The lockup of the two RFPs in conjunction with the Recirc Pump run back caused the reactor water level to increase to the high water level Main Turbine trip setpoint. At 1121 hours, the Main Turbine trip caused a closure of the Turbine Stop Valves which is an input to the Reactor Protection System (RPS) scram logic. Immediately following the scram, Primary Containment Isolation System (PCIS) Group II/III isolations also occurred when the Reactor water level decreased below 0'. Troubleshooting revealed that a failed Static Inverter caused a momentary loss of electrical power to the 30Y050 panel which in turn caused the two RFPs to lockup and both Recirc Pumps to runback. After the scram occurred, the appropriate PCIS and RPS scram logics were reset. The failed transformer was replaced and infrared thermography was performed on the Unit 2 and 3 Static Inverters to identify elevated component temperatures. No questionable indications were identified on either unit. An evaluation will be performed to establish a frequency for performance of infrared thermography on Static Inverters and to identify what additional transformer testing can be performed. In addition, PM activities for the replacement transformers will be initiated. No previous similar events have been identified.
278 | 2781995001 | 1995-03-23 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Peach Bottom 3 | B | GE | PO | 65 | On 3/23/95, the main steam supply valve to the 'B' Steam Jet Air Ejector (SJAE) system isolated when its air-operator failed closed. This caused a rapid decrease in Main Condenser vacuum. At 1618 hours, with reactor power reduced to 65%, an auto half-scram signal was received due to low condenser vacuum. Therefore, the unit was manually scrammed. An investigation has determined that excessive leakage around the diaphragm in the air-operator caused the isolation. Following the event, the scram and isolation logics were reset and affected systems were restored to appropriate conditions. Replacement diaphragms were installed in both SJAE trains and tested satisfactorily. An investigation is currently underway to identify the cause of the excessive air leakage. Additionally, the Steam Jet Air Ejector/Off-Gas system is being evaluated to determine ways to increase its overall reliability. No actual safety consequences occurred as a result of this event. No previous similar LERs have been identified.
278 | 2781995003 | 1995-07-30 | QP5 | Excessive Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Peach Bottom 3 | B | GE | PO | 70 | On 7/30/95, 'A' Reactor Feed Pump (RFP) speed unexpectedly maned to increase and resulted in increased feedwater flow to the reactor core. The 'C' RFP speed automatically decreased to compensate but reactor water level continued to increase. This condition caused the reactor water level to reach the high water level Main Turbine trip setpoint. The Main Turbine trip caused a closure of the Turbine Stop Valves which is an input to the Reactor Protection System (RPS) scram logic. Immediately following the scram, Primary Containment Isolation System (PCIS) Group II/III isolations occurred and the 'C' RFP was used to restore and maintain reactor water level. The PCIS and scram logics were reset and the affected systems were restored to the appropriate configuration. The cause of the scram was that a Main Turbine trip occurred due to a high reactor water level condition. Troubleshooting revealed that the 'A' RFP Motor Control Unit (MCU) failed causing an increase in the 'A' RFP speed <br /><br /> Additional troubleshooting was performed which determined that the Firing Circuit within the 'A' MCU failed. The exact cause of the Firing Circuit failure has not been determined yet but a Failure Analysis is being performed. Based on the results of the Failure Analysis, generic implications will be considered. Following replacement of four electronic cards within the Firing Circuit, the instrument loop was tested satisfactorily. No previous similar events have been identified.
278 | 2781995007 | 1995-12-02 | QR5 | Turbine Trip | [45 empty] | Peach Bottom 3 | B | GE | PO | 100 | On 12/02/95, an unexpected Main Turbine trip occurred and caused closure of the Turbine Stop Valves which initiated a full reactor scram. Immediately following the scram, Primary Containment Isolation System (PCIS) Group II/III isolations occurred as expected. The Reactor Protection System scram and PCIS logics were reset. Troubleshooting revealed that the Mechanical Trip Solenoid Valve's coil was momentarily energized due to a combination of two grounds in the DC electrical power system. The first was a intermittent ground on a terminal strip associated with the Mechanical Trip Solenoid. The second was a momentary ground induced during the performance of a Routine Test (RT). This ground occurred during the installation of grounded test equipment onto a relay contact. The RT required the technician to install test equipment in a location which was difficult to access. The simultaneous occurrence of these two grounds provided enough DC current to pickup the Mechanical Trip Solenoid causing a Main Turbine Trip. The terminal strip which caused the initial ground was replaced and generic implications will be considered. The RTs used to perform this type testing on the Diesel Generators will be evaluated to identify if alternative testing methods are possible. RT revisions will be implemented as appropriate. The pertinent information from this event will be provided to the appropriate Station personnel. No previous similar events have been identified.
278 | 2781997002 | 1997-03-09 | QR3 | Reactivity Control Imbalance | [45 empty] | Peach Bottom 3 | B | GE | PO | 14 | On 3/9/97, at 0600 hours, the 3B reactor recirculation pump unexpectedly tripped when the Unit 3 main turbine was manually tripped at 14 percent power. The main turbine was tripped during preparations to enter the drywell with the unit in single-loop operation. An auxiliary switch in the #4 13kv feeder breaker failed to change state after a manual bus transfer. This switch verifies the 13kv transfer from the main generator output to off-site sources for the 3B reactor recirculation pump motor logic. Without this transfer verification the 3B reactor recirculation pump motor breaker tripped when the main turbine was manually tripped and the generator locked-out. The unit was manually scrammed, in accordance with procedure, due to the loss of all forced core circulation at power. Examination of the auxiliary switch revealed internal binding due to a buildup of a dirt-like substance on various shaft pieces and contacts. The switch assembly was cleaned, lubricated and exercised until it functioned properly, then reinstalled. A failure analysis will be performed to further pinpoint the failure mechanism and any generic implications. No previous similar events have been identified.
278 | 2782000001 | 2000-08-07 | QR8 | Spurious Reactor Trip | [45 empty] | Peach Bottom 3 | B | GE | PO | 100 | On August 7, 2000, at 2126 hours, the Unit 3 reactor experienced an automatic shutdown (scram) due to an invalid low reactor water level signal sensed by the Reactor Protection System (RPS). The cause of the invalid reactor water level was the failure of the packing gland follower on RRV 3-2-654B which resulted in the depressurization of the variable leg to various instruments. A Primary Containment Isolation System (PCIS) Group 2 and Group 3 isolation signal, and secondary containment isolation also resulted. RPS, PCIS, and secondary containment isolation are Engineered Safety Features (ESF). During the scram recovery, due to a false low reactor water level signal, the operating crew was directed by procedure to override the low reactor level and high drywell pressure initiation signals on Standby Gas Treatment (SGT) to allow for restoration. The override removed the automatic start function of both SGT subsystems. In addition, the Unit was in Mode 3 when the initiation signal was overridden and SGT was required to be operable per Technical Specifications. As a result, this placed the unit in Technical Specification LCO 3.0.3. The LER is being submitted pursuant to the requirements of 10 CFR 50.73 (a)(2)(iv)due to the automatic actuation of Engineered Safety Features (ESF).Additionally, the reporting requirements of 10CFR50.73 (a)(2)(i)(B)and 10CFR50.73 (a)(2)(v)were met due to entry into Technical Specification LCO 3.0.3 and loss of safety function of Standby Gas Treatment (SGT) during the reactor scram recovery.
278 | 2772003004 | 2003-09-15 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Peach Bottom 3 | B | GE | PO | 90 | At approximately 0132.on 9/15/03, Units 2 and 3 automatically scrammed and received Primary Containment Isolations as a result of an interruption of power to the Reactor Protection System (RPS) and the Primary Containment Isolation System (PCIS) logic circuits. This interruption of power was caused by a brief loss of two, of the three PBAPS off-site power sources caused by an electrical grid disturbance approximately 35 miles away from the site. The disturbance was the result of failure of off-site protective relaying during a lightning storm. The Emergency Diesel Generators (EDGs) started and provided on-site power. On Unit 3, one Safety Relief Valve (SRV) remained Open, after actuation. It subsequently closed, when reactor pressure was reduced. At approximately 0235 hours, the E-2 EDG tripped on low, jacket coolant pressure. A discretionary Unusual Event was declared by the Shift Manager as a result of the E-2 EDG trip combined with the off-site grid concerns. The High Pressure Coolant Injection and Reactor Core Isolation Cooling systems were used to provide reactor water level control. Safety Relief Valves were used for reactor pressure control. The Suppression Pool cooling system was used for containment heat removal. Normal power was restored to the on-site emergency busses and the Unusual Event was terminated at 1046 hours. The cause of the event was due to less than adequate maintenance and testing on protective relaying on the off-site electrical distribution system. Appropriate maintenance, testing and other upgrades are being pursued.
278 | 2782018003 | 2018-09-30 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Peach Bottom 3 | B | GE | PO | 100 | On 9/30/18, an automatic reactor scram of Unit 3 occurred due to low reactor vessel water level following the loss of two condensate pumps. Plant equipment responded properly. The High Pressure Coolant Injection and Reactor Core Isolation Cooling systems automatically initiated on reactor low water level and restored level, in addition to the '3C' condensate pump and feedwater system. Reactor cooldown commenced in accordance with plant procedures. <br /><br /> The cause of the event was determined to be due to an electrical fault in the power cable for `3B' condensate pump and actuation of ground protective circuitry for the '3A' condensate pump. The electrical fault in power cables for the '3B' pump caused a ground current transient that raised the ground potential of the '3A' condensate pump transformer, resulting in a trip of the '3A' pump. Subsequently, power cables for the `3B' pump were replaced and ground circuitry for the '3A' pump was corrected to prevent such interaction.<br /><br /> There were no actual safety consequences as a result of this event. The '3C' condensate pump and reactor feedwater remained available for post-scram recovery.
280 | 2801987011 | 1987-05-16 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Surry 1 | P | WE | PO | 100 | On May 16, 1987 at 0824 hours, with Unit 1 at 100% power, a low flow reactor trip occurred when "A" loop reactor coolant system (RCS) (EIIS-AB) flow decreased to 47%. Following the reactor trip, the source range channels (EIIS-DET) did not automatically reinstate. All other protection and control systems functioned properly. Operators followed appropriate plant procedures and stabilized the plant following the reactor trip. This event occurred when the "A" hot leg loop stop valve (EIIS-ISV) stem failed, permitting the disc to drop, partially blocking loop flow. A metallurgical analysis was performed which determined that the stem failure was attributed to stress corrosion cracking. The stress corrosion cracking was due to a combination of excessive backseating force and a process of thermal aging. At the next outages of sufficient duration, samples from the Unit 1 and Unit 2 stems will undergo metallurgical analysis, and the Unit 2 stems will undergo ultrasonic testing as was previously performed on Unit 1. The failure of source range channels to reinstate was due to the under compensation of the intermediate range channel NI-36. The source range channels were manually reinstated, and technicians readjusted the intermediate range compensating voltage.
280 | 2801987019 | 1987-08-07 | QR6 | Manual Reactor Trip | [45 empty] | Surry 1 | P | WE | PO | 98 | On August 7, 1987 at 0120 hours, with the unit at approximately 98% power, a manual reactor trip was initiated, following a short rampdown, due to loss of cooling and oil flow for the 'B' Main Transformer EIIS-XFMR . The transformer local annunciator panel EIIS-ANN had failed to initiate a TROUBLE alarm on the control room annunciator panel. Following the trip, all control and protection systems functioned properly except: - One channel of source range nuclear instrumentation (SR NI) EIIS-IG did not automatically reinstate. - The 'A' main feedwater pump (MFP)) EIIS-P did not automatically trip and the pump's minimum flow recirc. valve did not open on a low feedwater flow condition. Operators manually reinstated the SR NI and tripped the 'A' MFP. The unit was quickly stabilized at hot shutdown. Power was lost to the 'B' Main Transformer cooling fans and oil circulating pumps when an undervoltage relay EIIS-RLY in the cooling control circuit failed. The relay and annunciator panel failures are attributed to aging. One channel of SR NI failed to reinstate due to under-compensation of one channel of IR NI. The 'A' MFP did not trip and its minimum flow recirc. valve did not open due to a failed air regulator diaphragm to the pneumatic pressure switch which senses main feedwater flow. The failed relay and the local annunciator panel were replaced. The transformer was checked for winding or other internal damage and was determined to be undamaged. Since the circuit components susceptible to failures due to their age will be identified and replaced.
280 | 2801987024 | 1987-09-20 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Surry 1 | P | WE | PO | 100 | On September 20, 1987 at 2028 hours, with Unit 1 at 100% power, a Low Reactor Coolant System (RCS) Flow reactor trip occurred when the 'B' Reactor Coolant Pump (RCP) (EIIS-AB P) tripped. Approximately 35 seconds after the reactor trip, a High Steam Flow with Low RCS Tavg Safety Injection occurred. Operators performed the appropriate emergency and function restoration procedures and quickly stabilized the unit. <br /><br />The 'B' Reactor Coolant Pump breaker tripped on instantaneous ground fault. Inspection of the motor leads revealed a complete separation of the 'A' phase main load connection bus bar. An engineering evaluation has concluded that the failure was caused by vibration of the unsupported length of feeder cable leads which fatigued and cracked the copper at the knee of the 90 degree bend in the bus bar. The failed bus bar was replaced. The other bus bars on A, B and C RCPs were visually inspected and meggered to verify their integrity. A cable restraint will be installed in the motor termination box to secure the feeder cable leads to prevent vibration. <br /><br />The High Steam Flow Safety Injection initiation was determined to be spurious.
280 | 2801988003 | 1988-02-16 | QR8 | Spurious Reactor Trip | [45 empty] | Surry 1 | P | WE | PO | 100 | On February 16, 1988 at 1143 hours, with Unit 1 at 100% power, a reactor trip occurred as a result of a Nuclear Instrumentation System (NIS) power range Lo setpoint Hi flux and NIS intermediate range Hi flux trip signals. Operators followed appropriate plant procedures and quickly stabilized the plant following the trip. At the time of the reactor trip, instrument technicians were performing a periodic test (PT 8.1) on the reactor protection system logic. During performance of the test the technician performed a procedural step in the wrong train of the reactor protection system. When the step was performed from the incorrect test rack, the permissive P-10 was initiated, generating a trip signal. The instrument technicians returned the switches in the protection cabinet to the correct positions. A peer group review of this event and its contributing factors was conducted by the instrument technicians. A Human Performance Evaluation System review has been performed.
280 | 2801988029 | 1988-08-15 | QR8 | Spurious Reactor Trip | [45 empty] | Surry 1 | P | WE | PO | 100 | On August 15, 1988 at 0927 hours, a Unit 1 reactor trip and safety injection occurred due to the spurious initiation of train "A" High Consequence Limiting Safeguard (Hi CLS). The spurious signal was generated during the performance of a periodic test on the train "A" Hi CLS system. A relay malfunction is the suspected cause of the spurious signal. The relay is actuated by a test terminate button. It is believed that a single relay contact failed to close when the button was depressed, resulting in a Hi CLS signal. Operators followed appropriate plant procedures and quickly stabilized the plant following the trip. The suspect relay will be analyzed by the system lab and recommendations will be considered when the report is received.
280 | 2801989026 | 1989-07-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Surry 1 | P | WE | PO | 63 | On July 9, 1989 with Unit 1 at 63% power, instrument technicians were calibrating Power Range Nuclear Instrumentation (NI) when a failure of the NI occurred. This resulted in a spurious NI dropped rod signal and automatic initiation of a 30% power turbine runback. Following the turbine runback operators had difficulty stabilizing steam generator levels due to inappropriate operator response and equipment malfunction. A turbine trip/reactor trip occurred due to a high-high level condition in the "B" steam generator two minutes and 45 seconds after initiation of the turbine runback. The failure of the power range NI was due to a blown control power fuse caused by the use of a voltmeter with an ungrounded power supply. The personnel involved were disciplined. This event and similar events related to improper use of meters will be discussed during the instrument technicians continuing training classes. Instrument technicians have been issued instructions to use grounded meters for testing unless specifically directed otherwise.
280 | 2801989044 | 1989-12-21 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Surry 1 | P | WE | PO | 100 | On December 21, 1989 at 2156 hours with Unit 1 at 100% power, a manual reactor trip was initiated by the Unit 1 licensed control room operator (CRO). Loss of power to a semi-vital bus caused numerous control room alarms to annunciate and de-energized the control rod position indication system which resulted in erroneous indications of control rods inserting into the reactor. These indications prompted the operator to immediately initiate a manual reactor trip/turbine trip per approved procedures. Operators performed the appropriate plant procedures and quickly stabilized the plant following the trip. The loss of power to the semi-vital bus was caused by a fault on the "A" Reserve Station Service Transformer that isolated the transformer from the station's power distribution system. The transformer supplied the semi-vital bus through the IJ 4160V emergency bus. The fault was caused by material blown from the turbine building roof striking the primary leads to the transformer. The #3 Emergency Diesel Generator automatically restored power to the emergency bus seconds after the bus was de-energized. A four hour non-emergency report was made to the Nuclear Regulatory Commission per 10CFR 50.72.
280 | 2801990004 | 1990-05-22 | QR6 | Manual Reactor Trip | [45 empty] | Surry 1 | P | WE | PO | 100 | On May 22, 1990 at 1150 hours with Units 1 and 2 at 100% power, a fault occurred on the Unit 1 "A" main transformer as a result of an inadvertent actuation of the transformer's deluge system. The fault initiated a Unit 1 generator differential lockout which immediately initiated a turbine trip/reactor trip. The fault also resulted in the lockout of the "A" Reserve Station Service Transformer RSST). Approximately 10 seconds later, the Unit 2 control room operator initiated a manual reactor trip after observing erratic control rod Individual Rod Position Indications (IRPI). Operators performed the appropriate plant procedures and quickly stabilized the units following the trips. The erratic Unit 2 IRPI indications were due to voltage transients that occurred an both units' emergency buses which were caused by the Unit 1 generator trip, the "A" RSST lockout, and subsequent motor starts. The #3 Emergency Diesel Generator automatically restored power to the Unit 1 "J" emergency bus which was de-energized by the "A" RSST lockout. A four hour non-emergency report was made to the Nuclear Regulatory Commission in accordance with 10CFR50.72.
280 | 2801990006 | 1990-07-01 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [6 empty] | X | [8 empty] | X | [19 empty] | X | [5 empty] | Surry 1 | P | WE | PO | 100 | On July 1, 1990 at 1802 hours, with Unit 1 at 100% power, the "A" Reserve Station Service Transformer tripped due to actuation of its sudden pressure relay. The transformer trip deenergized the 1J 4160V emergency bus and the #3 Emergency Diesel Generator started and loaded onto the 1J bus as designed in approximately nine seconds. An Individual Rod Position Indication (IRPI) control rod stop and turbine runback signal was received, and the unit load was automatically reduced to approximately 95% power. After the turbine runback, with plant conditions stable at 95% power, operators observed Instrument Air (IA) pressure decreasing rapidly. Before instrument air could be restored, the Reactor Operator (RO) received indication of the "C" Main Steam Trip Valve (MSTV) beginning to close and manually tripped the reactor at 1807 hours. Instrument air was restored approximately two minutes following the manual trip by bypassing and isolating a failed IA dryer. The unit was brought to stable hot shutdown conditions using the "A" and "C" steam generator atmospheric Power Operated Relief Valves (PORVs). A four hour non-emergency report was made to the Nuclear Regulatory Commission in accordance with 10CFR50.72.
280 | 2801992001 | 1992-01-02 | QR3 | Reactivity Control Imbalance | [45 empty] | Surry 1 | P | WE | PO | 56 | On January 2, 1992 at 1649 hours, with Unit 1 at 56% reactor power, troubleshooting was in progress for "B" shutdown bank control rod E-5 to determine why E-5 had dropped into the core at 0754 that morning during the performance of biweekly control rod freedom of movement testing. As "D" control bank was manually stepped out by the operator to control delta flux, a second rod, "D" control bank control rod H-2 dropped. Control Rod H-2 was verified to be in the core and the reactor was manually tripped in accordance with station abnormal procedures. This event occurred as the result of personnel error in that the troubleshooting guide prepared by Electrical Maintenance for rod E-5 did not identify shared circuitry between rod E-5 and H-2 which would result in H-2 being dropped if control rods were stepped during troubleshooting. Following the reactor trip, "A" main feed pump tripped when its recirculation valve failed to open due to a failed solenoid, intermediate range nuclear instrumentation indication was erratic due to high voltage power supply problems, steam generator atmospheric power operated relief valve for "A" steam generator responded poorly while the valves for "B" and "C" steam generators did not respond as expccted, and the turbine generator electro-hydraulic control system indications were erratic. A four hour non-emergency report was made to the Nuclear Regulatory Commission in accordance with 10CFR50.72.
280 | 2801992007 | 1992-05-07 | QR5 | Turbine Trip | [45 empty] | Surry 1 | P | WE | PO | 78 | On May 7, 1992 at 1006 hours with Unit 1 at 78% power and Unit 2 at 100% power, a Unit 1 Reactor Trip by Turbine Trip occurred. The trip was caused when contract maintenance personnel were attempting to stop a body to bonnet oil leak on the thrust bearing trip test valve. When the bonnet of the test valve was loosened, the valve disc was lifted off its seat. This allowed oil pressure to simulate a thrust bearing high pressure, which initiated a turbine trip. The reactor then tripped due to turbine trip. Operators performed the appropriate emergency plant procedures and quickly stabilized the unit. All safety systems functioned as designed following the trip, therefore, the health and safety of the public were not affected. Maintenance activities being performed by turbine contract maintenance personnel were halted and personnel involved were instructed to leave the site. A Root Cause Evaluation and a vendor investigation were initiated to propose corrective actions to prevent recurrence. Proposed corrective actions will be reviewed by mangement and appropriate work control measures implemented to prevent recurrence, prior to the vendor performing future maintenance activities.
280 | 2801993001 | 1993-01-08 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Surry 1 | P | WE | PO | 100 | On January 8, 1993 at 1729 hours, with Unit 1 operating at 100% power, a reactor trip and safety injection occurred due to spurious initiation of the train 'A' high consequence limiting safeguards (Hi-CLS). The spurious signal was generated during troubleshooting by either a loose negative lead or an intermittently closing contact on relay 3/4-CLS-1A. On January 9, 1993 at 0722 hours, with Unit 1 at hot shutdown, a spurious initiation of train A safety injection occurred during testing after replacement of relay 3/4-CLS-1A. The spurious signal was caused by testing prior to removal of a temporary modification (electrical jumper). After both spurious actuations, operators used the appropriate procedures to stabilize the unit. Failed components were replaced and a root cause evaluation was conducted. An engineering evaluation will be performed to identify single point failures which can cause spurious actuations. Circuitry modifications and relay preventive maintenance will be evaluated. A drawing effort will be corrected and the event will be discussed in safety evaluation training. This report is required by 10 CFR 50.73(a)(2)(iv).
280 | 2801993002 | 1993-02-09 | QR8 | Spurious Reactor Trip | [45 empty] | Surry 1 | P | WE | PO | 100 | At 1043 hours on February 9, 1993, with Unit 1 at 100% power and Unit 2 at 94% power, a Unit 1 reactor trip and turbine trip signal occurred when the 'A' Reactor Trip Breaker unexpectedly opened. At the time of the trip, licensee technicians were completing regularly scheduled surveillance testing on the Unit 1 'B' Train Reactor Protection System. When a technician depressed the push button to open the 'B' Reactor Trip Bypass Breaker to restore the breaker arrangement to its normal configuration, the 'A' Reactor Trip Breaker opened. The cause of the reactor trip breaker opening was a failure of the shunt trip (ST) relay on the 'A' Reactor Trip Breaker. Post-trip response was satisfactory. The reactor was placed in a safe, hot shutdown condition, and the health and safety of the public were not affected. The ST relay was replaced and the defective relay has been returned to the vendor for failure analysis. This report is required by 10 CFR 50.73(a)(2)(iv).
280 | 2801994006 | 1994-05-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Surry 1 | P | WE | PO | 100 | On May 11, 1994, with Unit 1 initially at 100% power, the reactor was manually tripped at 2109 hours. The trip was initiated when one of the two sources of main feedwater was isolated and Operators were unable to recover steam generator levels. The cause of partial feedwater isolation was inadvertent actuation of a relay in the safety injection actuation circuitry during logic testing. Actuation of this relay caused the tripping of the power supply to one of the Main Feedwater (MFW) pump motors and the closure of the MFW pump's discharge isolation valve. The Reactor Protection System functioned as designed, and post-trip response was satisfactory. The reactor was placed in a safe, hot shutdown condition. The health and safety of the public were not affected. This report is being made pursuant to 10CFR50.73(a)(2)(iv).
280 | 2801995001 | 1995-01-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Surry 1 | P | WE | PO | 100 | Unit 1 was operating at 100% reactor power on January 8, 1995, when Main Feedwater Pump (MFWP) B tripped at 1552 hours on low lube oil pressure. A Unit 1 automatic reactor trip from 74% reactor power followed at 1554 hours as a result of a Steam Generator (SG) low-low water level signal. All control rods fully inserted, however, insertion of Control Rod K-2, which had a previously existing inoperable individual rod position indicator (IRPI), could not be verified. Prior flux mapping indicated Control Rod K-2 was operable and capable of being tripped. Following the reactor trip, the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) started automatically but experienced diverging governor valve oscillations during its ramp to full flow and tripped approximately 52 seconds later. The MFWP B trip was caused by a sheared lube oil teflon coupling. The coupling failed due to overtightening. IRPI K-2 was repaired and the Control Rod K-2 was verified to be fully inserted. that the most probable cause of the trip was the specific governor (governor 227) installed in the governor control system. Governor 227 was tested by the vendor but the cause of the failure was not identified. Enhancements to the TDAFWP procedures were implemented. Governor 227 will not be re-installed. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
280 | 2801995003 | 1995-04-12 | QR3 | Reactivity Control Imbalance | [45 empty] | Surry 1 | P | WE | PO | 45 | On April 12, 1995, Unit 1 was operating at 45% reactor power due to a dropped rod and an out of band delta flux. Efforts to correct delta flux caused by the dropped rod were not performed because the same circuit supplying the dropped rod also supplied another control rod in a different control bank. It was believed that movement of this control bank to correct delta flux or as part of an orderly shutdown could have caused a second rod to drop. A decision was made to manually trip the reactor. At 1756 hours, after Operator preparation and briefings, the reactor was manually tripped. Following the trip, the turbine and generator tripped as designed. As expected, all Auxiliary Feedwater pumps automatically started upon receipt of the low-low Steam Generator level signal. At 2120 hours, due to the automatic Engineered Safety Feature (Auxiliary Feedwater) actuation, a four hour non-emergency report was made to the NRC Operations Center in accordance with 10CFR50.72 (b)(2)(ii). The cause of the dropped rod was a cable failure in containment. The cable supplied power to the stationary coil for Control Rod J-7. This event is being reported as a result of actuation of Engineered Safety Features, pursuant to 10CFR50.73(a)(2)(iv).
280 | 2801997003 | 1997-02-19 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | Surry 1 | P | WE | PO | 100 | At 2040 hours on February 19, 1997, with Unit 1 at 100 percent power and Unit 2 at Hot Shutdown, a Technical Specification 3.12.F.2 two hour Limiting Condition of Operation was entered due to Reactor Coolant System (RCS) pressure being less than 2205 psig. An Abnormal Procedure was entered in response to the decreasing RCS pressure. At 2052 hours, a Unit 1 shutdown was commenced. At 2259 hours, a manual reactor trip was initiated due to a continuing decrease in RCS pressure. Upon receipt of the reactor trip signal, the Reactor Protection System actuated and functioned as designed, and all control rods inserted into the core. Station operating personnel acted promptly to place the plant in a safe, hot shutdown condition in accordance with the proper procedures. The shutdown margin was calculated and the critical safety function status trees were monitored to verify that the unit conditions were acceptable. Plant response was as expected and the unit stabilized at hot shutdown. No conditions adverse to safety resulted from this event and the health and safety of the public were not affected. A detailed Reactor Trip Report and a Root Cause Evaluation is being performed for this event. The cause of the trip was inability to maintain RCS pressure due to loss of the Group C pressuizer proportional heaters due to failure of the Robicon controller unit. Additional approved recommendations from the Root Cause Evaluation will be implemented. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv) and 10 CFR 50.73(a)(2)(i).
280 | 2801998002 | 1998-02-02 | QR5 | Turbine Trip | [45 empty] | Surry 1 | P | WE | PO | 100 | On February 2, 1998, at 0526 hours, with Surry Unit 1 at 100% reactor power and 855 Mwe, an 'Excitation Loss Of Power' annunciator was received followed immediately by a 'Generator Differential Lockout Relay Trip' annunciator. This caused an automatic trip of the Unit 1 main generator followed by an automatic turbine trip. The automatic turbine trip resulted in an automatic reactor trip. The most probable cause of the loss of generator excitation power was a degraded generator voltage regulator subcomponent failure. At the time of the trip the generator voltage regulator was in the manual base adjust position due to a malfunction in the automatic circuit. Extensive testing of the voltage regulator circuitry and its sub-components did not result in the identification of a specific failed component. A root cause evaluation has been initiated to determine the cause of the Loss of Field and Main Generator Lockout annunciators, evaluate corrective actions from previous events, and provide recommended corrective actions to prevent recurrence. No conditions adverse to safety resulted from this event and the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
280 | 2801998013 | 1998-11-22 | QP5 | Excessive Feedwater Flow | [45 empty] | Surry 1 | P | WE | PO | 28 | On November 22, 1998, at 04:30, with Unit 1 at 28% power, control room annunciators alarmed indicating an incorrect level in steam generator (SG) "B" and a feedwater/steam flow mismatch. In response to an apparent increase in steam flow, the main feedwater regulating valve, 1-FW-FCV-1488, began to open further. Although a control room operator began to manually control 1-FW-FCV-1488 to try to prevent a high level condition, the "B" SG reached its high level turbine trip setpoint. The Unit 1 turbine automatically tripped, which was immediately followed by an automatic reactor trip. When the reactor coolant system cooled to the low average temperature (low T sub avg) setpoint of 543 degrees F, a safety injection (SI) actuation occurred. The SI initiation resulted from the low T sub avg condition coincident with an apparent high steam flow condition. The SI actuation was spurious since it resulted from an invalid signal. The event was caused by a short circuit in the summator for the main steam line "C" loop channel III flow transmitter. Root Cause Evaluation recommendations, designed to prevent the recurrence of a similar event, were implemented. The NRC was notified pursuant to 10 CFR 50.72 (b)(2)(ii) on November 22, 1998 at 07:20. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv).
280 | 2801998014 | 1998-11-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Surry 1 | P | WE | PO | 81 | On November 26, 1998, at 21:08, the Unit 1 steam generator (SG) "B" main feedwater regulating valve, 1-FW-FCV-1488, failed closed. A control room annunciator alarmed indicating a difference between the SG "B" feedwater and steam flow parameters. In response, the control room operator placed 1-FW-FCV-1488 in the manual control mode and attempted to open the valve. 1-FW-FCV-1488 remained closed, however, and the "B" SG level continued to decrease. To avert an automatic reactor trip due to low SG level coincident with a steam/feedwater flow mismatch, the control room operator initiated a manual reactor trip. The Unit 1 reactor tripped from 81% power and was followed by an automatic turbine trip, as designed. Appropriate operator actions were taken in accordance with emergency operating procedures to ensure the performance of system automatic actions and to respond to abnormal conditions. The event was caused by the dislocation of a retaining clip in the positioner pilot valve, which caused 1-FW-FCV-1488 to fail closed. Approved Root Cause Evaluation recommendations, designed to prevent the recurrence of a similar event, will be implemented. The NRC was notified pursuant to 10 CFR 50.72 (b)(2)(ii) on November 26, 1998 at 23:35. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv).
280 | 2802000004 | 2000-10-24 | QR5 | Turbine Trip | [45 empty] | Surry 1 | P | WE | PO | 100 | On October 24, 2000, at 07:41, with Unit 1 at 100% power, control room annunciators alarmed indicating a low low steam generator (SG) level and an automatic reactor trip of Unit 1 occurred. Immediately prior to the trip, the main steam dump valves were observed to have received an open demand, and a loss of turbine load was exhibited. The event was caused by human error due to work being performed on the wrong unit. Work was being conducted on the Unit 1 Electrical Hydraulic Controls (EHC) System instead of the intended Unit 2 EHC System. Approved Root Cause Evaluation recommendations, designed to prevent the recurrence of a similar event, will be implemented. The NRC was notified pursuant to 10 CFR 50.72 (b)(2)(ii) on October 24, 2000 at 10:30. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv) as an event that resulted in the automatic actuation of engineered safety features and the reactor protection system.
280 | 2802003001 | 2003-01-14 | QR6 | Manual Reactor Trip | [45 empty] | Surry 1 | P | WE | PO | 100 | At 0137 hours on January 14, 2003, Surry Unit 1 Reactor was manually tripped from 100% power due to degrading conditions on the Reactor Coolant Pump (RCP) 'C'. The operating crew received alarms indicating elevated shaft vibrations with the RCP 'C' motor followed by indications of increased lower radial bearing temperatures. In accordance with approved procedures, the operating crew manually tripped the reactor and secured the RCP 'C'. Automatic actuations occurred as expected, including Turbine Trip by Reactor Trip, Auxiliary Feedwater initiation, Main Generator Trip, and AMSAC initiation. The motor lower radial bearings on RCP 'C' were replaced and the unit was returned to service. A root cause evaluation was initiated to determine the cause of the high bearing temperatures and high shaft vibrations and to address actions to preclude recurrence. This is a reportable event pursuant to 10CFR50.73(a)(2)(iv)(A) since the event resulted in manual actuation of the reactor protection system and the initiation of the Auxiliary Feedwater system.
280 | 2802003002 | 2003-01-25 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Surry 1 | P | WE | PO | 27 | On January 25, 2003, at 0700 hours a Unit 1 automatic reactor trip occurred during startup at 27% reactor power due to low-low level in "B" steam generator (SG). Automatic actuations occurred as expected, including Turbine Trip by Reactor Trip, and Main Generator Trip. The Turbine Driven Auxiliary Feedwater Pump (TDAFWP) started automatically, but tripped on overspeed. A root cause evaluation (RCE) determined that the difficulties with manual control of SG water levels at low power and the subsequent Unit 1 reactor trip were due to inadequate modification of the main feedwater regulating valves. An RCE for the overspeed trip of the TDAFWP was performed, however no single root cause was identified. The probable causes were inadequate margin between the overspeed trip setpoint and nominal speed, sluggish response of the governor at low temperatures, steam supply line water condensation, and inability of the governor valve to go fully closed. The TDAFWP governor was replaced and post maintenance testing completed on January 28, 2003. Training was provided to the operating shift responsible for the unit restart. Unit 1 was restarted and achieved 100% reactor power on January 31, 2003 at 0755 hours. This report is being submitted in accordance with 10CFR50.73(a)(2)(iv)(A).
280 | 2802003004 | 2003-09-18 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Surry 1 | P | WE | PO | 79 | On September 18, 2003, with Surry Power Station Unit 1 at 79% reactor power and Unit 2 at 100% reactor power, a manual reactor trip was initiated on Unit 1 at 1728 and on Unit 2 at 1732 due to the loss of the '1 G' and '2G' buses which supply power to all eight circulating water pumps for both units. Automatic actuations occurred as expected, including Turbine Generator Trip, Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuitry (AMSAC) initiation, and Auxiliary Feedwater (AFW) initiation. As a result of the loss of the circulating water (CW) pumps, the emergency service water (ESW) pumps weree started. After start, 2 of the 3 ESW pump diesel engines tripped on cooling water high temperature. The ESW pumps were restarted successfully. At 1845, the 2G bus was energized, CW pumps were started and the ESW pumps were secured. Root cause evaluations determined the cause of the loss of all AC electrical power to the CW pumps and tripping of the two ESW pumps were design issues. There were no significant safety consequences or implications for this event. This event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) since the event resulted in manual actuation of the reactor protection system and the initiation of the AFW system and 10CFR50.73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications.
280 | 2802008001 | 2008-04-20 | QR6 | Manual Reactor Trip | [45 empty] | Surry 1 | P | WE | PO | 37 | On April 20, 2008, Unit 1 was placed online following repairs to the "B" 6th point Feedwater Heater. At 54% reactor power, a rapid load reduction was initiated in response to high turbine bearing vibrations. At 2216 hours, due to sustained high turbine vibrations, a Unit 1 manual reactor trip was initiated with the reactor at 37% power. All safety systems functioned as designed and the operating staff stabilized the unit at Hot Shutdown. Auxiliary feedwater (AFW) automatically initiated, as expected, due to low steam generator levels. The cause of the event was high turbine vibrations resulting from improperly installed balance weights. The installation was made using the turbine vendor's recommendations that were in error. Updated vendor information was received and the balance move was independently verified by station personnel. The turbine was rebalanced and the unit placed on line April 21, 2008 and ramped to 100% reactor power with acceptable turbine vibrations. Dominion will participate in the vendor's evaluation of this event and procedures will be revised to ensure independent review of vendor data. There were no significant safety consequences associated with this event. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv)(A) for a manual actuation of the reactor protection system and automatic AFW initiation.
280 | 2802010003 | 2010-06-08 | C2 | Loss of Vital Low Voltage ac Bus (<600 V) |  |  | X | [14 empty] | X | [27 empty] | Surry 1 | P | WE | PO | 100 | On June 8, 2010 at 0948 hours, with Units 1 and 2 at 100% power, the Unit 1 120 VAC Vital Bus 1- III was lost during maintenance. Main Feedwater Recirculation Valve A opened and the Main Feedwater Regulating Valves re-aligned. The resultant feedwater flow/steam flow mismatch coincident with low steam generator (SG) water level on SG A, resulted in a reactor trip. Safety Injection initiated due to loss of Vital Bus instrumentation and a momentary RCS cool down. The reactor was placed in hot shutdown and the health and safety of the public were not affected. The cause was inadvertent contact of a lead during Uninterruptible Power Supply (UPS) maintenance due to human error. Procedures and training will be revised to prevent recurrence. This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A), automatic actuation of the reactor protection system. Following the trip, a resistor-capacitor suppressor failed in the Control Room Nuclear Instrument cabinet, resulting in a small fire. The fire was quickly extinguished. Therefore, this report is also being submitted pursuant to 10CFR50.73(a)(2)(x).
280 | 2802011001 | 2011-04-16 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Surry 1 | P | WE | PO | 100 | On April 16, 2011, at 1849 hours, with Surry Power Station Unit 1 at 100% reactor power and Unit 2 at 98.3% reactor power, an automatic reactor trip occurred on Unit 1 and on Unit 2 due to the loss of offsite power resulting from damage inflicted in the switchyard from a tornado. All automatic safety systems, including Emergency Diesel Generators, performed as designed. The loss of offsite power resulted in violating several Technical Specifications including unavailability of independent offsite power. Following the unit trips, Pressurizer/Pressurizer spray temperature difference and Pressurizer heatup rate were also exceeded. A Notification of Unusual Event was declared at 1855 hours due to loss of offsite power to both emergency busses on both units. This event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) since the event resulted in automatic actuation of reactor protection systems, 10CFR50.73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications, and 10CFR73.71(a)(4) for delayed implementation of compensatory measures for loss of power to one source of surveillance equipment.
280 | 2802015003 | 2015-10-13 | QR5 | Turbine Trip | [45 empty] | Surry 1 | P | WE | PO | 100 | On October 13, 2015 at 1815 hours, with Unit 1 at 100 percent power and Unit 2 at 93.5 percent power at the end of life coastdown, Unit 1 experienced a reactor trip initiated from a turbine trip by main generator trip. The main generator trip was due to a loss of the main generator field that caused a loss of field protection relay to trip. <br /><br /> All three auxiliary feedwater pumps automatically started on low-low steam generator water level providing flow to the steam generators. Main steam trip valves were closed due to primary cooldown in accordance with emergency operating procedures and the plant was stabilized using steam generator power operated relief valves. The direct cause of the loss of main generator field of the Unit 1 generator was an electrical fault in the main generator exciter spacer coupling. Corrective actions to prevent recurrence will be implemented through the corrective action program when the root cause evaluation is completed. <br /><br /> This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System.
281 | 2811987003 | 1987-04-04 | QR5 | Turbine Trip | [45 empty] | Surry 2 | P | WE | PO | 11 | On April 4, 1987, Unit 2 was ramping down for a maintenance outage. At 0220 hours, a reactor trip by generator anti-motoring turbine trip occurred. Following this event, control and safety systems functioned as designed and the unit was quickly stabilized at hot shutdown. <br /><br /> In accordance with the approved shutdown procedure, operators had closed the turbine governor valves (EIIS-SVC) in preparation for removing the main generator (EIIS-GEN) from service. However, due to leakage past these valves, a status light, which is a permissive indication for opening the generator output breakers, was not received. When differential pressure across the high pressure turbine (EIIS-TG) decreased below the anti-motoring setpoint, the turbine tripped. <br /><br />The governor valves will be inspected during the next outage of sufficient duration and repairs will be made based upon the results of this inspection.
281 | 2811988004 | 1988-03-27 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Surry 2 | P | WE | PO | 100 | On March 27, 1988 at 1621 hours, with Unit 2 at 100% reactor power, Vital Bus (VB) (EIIS-ED) 2-III was de-energized due to the loss of 2-III inverter (EIIS-INVT). A turbine runback was automatically initiated due to the loss of power to the Power Range Nuclear Instrument NI-43 (EIIS-IG) which is powered from VB 2-III. Abnormal Procedure AP-10.2, "Loss of Vital Bus 1-III or 2-III", was entered and as required by the procedure, the reactor (EIIS-RCT) and 'A' Reactor Coolant Pump (RCP) (EIIS-P), were manually tripped at 1622 hours. Approximately 30 seconds later, a High Steam Flow/Low Reactor Coolant System (RCS) (EIIS-AB) Tavg Safety Injection (SI) (EIIS-BQ) occurred. Operators followed appropriate plant procedures and quickly stabilized the unit following the reactor trip/safety injection. An engineering evaluation of the inverter determined that an internal inductor failed due to age, thus causing a current surge which blew the fuse and tripped the AC output breaker. One of two of the station vital bus inverters per unit have been replaced with an uninterruptible power supply. The remaining two vital bus inverters (2-III and 1-III) will be replaced with uninterruptible power supplies during the upcoming refueling outages.
281 | 2811988010 | 1988-05-16 | QR5 | Turbine Trip | [45 empty] | Surry 2 | P | WE | PO | 100 | On May 16, 1988 at 0324 hours, with Unit 2 at 100% power, a reactor trip occurred as a result of steam generator (S/G) (EIIS-HX) low low level. At 49 seconds after the trip, safety injection (EIIS-BQ) was manually initiated in accordance with Emergency Procedure 1.0 due to pressurizer (EIIS-PZR) level decreasing to 13%. The cause of the reactor trip was rapid closure of the turbine governor valves (EIIS-SCV) which resulted in shrink of the S/G levels to the reactor trip setpoint. <br /><br />Extensive testing was conducted on the turbine control circuitry and the EHC system. No deficiencies were detected. The turbine impulse pressure transmitter (EIIS-PT) was calibrated. Further monitoring of the EHC system will be performed during the unit startup.
281 | 2811988022 | 1988-09-10 | QR5 | Turbine Trip | [45 empty] | Surry 2 | P | WE | SU | 4 | On September 10, 1988 at 0158 hours, with the Unit 2 reactor at 4% power, during a shutdown for a refueling outage, a reactor trip by turbine trip occurred. The event occurred while operators were attempting to maintain the turbine at synchronous speed, with the generator output breakers open. When the valve position limiter was raised, per the procedure, an unexpectedly rapid opening of the turbine governor valves and a rapid increase in turbine first stage pressure occurred, resulting in a turbine trip/reactor trip. Operators followed appropriate plant procedures and quickly stabilized the plant following the trip. <br /><br />The cause of the event has been attributed to a combination of an inadequate procedure, a faulty valve position limit indication, and an unexpectedly fast valve position limiter setting response. The controlling procedure used during the event will be revised to ensure that the turbine control system is placed in the configuration intended. Testing will be performed on the Electro Hydraulic Control (EHC) system, which will determine if any additional actions will be required.
281 | 2811989009 | 1989-09-18 | QR5 | Turbine Trip | [45 empty] | Surry 2 | P | WE | PO | 14 | On September 18, 1989, at 1042 hours, with Unit 2 reactor at 14% power and the turbine at 1800 rpm under no load conditions, a reactor trip signal was generated. A generator backup differential lockout relay 86 BU tripped the turbine, and since reactor power was greater than 10%, the turbine trip initiated a reactor trip. Operators performed the appropriate plant procedures and quickly stabilized the plant following the trip. The 86 BU generator backup lockout relay trip was caused by the spurious actuation of the generator backup impedance relay (KD-41). The exact cause of the spurious actuation of the relay could not be determined, however faults were discovered in the relay. The faulted KD-41 relay was replaced and appropriate testing was performed. The generator startup procedure has been revised to ensure that reactor power is less than 10% prior to closing the exciter field breaker. A four hour non-emergency report was made to the Nuclear Regulatory Commission in accordance with 10CFR50.72.
281 | 2811989010 | 1989-09-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Surry 2 | P | WE | PO | 25 | On September 19, 1989 with Unit 2 Reactor Power at 25%, shortly after placing Unit 2 on line, an automatic reactor trip was generated at 0051 hours as a result of a lo lo steam generator level. A four hour non-emergency report was made to the Nuclear Regulatory Commission (NRC) at 0120 hours per 10CFR50.72. A rapid turbine load increase occurred during startup which led to oscillations in the steam generator (S/G) water levels, eventually leading to the lo lo S/G water level trip. The cause of the rapid turbine load increase was the operator raising the governor valve position limiter more rapidly than desired. The operators performed the appropriate emergency procedures, and quickly stabilized the unit following the reactor trip. The lessons learned from this event and subsequent unit startup have been disseminated to all operations personnel.
281 | 2801990004 | 1990-05-22 | QR6 | Manual Reactor Trip | [45 empty] | Surry 2 | P | WE | PO | 100 | On May 22, 1990 at 1150 hours with Units 1 and 2 at 100% power, a fault occurred on the Unit 1 "A" main transformer as a result of an inadvertent actuation of the transformer's deluge system. The fault initiated a Unit 1 generator differential lockout which immediately initiated a turbine trip/reactor trip. The fault also resulted in the lockout of the "A" Reserve Station Service Transformer RSST). Approximately 10 seconds later, the Unit 2 control room operator initiated a manual reactor trip after observing erratic control rod Individual Rod Position Indications (IRPI). Operators performed the appropriate plant procedures and quickly stabilized the units following the trips. The erratic Unit 2 IRPI indications were due to voltage transients that occurred an both units' emergency buses which were caused by the Unit 1 generator trip, the "A" RSST lockout, and subsequent motor starts. The #3 Emergency Diesel Generator automatically restored power to the Unit 1 "J" emergency bus which was de-energized by the "A" RSST lockout. A four hour non-emergency report was made to the Nuclear Regulatory Commission in accordance with 10CFR50.72.
281 | 2811990003 | 1990-05-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Surry 2 | P | WE | PO | 100 | On May 31, 1990 at 2005 hours with Unit 2 at 100% power, a manual reactor trip was initiated by the Unit 2 licensed control room operator. A malfunction of the "A" Main Feedwater Regulating Valve (MFRV) positioner caused the valve to close, decreasing feedwater flow to the "A" Steam Generator (S/G) to near zero. Operators performed the appropriate plant procedures and quickly stabilized the plant following the trip. Safety systems functioned as designed with the exception that one Individual Rod Position Indicator (IRPI) rod bottom bistable light failed to illuminate and several others did not illuminate immediately. The failure of the MFRV was caused by blockage of the positioner air supply inlet filter/orifice assembly. The failure of the rod bottom light to illuminate was caused by a faulty light bulb. The delayed illumination of the other rod bottom lights was the result of a semi-vital bus voltage fluctuation. The maintenance procedure will be revised to require replacement of the filter/orifice assemblies during each refueling. Operation of the load tap changer for the "C" Reserve Station Service Transformer (RSST) is under evaluation. A four hour non-emergency report was made to the Nuclear Regulatory Commission per 10CFR 50.72.b.2.ii.
281 | 2811990004 | 1990-08-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Surry 2 | P | WE | PO | 100 | On August 27, 1990 at 0925 hours, with Unit 2 operating at 100% power, the "A" Main Feedwater Regulating Valve (MFRV) closed following the inadvertent grounding of its control signal during periodic surveillance testing. Closure of the "A" MFRV resulted in a mismatch between "A" Steam Generator (S/G) feedwater flow and steam flow causing several annunciators to alarm. The reactor operator immediately attempted to reopen the "A" MFRV by increasing the controller demand in manual but the valve did not respond. Since a low S/G level coincident with steam flow-feedwater flow mismatch reactor trip was imminent, the reactor operator manually tripped the reactor at approximately 27% level in the "A" S/G. The operators followed appropriate plant procedures and quickly stabilized the unit following the manual trip. A four hour non-emergency report was made to the Nuclear Regulatory Commission in accordance with 10CFR50.72.
281 | 2811991007 | 1991-08-02 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Surry 2 | P | WE | PO | 92 | At 1657 hours on August 2, 1991, with Unit 1 at 100% power and Unit 2 at 92% power, an Engineered Safeguards Feature actuated in Unit 2. A safety injection/reactor trip occurred as a result of a high steam flow signal coincident with a low steam line pressure signal. These conditions did not actually exist, but were generated by a combination of an erratic steam generator pressure channel and an electrical fault in a vital bus distribution panel. Troubleshooting was in progress on both problems, but the actuation occurred before corrective action could be completed. ESF functions performed as expected except for the failure of Emergency Diesel Generator #3 to achieve rated speed and the failure of the Containment Sump Pump Discharge Trip Valve (02-DA-TV-200A) to fully shut. A Notification of Unusual Event (NOUE) was declared at 1710 hours, and appropriate reports were made. On-shift operating personnel promptly placed the plant in a stable condition. The NOUE was terminated at 1840 hours. A Root Cause Evaluation of the Emergency Diesel Generator problem is being conducted. The results of this evaluation will be reported in Licensee Event Report S1-91-017. A Component Failure Analysis of the Containment Sump Discharge Trip Valve has been conducted, and the results are included in this supplementary report. This event is reportable pursuant to 10CFR50.73(a)(2)(iv).
281 | 2811991011 | 1991-12-17 | QP5 | Excessive Feedwater Flow | [45 empty] | Surry 2 | P | WE | PO | 23 | On December 17, 1991, at 2254 hours, with Units 1 and 2 at 100% and 23% power, respectively, a Unit 2 automatic reactor trip occurred as a result of a turbine trip due to high steam generator (SG) level. The required safety systems performed as designed, appropriate operator actions were taken to ensure the performance of system automatic actions, and the unit was quickly brought to a stable no-load condition. The cause of this event is attributed to the failure of the "B" main feedwater regulating valve (MFRV) to maintain a demand position. This condition resulted in a high SG level, the main feedwater pumps tripping, automatic start of auxiliary feedwater (AFW) pumps, turbine trip, and an automatic reactor trip. The "B" MFRV was inspected on December 18, 1991. The positioner was found to be worn and was replaced and tested. During the subsequent unit startup on December 18, 1991, a similar less severe oscillation of the subject valve was noted. Therefore, a Root Cause Evaluation is being performed to determine the cause of this condition. A non-emergency four-hour report, pursuant to 10CFR 50.72(b)(2)(ii), was made to the Nuclear Regulatory Commission at 0235 hours on December 18, 1991. This event is being reported, pursuant to 10 CFR 50.73(a)(2)(iv), as an unplanned Engineered Safety Feature actuation as a result of a valid signal.
281 | 2811993002 | 1993-06-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Surry 2 | P | WE | PO | 80 | Unit 2 was operating at 100% power on June 20, 1993, when Main Feedwater Pump 2-FW-P-1A tripped at 0415 hours. A Unit 2 automatic reactor trip followed at 0416 hours as a result of a low steam generator water level with steam/feedwater flow mismatch reactor protection signal from Steam Generator 2-RC-E-1A. Appropriate operator actions were taken to ensure the performance of system automatic actions and to respond to abnormal conditions. The Unit was quickly brought to a stable, no-load condition. The event was caused by the occurrence of an instantaneous electrical ground on the 2-FW-P-1A inboard motor and subsequent pump trip. A Root Cause Evaluation is being performed to determine the cause of the 2-FW-P-1A inboard motor electrical ground and to evaluate the conditions experienced following the reactor trip. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
281 | 2811993003 | 1993-08-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Surry 2 | P | WE | PO | 97 | At 2005 hours on August 3, 1993, with Unit 1 at 100% power and Unit 2 at 97% power, Unit 2 experienced an automatic reactor trip. The trip occurred when the "A" Main Feedwater Regulating Valve (MFRV) unexpectedly closed, causing a feed flow/steam flow mismatch coincident with a low water level in the "A" steam generator. Reactor Protection System functions actuated as designed, and post-trip response was satisfactory. The reactor was placed in a safe, hot shutdown condition, and the health and safety of the public were not affected. The cause of the closure of the MFRV was traced to an erratic power supply in the manual/automatic control station. This report is required by 10CFR50.73(a)(2)(iv).
281 | 2811993004 | 1993-08-23 | QR5 | Turbine Trip | [45 empty] | Surry 2 | P | WE | PO | 98 | At 0519 hours on August 23, 1993, with Unit 1 at 100% power and Unit 2 at 97.5% power, the Unit 2 reactor tripped due to a turbine - generator trip. Control room operators promptly initiated the appropriate emergency operating procedures. The reactor was placed in a stable, Hot Shutdown condition. The turbine-generator trip was caused by a loss of excitation field for the main generator due to a component failure in the voltage regulator (VR). During troubleshooting of the VR, a failed phase shifter card was discovered and replaced. As an additional precaution, two other cards were replaced along with the fuses between the field breaker and the firing circuit drawer. Following the trip, a fire watch notified the Shift Supervisor that sliding Fire Door 18 had shut. As a result, he could not complete his fire watch rounds of the Unit 1 Emergency Switchgear Room (ESGR) at 0523 hours, in accordance with Technical Specification 3.21. This fire door separates Unit 1 and 2 ESGRs. Following stabilization of Unit 2, an operator was dispatched and the sliding fire door was opened and relatched. During this event the health and safety of the pubic were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv) and 10 CFR 50.73(a)(2)(i)(b).
281 | 2811993005 | 1993-08-27 | QR8 | Spurious Reactor Trip | [45 empty] | Surry 2 | P | WE | PO | 97 | On August 27, 1993 at 1741 hours, with Unit 1 at Cold Shutdown, a Unit 2 automatic reactor trip occurred when both reactor trip breakers opened simultaneously. This Reactor Protection System (RPS) actuation occurred when train B safety injection master relay SIA-B partially actuated unexpectedly during monthly safeguards actuation logic functional testing. Only one of the four sets of contacts on the master relay made-up. This partial actuation resulted in a reactor trip signal which de-energized each reactor trip breakers' undervoltage trip coil. Both reactor trip breakers opened as designed. Proper procedure implementation and operator action stabilized the Unit at the Hot Shutdown condition. The Unit was subsequently brought to Cold Shutdown. The relay was replaced and tested. A Root Cause Evaluation (RCE), including additional testing, was conducted. The evaluation determined that the event resulted from relay chatter and low relay actuation and reset voltages. However, field tests could not identify a source of the voltage for the observed chatter. RCE recommendations to monitor testing for voltage sources and cover test connection jacks are being implemented. The health and safety of the public were not affected. This report is required by 10CFR50.73 (a)(2)(iv) for a Reactor Protection System actuation.
281 | 2811993006 | 1993-11-15 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Surry 2 | P | WE | PO | 95 | On November 15, 1993, at 2019 hours, with Unit 1 at 95% power and Unit 2 at 95% power, Unit 2 experienced an automatic reactor trip. The trip occurred when an electrical circuit failure caused all three Main Feedwater Regulating Valves to go shut, isolating feedwater flow to all three steam generators. The resultant feedwater flow/steam flow mismatch coincident with low steam generator water levels actuated the Reactor Protection System (RPS), and the reactor trip breakers opened. The RPS functioned as designed, and post-trip response was satisfactory. The reactor was placed in a safe, hot shutdown condition, and the health and safety of the public were not affected. The electrical failure was traced to a defective circuit breaker which was replaced. Three similar breakers whose failure alone could cause a reactor trip were also replaced. Additional corrective actions are under evaluation. This report is required pursuant to 10CFR50.73(a)(2)(iv).
281 | 2811995004 | 1995-05-11 | QR3 | Reactivity Control Imbalance | [45 empty] | Surry 2 | P | WE | PO | 100 | Unit 2 was operating at 100% power on May 11, 1995 when the rod control system urgent failure annunciator alarmed in the control room at 1445 hours. While investigating the alarm condition, Instrumentation and Control personnel removed and inspected several circuit cards from rod control system power cabinet 2BD including failure detector circuit card J1. When circuit card J1 was reinstalled, the rod control system urgent failure alarm cleared. The rod control system urgent failure annunciator alarmed a second time at 1842 hours. While troubleshooting this condition, the four Control Bank B, Group 2 control rods dropped into the reactor core. In response, a manual reactor trip was initiated at 2231 hours. Appropriate operator actions were taken in accordance with emergency operating procedures to ensure the performance of system automatic actions and to respond to abnormal conditions. The unit was quickly brought to a stable, no-load condition. A Root Cause Evaluation (RCE) Team investigation was initiated to determine the cause of this event and to recommend corrective actions. The RCE Team concluded that this event was caused by the installation of a damaged stationary gripper coil regulation circuit card. The results of the RCE Team investigation will be presented to management and recommendations that are designed to prevent the recurrence of this event will be implemented. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv).
281 | 2811995005 | 1995-05-21 | QR3 | Reactivity Control Imbalance | [45 empty] | Surry 2 | P | WE | PO | 100 | Unit 2 was operating at 100% power on May 21, 1995 when Control Rod B-6, Control Bank A, Group 2 dropped into the reactor core at 1222 hours. At 1223 hours the remaining Control Bank A, Group 2 control rods dropped into the core. A manual reactor trip was initiated at 1223 hours as required by abnormal procedures. Appropriate operator actions were taken in accordance with emergency operating procedures to ensure the performance of system automatic actions and to respond to abnormal conditions. The unit was quickly brought to a stable, no-load condition. A Root Cause Evaluation (RCE) Team investigation was initiated to determine the cause of this event and to recommend corrective actions. The RCE Team concluded that this event was caused by a loose solder connection on a stationary gripper coil regulation circuit card. The loose solder connection was attributed to the age of the circuit card and heat from the operating environment. The results of the RCE Team investigation will be presented to management and recommendations that are designed to prevent the recurrence of this event will be implemented. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv).
281 | 2811995006 | 1995-06-14 | QR5 | Turbine Trip | [45 empty] | Surry 2 | P | WE | PO | 100 | On June 14, 1995, Unit 2 was operating at 100% power. At 1415 hours, the Main Transformer and Generator Differential Lockout Relay Trip annunciator alarmed in the main control room. The annunciator was initiated by the main transformer protective relaying circuitry phase A. The actuation of the Main Transformer Protective Differential Relay 2-EP-87-TL-A initiated a generator trip, followed by turbine and reactor trips. Appropriate operator actions were taken in accordance with emergency operating procedures to ensure the performance of system automatic actions and to respond to abnormal conditions. The unit was quickly brought to a stable, no-load condition. A Root Cause Evaluation (RCE) was initiated to determine the cause of this event and to recommend corrective actions. At the time of the reactor trip, a heater transformer was being replaced in a main transformer control cabinet. The RCE investigation concluded that an inadvertent action during this maintenance activity could have caused relay 2-EP-87-TL-A to actuate. <br /><br /> However, a walk-through task analysis and interviews with the personnel involved could not confirm that an inadvertent action had occurred. As an enhancement, the main transformer control cabinets will be labeled to indicate the potential consequences while working in these cabinets. Appropriate portions of the main transformer protective relaying circuitry were extensively tested. No electrical faults were identified. Relay 2-EP-87-TL-A was replaced as a precautionary measure. The exact cause of this event could not be determined. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv).
281 | 2811995007 | 1995-11-07 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Surry 2 | P | WE | PO | 100 | On November 7, 1995, Unit 2 was operating at 100% power. At 0956 hours, a reactor coolant low flow signal on one out of three loops caused a reactor trip, The low flow signal was caused by the automatic opening of the Reactor Coolant Pump (RCP) Breaker 25C3 due to a phase to ground fault in the RCP C motor. <br /><br /> Appropriate operator actions were taken in accordance with emergency operating procedures to verify the performance of system automatic actions. The unit was quickly brought to a stable, no-load condition. Therefore, the health and safety of the public were not affected at any time during this event. <br /><br /> A Root Cause Evaluation investigation was initiated to determine the cause of this event and to recommend corrective actions. determined that the internal motor stator windings were grounded. The failed motor is being sent offsite to determine the cause of the grounded condition.<br /><br /> The NRC was notified pursuant to 10 CFR 50.72 (b)(2)(ii) on November 7, 1995 at 1240 hours. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv) as an automatic actuation of the Reactor Protection and Auxiliary Feedwater Systems.
281 | 2811996004 | 1996-06-06 | QP5 | Excessive Feedwater Flow | [45 empty] | Surry 2 | P | WE | SU | 16 | On June 6, 1996, power escalation was in progress for Unit 2 upon completion of a scheduled refueling outage. Control Room Operators were transferring from manual feedwater flow control with the Main Feedwater Regulation Valve (MFRV) Bypass Valves to automatic feedwater control with the MFRVs. At 2344 hours, with Unit 2 at 16% power, a high-high Steam Generator B level signal automatically tripped the running main feedwater pump and the main turbine. The turbine trip generated a reactor trip signal. The Reactor Protection System actuated and functioned as designed, and all control rods inserted into the core. Following the trip, Control Room Operators acted promptly to place the plant in a safe, hot shutdown condition in accordance with the proper procedures. The Shift Technical Advisor calculated the shutdown margin and monitored the critical safety function status trees to verify that the unit conditions were acceptable. Plant response was as expected and the unit stabilized at hot shutdown. <br /><br /> During this event the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
281 | 2811996005 | 1996-08-03 | QR6 | Manual Reactor Trip | [45 empty] | Surry 2 | P | WE | PO | 88 | At 1505 on August 3, 1996, with Unit 2 at 88% power, the control room operators manually tripped the reactor when steam/feed flow mismatch alarms were received. The alarms resulted from the closure of the turbine governor valves due to a loss of Electro Hydraulic Control (EHC) fluid pressure which occurred due to the failure of a mechanical fitting joint in EHC piping.<br /><br /> Upon receipt of the manual reactor trip, Reactor Protection System functioned as designed and all control rods inserted into the core. Station operating personnel promptly placed the plant in a stable, Hot Shutdown condition in accordance with the proper procedures. The shutdown margin was calculated and found to be satisfactory. The health and safety of the public were not affected by this event.
281 | 2811996006 | 1996-12-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Surry 2 | P | WE | SU | 11 | POWER LEVEL - 011%. At 0233 hours on December 13, 1996, with Unit 2 at 11% power, an automatic reactor trip occurred during a planned shutdown. The reactor trip was caused by a steam flow/feedwater flow mismatch in coincidence with low Steam Generator (S/G) level in the 'A' S/G. Upon receipt of the automatic reactor trip, the Reactor Protection System (RPS) functioned as designed and rod bottom lights were lit for all control rods except 2-RD-RPI-P-6. All electrical buses remained energized by off-site power and all emergency diesel generators were operable. Station operating personnel promptly placed the plant in a stable, hot shutdown condition in accordance with the. appropriate procedures. The shutdown margin was calculated and found to be satisfactory. The health and safety of the public were not affected by this event since all plant parameters remained within the normal range and all required safety equipment operated as designed.
281 | 2811997001 | 1997-02-18 | QR6 | Manual Reactor Trip | [45 empty] | Surry 2 | P | WE | PO | 100 | On February 18, 1997, at 1449 hours, with Unit 2 operating at 100% reactor power, a loss of turbine Electro-Hydralic Control (EHC) control power caused the turbine governor valves to close. The reactor was manually tripped at 1450 hours. The Reactor Protection System actuated and functioned as designed, and all control rods inserted into the core. Three Individual Rod Position Indicators (IRPI) were observed between 10 and 15 steps. The Turbine Driven Auxiliary Feedwater Pump (TDAFWP) started and operated as designed, however, a second start was initiated and the pump tripped on overspeed. The most probable cause of the loss of EHC control power was a momentary short that lead to an over-voltage condition and tripped two redundant +15 VDC power supplies. An automatic turbine trip should have been initiated by the loss of EHC control power, but did not occur. The lack of a turbine trip was due to a faulty relay card. The power supplies and relay card were replaced. Two IRPIs were recalibrated and the calibration on the remaining IRPI verified with recent data. Emergency procedures were revised to reduce the possibility of a re-start signal until the TDAFWP governor reset. No conditions adverse to safety resulted from this event and the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
281 | 2811997004 | 1997-12-02 | QR6 | Manual Reactor Trip | [45 empty] | Surry 2 | P | WE | PO | 100 | On December 2, 1997, at 0930 hours, Surry Unit 2 was manually tripped from 100% reactor power when the Main Steam Trip Valve (MSTV) Closed annunciator was received and MSTV A position lights indicated intermediate position. The manual reactor trip was initiated to minimize a unit transient for a MSTV closure event. Automatic actuations occurred as expected. Six Individual Rod Position Indicators (IRPI) initially indicated between 10 and 20 steps and all eventually drifted to less than 10 steps. It was later determined that MSTV A was full open and no signals were present for the valve to close. <br /><br /> The cause of the event was movement of the MSTV A open limit switch arm from its full open position. The limit switch arm and valve position arm were determined to have marginal overlap. Work activity in the area may have caused the repositioning of the limit switch. The position of the switch was subsequently adjusted to provide sufficient overlap. <br /><br /> Prior to returning to 100% reactor power, the Turbine Driven Auxiliary Feedwater (TDAFW) pump turbine tripped on overspeed during routine testing. The governor was replaced and a root cause evaluation was initiated to determine the cause for the overspeed trip. <br /><br /> No conditions adverse to safety resulted from this event and the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
281 | 2811999003 | 1999-07-05 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Surry 2 | P | WE | PO | 100 | On July 5, 1999, at 11:22, the Unit 2 reactor automatically tripped from 100% power as a result of low flow in the "A" loop of the reactor coolant system (RCS). The plant responded to the reactor trip, as designed. The auxiliary feedwater pumps were secured and withdrawal from the condensate storage tank (CST) was terminated at 12:07. The Technical Specification (TS) two hour action statement for refilling the tank was inadvertently not entered, and refilling of the CST began at 19:05. At 18:10, the "A" cold leg loop stop valve, 2-RC-MOV-2591, was removed from its backseat as a part of the normal unit cooldown sequence. When an attempt was made to reopen the valve fully, a full open position was not indicated. Since compliance with TS 3.17.1 was not maintained, a 30 hour action statement to place the unit in a cold shutdown condition was entered in accordance with TS 3.0.1. A root cause evaluation (RCE) investigation determined that the low flow condition in the "A" RCS loop resulted from the separation of the 2-RC-MOV-2591 valve's disc assembly from the stem, which allowed the disc assembly to drop into the flow stream. Approved RCE recommendations, designed to prevent the recurrence of a similar event, will be implemented through the corrective action program. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv) and 10 CFR 50.73 (a)(2)(i)(B).
281 | 2812002003 | 2002-11-23 | QR5 | Turbine Trip | [45 empty] | Surry 2 | P | WE | PO | 85 | On November 23, 2002, at 0332 hours, Unit 2 was at 85% power for the performance of the Turbine Governor Valve Freedom Test. During the performance of the test, while closing # 3 Turbine Governor Valve, the Turbine Valve Limiter failed to zero causing all four governor valves to close. The Control Room received a Low Low Steam Generator Level signal resulting in an automatic reactor trip. This is reportable under 10CFR50.73(a)(2)(iv)(A), as an event that resulted in the manual or automatic actuation of any engineered safety feature, including the reactor protection system.
281 | 2812003001 | 2003-01-25 | QR5 | Turbine Trip | [45 empty] | Surry 2 | P | WE | PO | 100 | On January 25, 2003 at 1414 hours with Unit 2 at 100% power, the reactor tripped due to turbine trip from a main generator trip. The main generator trip was due to Main Transformer and Generator Leads current differential lockout. The differential lockout resulted from a shorted main generator current transformer (CT) lead. Emergency systems functioned as required for the Unit 2 trip. At the time of the Unit 2 reactor trip, Unit 1 was off-line. Load shed occurred on the Unit 1 station service busses as designed. The Unit 1 `B' Main Feed Pump tripped, and since the Unit 1 'A' Main Feed Pump had previously been shut down, a start signal was initiated to both Unit 1 Motor Driven Auxiliary Feedwater Pumps (MDAFWPs) at approximately 1414 hours. The damaged CT leads were repaired. Inspection of like components on Units 1 and 2 was performed, and repairs made as necessary. The automatic actuation of the Unit 2 reactor trip, the actuation of Unit 2 Auxiliary Feedwater, and the automatic actuation of Unit 1 Auxiliary Floodwater are reportable in accordance with 10CFR50.73(a)(2)(iv)(A).
281 | 2802003004 | 2003-09-18 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Surry 2 | P | WE | PO | 100 | On September 18, 2003, with Surry Power Station Unit 1 at 79% reactor power and Unit 2 at 100% reactor power, a manual reactor trip was initiated on Unit 1 at 1728 and on Unit 2 at 1732 due to the loss of the '1 G' and '2G' buses which supply power to all eight circulating water pumps for both units. Automatic actuations occurred as expected, including Turbine Generator Trip, Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuitry (AMSAC) initiation, and Auxiliary Feedwater (AFW) initiation. As a result of the loss of the circulating water (CW) pumps, the emergency service water (ESW) pumps weree started. After start, 2 of the 3 ESW pump diesel engines tripped on cooling water high temperature. The ESW pumps were restarted successfully. At 1845, the 2G bus was energized, CW pumps were started and the ESW pumps were secured. Root cause evaluations determined the cause of the loss of all AC electrical power to the CW pumps and tripping of the two ESW pumps were design issues. There were no significant safety consequences or implications for this event. This event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) since the event resulted in manual actuation of the reactor protection system and the initiation of the AFW system and 10CFR50.73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications.
281 | 2812004001 | 2004-05-21 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Surry 2 | P | WE | PO | 100 | On May 21, 2004, at 2108 hours with Units 1 and 2 at 100% power, the Unit 2 main generator leads "A" phase Coupling Capacitor Voltage Transformer (CCVT) in the switchyard failed. The generator protective relays actuated, tripping the main generator, and resulting in trips of the turbine and reactor. Emergency systems functioned as required, including the Reactor Protection System (RPS) and Auxiliary Feedwater (AFW) System. A Notification of Unusual Event was declared related to the switchyard CCVT failure. Unit 2 was stabilized at hot shutdown. The cause of the CCVT failure was age-related degradation. The failed CCVT was replaced. On May 22, 2004, following refill of the Emergency Condensate Storage Tank, an unisolable leak in a buried Unit 2 AFW recirculation line was discovered. The AFW system was declared inoperable. Further evaluations determined that the AFW system was capable of performing its intended function. The cause of the AFW piping leak was external galvanic corrosion of the buried carbon steel piping due to the failed corrosion protection. The recirculation line was rerouted. There were no significant safety consequences associated with this event. The automatic actuations of the RPS and the AFW are reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A). The AFW leak is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(vii).
281 | 2812006002 | 2006-10-07 | QR6 | Manual Reactor Trip | [45 empty] | Surry 2 | P | WE | PO | 100 | On October 7, 2006, at 1711 hours, with Units 1 and 2 at 100% power, Unit 2 reactor was manually tripped when the Main Control Room received alarms associated with steam flow and feed flow mismatch and a report of a steam leak in the Turbine Building. The Unit 2 cross-under safety valves lifted unexpectedly causing Turbine Building siding to detach and contact Reserve Station Service Transformer (RSST) components. This resulted in faults and lockouts that de-energized two transfer busses, two Unit 2 reactor coolant pumps (RCPs), the Unit 2 containment air monitor, and caused the loss of offsite power to a Unit 2 and both Unit 1 emergency buses. Emergency systems functioned as designed, including the Reactor Protection System, Emergency Diesel Generators, and Auxiliary Feedwater System. Unit 1 was reduced to 73% power and Unit 2 was stabilized at hot shutdown. The cause of the event was a spurious signal from the Turbine Overspeed Protection Circuit (OPC). Modification of the OPC circuit will prevent recurrence during power operation. There were no significant safety consequences associated with this event. This report is provided pursuant to 10 CFR 50.73(a)(2)(iv)(A) for the automatic actuation of the Unit 2 RPS and AFW system, and 10 CFR 50.73(a)(2)(i)(B) for the loss of power to one emergency bus, two Unit 2 RCPs, and the Unit 2 containment air monitor.
281 | 2812011001 | 2011-02-02 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Surry 2 | P | WE | PO | 98 | On February 2, 2011, at 0533, the Unit 2 reactor automatically tripped from 98.3% power as a result of low flow in the "C" loop of the reactor coolant system (RCS). The plant responded to the reactor trip as designed. All three auxiliary feedwater (AFW) pumps automatically initiated on low-low steam generator (SG) water level providing flow to the SGs. The AFW pumps were secured by 0613. At 1222, the reactor coolant pump for "C" loop was stopped. With no flow, compliance with Technical Specification (TS) 3.17.1 was not maintained and a 30 hour action statement to place the unit in a cold shutdown condition was entered in accordance with TS 3.0.1. A preliminary root cause evaluation (RCE) determined that the low flow condition in the "C" RCS loop resulted from a separation of a loop stop valve's disc assembly from the stem, which allowed the disc assembly to drop into the flow stream. Approved RCE recommendations, designed to prevent the recurrence of a similar event, will be implemented through the corrective action program. This report is being submitted pursuant to 10CFR50.73 (a)(2)(iv)(A) as an event that resulted in the automatic actuation of engineered safety features and the reactor protection system and pursuant to 10CFR50.73 (a)(2)(i)(B) for operation prohibited by TS 3.17.1.
281 | 2802011001 | 2011-04-16 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Surry 2 | P | WE | PO | 100 | On April 16, 2011, at 1849 hours, with Surry Power Station Unit 1 at 100% reactor power and Unit 2 at 98.3% reactor power, an automatic reactor trip occurred on Unit 1 and on Unit 2 due to the loss of offsite power resulting from damage inflicted in the switchyard from a tornado. All automatic safety systems, including Emergency Diesel Generators, performed as designed. The loss of offsite power resulted in violating several Technical Specifications including unavailability of independent offsite power. Following the unit trips, Pressurizer/Pressurizer spray temperature difference and Pressurizer heatup rate were also exceeded. A Notification of Unusual Event was declared at 1855 hours due to loss of offsite power to both emergency busses on both units. This event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) since the event resulted in automatic actuation of reactor protection systems, 10CFR50.73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications, and 10CFR73.71(a)(4) for delayed implementation of compensatory measures for loss of power to one source of surveillance equipment.
281 | 2812014002 | 2014-10-13 | QR8 | Spurious Reactor Trip | [45 empty] | Surry 2 | P | WE | PO | 100 | On October 13, 2014 at 07:58, with Units 1 and 2 at 100% power, Unit 2 experienced a reactor trip due to a spurious opening of the Unit 2 "B" reactor trip breaker due to a loose screw on a reactor protection trip relay for the reactor trip breaker.<br /><br /> All three auxiliary feedwater pumps automatically started on low-low steam generator water level providing flow to the steam generators. The rapid increase in steam generator pressure on the relief valve setpoints resulted in the lifting of all three steam generator power operated relief valves. Unit 2 was placed in hot shutdown and the health and safety of the public were not affected. The loose screw on the reactor protection trip breaker relay was tightened and the breaker was closed successfully. Remaining connections on the Unit 2 relay control circuitry were checked for tightness. Unit 1 reactor trip breaker relay control circuitry will be checked for tightness at the next available opportunity. Torque requirements for terminal screws will be incorporated into the Surry Electrical Installation Specification and applicable procedures will be revised to include the torque requirements.<br /><br /> This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System.
281 | 2812015001 | 2015-07-21 | QR5 | Turbine Trip | [45 empty] | Surry 2 | P | WE | PO | 6 | On July 21, 2015 at 05:05, with Unit 1 at Hot Shutdown and Unit 2 at approximately 6% power, Unit 2 experienced a reactor trip initiated from a turbine trip during performance of the Turbine Overspeed Protection Control system circuitry testing. The turbine trip was caused by governor valves rapidly opening due to a speed error which had accumulated between the turbine speed and reference setpoint resulting in a rapid increase in impulse pressure. The root cause of this event was inadequate instructions in the Overspeed Protection Control testing section of the operating procedure. The testing will be removed from operating procedures and placed in test procedures that are not performed as part of routine turbine startup. <br /><br /> All systems functioned as required. Initiation of auxiliary or emergency systems was not required. Unit 2 was placed in hot shutdown and the health and safety of the public were not affected. <br /><br /> This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System.
281 | 2812016001 | 2016-10-09 | QR5 | Turbine Trip | [45 empty] | Surry 2 | P | WE | PO | 100 | On October 9, 2016 at 0254 hours, with Unit 1 and Unit 2 at 100 percent power, Unit 2 experienced an automatic reactor trip initiated by a turbine trip due to generator differential lockout relay actuation. At the time of the trip, high wind and heavy rain conditions existed due to the effects of Hurricane Matthew. All three auxiliary feedwater pumps automatically started on low-low steam generator water level as expected. All plant systems functioned as required, and Unit 2 was stabilized at hot shutdown. The trip response was not affected by any previously inoperable systems, structures, or components. <br /><br /> The direct cause of the generator differential lockout was an electrical ground overcurrent initiated by water accumulation in the "A" phase of the "A" station service transformer leads termination enclosure. Affected electrical enclosures were drained, the system was tested, and modifications to the enclosures to prevent recurrence of water intrusion were completed prior to returning Unit 2 to power operation on October 13, 2016. <br /><br /> This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System.
282 | 2821987004 | 1987-03-30 | QR8 | Spurious Reactor Trip | [45 empty] | Prairie Island 1 | P | WE | PO | 72 | On March 30, 1987, Unit 1 was at 72% power in coastdown operation prior to refueling. The Safeguards Logic Test was in progress; Train A testing was complete and Train B Steam Pressure Safety Injection (SI) testing was being done. The procedure calls for the relay rack to be placed in the TEST position; this step was missed. A later step calls for an SI signal to be initiated, and when it was, at 1419, Train B SI was actuated and the reactor tripped automatically. <br /><br />Cause of the event was human error, a misunderstanding between the two instrument and control specialists in the relay room which resulted in omission of a critical step in the procedure. <br /><br />This event is reportable under 10CFR50.73.(a)(2)(iv). There was no effect on public health and safety since plant systems responded to the event as required. The unit was restated at 1202 the next day; the delay in restart was due to inadequate end-of-cycle core reactivity. <br /><br /> The event was discussed with the personnel involved. The Safeguards Logic Tests for each unit were rewritten in a reorganized and simplified manner. <br /><br />Safeguards logic testing has resulted in several reactor trips and SI actuations on both units, but only two since reporting of these events has been required. Those events are described in Unit 2 LER's 86-001 and 86-003.
282 | 2821987013 | 1987-07-11 | QR8 | Spurious Reactor Trip | [45 empty] | Prairie Island 1 | P | WE | PO | 20 | On July 11, 1987, Unit 1 was being restarted after a short maintenance outage. At 2145 the tubine-generator was put on line and after initial loading the operator increased feedwater flow to match steam flow. The insurge of cold water cooled the reactor coolant system several degrees. The operator then pulled control rods to increase temperature. These two events caused reactor power to be about 20%; normally, power at this point would be less than 10%. Control for the main feedwater valves was then placed in AUTO. Reactor coolant system temperature and pressure was still fluctuating, and while the operator attempted to stabilize it the reactor tripped at 2159 from about 23% power when the NIS power range high flux low setpoint was reached. <br /><br />Cause of the event was failure to block the power range high flux low setpoint trip prior to exceeding the trip setpoint. Although the operator had about 10 minutes to block this trip, he was directing his attention to a fluctuating reactor coolant system temperature and pressure. <br /><br />This event is reportable under 10CFR50.73(a)(2)(iv). Public health and safety were unaffected since all systems responded to the reactor trip signal as required. The event was discussed with involved personnel. Simulator training will stress adherence to the startup procedure. <br /><br /> A related event was reported as Unit 1 LER 84-001.
282 | 2821989010 | 1989-07-21 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On July 21, 1989 Unit 1 was at 100% power. During the afternoon, a "hot lacquer" smell was noticed coming from 4160V Bus 11. 4160V Bus 11 supplies No. 11 Reactor Coolant Pump and No. 11 Feedwater Pump. The problem was investigated and determined to be of no immediate concern but worthy of increased awareness. An "Operations Note" was issued to alert operators of the problem. During a subsequent investigation for the source of the smell, an operator pulled open the potential fuse drawer for 4160V Bus 11, causing undervoltage relays to trip. After a 5 second time delay timed out, the breaker for No. 11 Reactor Coolant Pump tripped and the reactor tripped at 2345 on July 21, 1989 due to single loop loss of flow reactor trip signal. The unit was returned to service at 2204 on July 22, 1989.<br /><br /> 4160V Bus doors have been labeled, cautioning personnel of the consequences of opening the potential fuse drawers. Potential fuse drawer fronts will also be labeled.
282 | 2821990017 | 1990-11-21 | QR5 | Turbine Trip | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On November 21, 1990, Unit 1 was at 100% power. At about 1540 an operator making rounds of the turbine building noticed that No. 11 Bus Duct Cooling Fan was not running and that its supply breaker had tripped. He notified the Control Room of his findings, and he was then instructed to start No. 12 Bus Duct Cooling Fan to re-establish the flow of cooling air through the generator bus ducts. When No. 12 Bus Duct Cooling Fan was started at 1545, the main generator tripped, resulting in a turbine trip/reactor trip. <br /><br /> The turbine building operator had determined that there was no bus duct cooling fan running, but bus duct temperature appeared normal. Actual bus duct temperature was highly elevated, but the temperature sensors are located in the bus duct cooler suction duct such that representative bus duct temperature is not sensed if a fan is not running. When the standby fan was started, hot air in the bus ducts was drawn into the suction duct and past the temperature sensors, which then initiated a generator trip on high temperature of 85 degrees C. <br /><br /> An investigation was begun and the cause of the trip was determined. The unit was returned to service at 1541 the next day.
282 | 2821991011 | 1991-08-16 | QR3 | Reactivity Control Imbalance | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | At 0127 hours on August 16, 1991 Unit 1 tripped unexpectedly from 100% power. The "first out" annunciator was the negative flux rate trip. Review of rod position indication just prior to and after the trip indicated that the four Control Bank A, Group 2 rods that are powered from power cabinet 2AC began to fall into the core prior to receipt of the reactor trip signal. Extensive testing of the rod control system was done. Testing of the failure detection circuitry (urgent failure alarm) showed some conditions exist under which some rods would unexpectedly drop. The system does not provide protection against dropping rods for all component malfunctions or failures. <br /><br /> The most likely cause of the event was intermittent failure in a firing card for the stationary grippers supplied by power cabinet 2AC, causing interruption of power to the Control Bank A, Group 2 rods. During post trip testing which simulated high temperatures found on firing components during normal operation, the card developed an unacceptable wave form in an oscillator circuit. This card had previously tested satisfactorily at room temperature. The intermittent control circuit failure occurred such that the failure detection circuitry did not protect the affected rods against dropping.
282 | 2821993005 | 1993-02-18 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On February 18, 1993, Unit 1 was at 100% power. Cleaning of floors in the Turbine Building was in progress. A plant services attendant was burnishing the floor in the area of Bus 12. Bus 12 supplies 4KV power to No. 12 RCP and No. 12 Feedwater Pump. While moving the machine along the end of Bus 12, a caster wheel of the machine caught in a joint in the floor. This forced the burnishing machine toward the bus and into the lower door hinge of Breaker 12-1, the offsite power supply to Bus 12. When the machine hit the door hinge of Breaker 12-1, the attendant heard the breaker operate. The attendant immediately called the control room to report the event. At 0814 the reactor had tripped; the first out annunciator received was 'One Loop Lo Flow or RCP Bkr Open.' <br /><br /> The reactor protection system responded as designed to the loss of Bus 12 and the unit was stabilized in the hot shutdown condition in accordance with plant procedures following the reactor trip. <br /><br /> Cause of the event was determined and restart accomplished in accordance with plant procedures. The unit was returned to service at 2333 hours.
282 | 2821996012 | 1996-06-29 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Prairie Island 1 | P | WE | PO | 100 | On June 29, 1996, both Units 1 and 2 were operating at 100% power. In summary, both reactors tripped following the loss of three of four 345 KV offsite transmission lines to the plant substation, due to high winds. The plant safeguards busses were supplied power by the four safeguards diesel generators for several hours. <br /><br /> All safeguards diesel generators provided the needed electrical power throughout the duration of the event. In addition, all cooling water (essential service water) pumps functioned as required. The event was mitigated by the proper functioning of the safety related equipment and the proper management of the event by operators.
282 | 2821997008 | 1997-06-02 | QR3 | Reactivity Control Imbalance | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On June 2, 1997, Prairie Island Unit 1 was at steady-state, 100% power with the Rod Control System in automatic. At approximately 11:10 AM, Unit 1 control room operators received a "Rod Control System Non-Urgent Failure Alarm" followed seconds later by a "Rod Control System Urgent Failure Alarm". Approximately thirty seconds later, Unit 1 tripped from 100% power on a Negative Flux Rate Trip generated by Power Range Nuclear Instrumentation. The plant response to the reactor trip was as expected, except that following the trip, leakage past the normally closed Feedwater Regulation Bypass Valve to 11 Steam Generator (11 FRBV) resulted in a faster than expected cooldown rate. Operators took manual actions to stop the cooldown. A short to ground was found in the (+) stationary gripper coil wire in a Control Rod Drive Mechanism (CRDM) cable. The cause of the shorted cable has been initially attributed to foreign material within the cable connector during original manufacture of cable assemblies. Corrective actions are being taken to ensure the cause of the failure is thoroughly understood and any actions necessary to prevent recurrence are identified. The CRDM cables on Unit 2 will be meggared during the next Unit 2 refueling outage.
282 | 2821998008 | 1998-06-05 | QR3 | Reactivity Control Imbalance | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On June 5th, 1998, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was at steady-state, 100% power with the Rod Control System in automatic. At approximately 7:00 PM, Unit One tripped from 100% power on a Negative Flux Rate Trip generated by Power Range Nuclear Instrumentation. Subsequent investigation revealed that Control Rod G7 dropped because of equipment failure, and caused the Negative Flux Rate Trip. Efforts to establish the equipment failure mechanism that caused the trip are ongoing.
282 | 2821998016 | 1998-10-29 | QR3 | Reactivity Control Imbalance | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On October 29, 1998 Unit 1 was at steady-state, 100% power with the Rod Control System in automatic. At approximately 2350, Unit 1 tripped on a Negative Flux Rate Trip generated by Power Range Nuclear Instrumentation. Subsequent investigation revealed that Control Rod G3 dropped because of equipment failure, and caused the Negative Flux Rate Trip.
282 | 2821999001 | 1999-01-05 | H1 | Fire | [7 empty] | X | [5 empty] | X | [19 empty] | X | [10 empty] | X | Prairie Island 1 | P | WE | PO | 100 | At approximately 1311 on January 5, 1999, with Unit 1 operating at 100% power and no electrical switching in progress an internal fault occurred in the Unit 1 Main (1M) transformer. The fault caused an explosion in the transformer and Unit 1 Turbine Trip / Reactor Trip. As a result of the explosion, the 1M transformer was breached and a large was expelled and ignited in an area approximately 40 feet north of the transformer. The Fire Brigade was spa the site and extinguished the burning oil fire at approximately 1325. As a result of the fault, explosion, and fire, both 1M and 1R (Unit 1 reserve transformer) were locked out. This caused the loss of non-safeguards buses 11, 12, 13, & 14 and major equipment on Unit 1 powered from these buses including both reactor coolant pumps (RCPs), both feedwater pumps, both circulating water pumps, all condensate pumps, all heater drain pumps, 11 cooling water pump, all Turbine Building and Auxiliary Building lighting (except for battery backed emergency lighting), motor driven fire pump, spent fuel pool cooling, and a loss of all non-safeguards 480V buses fed from these buses. With the loss of both RCPs, Unit 1 was on natural circulation. No diesel generators started. One safeguards bus was never lost, the other successfully transferred sources automatically. After the initial response to the event was completed and the unit stabilized, power was restored to non-safeguards 4KV buses and the RCPs were restarted between 7 and 8 hours following the transformer fault. The unit was restored to normal power operation over the following week.
282 | 2822001004 | 2001-08-01 | QR3 | Reactivity Control Imbalance | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On August 1, 2001, Prairie Island Unit 1 experienced an automatic reactor trip due to negative flux rate. Following the trip, several control rods initially failed to provide rod bottom position indication. This required the operating crew to enter emergency operating procedures and initiate boration to compensate for the apparent loss of shutdown. With the exception of the erroneous rod position indication, the plant response and operator actions subsequent to the trip were as expected. The event was initiated by water intrusion into a control rod drive power supply cabinet. The water caused varistors in the 12 AC Control Rod Power Cabinet to malfunction. This, in turn, caused the Control Bank C2 control rods to drop into the core, resulting in the negative flux rate trip. The source of the water was spillage from an overhead room cooler drip tray. A partially plugged drip tray drain, combined with high ambient humidity, led to a condensation rate from the cooler coils that exceeded the capacity of the drain until the drip tray overflowed onto the control rod drive power supply cabinet below. Corrective actions include development of a preventative maintenance task to periodically inspect and clean the drip tray drains. The control rod position indication error was caused by an unanticipated bias (equating to approximately 8 steps) that was introduced by a revised calibration procedure. The control rod position indications were recalibrated using the previously accepted methodology.
282 | 2822001005 | 2001-08-03 | QC5 | Loss of Non-safety-Related Bus | [7 empty] | X | [25 empty] | X | [11 empty] | Prairie Island 1 | P | WE | PO | 25 | On August 3, 2001, with Unit 2 at 100% power, Unit 1 was undergoing an orderly startup following the reactor trip that occurred on August 1, 2001. At about 8:40 pm CDT, with Unit I at approximately 25% power, operators were transferring the power supply to the non-safeguards 4 kV buses from the Unit 1 Reserve transformer to the Unit 1 Main Auxiliary transformer. Within seconds of closing the source breaker from the Main auxiliary transformer to 4 kV Bus 12, the breaker failed. The breaker failure initiated a fire in Cubicle 12-4 of Bus 12. The failure actuated the Generator Transformer protective relaying scheme, including a lockout of Bus 12. The bus lockout opened the Breaker 12-1, Bus 12 source from the 1 RX transformer, and actuated the protective relaying scheme. The protective relaying scheme caused a turbine/reactor trip and actuation of the Auxiliary Feedwater System. To support firefighting, Bus 11 was deliberately de-energized, thus, both reactor coolant pumps were unpowered and the unit was cooled down via natural circulation. The fire was extinguished about one hour and 30 minutes after the event. The unit was brought to cold shutdown within the time allowed by Technical Specifications. Remaining unit equipment responded as expected and, overall, the organization effectively responded to the event (although some improvements were recommended following an evaluation of organizational response). A root cause evaluation is complete, the damaged equipment has been repaired, and actions are being taken to prevent recurrence of the event and to improve organizational response to events.
282 | 2822002002 | 2002-11-15 | QR6 | Manual Reactor Trip | [45 empty] | Prairie Island 1 | P | WE | PO | 12 | On November 15, 2002, Unit I was undergoing an orderly shutdown in preparation for a planned refueling outage. Prior to the shutdown, an existing problem with the steam generator blowdown flash tank vent line bellows to 13A Feedwater Heater had been identified and contingency plans were in place for monitoring the level of the 13A Feedwater Heater during the load decrease. At approximately 2020 during the load decrease, Operators made the decision as planned, to manually trip the reactor when it was determined that a Hi Hi Level in the heater, could not be reduced. Reactor power at the time of the trip was 12%. During performance of reactor trip recovery procedures, 11 Turbine Driven Auxiliary Feedwater Pump auto started at 2055 when the running Main Feedwater Pump was secured. Following investigation and repair to the steam generator blowdown flash tank vent line bellows and completion of all refueling outage activities, the unit was returned to service on December 6, 2002.
282 | 2822006001 | 2006-04-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On April 14, 2006, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was operating at 100% power. At approximately 1425 CDT, an 11 FEEDWATER PUMP LOCKED OUT annunciator was received in the control room. Unit 1 operators responded per the alarm response procedure and manually tripped the reactor. The trip was uncomplicated and all systems operated as expected and operator response and recovery actions were as expected. Initial investigation of the cause of the 11 Feedwater Pump trip determined the feedwater pump tripped because the 11 Condensate Pump had tripped. The 11 Condensate Pump motor was shipped off site for repairs and the stator windings were found to have grounded. The root cause evaluation (RCE) of this event determined the condensate pump trip was caused by degraded motor insulation due to aging and environmental conditions. The RCE further determined that the organizational root cause of the condensate pump motor trip was a lack of an adequate long range planning and budgeting process to prioritize and budget large motor maintenance.
282 | 2822008002 | 2008-07-31 | QR8 | Spurious Reactor Trip | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On July 31, 2008, Prairie Island Nuclear Generating Plant (PINGP), Unit 1 was operating at 100 percent power. At 0817 CDT during performance of the quarterly analog protection functional test, Unit 1 reactor tripped. At the time of the trip the yellow channel over-temperature delta T (OT delta T) bistables were in the tripped condition as directed by the testing procedure when a red channel OT delta T reactor trip signal was generated due to a failed controller. The red channel OT delta T setpoint was not expected to be challenged nor was a reactor trip expected at any point during yellow channel OT delta T analog testing. All automatic actions for a reactor trip occurred as required with two exceptions: The Unit 1 turbine-driven auxiliary feedwater pump (11 TDAFWP) auto started as designed, but tripped 42 seconds later on low discharge pressure (see LER 1-08-03); and a Unit 1 Turbine 2 Reheat Stop Valve indicated intermediate vice closed due to a fault with the position indication. Operator response and recovery actions were as expected. The reactor trip was caused by a failed F delta Q proportional controller, which was subsequently replaced. Planned corrective actions include replacement of all similar controllers.
282 | 2822009005 | 2009-05-18 | QR5 | Turbine Trip | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On May 18, 2009 at 1305 hours, the site experienced a lockout of the 12 Circulating Water pump due to a ground fault in the power supply cable. This resulted in a turbine trip and associated reactor trip of Unit 1. Corrective actions taken or planned include repair of the faulted cable and improvements in the implementation of the cable monitoring program.
282 | 2822011002 | 2011-07-01 | QR6 | Manual Reactor Trip | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On July 1, 2011, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was manually tripped from approximately 100% steady-state power. The manual reactor trip was in response to the right main turbine stop valve failing closed as the result of an Electro-Hydraulic (EH) oil leak located at the stop valve. As designed, 11 and 12 Auxiliary Feed Water (AFW) pumps auto started on steam generator low water level. The causal evaluation determined that right main turbine stop valve failed closed due to excessive oil leakage from a failed O-ring. An age related compression set and slight extrusion near the outside contact surface resulted in the failed O-ring.
282 | 2822015004 | 2015-05-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Prairie Island 1 | P | WE | PO | 100 | On May 31, 2015, at 2220 CDT, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 reactor was manually tripped while operating at 100 percent power due to a lockout trip of 11 Condensate Pump followed by a lockout trip of 11 Main Feedwater Pump. The manual reactor trip was directed by the annunciator response procedure for the lockout alarm, C47010-0101, 11 FEEDWATER PUMP LOCKED OUT. This also resulted in a turbine trip as designed. The Operations crew entered the reactor trip emergency operating procedures and stabilized the unit in Mode 3, at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. <br /><br /> The manual trip is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated to start the auxiliary feedwater pumps as designed on low narrow range steam generator level and provided makeup flow to the steam generators. The auxiliary feedwater actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). Steam generator levels have been returned to normal. <br /><br /> The cause for 11 Condensate Pump Motor failure was due to voids within the insulation resulting from inadequate Vacuum Pressure Impregnation (VPI). The voids allowed partial discharge to occur while in-service, which caused a turn to turn failure and a subsequent groundwall failure. <br /><br /> Corrective action is to determine the best test method(s) for identifying motor insulation degradation and initiate additional actions to perform implementation of these test methods.
282 | 2822020001 | 2020-08-26 | QR8 | Spurious Reactor Trip | [45 empty] | Prairie Island 1 | P | WE | PO | 95 | On August 26, 2020, Prairie Island Nuclear Generating Plant (PINGP), Unit 1 reactor automatically tripped on a spurious Power Range Negative Rate trip signal. Surveillance testing was in progress on the Nuclear Instrumentation System (NIS) Power Range Channel which placed one of the Neutron Flux Power Range bistables in trip, reducing the normal two-out-of-four trip logic to one-out-of-three trip logic. <br /><br /> This event is reportable under 10CFR 50.73(a)(2)(iv)(A) due to the Reactor Protection System (RPS) actuation.<br /><br /> There were no nuclear safety impacts. The system operated as designed and initiated an automatic reactor trip that placed the plant in a safe condition. All systems responded normally. Operations stabilized the plant without complication. <br /><br /> The direct cause of this event was attributed to a spurious negative rate signal of 1N41 Reactor Trip bistable during NIS Power Range Channel Calibration surveillance testing. <br /><br /> The corrective actions include replacement of 1N41 components as well as a design modification.
285 | 2851989019 | 1989-09-24 | QR6 | Manual Reactor Trip | [45 empty] | Fort Calhoun | P | CE | PO | 6 | On September 24, 1989, Fort Calhoun Station Unit 1 was operating at approximately 70% power in Mode 1. AT 1259 hours indication of high temperature for Reactor Coolant Pump RC-3A upper motor thrust bearing was received in the control room. After maximization of both the cooling water flow to the oil coolers and the oil flow to the bearing failed to reduce the indicated temperature, the Shift Supervisor initiated a controlled plant shutdown at 1320 hours. At 1518 hours, with reactor power between 5 and 6 percent, RC-3A thrust bearing temperature indication spiked to 267 degrees. The reactor was immediately manually tripped and RC-3A was shut down. This trip is reportable pursuant to 10 CFR 50.73(a)(2)(iv). Investigation revealed the cause of the indicated high temperature to be damaged cable for the bearing resistive temperature device (RTD), although cause of the damage could not be determined. There was no evidence of actual excessive bearing temperature. The damaged cable and the RTD were replaced. Other similar RTD wiring will be inspected and investigation into the cause of the cable damage will be completed during the 1990 refueling outage.
285 | 2851990026 | 1990-11-19 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Fort Calhoun | P | CE | PO | 100 | On November 19, 1990 while the plant was operating at 100% power, a pipe joint at an isolation valve in the Turbine Building instrument air header failed. The resulting loss of instrument air pressure caused a feedwater transient which ultimately resulted in manual tripping of the reactor. The root cause for this event was improper installation of the isolation valve (inadequate joint insertion coupled with poor soldering technique) under a modification in 1984. The contributing cause was inadequate control of the installation process. <br /><br /> The completed corrective actions for this event included repairing the failed joint, installing braces around all applicable header isolation valves, checking the turbine building header for leaks, and repairing one additional leak. The administrative controls over modifications have been improved since 1984. The long term corrective actions for this event include reinstalling the isolation valves using better techniques, providing better training on soldered joints, and discussing this event in licensed and non-licensed operating personnel requalification training.
285 | 2851992014 | 1992-05-14 | QR5 | Turbine Trip | [45 empty] | Fort Calhoun | P | CE | PO | 98 | On May 14, 1992, a steam leak was identified coming from a capped connection on the turbine trip switch (LA-1303B) on Moisture Separator ST-3C. The level float chamber associated with this switch was valved out and the connection repaired. The upper isolation valve for the float chamber was then cracked open as the first step to returning the float chamber to service. At 1557 hours, the turbine tripped due to a 'false' high moisture separator level indication on LA-1303B. The turbine trip subsequently caused the Reactor Protective System to trip the reactor on Loss of Load. <br /><br /> The overall effect of the event on nuclear safety was minimal. The Loss of Load trip is an anticipatory trip designed to protect plant equipment and is not credited in the plant safety analysis. The plant responded as designed. <br /><br /> The root cause of this event was found to be the Shift Supervisor's decision not to disable the turbine trip circuit prior to opening the float chamber's upper isolation valve. <br /><br /> Corrective actions will include discussion of this event with appropriate personnel, review of the definition of emergency maintenance and the applicability of a Standing Order which addresses non-routine activities requiring formalized plans.
285 | 2851992023 | 1992-07-03 | QC4 | Loss of ac Instrumentation and Control Bus. | [6 empty] | X | [19 empty] | X | [18 empty] | Fort Calhoun | P | CE | PO | 100 | On July 3, 1992, at 2336, while the plant was operating at 100% power, the Reactor Protection System automatically tripped the reactor due to high pressurizer pressure. The event was initiated as a result of maintenance on a non-safety related inverter. During replacement of a degraded circuit board, power was momentarily lost to the instrument bus that supplies power to the Turbine Electrohydraulic Control System, resulting in closure of the turbine control valves. A subsequent failure of a pressurizer code safety valve resulted in high pressure in the pressurizer quench tank that blew the tank's rupture disk and resulted in the loss of approximately 21,500 gallons of contaminated water to the containment building sump. <br /><br /> The consequences of the event are bounded by the Fort Calhoun Station Updated Safety Analysis Report.<br /><br /> The root cause of the momentary loss of power to the instrument bus was determined to be the inability to isolate and test the non-safety related inverters after maintenance without potentially losing power to the respective 120V AC instrument buses. The root cause of the malfunction of Pressurizer Safety Valve RC-142 was determined to be the adjusting bolt locknut that loosened and allowed the set pressure adjusting bolt to back out. <br /><br /> Corrective actions include a modification to enhance the ability to test the non-safety related inverters, addition of a positive mechanical locking device for the pressurizer safety valve adjusting bolts and completion of a comprehensive Recovery/Restart Action Plan.
285 | 2851992028 | 1992-08-22 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | Fort Calhoun | P | CE | PO | 100 | On August 22, 1992 at 0152 (CDT) while the plant was operating at 100% power, the Reactor Protection System automatically tripped the reactor on Thermal Margin/Low Pressure (TM/LP). The event was initiated by the failure of an AC to DC power converter which affected the first stage turbine pressure signal and resulted in the repositioning of the Turbine Control Valves. The decrease in secondary steam demand caused an increase in Reactor Coolant System (RCS) pressure which was terminated by a premature opening of one of two Pressurizer Safety Relief Valves, followed by the Reactor trip. <br /><br /> The root cause of this event was the failure of an AC to DC power converter in the Turbine Electrohydraulic Control (EHC) panel. The root cause of the premature lift of RC-142 was that the (laboratory) test environment in which valve set pressure qualification was performed, did not provide an adequate representation of the actual field environment. <br /><br /> Corrective actions include a modification to change the power source for EHC pressure transmitters, reducing the pressure setpoint for initiating a High Pressurizer Pressure trip and Power Operated Relief Valve operation and adjusting Pressurizer Safety Valve set pressures using revised test procedures.
285 | 2851993011 | 1993-06-24 | QR5 | Turbine Trip | [45 empty] | Fort Calhoun | P | CE | PO | 100 | On June 24, 1993 at 1322, the Fort Calhoun Station (FCS) experienced a reactor trip due to a Loss of Load. Work was in progress in the FCS switchyard involving Type SBFU Static Circuit Breaker Failure Relays, when a door mounted Type AR relay was inadvertently actuated. This, in turn, tripped two breaker failure lock-out relays, which resulted in opening of station output breakers and de-energized both 4.16kV non-vital buses. One non-vital bus failed to properly load shed on the loss of voltage, and as a result breakers remained closed on the bus even though the bus was de-energized. Initial Operator actions, based on Control Room indications that these breakers were closed, resulted in a short-term interruption of feedwater and condensate flow.<br /><br /> This event was determined to have resulted from lack of proper job planning, lack of a formal decision making process, incomplete communications and inadequate implementation of a procedure. <br /><br /> Corrective actions include actions to improve the conduct of work within the switchyard, and training for Operations personnel on use of all available indications in decision making.
285 | 2851993018 | 1993-12-06 | QR5 | Turbine Trip | [45 empty] | Fort Calhoun | P | CE | PO | 100 | On December 6, 1993 at approximately 0227 hours, the main turbine and the reactor tripped during Electro-Hydraulic Control (EHC) pump start testing. <br /><br /> The main turbine trip and resultant reactor trip occurred because of the configuration of the EHC System hydraulic fluid tubing connected to pressure switches PS-5096, PS-5097, and PS-5098, and to associated solenoid valves PS-5097-20 and PS-5098-20. The tubing configuration had been changed during the recent refueling outage by Facility Change Engineering Change Notice (ECN) 93-162. The Root Cause of this event was determined to be inadequate design of the ECN. Specifically, personnel involved in the design and review of the ECN failed to analyze the effects of increased lengths of hydraulic tubing on the operation of the EHC system. The contributing cause is inadequate pre-operational testing specified in the ECN.<br /><br /> Corrective actions include correcting the configuration of the EHC System tubing; establishment of guidance to identify which Facility Change ECNs have the potential to impact plant safety or reliability, and to specify the appropriate level of review by plant personnel for these ECNs; procedural changes to ensure proper pre-operational testing; and training for appropriate personnel.
285 | 2851994001 | 1994-02-11 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Fort Calhoun | P | CE | PO | 100 | On February 11, 1994 at 0340, an invalid Containment Pressure High Signal (CPHS) occurred. The CPHS initiated Engineered Safeguards actuations including safety injection actuation containment isolation actuation, steam generator isolation, and starting of emergency diesel generators. Steam generator isolation also resulted in a turbine/reactor trip. The cause of the event was a coil-shorting failure of a supervisory relay, resulting in actuation of the CPHS lockout relay. <br /><br /> Post-event investigation determined that if a coil-shorting failure of certain other supervisory relays were to occur coincident with certain design basis accidents, the result could involve premature actuation of lockout relays associated with the Recirculation Actuation Signal (RAS). It was concluded that these concerns represented conditions outside the design basis of the plant. The cause of the design basis concerns was determined to be failure of the original plant design to anticipate a potential failure mode. <br /><br /> The failed CPHS supervisory relay was replaced, and will be sent off-site for investigation of the failure mechanism. An engineering analysis was performed with respect to engineered safeguards supervisory relays. Eight supervisory relays have been disconnected to address the design basis concerns identified by the engineering analysis.
285 | 2851995003 | 1995-05-11 | QR6 | Manual Reactor Trip | [45 empty] | Fort Calhoun | P | CE | PO | 100 | On May 11, 1995, it was determined that the upper oil reservoir lube oil cooler heat exchanger for the Reactor Coolant Pump (RCP) RC-3D motor had developed a leak. The leak was allowing Component Cooling Water (CCW) into the lube oil system for the RCP motor. To minimize possible damage to the motor bearings, the reactor was manually tripped (from 100 percent power) at 1105 and RC-3D was secured. Following eddy current testing and plugging of several heat exchanger tubes, the plant was returned to power operation on May 15, 1995. <br /><br /> On May 23, 1995, a similar leak developed in the same lube oil cooler. The reactor was again manually tripped (from 97 percent power) at 0029 on May 24, 1995 and RC-3D was secured. <br /><br /> Destructive examination indicates that the failures involved intergranular stress corrosion cracking associated with nitrites in the CCW. The tubes had been in service since initial plant startup in 1973. <br /><br /> The tube bundles for all four RCP motor upper oil reservoir lube oil coolers have been replaced. Additional corrective actions will include determining appropriate actions to ensure adequate heat exchanger reliability.
285 | 2851995003 | 1995-05-24 | QR6 | Manual Reactor Trip | [45 empty] | Fort Calhoun | P | CE | PO | 97 | On May 11, 1995, it was determined that the upper oil reservoir lube oil cooler heat exchanger for the Reactor Coolant Pump (RCP) RC-3D motor had developed a leak. The leak was allowing Component Cooling Water (CCW) into the lube oil system for the RCP motor. To minimize possible damage to the motor bearings, the reactor was manually tripped (from 100 percent power) at 1105 and RC-3D was secured. Following eddy current testing and plugging of several heat exchanger tubes, the plant was returned to power operation on May 15, 1995. <br /><br /> On May 23, 1995, a similar leak developed in the same lube oil cooler. The reactor was again manually tripped (from 97 percent power) at 0029 on May 24, 1995 and RC-3D was secured. <br /><br /> Destructive examination indicates that the failures involved intergranular stress corrosion cracking associated with nitrites in the CCW. The tubes had been in service since initial plant startup in 1973. <br /><br /> The tube bundles for all four RCP motor upper oil reservoir lube oil coolers have been replaced. Additional corrective actions will include determining appropriate actions to ensure adequate heat exchanger reliability.
285 | 2851995005 | 1995-08-24 | QR8 | Spurious Reactor Trip | [45 empty] | Fort Calhoun | P | CE | PO | 100 | On Thursday, August 24, 1995, at 1114 while operating at 100% power (mode 1) the plant experienced a reactor trip and associated diesel generator start. The trip occurred during the performance of IC-PM-DSS-1001, 'Diverse Scram System Actuation Relay Operability Test,' when a licensed operator inadvertently repositioned the incorrect switch from TEST to NORMAL. Generally plant systems responded normal to the trip except for diesel generator number 1, Which went to full speed (900 RPM rather than idle speed (500 RPM). The diesel start problem is fully described in LER 95-006. <br /><br /> The Root Cause of the plant trip was inadequate attention to detail. This is a human error that could have been prevented with additional self checking. <br /><br /> Corrective actions include instituting the use of peer-verification for operating equipment from the control room that could cause a significant plant transient and making peer-verification and self-checking a specific item of evaluation during Operations self-assessments.
285 | 2851996002 | 1996-03-28 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Fort Calhoun | P | CE | PO | 30 | On March 29, 1996, the Fort Calhoun station was conducting a plant shutdown because of a condenser tube leak. At 2235, while attempting to isolate one of the condensers the Fort Calhoun Station reactor was manually tripped from approximately 30% power, because of a partial loss of vacuum in the main condenser. All safety systems functioned as designed and the plant proceeded into Mode 3 (Hot Shutdown). <br /><br /> The damaged condenser tube had been discovered during a previous maintenance shutdown conducted immediately prior to this event (March 15 - 25). The leak was not repaired prior to the plant startup following this shutdown due to a combination of problems. The personnel who were informed of the potentially leaking condenser tube did not fully investigate the concern, and, the applicable maintenance procedure does not provide clear direction for documenting identified tube leaks. <br /><br /> The condenser tube leak was plugged and the condenser tube will be reinspected during the next refueling outage to determine the cause of the failure. The procedure will be revised to address disposition of identified condenser tube leaks.
285 | 2851997003 | 1997-04-21 | K1 | Steam Line Break Outside Containment | [9 empty] | X | [26 empty] | X | [8 empty] | Fort Calhoun | P | CE | PO | 100 | On April 21, 1997 at 2023 with the plant operating at 100% power, a section of the high pressure turbine fourth stage extraction steam line ruptured at a large radius elbow (sweep) resulting in the Control Room Operators manually tripping the reactor. Although several secondary systems housed in the Turbine Building were damaged, safety related systems functioned as required, and the reactor was safely shutdown. There were no personnel injuries resulting from this event. <br /><br /> Preliminary information suggests that the physical cause of the steam extraction line rupture was Flow-Accelerated Corrosion (FAC). It was determined that over-reliance was placed on one factor, that typically wear rates for sweeps are low, consequently omitting the failed site from previous inspections. Consideration of other factors (e.g., industry experience/industry practice) could have resulted in selection of the failed site for inspection. <br /><br /> Corrective actions include replacing the affected piping and inspecting and replacing additional piping as needed. Long term corrective actions include completing the failure analysis of the affected pipe and upgrading the erosion corrosion program.
285 | 2852003003 | 2003-09-12 | QR3 | Reactivity Control Imbalance | [45 empty] | Fort Calhoun | P | CE | PO | 15 | During a reactor shutdown in preparation for a refueling outage, the power reduction was stopped because the operators were unable to maintain the axial shape index (ASI) within the expected band. In order to minimize the operational challenge, management provided two reactor trip criteria. At 2037, with the power reduction close to a nominal 15 percent power, it was noted that ASI might not be maintained within the required margin if the shutdown continued. At 2055 on September 12, 2003, Operations determined that a reactor trip was required because one of management's reactor trip criteria was about to be met. The reactor operators were directed to trip the reactor using the manual push button. A four (4) hour non-emergency report was made to the NRC Operations Center at 0010 CDT on September 13, 2003, pursuant to 10CFR 50.72(b)(2)(iv). This report is being made pursuant to 10CFR50.73(a)(2)(iv). No formally approved written guidance was provided to the operator and therefore this event is reportable. Management failed to recognize that a manual trip of the reactor without a change to the shutdown procedure would be reportable. Appropriate procedural revisions to allow the flexibility in plant procedures to allow a manual reactor trip from power levels greater than 2 percent are being processed.
285 | 2852005001 | 2005-02-26 | QP5 | Excessive Feedwater Flow | [45 empty] | Fort Calhoun | P | CE | PO | 15 | On February 26, 2005, operators completed a scheduled power reduction to 12% power. At 2100 CDT, the turbine was tripped with no noted complications. At 2121, the turbine was reset in preparation for turbine testing. The reactor operator (RO) noticed that intermediate stop valve (ISV-2) did not open as expected. At 2134, while troubleshooting ISV-2, a RO informed the control room supervisor that pressurizer level and pressure were lowering and another RO informed the control room supervisor that he was experiencing a problem with feedwater control. The operations crew identified that reactor coolant system (RCS) temperature was lowering and power was rising. The reactor protection system loss of load trip units enabled and the reactor automatically tripped. The immediate cause for the reactor trip was due to control board operator performance errors related to control of RCS temperature and steam generator (SG) level. These errors resulted in a lowering of RCS temperature, which, resulted in an increase in reactor power activating the loss of load trip. The root cause of this event was that administrative controls are overly biased towards full power operation. The reactor shutdown was completed as required. SG level and reactor temperature were returned to normal control bands. Procedure changes are being completed to address the root cause.
285 | 2852008001 | 2008-03-15 | QR5 | Turbine Trip | [45 empty] | Fort Calhoun | P | CE | PO | 85 | The plant was operating at a reduced power level (nominal 85 percent) due to turbine control system problems. The station was preparing a troubleshooting plan when on March 15, 2008, at 0833 CDT, a reactor trip occurred. The operators entered Emergency Operating Procedure (EOP) 00 “Standard Post Trip Actions.” The main steam and feedwater system operated normally. All control rods inserted fully. The apparent cause of the reactor trip was the failure of a circuit board in the EHC control system resulting in the closure of turbine control valves CV-1 and CV-3. Closure of these valves results in a preemptive trip of the reactor due to the loss of load. The root cause of the circuit board failure was an improperly adjusted potentiometer, which resulted in a long term overcurrent condition to one of the transformers on the affected circuit board. The overcurrent condition resulted in the failure of the affected transformer. The failed circuit board was replaced. The output of the affected potentiometer was verified to be correctly adjusted. Post maintenance testing was performed on the EHC system to ensure its reliability.
285 | 2852010006 | 2010-12-23 | QR5 | Turbine Trip | [45 empty] | Fort Calhoun | P | CE | PO | 100 | Fort Calhoun Station was operating at full power (nominal 100 percent). The station was preparing a scaffolding for an upcoming outage when on December 23, 2010, at 1050 Central Standard Time (CST), a reactor trip occurred. The operators entered Emergency Operating Procedure (EOP) 00, "Standard Post Trip Actions." The main steam and feedwater systems operated normally. All control rods inserted fully. The apparent cause of the turbine and subsequent reactor trip was the inadvertent actuation, caused by bumping, and sticking of one of four turbine moisture separator high water level turbine trip switches while reactor power was above 15 percent. The root cause was insufficient performance monitoring of the moisture separator high level trip mercury switches which resulted in degraded performance and increased risk for susceptibility to binding. Following the initial determination of the erroneous moisture separator high level trip signal, immediate actions included: halting all work near the moisture separator sensing lines and level switches, posting the affected areas as "Protected Equipment," and initiating a stop work action for all ongoing scaffold work within the turbine building. The Ioisture separator level switches and logic will be replaced during the 2011 refueling outage.
285 | 2852014003 | 2014-03-17 | QR5 | Turbine Trip | [45 empty] | Fort Calhoun | P | CE | PO | 100 | On March 17, 2014, at 12:02 Central Daylight Time (CDT), a turbine trip and subsequent reactor trip occurred while operating at nominal 100 percent power. Maintenance was in progress on the main generator stator cooling system when system inventory was lost resulting in an automatic turbine trip due to low system pressure. Immediate response by operations personnel included implementing procedure emergency operating procedure (EOP) -00, Standard Post Trip Actions, and subsequent entry into procedure EOP-01, Reactor Trip Recovery. Based on plant system response this is considered an uncomplicated trip.<br /><br /> The station determined that the root cause of the plant trip was that operational risk was not effectively identified or mitigated by individuals throughout the organization.<br /><br /> The leak was isolated shortly after the trip by fully removing the probe and closing the isolation valve. Fort Calhoun Station will be implementing the Exelon risk management procedure, WC-AA-104, Integrated Risk Management. This procedure provides direction consistent with industry best practices, and requires individual review of each category of risk identification and mitigation.
285 | 2852014007 | 2014-12-17 | QR5 | Turbine Trip | [45 empty] | Fort Calhoun | P | CE | PO | 100 | On December 17, 2014, at 1014 Central Standard Time (CST), the Fort Calhoun Station (FCS) reactor tripped due to a loss of load signal from the main turbine. The loss of load signal actuates the reactor protective system (RPS) which tripped the plant. The trip of the turbine was caused by a spurious actuation of a relay on the station unit auxiliary transformer that normally provides power to 4160 VAC bus 1A2.<br /><br /> The root cause was that FCS had not ensured that an identified single point vulnerability for T1A-2 transformer was eliminated or had an adequate mitigating strategy.<br /><br /> The control cabinet sealing was improved to reduce moisture from the interior of the cabinet. The relay that caused the trip was removed from the trip circuit. The station will modify the control circuits to eliminate the single point vulnerability in the transformer control cabinets.
285 | 2852016003 | 2016-06-22 | QR5 | Turbine Trip | [45 empty] | Fort Calhoun | P | CE | PO | 100 | An automatic turbine trip occurred resulting in an automatic Reactor Protective System (RPS) actuation from mode 1 at 100% power due to loss of turbine load at 0841 Central Daylight Time on June 22, 2016. System actuation and responses were as designed. There were no Safety Systems inoperable that contributed to this event. The trip occurred during Post Modification Testing activities on the turbine Emergency Trip System (ETS) pressure loop trip. Engineering failed to identify and disable the transmitter deviation based trip. The differences between the substituted input values selected for testing and the output of the signal selector block were sufficient to trigger the two transmitters-in-deviation trip for the ETS loop.
286 | 2861987001 | 1987-01-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On January 31, 1987, a reactor trip and subsequent turbine trip were initiated automatically by low steam generator (SG) water level. Investigation determined that foreign matter had accumulated in the multiple orifice and check valve assembly in the control oil system for No. 32 main boiler feedwater pump (MBFP), causing the pump to trip. The resultant decrease in feedwater system flow caused SG levels to decrease to the reactor trip setpoint. Shortly after the reactor trip, No. 33 auxiliary boiler feedwater pump (ABFP), which had started automatically, tripped due to its discharge pressure limiter setpoint being improperly set. The pump was promptly restarted manually by plant operators and functioned normally. The MBFP oil system was cleaned and inspected, and the ABFP discharge pressure limiter was re-adjusted before the unit returned to service.
286 | 2861987002 | 1987-02-11 | QC5 | Loss of Non-safety-Related Bus | [13 empty] | X | [30 empty] | X | Indian Point 3 | P | WE | PO | 100 | On February 11, 1987, No. 34 static inverter tripped due to an overcurrent condition caused by a short-circuited solenoid valve. This resulted in a runback of both main boiler feedwater pump speed controllers (these controllers are powered from No. 34 static inverter) and a subsequent reactor trip on steam flow feedwater flow mismatch with coincident low steam generator (SG) level. A high steam flow safety injection (ST) actuation and other system abnormalities occurred due to the loss of the static inverter. The failed solenoid valve was replaced and all other affected systems were verified to be functioning normally before start-up. To prevent recurrence, the design of No. 34 static inverter was improved to allow isolation of single branch circuits if a short circuit develops.
286 | 2861987003 | 1987-04-04 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | SU | 3 | On April 4, 1987, while rolling the main turbine generator (TG) to synchronous speed during startup, the main turbine governor malfunctioned, causing an increase in TG speed. The main turbine tripped automatically when TG speed reached the overspeed trip setpoint. An automatic reactor trip was generated by the turbine trip signal. Inspection of the governor system found that a reduction in control oil pressure had occurred, making the governor unstable. The governor will be repaired during the upcoming refueling outage. To prevent recurrence, an engineering study will be initiated to determine the feasibility of raising the trip setpoint for a reactor trip resulting from a turbine trip. The unit was returned to service using a load limit control system during turbine roll up.
286 | 2861987004 | 1987-04-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 3 | P | WE | PO | 99 | On April 17, 1987, a short circuit developed in a reactor coolant pump oil reservoir level switch, causing a momentary decrease in voltage on No. 33 instrument bus (IB). The voltage decrease caused a partial closure of all main feedwater regulating valves which resulted in an automatic reactor trip. A high steam flow safety injection signal was also generated after the trip due to the actuation of bistables powered by No. 33 IB. Since the reactor coolant system was at normal operating pressure no water was injected as a result of the SI actuation. The failed switch was repaired, and an evaluation of the IB supply circuits will be undertaken to determine if corrective actions are necessary.
286 | 2861987012 | 1987-12-22 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On December 22, 1987, with the reactor at 100 percent power, an automatic unit trip occurred while plant personnel were performing a monthly surveillance test on the Reactor Coolant Low Flow Protection System. All plant systems functioned properly following the trip with two exceptions: 1) motor operated disconnect F1-3 did not automatically open following the opening of generator output breakers and would not open via its Control Room flight panel switch, and 2) the plant computer provided an incomplete Sequence of Events Report. It was determined that, the tripping of a bistable switch associated with a Low Reactor Coolant Flow Logic relay during the test (Loop 4, Channel I) in conjunction with a high resistance contact on a similar relay in the same loop (Loop 4, Channel III) resulted in the de-energization of a Low Reactor Coolant Flow matrix output relay and caused the reactor trip. Reactor Coolant flow was actually normal at the time of the trip. The relay for Loop 4, Channel III was found to be faulty due to tarnish build-up on a relay contact. After replacing the faulty relay, the reactor was brought critical on December 23, 1987. The unit was synchronized to the bus on December 24, 1987.
286 | 2861988001 | 1988-02-02 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Indian Point 3 | P | WE | PO | 100 | On February 2, 1988, with the reactor at 100 percent power, a manual unit trip was initiated by plant operators due to the loss of both main boiler feed pumps (MBFPs) and the anticipated decrease of steam generator levels. All plant systems functioned properly following the trip. It was determined subsequent to the trip that both MBFPs had tripped due to a Control/Auto Stop Oil System pressure perturbation caused by bearing seizure of the No. 31 A.C. oil pump. This seizure of the No. 31 oil pump caused a rapid decrease in system oil pressure from which the standby oil pump could not recover before the MBFPs tripped. Investigations revealed overgreasing had caused the bearing on the No. 31 A.C. oil pump to seize. The overgreasing of the bearing occurred previous to this event and is attributed to procedural deficiencies concerning lubrication activities. A preventative maintenance procedure on equipment lubrication has been implemented to preclude similar occurrences. The No. 31 A.C. oil pump was repaired and cleaned with both sets of bearings replaced, and the motor was returned to service. Following the No. 31 oil pump repairs, the reactor was brought critical and synchronized to the bus on February 3, 1988. Full reactor power was reached on February 4, 1988.
286 | 2861988002 | 1988-03-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On March 31, 1988, with the reactor at 100% power, Main Boiler Feed Pump (MBFP) No.32 tripped. Operators responding to the pump loss took manual control of the plant starting Auxiliary Boiler Feed Pump (ABFP) No.31 and 33 and initiated a turbine runback. Steam Generator levels initially decreased but turned around and started increasing requiring the shutdown of the ABFPs. The operators were subsequently unable to prevent an automatic unit trip due to High Steam Generator Level. All plant systems functioned properly following the unit trip with the exception of the No.33 ABFP recirculation valve which failed to automatically close. The valve was manually closed by the control room operator. It was determined subsequent to the trip that the MBFP had tripped due to a limit switch on its motor operated discharge valve making up. This limit switch movement was caused by "water hammer" vibration. The No.33 ABFP failure was determined to have occurred due to a damaged flow controller which was caused by a broken glass faceplate. No proximate cause was identified and the faceplate was replaced with plexiglas and the controller returned to service. The No.32 MBFP discharge valve limit switch was adjusted to provide less sensitive indication off the open seat and the valve was returned to service. Following the flow controller and discharge valve repairs the reactor was brought critical and synchronized to the bus on April 2, 1988. Full reactor power was reached on April 4, 1988.
286 | 2861988005 | 1988-06-12 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On June 12, 1988 with the reactor at 100% power, a unit trip occurred. The trip was generated on a low-low steam generator level received from 32 steam generator. All plant systems functioned properly following the unit trip with the exception of three high pressure steam dump valves which did not fully close and the main boiler feed pump recirculation valves which did not open. It was determined subsequent to the trip that the main turbine control valves had closed due to the failure of the smoothing orifice relief device in the main turbine control oil system. The valve trim on both main boiler feed pump recirculation valves was replaced and operating pressure on the valve operators was adjusted. The high pressure steam dumps were isolated and Technical Services evaluated continued operation with these valves isolated. The smoothing orifice relief device was repaired and long term corrective action includes periodic inspection to prevent recurrence of this event. The plant was brought critical and synchronized to the bus on June 15, 1988.
286 | 2861988006 | 1988-10-09 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On October 9, 1988, with the reactor at 100 percent power, a unit trip was initiated by loss of auto stop oil in the main turbine generator. Plant systems functioned properly following the trip with the following exceptions: three condenser steam dump valves failed to fully close; the main turbine generator air pilot valve stuck in an intermediate position; the 480 volt bus 5A undervoltage protection circuit malfunctioned, resulting in a "non-SI blackout" actuation for the bus; the source range nuclear instrumentation N-32 did not automatically reenergize; control rod drive mechanism fans 31 and 33 could not be restarted after bus 5A was reenergized; and the condensate polisher facility bypass valve did not open. It was determined that the main turbine generator trip had resulted from shifting of the governor impeller assembly due to a sheared retaining pin. Following repairs to the above listed equipment, the reactor was brought critical and synchronized to the bus on October 15, 1988. Full reactor power was reached on October 17, 1988.
286 | 2861989015 | 1989-10-19 | QR3 | Reactivity Control Imbalance | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On October 19, 1989, with the reactor at 100 percent power, control room operators initiated a manual reactor trip when they observed 12 control rods fully insert into the reactor core. Instrumentation and controls technicians were performing surveillance test 3PT-M62, "480 Volt Undervoltage and Degraded Grid" at the time of the event. All systems functioned properly following the trip with these exceptions: the computer generated "sequence of events" record was lost; the Station Auxiliary Transformer tap changer responded sluggishly; operators encountered difficulty in restarting control rod drive mechanism cooling fan #31; the condensate polisher facility bypass valve did not open; a leak developed on a pressurizer safety valve loop drain valve. While the plant staff was unable to determine the exact root cause of the event, the initiating occurrence was a "Non-SI Blackout" actuation on 480 volt bus 5A. It has been concluded that this resulted from a personnel error sustained during the performance of surveillance test 3PT-M62. Following a safety review by the Plant Operations Review Committee and approximately 100 hours of planned corrective maintenance, plant operators brought the reactor critical on October 23, 1989, synchronized the generator to the bus on October 24, 1989, and reached full power on October 25, 1989.
286 | 2861990004 | 1990-06-29 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On June 29, 1990 with the reactor at 100 percent power, a unit trip was initiated as the result of actuation of the main generator lockout relays. All plant systems functioned properly following the trip. It was determined that the actuation of the generator lockout relays resulted from the mechanical failure of protective relay, MCT1, which provides expanded breaker protection for the 345KV electrical output breakers. This relay was replaced and tested successfully. The reactor was brought critical on June 30, 1990 at 1852 hours and full power operations reached on July 2, 1990 at 0515 hours.
286 | 2861991003 | 1990-12-27 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Indian Point 3 | P | WE | PO | 48 | On December 27, 1990, with the reactor at 48 percent power, a manual unit trip was initiated because control room operators observed all circulating water pumps had tripped off. Plant systems functioned properly following the trip, with the exception of 32 reactor coolant pump, which tripped during 6.9KV transfer from onsite to offsite power. The cause of the loss of circulating water pumps was a fault in a non-safety-related transformer. Following repairs, the unit was returned to service on December 28, 1990.
286 | 2861991004 | 1991-03-20 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On March 20, 1991 with the reactor at 100 percent power, a unit trip was initiated as the result of an electrical fault on a 345 KV bus section, remote to the site. The fault isolation circuitry opened both generator output breakers and generated a plant trip via the generator lockout relays. The components affected were subsequently repaired and tested. The plant returned to service on March 22, 1991.
286 | 2861991005 | 1991-03-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 3 | P | WE | PO | 25 | On March 22, 1991, with the reactor at 25 percent power, a unit trip was initiated as the result of a steam generator low-low level trip. All plant systems functioned properly following the trip. The cause of this event was determined to be cyclic fatigue failure of the locking pin on the 31 main boiler feed pump check valve. The discharge check valves on both main feed pumps were overhauled and retested.
286 | 2861992013 | 1992-09-03 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Indian Point 3 | P | WE | SU | 1 | On September 3, 1992 Indian Point Unit 3 was in hot standby at approximately 1 percent power after making balance moves on the main turbine generator. Steam generator levels were being manually maintained via 31 Main Boiler Feed Pump and the low flow bypass valves. Personnel error by the licensed operators resulted in the 34 steam generator level decreasing to the low level trip setpoint. The reactor tripped on 34 steam generator low level at 1817 hours. All control rods fully inserted and all systems functioned as required. Steam generator levels were returned to the normal band using auxiliary feedwater.
286 | 2861992015 | 1992-09-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 3 | P | WE | PO | 63 | On September 15, 1992, the reactor automatically tripped from 63% power on 'Steam Generator #34 mismatch,' an anticipatory low steam generator level reactor trip. The trip was caused by two independent instrumentation/control failures on the same steam generator. The root causes were that implementation of corrective action from a prior event had not been completed and the conservative placement of a protection channel in the fail-safe mode as directed by plant procedures. Corrective action includes the establishment of a refurbishment program which will replace or refurbish the steam generator level controllers. A testing laboratory concluded that the failure of the capacitor, used in the low level bistable, was due to an internal fabrication defect. The plant was returned to service on October 12, 1992.
286 | 2861995012 | 1995-06-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 3 | P | WE | PO | 12 | On June 29, 1995, with reactor power at 12%, turbine load at approximately 50 MW, and feedwater pump control in automatic, the reactor operator observed that levels in the steam generators were 'decreasing as a result of decreasing feedwater flow. The operator changed the feedwater controller to manual and attempted to increase feedwater pump output with the feedwater pump controller but it failed to respond. A manual reactor trip was initiated in anticipation of receiving an automatic trip. The reactor trip and auxiliary feedwater systems functioned as required. The cause was rust-clogged orifice screen filters of the feedwater pump turbine control oil system due to inadequate guidelines in the equipment layup procedure. The control system oil was flushed, screen filters cleaned and replaced, and the oil sampled and analyzed. Orifice screen filter differential pressure alarm switches were calibrated to vendor recommendations.
286 | 2861995018 | 1995-09-14 | QR6 | Manual Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 54 | On September 14, 1995, at approximately 1938 hours, during a unit shutdown to repair a hydrogen leak on hydrogen cooler 32 of the main generator hydrogen cooling system, reactor operators initiated a manual reactor trip from approximately 54.4% reactor power. The trip was initiated in response to a generator stator high differential temperature alarm on the main generator system. All safeguards equipment responded as expected. The high generator stator differential temperature was caused by a reduction in service water cooling flow through hydrogen cooler 32 as a result of gas binding due to hydrogen gas leakage into the tubes of the heat exchanger. Corrective actions include repair and inspections of the hydrogen coolers, evaluation of heat exchanger preventive maintenance program to ensure adequate inspections are being performed, review and assessment of eddy current test results and development of a report on the causes and corrective actions to prevent recurrence, and determination of whether any actions for a leaking cooler should be proceduralized. This event did not affect the health and safety of the public.
286 | 2861996009 | 1996-04-02 | QR6 | Manual Reactor Trip | [45 empty] | Indian Point 3 | P | WE | SU | 13 | On April 2, 1996, with the plant in startup, reactor operators initiated a manual reactor trip from approximately 13 percent power. The trip was initiated in response to a generator stator high differential temperature alarm for the main turbine generator (MTG). Primary systems functioned properly. The high generator stator differential temperature was caused by a reduction in service water cooling flow through the 33 hydrogen cooler of the main generator. The reduction of cooling flow was due to gas binding in the cooling system's high point, and inadequate balance of the cooling water flow between the four coolers. Corrective actions included venting and flow balancing the coolers; revision of the MTG system operating procedure and Alarm Response Procedure for temperature balancing and venting of the coolers, setpoints, trip criteria, applicability of alarm, guidance on operation of the MTG Data Logger; trained Operators in the use of the MTG Datalogger. This event had no effect on the health and safety of the public.
286 | 2861997005 | 1997-05-14 | QR6 | Manual Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 74 | On May 14, 1997, with the plant at approximately 74%, reactor operators initiated a manual reactor trip in response to a turbine runback. The runback was due to an Overpower Delta-T Channel Signal in one of the four loops. Control Room indications did not indicate that the setpoint was exceeded, but the bistable alarm light was illuminated. The plant was stabilized at hot shutdown and subsequent decisions were made to proceed to cold shutdown for early commencement of a scheduled refueling outage. All safety related and major plant equipment involved in the trip operated as expected. Operators and plant personnel responded in an appropriate manner using conservative decision making, good communication and direction, and proper procedure adherence. Corrective actions included the performance of a post trip evaluation in accordance Administrative Procedures. I&C Engineering is performing an Equipment Failure Evaluation (EFE) to determine the actual cause of the overpower delta-T runback signal. This event did not affect the health and safety of the public.
286 | 2861997024 | 1997-09-10 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | SU | 7 | On September 10, 1997, with the reactor power at approximately 7 percent, a reactor trip (RT) occurred as a result of a turbine trip (TT) during a turbine generator (TG) trip test. During performance of a TG test, operators closed the switch stabs to the TT solenoids with the TT relays in the tripped condition. This operation re-instated the trips into the TT logic and initiated a TT. Reactor power (RP) was below the permissive P-10 actuation level and permissive P-7 was active. Operators knew that prior to the test one of the two inputs for the trip logic for actuating P-10 was active [Power Range (PR) channel]. The P-7 permissive includes a bypass of the TT signal to the reactor protection system which is activated with input from P-10. A RT occurred because another PR channel actuated and made up the trip logic, thereby defeating the P-7 bypass. The cause of the RT was an error in the test procedure which did not require the TT relays to be reset prior to reinstating these trips into the TT logic, and failure of operators to detect a change in permissive status (P-10/P-7 reset). The procedure error was introduced as a result of inadequate review of changes incorporated into the procedure. A contributing cause was failure to perform self checking during procedure use. Corrective actions include revision of the test procedure, verified operability and calibration of permissive bistables and indicators, review and validation of recently revised operating tests/procedures needed to be performed for startup which may cause a transient, and briefed the operating crew on STAR principles. An analysis will be performed on cause of the procedure and operator error. There was no effect on public health and safety.
286 | 2861997025 | 1997-09-15 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 30 | On September 15, 1997 the plant was operating at approximately thirty percent reactor power. At 1623 hours, the plant experienced an inadvertent automatic reactor trip when the logic for two out of four channels for low pressurizer pressure was completed. One channel was placed in trip as per procedure in order perform instrument channel testing in accordance with Technical Specifications. At that time, the logic relay for another channel was already effectively tripped due to a high resistance contact causing an insufficient voltage being applied to the corresponding reactor trip relay. After the trip, the relay with the high resistance contact was replaced. Voltage drops across contacts on reactor protection relays were measured, relay contacts were cleaned and found to be acceptable. Review of the plant trip identified that other protective equipment responded as designed after the trip. Corrective action to preclude future similar events will be developed by engineering to include a preventative maintenance program for reactor protective relays. The event had no affect on the health and safety of the public.
286 | 2861998006 | 1998-08-30 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On August 30, 1998, with reactor power at 100 percent, an inadvertent automatic reactor trip occurred. The trip occurred during testing, when the logic for two out of three channels of high pressurizer level initiated a trip signal. In accordance with the surveillance test procedure, one channel of pressurizer high level was placed in trip in order to perform instrument channel testing per the Technical Specifications. At that time, an undetected logic relay contact for another channel was in the tripped condition. When the two out of three logic for trip was made up, a reactor trip was initiated. Subsequent to the reactor trip a high pressure (HP) condenser steam dump valve stuck open. Operators closed the main steam isolation valves to stop steam flow. The cause of the trip was a high resistance contact of a relay in the Reactor Protection System logic matrix for channel II of high pressurizer level. Corrective actions included replacement of relays in train B channels I and II, and in train A, channel II associated with pressurizer high level, and isolation of the HP condenser steam dump valve. A failure analysis will be performed on suspected relays, a modification is being developed to allow trip by-pass, and surveillance testing will be assessed for revision. The event had no effect on public health and safety.
286 | 2861999003 | 1999-03-09 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On March 9, 1999, an automatic reactor trip (RT) occurred after Instrumentation and Control personnel completed installation of a temporary modification (TM). The TM was installed downstream of the normally closed low pressure side blowdown line isolation valve for Reactor Coolant System (RCS) flow transmitter FT-436. FT-436 is one of three differential pressure transmitters on RCS loop 3. To implement the TM the transmitter's low pressure supply side isolation valve (ISV) was closed (and the bistable placed in trip) then opened to return the transmitter to service. Upon opening, a RT occurred and auxiliary feedwater actuated. The plant was stabilized in the hot shutdown condition. The direct cause of the RT was due to satisfying the reactor protection system (RPS) logic of two out of three RCS low flow in a single loop. The RPS logic was satisfied because the bistable for FT-436 was in the tripped condition and the bistable for FT-435 actuated due to a pressure oscillation in the common high pressure side transmitter sensing line. The oscillation, caused by unisolating FT-436, was sufficient to actuate (trip) the low flow bistable for FT-435. The root cause was inadequate planning and change management for the TM, due to a failure to assess the risks, consequences and system interactions associated with the TM. A contributing cause was the sensitivity of FT-435. Corrective actions included an inspection of like valves to confirm leak tightness, installation of a TM on FT-435, evaluation of the TM procedure for adequacy in addressing plant mode and system interactions, and a procedure revision to prevent work on RCS FTs above P-8. FT-435 and FT blowdown valves not previously replaced will be replaced, and an Operating Experience report was issued. The event had no effect on public health and safety.
286 | 2861999010 | 1999-08-12 | P1 | Total Loss of Feedwater Flow |  |  | X | [10 empty] | X |  |  |  |  | X | [25 empty] | X | Indian Point 3 | P | WE | PO | 100 | On August 12, 1999, with the reactor at 100% power, an automatic reactor trip (RT) occurred. The RT occurred after a component failure of the 34 Static Inverter caused a loss of the 34 Instrument Bus (IB). With the loss of the 34 IB, a low low level occurred on the 33 Steam Generator (S/G). This low low level on 33 S/G was due to the plant's response to an IB failure. This satisfied the Reactor Protection System (RPS) logic of two out of three low low level signals on any one S/G causing the RT. The plant was stabilized in hot shutdown condition and the transient was terminated. Safe Shutdown systems responded as required. The cause of the 34 Instrument Bus (IB) failure was a failed power resistor in the 34 Static Inverter which prevented the Static Inverter from providing proper output to the IB. Significant corrective actions include performing a Failure Analysis on the failed power resistor, replacement of the failed power resistor and other Static Inverter components which failed as a result of the resistor, and evaluating the need for adding an Automatic Bus Transfer system to the 34 Static Inverter. This event qualifies as an unplanned reactor scram with the loss of normal heat removal, but was not a safety system functional failure in accordance with the guidelines of NEI 99-02. This event had no effect on the public health and safety.
286 | 2862000007 | 2000-06-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 3 | P | WE | PO | 22 | On June 4, 2000, an automatic reactor trip (RT) occurred during plant startup with the main turbine generator tied to the grid and reactor power being raised to 30%. At approximately 22% reactor power, control of feedwater (FW) to the steam generators (SG) was being transferred from bypass feedwater flow to main FW flow by manually adjusting FW regulating valves (FRV). When adjustment to main boiler FW pump speed was made by a licensed operator, FW flow increased and the level in the 33 SG reached the high-high, level setpoint initiating a turbine trip (TT). The TT caused a rapid decrease in SG water level due to shrink. When the 31 SG reached the low-low level setpoint an automatic RT was initiated. Required equipment functioned as designed. The power operated relief valves (PORVs) and pressurizer safety valves did not lift due to the transient. Auxiliary feedwater actuated per design as a result of the RT. The plant was stabilized in the hot shutdown condition. The RT was caused by a cognitive personnel error by a licensed operator who failed to adequately control FIR pump speed during direction of an operator trainee who was controlling FRVs. Significant corrective actions taken include removal of responsible licensed operators from shift duty, preparation of an action plan for assessment of operations personnel performance and identification of improvements/recommendations. The event had no effect on public health and safety.
286 | 2862000008 | 2000-06-09 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On June 9, 2000 an automatic reactor trip (RT) occurred. The RT occurred as a result of a main turbine trip with reactor power greater than the P-8 permissive set point. The main turbine trip was caused by a main generator trip initiated by the electrical protective relaying direct trip circuitry from the offsite 345 KV Buchanan Substation. This direct trip circuitry actuated the main generator primary and backup lockout (86P and 86 BU) relays. All primary and secondary plant systems responded as required after the automatic RT. Station offsite power was maintained throughout the event and there was no automatic start of the Emergency Diesel Generators. The Auxiliary Feedwater system automatically started after this RT due to a low-low Steam Generator (S/G) level resulting from the SIG water level "shrink." The most probable cause of the direct trip circuitry actuation was a low insulation resistance between several conductors in a cable routed between Indian Point 3 (IP3) and the Buchanan Substation 345 KV South Ring Bus Control House. Corrective actions include disconnecting the faulted conductors and wiring in spare conductors and testing the direct trip circuitry for acceptable functionality. This event had no impact on the public health and safety.
286 | 2862002003 | 2002-11-15 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On November 15, 2002, during full power operation, an automatic reactor trip (RT) occurred. The RT occurred due to the actuation of the reactor protection system (RPS), which was caused by a main turbine trip that was the result of actuation of the main generator primary and backup lockout relays. The main generator trip actuation was caused by the actuation of the electrical protective relaying direct trip circuitry from the 345 KV main output breakers. The 345 KV main output breaker No. 3 faulted open resulting in a trip signal to breakers Nos. 1, 3, and 6 which opened. Breaker 5 had opened prior to the event for unknown reasons. The protection associated with the breakers actuated the lockout relays. Station offsite power was maintained throughout the event. There was no automatic start of the Emergency Diesel Generators. The Auxiliary Feed Water pumps automatically started. The cause of the event was a RT actuation due to a failure of 345 KV main output breaker No. 3. The breaker No. 3 failure was due to high contact resistance caused by misalignment from poor vendor workmanship. Corrective actions include assessment of the output breakers, maintenance and testing of output breaker No. 1, verification that breaker No. 1 is capable of supporting 100% power, and implementation of a monitoring plan for breaker No. 1. Output breaker 3 was inspected, repaired and returned to service. The procedure for breaker maintenance will be revised. The event had no effect on public health and safety.
286 | 2862003001 | 2003-01-13 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On January 13, Operations manually tripped the reactor in accordance with Off Normal Operating Procedure ONOP-C-1 due to high differential pressure (dp) between sections of the main condenser. The high dp was due to a loss of circulating water in one condenser section as a result of the trip of the 35 circulating water pump (CWP) while the 36 CWP was tagged out of service for planned maintenance. All control rods fully inserted. The plant was stabilized in hot standby with decay heat being removed by the main condenser. Offsite power remained available and the emergency diesel generators did not start. The auxiliary feed water (AFW) system automatically started. The cause of the event was a high dp between condenser sections. The apparent cause of the 35 CWP trip was a failure of the positive DC exciter lead terminal lug that connects the exciter rotor to the main rotor of the pump motor. The failure was a result of the lead rubbing against the motor dust cover due to improper cable position during a previous maintenance activity. Corrective actions included troubleshooting and repair of the 35 CWP, testing and repair of the CWP Standby drive, and return to service of the 36 CWP. A discussion of the event and management expectations on human performance was communicated to the maintenance department and site population. Maintenance procedure MTR-004-CWP was revised to provide a caution regarding motor exciter leads and assembly details. Procedure PMP-052-CWS will be revised to include a requirement to open and inspect CWP motors brought on site from a vendor. The event had no effect on public health and safety.
286 | 2862003002 | 2003-04-29 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | Indian Point 3 | P | WE | PO | 59 | On April 29, 2003, during power ascension from refueling outage 3R12, the reactor was manually tripped due to a fire at the south end of the high-pressure turbine located at 53 ft. elevation of the Turbine Building. The fire was caused by the heat of the turbine casing igniting turbine lubricating oil that had leaked and soaked several of the high-pressure turbine insulating pads. The oil leak was from an improperly installed oil deflector for turbine bearing no. 2 during refueling outage 3R12. A Notice of Unusual Event (NUE) was declared at 0313 hours due to the fire exceeding 15 minutes. The fire was extinguished in approximately 15 minutes and declared out approximately 30 minutes later following verification of no reflash. The NUE was terminated at 0521 hours. Fire fighting foam and the C02 system were used to put the fire out. No damage to any equipment or personal injury occurred and no Engineered Safety Feature actuation was required as a result of the manual reactor trip. As immediate corrective actions, the oil deflector was repaired and the oil soaked insulation pads were replaced with new pads. The event had no effect on public health and safety. This event was entered into the Entergy Corrective Action Program under CR-IP3-2003-2795.
286 | 2862003003 | 2003-06-22 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On June 22, 2003, at approximately 1742 hours, following completion of maintenance activities on the 345kV Buchanan distribution system {FK}, Indian Point Unit 3 experienced an automatic turbine / reactor trip event {JE}. Prior to this event, Indian Point Unit 3 was in Mode 1, operating at 100 percent, steady-state power conditions. Generator output breaker No. 3 had been opened earlier at approximately 1654 hours to support maintenance activities on 345kV offsite feeder W-98 {FDR}. Indian Point Unit 3 remained in service utilizing generator output breaker No. 1. While attempting to close breaker No. 3, a fault occurred which resulted in the tripping of both generator output breakers No. 1 and 3. The cause for this event was attributed to a ground fault on Phase B of generator output breaker No. 3 {EL}. Control room personnel immediately entered Emergency Operating Procedure (EOP) E-0, "Reactor Trip or Safety Injection" to initiate plant recovery. No radiological releases or adverse safety implications to the public occurred as a result of this event. In accordance with 10 CFR 50.72(b)(2)(iv)(B), the NRC was notified (Event Number 39955) of this event at 2118 hours on June 22, 2003. This report is submitted pursuant to 10 CFR 50.73 (a) (2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of the reactor protection system.
286 | 2862003005 | 2003-08-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Indian Point 3 | P | WE | PO | 100 | On August 14, 2003, at approximately 1611 hours, during 100% steady state power, Indian Point Unit 3 experienced an automatic reactor trip initiated as a result of low reactor coolant loop flow due to the trip of the 34 Reactor Coolant Pump (RCP) breaker. The 34 RCP breaker tripped due to electrical supply bus under-frequency caused by an unstable off-site power grid (Northeast blackout). Off-site power was lost and all three Emergency Diesel Generators started and energized their assigned safety buses. Main feedwater isolated and the Auxiliary Feedwater (AFW) pumps automatically started. A Notification of Unusual Event (NUE) was declared at 1623 hours, in accordance with the Emergency Plan when off-site power was unavailable for greater than 15 minutes. The NUE was terminated on August 15, at 0210 hours, when off-site power was restored. The cause of the event was a loss of off-site power due to an unstable power grid. Corrective actions to address the cause of the event included a post trip review, root cause evaluation and plant assessment. There were no nuclear safety concerns exhibited during the event and all fission product barriers remained intact. There was no impact on the health and safety of the general public.
286 | 2862005002 | 2005-05-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On May 6, 2005, at approximately 10:32 hours, an automatic reactor trip was initiated due to a 32 steam generator (SG) steam flow/feedwater flow mismatch with low SG level trip during Instrumentation & Control (I&C) troubleshooting of the condensate system(CS). All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary FW system automatically started as expected due to a SG low level. The cause of the event was personnel error due to poor work practices during troubleshooting of the CS. The control switch for the condensate polisher (CP) post filter bypass valve was in auto when a wire was disconnected from a relay of a seal-in circuit causing the post filter bypass valve to close. The post filter bypass valve closure caused inadequate feedwater flow that resulted in the mismatch and low SG level. Operations and I&C personnel failed to verify and recognize the required switch position for the condition due to overconfidence. Corrective actions include counseling operations and I&C personnel and applicable plant staff on management expectations for a questioning attitude, pre-job briefs, peer checking; and use of the formal work process. The CP system operating procedure was revised for proper CP valve control switch position and seal-in circuit clearance. The work control procedure will be revised to define when work becomes troubleshooting and decide the level of risk assessment to be performed. The event had no effect on public health and safety.
286 | 2862005004 | 2005-06-10 | QR6 | Manual Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On June 10, 2005, at approximately 0924 hours, operations initiated a manual reactor trip following discovery of service water (SW) leakage inside the main generator exciter enclosure. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by theming condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator shrink effect. The cause of the leakage was a split gasket on the 32B exciter cooler due to over tightened heat exchanger head bolting. The root cause of the condition was the level and extent of training associated with resilient gasketed joint installation which does not encompass the effects of an improper tightening sequence encountered during the return to service test phase. Corrective actions included repair/replacement of applicable exciter cooler gaskets, leak inspections, counseling maintenance personnel on management's expectation on questioning attitude, self checking, use of the formal work process, and workmanship quality. Applicable heat exchanger maintenance procedures and training program will be reviewed and revised as necessary for proper gasket application/material and proper cooler bolt torque values and sequencing. The event had no effect on public health and safety.
286 | 2862006001 | 2006-07-06 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On July 6, 2006, at 0352 hours an automatic reactor trip (RT) occurred as a result of a short circuit that occurred in the junction box of the Main Generator output phase "B" differential protection current transformer (CT). The plant responded to the trip as designed. The Auxiliary Feed Water System (AFW) actuated and the AFW Pumps started as designed due to the Steam Generator (SG) shrink caused by the trip from 100% power. All plant systems operated normally with the exception 31 Main Boiler Feed Pump Recirculation Valve did not open due to a failed solenoid and the 32 Main Steam Line Trap was isolated due to having a minor steam leak. The root cause of this condition was determined to be design inadequacy in material application. The abrasive property of the conductors insulation jacket was not evaluated for use in a continuous vibration environment. Corrective actions included repair of damaged cables, coaching of personnel on the lessons learned, process/procedure revisions to improve the considerations on material selection in the design process and training enhancements to address material considerations. This event had no effect on public health and safety.
286 | 2862006002 | 2006-07-21 | QR6 | Manual Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On July 21, 2006, at 1031 hours, Operations initiated a manual reactor trip (RT) as a result of observing arcing under the main turbine generator (MTG) between scaffolding and Phase A&B of the Iso-phase bus housing. All control rods fully inserted and all primary systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater (AFW) system automatically started as expected due to a low steam generator (SIG) level. The direct cause of the RT was due to arcing between metal scaffolding contacting two phases (A&B) of the Iso-phase bus housing. The root cause was latent Organizational/Programmatic weakness. There was insufficient awareness across the organization regarding the potential impact of leaving or removing conductive materials in close proximity to the MTG Iso-phase bus housing while the unit is in operation. Scaffolding left in place from a previous shutdown inadvertently came in contact with the MTG Iso-phase bus enclosure during scaffold disassembly. The operational risk of this condition was not adequately assessed. The scaffold procedure has no specification for addressing clearances for electrical safety hazards related to electromagnetic flux concerns. Corrective actions include coaching personnel on the event and lessons learned, preparation of an improved method in the work control process for screening operational risks, and revision of the scaffold procedure to include clearance criteria and precautions. The event had no effect on public health and safety.
286 | 2862007001 | 2007-04-03 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Indian Point 3 | P | WE | PO | 53 | On April 3, 2007, with the 31 Main Boiler Feedwater Pump (MBFP) shutdown, the 31 MBFPcontrol circuit was de-energized in preparation for maintenance, when unexpectedly the logic control circuit for the 32 MBFP was lost resulting in loss of feedwater (FW)flow. Control room operators manually initiated a reactor trip (RT) at approximately 0417 hours, after observing rapidly decreasing steam generator (SG) levels. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat initially being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink effect.The cause of the RT was decreasing SG levels due to loss of 32 MBFP FW control as a result of the failure of the 32 MBFP Train A Lovejoy control logic power supply when the 31 MBFP instrument bus power supply was isolated. The 32 MBFP Train A control logic power supply failure was due to a bad pin connection on the power supply voltage regulator. The root cause was a failure of an auctioneered power supply that was not self revealing and was undetectable until it was required to carry load. Significant corrective actions include replacement of 32 MBFP Train A control logic power supply, establishment of a the 10 year Preventive Maintenance (PM) to replace all power supplies in the Lovejoy system, performance of an assessment for identification of other auctioneered power supplies and verification that PMs confirm that the power supplies can carry their load. The event had no effect on public health and safety.
286 | 2862007002 | 2007-04-06 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Indian Point 3 | P | WE | PO | 92 | On April 6, 2007, at 1109 hours, an automatic reactor trip (RT) occurred due to a turbine-generator trip as a result of a fault on the 31 main transformer. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as adequate offsite power remained available. Two of three 138 kV offsite power substation feeder stripped as a result of the event. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink effect. Control Room (CR) operators were notified of a fire at the 31 main transformer with the fire protection deluge system actuated. The plant fire brigade responded to the fire and applied foam.The fire brigade leader reported to the CR the fire was extinguished at 1121 hours.The CR was notified at approximately 1140 hours that a visible explosion had previously occurred. Based on the report of an explosion, the CR declared a Notice of Unusual Event (NUE) in accordance with the emergency plan which was terminated at 1254 hours.The direct cause of the RT was due to the actuation of the 86P and 86BU relays that sensed a fault from the failure of 31 main transformer 345 kV phase B bushing. The most probable cause was a design weakness associated with the type bushing used in the Phase B bushing. Significant corrective actions included replacement of 31 main transformer, and inspection, repair and replacement of damaged components as required associated with the 32 main transformer, the unit auxiliary transformer, and high voltage components. The event had no effect on public health and safety.
286 | 2862009003 | 2009-05-15 | QR6 | Manual Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On May 15; 2009, Control Room operators initiated a manual reactor trip for high steam generator (SG) 33 water level which could not be corrected due to a failed open 33 main feedwater (FW) regulating valve (FCV-437) . All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main. condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. In response to the event main FW isolated and the Auxiliary Feedwater System automatically started. The direct cause of the high SG level was the positioner feedback linkage on FCV-437 became disconnected causing the valve to open. The cause of the positioner feedback link disconnection was inadequate procedure direction and written instructions. The valve maintenance procedure did not contain steps to "perform wrench tightness of the rod jam nuts after positioner linkage was disconnected, and then reconnected during valve overhaul. There were also no steps in the diagnostic test procedure that directed workers to verify wrench tightness of the jam nuts. A contributing cause was ineffective use of Human Performance (HP) tools. Corrective actions included repair of the valve positioner linkage and verification of other position linkage assemblies. The valve Overhaul. procedure and diagnostics procedure will be revised to ensure direction to wrench tighten jam nuts and verify installation of lock washers on jam nuts, wrench tighten connection of linkage to the valve yoke and positioner, wrench tighten connection of the turnbuckle to yoke and verify mifiimum thread engagement of the rod to turnbuckle. The event had no effect on public health and safety.
286 | 2862009004 | 2009-05-28 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 61 | On May 28, 2009, the Control Room received 32 MBFP vibration alarms and reduced power to approximately 65% and removed the 32 MBFP from service. The 31 MBFP was unable to supply sufficient feedwater (FW) flow to maintain Steam Generator (SG) levels which resulted in all four main FW regulating valves (FRV) opening. SG-31, 33, 34 water levels recovered but the SG-32 water level increased and continued increasing after the 32 FRV was placed in manual. The 32 SG level reached the high level trip initiating a turbine trip that resulted in a reactor trip (RT) All required safety systems functioned properly including the Auxiliary Feedwater System which automatically started as expected. The root causes for the RT were 1) Ineffective problem solving, and 2) Poor vendor oversight. Contributing causes included 1) an inadequate procedure, 2) procedure adherence, 3) low FW flow in the 32 MBFP feed line and FRV controller short reset time, 4) Ineffective corrective actions. Significant corrective actions included: adjustment of the 31 MBFP governor, trained engineering personnel on Kepner-Tregoe problem solving technique, coached Maintenance personnel on requirements for contractor oversight and included the event in maintenance training, revised procedure 0-TUR-402-MFW to require stroke measurement of governor valves and linkage clearance check, new SG Water Level Controller settings under evaluation for implementation, Maintenance, Operations, Engineering and Outage Management were briefed on the root cause and lessons learned, and Maintenance and Engineering were briefed on expectations for effective problem solving. The event had no effect on public health and safety.
286 | 2862009006 | 2009-08-10 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On August 10, 2009, during a severe thunderstorm, the Control Room received indication of a Turbine Trip and Reactor Trip initiated by the Generator Primary Lockout Relay (86P). All control rods fully inserted and all required safety systems functioned properly. 6.9 kV Bus 2 failed to auto transfer to 6.9 kV bus 5 resulting in the trip of the 34 Reactor Coolant Pump and de-energization of 480 volt safeguards Bus 2A. Emergency Diesel Generator (EDG) 31 automatically started and re-energized 480 volt bus 2A. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. EDG-32 and 33 remained in standby as offsite power remained available. The Auxiliary Feedwater (AFW) System automatically started as expected due to Steam Generator low level from shrink effect. 6.9kV Bus 2 was energized from 6.9 kV bus 5 via closure of 6.9 kV bus 2-5 tie Breaker. The direct cause was actuation of the Generator Primary Lockout Relay (86P) due to misoperation of relay 85L1/345 due to extraneous voltage induced on ground during a lightning strike. The root cause was the 345 kV Primary Pilot Wire System is susceptible to the maximum ground potential rise (GPR) based on the original design. The susceptibility to GPR is due to 1) the calculated worst case GPR is higher than the insulating rating of the pilot wires, 2) The pilot wire system was not provided with equipment to protect against GPR. Corrective actions included inspection of 345 kV output feeder W96, testing of pilot wire cables, calibration and testing of applicable protection system relays. Enhancements will be implemented to the Station Grounding Plan, and the 138 kV and 345 kV pilot wire systems replaced. The event had no effect on public health and safety.
286 | 2862009007 | 2009-08-27 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On August 27, 2009, a Turbine Trip and Reactor Trip were initiated by main turbine control oil Autostop turbine trip. All control rods fully inserted and-all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. No Emergency Diesel Generator actuated as offsite power remained available. The Auxiliary Feedwater (AFW) System automatically started as expected due to Steam Generator low level from shrink effect. The cause of the trip was a loss of Turbine Autostop oil pressure below the trip setpoint due to a failed pipe adaptor fitting on the line connecting the Turbine Autostop oil to the Turbine solenoid trip device. The pipe adaptor fitting failed due to high cyclic fatigue caused by the improper installation of the Autostop,oil line fitting in the Turbine pedestal bulkhead wall. The cause of the event was the as-found configuration did not meet the Original Equipment Manufacturer (OEM) design expectation. This condition resulted in a configuration where the threaded fitting bottoms out in the threaded hole which induced additional stress on the fitting threads. The additional stress combined with normal stress caused a premature failure. Corrective actions included replacement of the failed fitting, inspection of Autostop oil lines, and monitoring vibrations on turbine bearing No. 1. An engineering change will be developed to redesign the turbine pedestal piping wall penetration for the autostop oil turbine protection solenoid valve. The event had no effect on public health and safety.
286 | 2862010002 | 2010-09-09 | QR6 | Manual Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On September 9, 2010, during full power operations, a water leak in the main generator exciter housing was observed by an operator during rounds and the condition reported to the control room. Operations initiated closure of the Exciter heat exchanger inlet cooling water valve (SWT-25-2) in order to isolate the B section of the exciter cooler. Almost immediately the leak worsened confirming that the leak was in the A section of the exciter cooler. Water was observed to be pooling in the Permanent Magnet Generator section of the exciter and a manual reactor trip was initiated. All control rods fully inserted and all required safety systems functioned properly and the plant was stabilized in hot standby. There was no radiation release. No Emergency Diesel Generator actuated as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink effect. The direct cause of the event was a leak in the 31 Exciter Air Cooler due to the failure of an Admiralty Brass tube (S-1-11) from erosion and corrosion. The root cause was component monitoring was less than adequate. The current Eddy Current Testing, Tube Air Pressure Testing, and visual inspection techniques do not effectively identify degradation in the tube sheet area. Corrective actions include: Inspections and testing of both exciter coolers was performed and 194 tube end sleeves were installed in both ends of all unplugged tubes of the 31 and 32 Exciter Air Cooler (tube S-1-11 was plugged and two other tubes had previous plugging), guidance will be developed for inclusion in a procedure for high risk heat exchangers with Admiralty Brass tubes to proactively sleeve tube ends as a mitigation strategy. The event had no effect on public health and safety.
286 | 2862012004 | 2012-10-29 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On October 29, 2012, an automatic reactor trip (RT) was initiated as a result of a main turbine-generator trip due to a trip of the Generator Primary and Backup Lockout relay 86P and 86BU on a direct trip from the Buchanan switchyard. The Buchanan switchyard south ring bus was isolated from output feeder W96 as a result of faults on 345 kV feeders W97 and W98 causing the generator output breakers 1 and 3 to open initiating a direct trip signal from Buchanan. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. The Emergency Diesel Generators did not start as offsite power remained available and stable. The cause of the RT was the trip of generator output breakers 1 and 3 due to isolation of the south ring bus from output feeder W96. Generator output breakers 1 and 3 tripped as a result of a fault on feeders W97 and W98 due to Con Edison 345 kV feeder line insulator damage from the effects of superstorm Sandy. Corrective action was taken to repair 345 kV feeders W97 and W98 by Con Edison. The event had no effect on public health and safety.
286 | 2862014001 | 2014-01-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On January 6, 2014, the 33 Steam Generator (SG) steam flow (SF) Feedwater flow (FF) mismatch and SG level control deviation alarms annuniciated. Operators noticed the selected feedwater (FW) flow (FF) channel at zero and swapped to the alternate channel and noted both FW flow channels at zero. With the 33 SG level at approximately 10% and lowering, operators started actions to initiate a manual reactor trip (RT) when an automatic RT occurred on a SF/FF mismatch coincident with low 33 SG level. All control rods fully inserted and all required safety systems functioned properly with the exception of the intermediate range excore neutron flux detector N-35 which was undercompensated. The plant was stabilized in hot standby with decay heat being removed by the main condenser {SG}. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. The Emergency Diesel Generators did not start as offsite power remained available and stable. Investigations determined the decreasing SG levels were due to reduced main FW flow as a result of a closed 33 Feedwater Regulating Valve (FRV). The closure of the 33 FRV-437 was due to no output from flow controller FC-437. The apparent cause was station personnel failed to apply lateral thinking and teamwork and question what other options were available besides procuring an identical controller. Corrective actions included replacing FC-437 and FC-417. A project to improve procurement and ease replacement of NUS modules will be developed. The event had no effect on public health and safety.
286 | 2862014004 | 2014-08-13 | QR8 | Spurious Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On August 13, 2014, Instrumentation and Control (I&C) technicians started performance of an 8-hour scheduled surveillance 3-PC-OL04A (Pressurizer Pressure Loop P-455 Channel Calibration) with Loop I in test and tripped. The test was approved by I&C and operations to be stopped for a break with the bistables still tripped, Channel I in test. During the break, an automatic reactor trip (RT) occurred as a result of meeting the trip logic for Overtemperature Delta Temperature (OTDT). All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as expected due to SG shrink effect. No work was being performed at the time of the RT and no actual OTDT existed. The direct cause of the RT was a spurious signal spiking on channel 3 of the OTDT circuitry with another channel tripped for testing. The two possible root causes were 1) a random failure of the OTDT static gain unit (Foxboro Integrator/Converter module QM-431D), 2) loose wiring connection on distribution block DB-4 (output of static gain unit QM-431) due to workmanship issue. Corrective actions included replacement of static gain module QM-431D and associated PR N-43 isolation amplifies NM306 and NM307, and static gain modules QM-421D, and QM-411D, replacement of three OPDT trip bistables (TC-421 A/B, TC-431 A/B, TC-441 A/B), replacement of setpoint module TM-432B (other setpoint modules had been previously replaced), and replacement of Loop 3 T(avg) E/I converter TM-432R. Procedure IP-SMM-WM-140 revised to include expectation on minimizing break times when a channel is tripped. The event had no effect on public health and safety.
286 | 2862015004 | 2015-05-09 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On May 9, 2015, an automatic reactor trip (RT) occurred due to a Turbine-Generator trip as a result of a failure of the 31 Main Transformer (MT). All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the condenser. There was no radiation release. The emergency diesel generators did not start as offsite power remained available. The auxiliary feedwater system actuated as expected due to steam generator low level from shrink effects. Control room operators received alarms on the fire detection panel of the activation of the 31 MT and curtain wall deluge valves. Report to operators that there was an explosion and fire on the 31 MT. The plant fire brigade responded to the fire. The 31 MT had failed. Due to collateral influence from the 31 MT failure, the deluge system for the 32 MT and Unit Auxiliary transformer had also activated. In accordance with the emergency plan a Notice of Unusual Event (NUE) was declared at 1801 hours, which was terminated at 21:04 hours. The direct cause was an internal fault of the A Phase high voltage winding in the upper portion of the transformer. The root cause was vendor design/manufacturing deficiency that caused an internal failure that resulted in a fault on the A phase HV side of the transformer and the A phase HV voltage bushing. Key corrective actions included replacement of the 31 MT with a spare transformer, associated acceptance testing, repair of the isophase bus ducting for the 31 MT, inspections, cleaning, testing of the 32 MT, the Unit Auxiliary Transformer, high voltage components, isophase buses and main generator. A 4-year PM was prepared to perform Partial Discharge testing on the Unit 2, and Unit 3 MTs, Unit 2 and Unit 3 Auxiliary Transformers and the Unit 3 GT Auto Transformer. The event had no significant effect on public health and safety.
286 | 2862015005 | 2015-06-15 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On June 15, 2015, an automatic reactor trip (RT) occurred due to a Main Turbine-Generator trip as a result of a direct generator trip from the Buchanan switchyard. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the condenser. There was no radiation release. The emergency diesel generators did not start as offsite power remained available. The auxiliary feedwater system actuated as expected due to steam generator low level from shrink effect. Prior to the RT, Con Edison requested that Main Generator Output breaker 1 be opened to support removing 345kV feeder W97 from service for removal of a Mylar balloon on a 345kV conductor at the Millwood substation. After breaker 1 was opened, Main Generator Output breaker 3 opened initiating a direct generator trip signal due to a fault in South Ring Bus breaker 5. Direct cause of the RT was failure of 345kV breaker 5 due to an internal fault which activated protective relays that opened the remaining Main Generator Output breaker 3 which initiated a trip sequence that resulted in a RT. The root cause was Indian Point Energy Center did not provide formal notification of industry operating experience (OE) to Con Edison owner of breaker 5. The specific OE pertained to ITE Type GA breakers. Corrective actions include replacement of breaker 5. Procedure EN-0E-100 (OE Program) was revised to add a section describing how to initiate formal notification to external groups when OE related to components they own and/or control can affect generation. A new site procedure was issued (SMM-LI-126) to formalize the site process for notifying external groups of OE that can affect generation. The event had no effect on public health and safety.
286 | 2862015007 | 2015-07-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On July 8, 2015, during surveillance testing, the Control Room received a 6.9kV motor trip alarm due to 31 Condensate Pump (CP) Motor circuit breaker trip on overcurrent. . Operators entered Alarm Operating Procedure 3-AOP-FW-1 due to loss of the 31 CP and initiated a load reduction. During this time the Main Boiler Feedwater Pump (MBFP) suction pressure decreased to its suction pressure cutback controller pressure range and its output decreased MBFP speed control to a minimum. The 31 MBFP speed control signal locked in at this minimum speed signal due to actuation of the MBFP Lovejoy speed control system Track and Hold feature. Due to this minimum 31 MBFP condition, the 31 MBFP recirculation valve opened causing the 31 MBFP check valve to close. With the 31 MBFP unloaded, Steam Generator (SG) water levels decreased and at 15 percent operators manually tripped the reactor. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. Direct cause was the 31 MBFP entered a Hold condition erroneously due to a miss-wired Track and Hold board in the speed control system. The root cause was the procurement for the MBFP Lovejoy Track and Hold boards was at an insufficient quality level commensurate with its criticality. There was a failure to mandate functional testing and wiring verification requirements on the vendor to ensure the procurement of a quality product. Corrective actions included replacement of MBFP track and hold board and 31 CP motor. A new replacement Track and Hold circuit board for both the 31 and 32 MBFP speed control system with the miss-wiring corrected was installed. The quality levels for the Track and Hold boards were revised from Q4 to Q3. MBFP Lovejoy speed control maintenance procedures and site vendor manuals were revised to include more detail. The event had no effect on public health and safety.
286 | 2862015008 | 2015-12-14 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On December 14, 2015, an automatic reactor trip (RT) occurred due to a Turbine-Generator trip caused by a fault on 345 kV feeder W96 transmission tower IP3-4. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the condenser. The auxiliary feedwater system actuated as expected due to steam generator low level from shrink effect. Inspections identified that an electrical fault damaged the 345 kV Transmission Tower line insulators. Direct cause of the RT was radial flashover of insulators on C phase of the 345 kV feeder W96 line at Transmission Tower IP3-4. The most likely cause is a pre-existing damaged insulator as a result of a prior flashover event that resulted in a repeat flashover due to environmental conditions. A single event with multiple flashovers associated with reduced insulation resistance due to a bird streamer is possible but less likely. Transmission Tower design does not have barriers to prevent avian perching on feeder towers. Corrective actions included inspection of Transmission Tower line insulators and ancillary hardware and replacement of damaged insulators and hardware. The preventive maintenance (PM) scope for the Unit 2 345 kV and 138 kV feeders was revised to include inspection and cleaning of Transmission Tower line insulators and hardware. An action request was generated to implement PM Template ENN-EP-G-004, Attachment 7.7 and Model Work Orders were revised and thermography and corona camera inspections performed. Bird guards will be installed on Entergy owned 345 kV and 138 kV Transmission Towers to preclude the effects of bird streaming. The event had no effect on public health and safety.
286 | 2862017004 | 2017-11-03 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On November 3, 2017, at 2022 hours, with reactor power at 100 percent, Indian Point Unit 3 experienced an automatic reactor trip on a turbine trip, which was in response to a main generator trip. The main generator trip was initiated by actuation of the Generator Protection System due to a main generator loss of field. <br /><br /> All control rods fully inserted and all required safety systems functioned properly. The Auxiliary Feedwater System (AFWS) automatically started as expected on steam generator low level to provide feedwater flow to the steam generators. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The direct cause of the loss of the main generator field was a failed Thyristor Firing Module drawer in the Automatic Voltage Regulator (AVR) system of the Main Generator Exciter System. The root cause was determined to be an inadequate refurbishment of obsolete power supplies in the AVR system. A plant modification has removed the obsolete power supplies from the design of the AVR system.<br /><br /> This event had no effect on the health and safety of the public. The event was reported to the Nuclear Regulatory Commission (NRC) on November 3, 2017 under 10 CFR 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System when the reactor is critical and a valid actuation of the AFWS.
286 | 2862018001 | 2018-02-16 | QR5 | Turbine Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On February 16, 2018, at 0201 hours, with reactor power at 100 percent, Indian Point Unit 3 experienced an automatic reactor trip on a turbine trip, which was in response to a main generator trip. The main generator trip was initiated by actuation of the Generator Protection System due to a main generator loss of excitation. <br /><br /> All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System (AFWS) automatically started as expected on steam generator low level to provide feedwater flow to the steam generators. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The direct cause of the loss of main generator excitation was the failure of an auctioneering diode (D8) in the Automatic Voltage Regulator Thyristor Firing Module A drawer power supply. The root cause was an improper refurbishment of obsolete Thyristor Firing Module power supplies. Corrective actions included modification of the Automatic Voltage Regulator to replace the obsolete power supplies with a new design, and creation of a Preventive Maintenance (PM) task to periodically replace the new power supplies in accordance with vendor recommendations and the PM Template.<br /><br /> This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission on February 16, 2018 under 10 CFR 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A) as an event that resulted in the automatic actuation of the Reactor Protection System when the reactor is critical and a valid actuation of the AFWS.
286 | 2862018003 | 2018-09-18 | QR6 | Manual Reactor Trip | [45 empty] | Indian Point 3 | P | WE | PO | 100 | On September 18, 2018, with the reactor at 100 percent power, at approximately 0525 hours Operators manually tripped the reactor and shut the Main Steam Isolation Valves due to a steam leak on the 6 inch elbow located upstream of the 36C Feedwater Heater. The steam leak was due to a failure of the 6 inch elbow. The cause of the failure was flow accelerated corrosion which lead to pipe wall thinning and subsequent pipe failure. Ultrasonic testing of the elbow showed flow accelerated corrosion thinning in the failed elbow and also in the adjacent upstream elbow.<br /><br /> This event was reported under 10 CFR 50.72(b)(2)(iv)(B) for any event or condition that results in actuation of the reactor protection system when the reactor is critical. This event was also reportable under 10 CFR 50.72(b)(3)(iv)(A) for any event or condition that results in valid actuation of any of the systems listed in paragraph 10 CFR 50.72(b)(3)(iv)(B). This included actuation of the Auxiliary Feedwater System as expected following manual reactor trip. Following the reactor trip, the plant was stabilized in hot standby with decay heat being removed from the steam generators via the Auxiliary Feedwater System and atmospheric steam dumps. <br /><br /> This event had no effect on the public health and safety.
287 | 2871988006 | 1988-11-14 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 35 | On November 14, 1988, at 0724 hours while operating at 100% full power, the Unit 3 Main Turbine (MT) tripped resulting in an anticipatory reactor trip. An investigation into the incident did not identify the cause of the MT trip. Subsequently, at 1130 hours the same day, permission was received to restart the reactor. At 1737 hours, with the reactor at 39% full power, the MT tripped again initiating a runback in reactor power by the Integrated Control System (ICS). At 1738 bours the Reactor Coolant System pressure reached the trip setpoint and tripped the reactor from 35% full power. The cause of this MT trip was determined to be a partially grounded Once Through Steam Generator (OTSG) High Level Trip Signal Monitor. The immediate corrective action was to stabilize the unit at hot shutdown. The supplemental corrective actions included determining the cause of the unit trip and replacing the faulty signal monitor. The root cause of the initial unit trip could not immediately be determined. The root cause of the second unit trip was a ground fault in the OTSG High Level Trip Signal Monitor.
287 | 2871988006 | 1988-11-14 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | On November 14, 1988, at 0724 hours while operating at 100% full power, the Unit 3 Main Turbine (MT) tripped resulting in an anticipatory reactor trip. An investigation into the incident did not identify the cause of the MT trip. Subsequently, at 1130 hours the same day, permission was received to restart the reactor. At 1737 hours, with the reactor at 39% full power, the MT tripped again initiating a runback in reactor power by the Integrated Control System (ICS). At 1738 bours the Reactor Coolant System pressure reached the trip setpoint and tripped the reactor from 35% full power. The cause of this MT trip was determined to be a partially grounded Once Through Steam Generator (OTSG) High Level Trip Signal Monitor. The immediate corrective action was to stabilize the unit at hot shutdown. The supplemental corrective actions included determining the cause of the unit trip and replacing the faulty signal monitor. The root cause of the initial unit trip could not immediately be determined. The root cause of the second unit trip was a ground fault in the OTSG High Level Trip Signal Monitor.
287 | 2871989002 | 1989-03-06 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | On March 6, 1989 at 0657 hours while operating at 100% Reactor Power, the Unit 3 Main Turbine (MT) tripped, resulting in an anticipatory Reactor trip. The MT trip was initiated by a generator lockout which was due to a loss of generator excitation. The reason for the loss of excitation could not be determined. Additionally, three pipe supports were damaged following the trip as a result of a water hammer in the Main Steam Turbine Bypass line. The immediate corrective action was to stabilize the unit at hot shutdown. Subsequent corrective actions included determining the cause of the trip and implementing a plan for the repair of the three pipe supports. The actual root cause of the trip could not be determined, therefore this event is classified as unknown.
287 | 2871989004 | 1989-08-18 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | On August 18, 1989, at 1233 hours, Oconee Unit 3 tripped from 100% full power. The reactor trip was an anticipatory trip resulting from a false Eletrohydraulic Control (EHC) System low hydraulic pressure trip signal. The false signal was generated when water drops made momentary contract across the terminal strip associated with the low hydraulic pressure trip had washed the floor around the EHC hydraulic power unit cabinet prior to the unit trip. The cabinet door was inadequately shut, potentially allowing moisture to enter the hydraulic power unit cabinet. Plant response to the trip was normal with no radiological releases or Engineered Safeguard actuations. The root cause of this incident is classified as an Inappropriate Action, poor work practice. Immediate corrective actions were stabilize the unit at hot shutdown conditions.
287 | 2871990001 | 1990-01-19 | QR3 | Reactivity Control Imbalance | [45 empty] | Oconee 3 | P | BW | PO | 100 | On January 19, 1990, Unit 3 tripped from 49% Full Power (FP) at 0849 hours following a rapid reduction in power from 100% FP after Control Rod Group 6 dropped into the core. A test was in progress at the time to verify proper operation of the control rod power supplies. During the testing of Group 6, a switch failure prevented the transfer from normal to auxiliary power supplies. Later technician actions resulted in a loss of magnetic field in the Group 6 control rod drive (CRD) mechanism stators and subsequent Group 6 rod drop. Operators realized that the rod group had dropped, but were not able to manually trip the reactor before the Reactor Protective System automatically tripped the unit on low Reactor Coolant System pressure. The unit was stabilized at hot shutdown conditions. An immediate trip investigation was initiated, but it did not discover the root cause of the event. A failure of the CRD transfer switch for Rod 6 of Group 6 occurred during a subsequent refueling outage and was recognized as the most likely cause of this event. A Unit 3 trip occurred on June 9, 1991 due to a failure of Group 5 rods. It now appears that a similar failure occurred on the transfer switch of Rod 6 Group 6 to produce the Group 6 rod drop of this report. The root cause of the June 9, 1991 trip and the event of this report is classified as equipment malfunction of Electro Switch model 87907S transfer switches. The major corrective actions were to replace the switch, provide more instructions in procedures, and investigate means to provide indication of CRD power supply transfer failures.
287 | 2871990002 | 1990-03-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Oconee 3 | P | BW | PO | 100 | At 1406 hours on March 7, 1990, Oconee Unit 3 experienced a Reactor Trip from 100% Full Power due to high Reactor Coolant System (RCS) pressure. A valve limit switch linkage arm had become disconnected, probably due to vibration during start-up, causing a closed indication which satisfied part of the control logic for automatic closure of a feedwater block valve. The rest of the logic was satisfied when a routine test supplied a low reactor power input to the control logic. The block valve closed, resulting in a partial loss of feedwater and, subsequently the Reactor Protective System tripped on high RCS pressure. Trip response was normal except that one Control Rod Drive Breaker exceeded its expected trip time and was replaced. The limit switch linkage was reconnected and the unit was restarted. The root cause is identified as equipment failure.
287 | 2871990003 | 1990-11-13 | QR3 | Reactivity Control Imbalance | [45 empty] | Oconee 3 | P | BW | PO | 100 | On November 13, 1990, at approximately 2256 hours, while at 100% Full Power, Oconee Unit 3 Control Rod Group 7 dropped into the core. From control room indicators Operations personnel recognized that the rod group had dropped and were able to trip the reactor from 60% Full Power before the Reactor Protective System could automatically trip the reactor on Low Reactor Coolant System Pressure. The post trip response was normal. Investigation of the dropped Control Rod Group revealed a failed Solid State Programmer, which controls power to the Control Rod Drive Stators. The programmer was replaced and the Unit was returned to critical at 0433 hours on November 14, 1990. The root cause of this event is identified as Equipment Failure.
287 | 2871991005 | 1991-04-01 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 3 | P | BW | PO | 87 | On April 1, 1991, at 0415 hours, one channel of the Unit 3 Diverse Scram System (DSS), an Anticipated Transient Without Scram (ATWS) mitigation system, spuriously actuated and both channels were bypassed. After some troubleshooting verified the input instrument was not at fault., the Operations Unit Supervisor attempted to return both channels to service, while the unit was operating at 87% Full Power. As he did so, at 1119 hours, spurious signals actuated both channels, resulting in three groups of control rods automatically dropping into the core. Per procedure, the control room operator manually tripped the reactor in response to the dropped rods. The trip response was normal and the unit was stabilized, with no safety system actuations either required or received. Troubleshooting discovered that one channel had actuated due to Equipment Failure of a bad circuit board (contributing cause) and the second actuated due to a Design Deficiency (root cause) which generated a high signal spike in the second channel when returning the first channel to service. A second root cause of Deficient Procedure was assigned due to less than adequate steps to reset the system. Corrective actions included replacing the bad circuit board, modifying the system, and enhancing procedures.
287 | 2871991006 | 1991-06-09 | QR3 | Reactivity Control Imbalance | [45 empty] | Oconee 3 | P | BW | PO | 100 | On June 9, 1991, with unit 3 at 100 percent full power, a Control Rod Drive (CRD) system verification test required by Technical Specifications was being performed. At 1506 hours, after transferring a single control rod in Group 5 to its auxiliary power supply, the entire rod group fell into the core. Reactor power dropped to approximately 30 percent full power prior to a reactor trip three seconds later on low pressure/temperature ratio. The plant post-trip response was normal. The unit was stabilized at hot shutdown conditions. The root cause of the event was found to be equipment malfunction: a failed transfer switch allowed the normal and alternate CRD power supplies to simultaneously energize the Group 5 CRD mechanisms. The failed transfer switch was replaced. Further investigations are centered around the history of the transfer switch, methods to prevent its failure, and methods to give the operator indication when power supply transfer failures occur.
287 | 2871991007 | 1991-07-03 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Oconee 3 | P | BW | PO | 100 | On July 3, 1991, at 1118 hours, while operating at 100 % Full Power, Oconee Unit 3 tripped as a result of a loss of feedwater. The loss was initiated when particles from a degraded seal clogged an Instrument Air flow path in the master valve controller for the condensate demineralizer system. This caused five parallel valves to fail closed, blocking all condensate flow. Demineralizer bypass valves could not open to compensate because an Operator had failed to return them to Automatic control. The loss of condensate flow resulted in the trip of condensate booster pumps due to low suction pressure, which then caused a trip of the main feedwater pumps, followed by the reactor trip. Emergency feedwater pumps started, but a solenoid valve failed, requiring manual operator action to control flow to one steam generator. The operators stabilized the unit at hot shutdown. Corrective actions included replacement of the defective parts and counselling of the Operator. The root cause was Equipment Failure with a contributing cause of Inappropriate Action.
287 | 2871991008 | 1991-11-23 | G1 | Very Small LOCA or Leak | [6 empty] | X | [18 empty] | X | [19 empty] | Oconee 3 | P | BW | PO | 100 | On November 23, 1991, Oconee Unit 3 was operating at 100% Full Power (FP) when the Control Room Operators (CROs) received several alarms at 0141 hours which indicated failed instruments inside the reactor building (RB). At 0143 hours, the CROs observed symptoms of excessive Reactor Coolant System (RCS) leakage and began assessing the leak rate. At 0203 hours, they started a rapid controlled shutdown. At 0214 hours, the Shift Supervisor concluded that leakage was approximately 60 to 70 gpm, and declared an ALERT. At 0327 hours, the unit tripped from 33% FP due to a control oscillation while the CROs were attempting to secure a feedwater pump. At 0641 hours, an additional unanticipated Reactor Protective System actuation occurred due to operator error. At 1720 hours the unit reached cold shutdown and the ALERT was terminated. The leak was determined to be a failed fitting on an instrument line at the top of a steam generator. A total of approximately 87,000 gallons of RCS leakage was confined within the RB. The instrument line was replaced, and additional fittings inspected. The root causes are Management Deficiency and Equipment Failure.
287 | 2871992001 | 1992-01-14 | QP5 | Excessive Feedwater Flow | [45 empty] | Oconee 3 | P | BW | PO | 94 | On January 14, 1992, at 1001 hours, while operating at 94% Full Power, Oconee Unit 3 tripped on loss of both Main Feedwater Pumps. Instrument and. Electrical (I&E) technicians were performing trouble checks on a suspected faulty controller in the Integrated Control System feedwater control circuits. The I&E technicians used an instrument with the test leads configured for current measurement rather than voltage, causing a false signal to be introduced into the controller. This increased the feedwater flow to the 3B Steam Generator, which resulted in high levels that tripped both Main Feedwater pumps. The Emergency Feedwater System activated and the unit stabilized at Hot Shutdown. After re-establishing Main Feedwater (FDW) a trip of the 3A Main FDW pump occurred on high discharge pressure due to a problem with the FDW pump speed control. Emergency Feedwater reinitiated, the second Main FDW pump was started and Emergency Feedwater was secured. The root cause of the unit trip was Inappropriate Action, Improper or Inadvertent action, Lack of attention to detail. Corrective actions included replacement of the defective parts and installing blank plugs in the current measuring jacks of instruments when issued.
287 | 2871992002 | 1992-02-27 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | On February 27, 1992, at 1627 hours, Oconee Unit 3 tripped from 100% full power. The unit was operating at steady-state conditions when the reactor tripped from an anticipatory turbine trip. All four Reactor Protective System channels tripped when the Main Turbine tripped on indicated loss of stator cooling. Post-trip response was normal and the Operators stabilized the unit at hot shutdown conditions. Upon investigation of the trip, it was discovered that Instrument and Electrical technicians had inadvertently jumpered a trip circuit on Unit 3 while performing a turbine/generator trip procedure associated with Unit 2 Refueling Outage. The root cause was inappropriate action, failure to adhere to established work practices and policies. Corrective actions included counselling the involved technicians and increased management attention and involvement with correct component identification and independent verification programs.
287 | 2871992003 | 1992-06-24 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Oconee 3 | P | BW | PO | 100 | On June 24, 1992, at approximately 1411 hours, while operating at 100 percent Full Power, Oconee Unit 3 tripped as a result of a momentary loss of the Integrated Control System power from power panelboard 3KI. During the implementation of a Nuclear Station Modification, a wiring problem was encountered with the installation of an indicator, resulting in a ground fault on power panelboard 3KI. An investigation revealed that the vendor has the same part number for two different indicators. The two root causes of this event were a Manufacturing Deficiency (Deficient communication, Lack of communication) and Design Deficiency (Deficient documentation, incomplete documentation). Corrective actions include the evaluation of the inverter and static switch performance which led to the momentary loss of 3KI and review of exempt changes and Nuclear Station Modifications that include Dixson Indicators.
287 | 2871992004 | 1992-09-29 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 3 | P | BW | PO | 73 | On September 29, 1992, at 0916 hours, Unit 3 tripped from approximately 4% Full Power (FP) following a rapid reduction in power from approximately 73% FP after the Regulating Control Rod Groups dropped into the core. Prior to this transient Instrument and Electrical (I&E) technicians were troubleshooting a problem in the Control Rod Drive (CRD) system. At 0916 hours, I&E technicians opened a CRD breaker associated with the 3A CRD power supply and Control Room Operators observed that a group of Control Rods fell into the core. The Transient Monitor system indicated Groups 5, 6, and 7 dropped into the core. Approximately 13 seconds later the Reactor tripped on low Reactor Coolant System pressure. The unit post-trip response was normal and was stabilized at hot shutdown conditions. The root cause of the event is Unknown: Possible Equipment Malfunction with the 3B CRD power supply. Corrective actions include replacing a programmer, revising procedures and installing a modification.
287 | 2871993001 | 1993-01-26 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | On January 26, 1993, at 1005 hours, while operating at 100% Full Power, Oconee Unit 3 tripped from a Reactor Protective System anticipatory trip signal. While troubleshooting a problem in Unit 3's Power Factor meter transducer, Instrumentation and Electrical technicians incorrectly tested the voltage input of the transducer with a multimeter in the current measuring mode. This resulted in a partial loss of power to the Generator Output Megawatt meter and a false signal to the Integrated Control System. The Turbine control Valves opened in response to this false signal to recover the apparent lost megawatts. A large decrease in Feedwater Pump discharge pressure caused an Anticipated Transient Without Scram Mitigation System Actuation Circuitry actuation, starting the Emergency Feedwater pumps and tripping the Main Turbine. Main Turbine Anticipatory trip signal tripped the reactor. Post Trip response was normal. During the trip recovery, while transferring from the Emergency Feedwater to the Main Feedwater pumps, a loss of automatic initiation of both emergency feedwater flow paths resulted when both Emergency Feedwater Control Valves were not placed in "AUTO" as directed by procedure. The cause of the unit trip was Inappropriate Action (Improper Action, Lack of Attention to Detail). The cause of the second event was Inappropriate Action (Improperly Followed the Correct Procedure). Corrective actions included replacement of the blown fuses, faulty transducer, and revision of the station drawings and individual counseling to improve personnel performance.
287 | 2871994001 | 1994-03-01 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | At 1014:30 hours, March 1, 1994, Unit 3 tripped from 100% Full Power. All systems responded as expected. The response of Operators and automatic systems brought the unit to stable hot shutdown conditions. The initiating signal was an Anticipatory Reactor Trip on Turbine Trip due to a false emergency high level in a Moisture Separator/Reheater (MSR), even though there were no other high level indications or alarms. Troubleshooting personnel identified a defective mercury contact switch assembly in one of four MSR high level instruments. Root cause was Equipment Failure. The defective contact assembly was replaced prior to restart of the unit.
287 | 2871994002 | 1994-08-10 | QC4 | Loss of ac Instrumentation and Control Bus. | [13 empty] | X | [30 empty] | X | Oconee 3 | P | BW | PO | 100 | On August 10, 1994, at 0426 hours, while operating at 100% full power, Unit 3 tripped as a result of a momentary loss of power to the Integrated Control System inverter, 3KI. Operators observed an overcooling of the Reactor Coolant System and also noted a diverging pressure trend between 3A and 3B Steam Generators (S/G) and suspected a leak or rupture of the 3B main Steam header. They isolated the 3B S/G, then noted that the Turbine Bypass Control valves (TBVs) were partially open and closed them. The open TBVs had caused the overcooling and depressurization of the S/Gs. The Unit was then stabilized at Hot Shutdown condition with decay heat removal via 3A S/G. The event was terminated when the 3B S/G was unisolated, refilled, and pressurized. The cause of the event was determined to be blown fuses on 3KI inverter, but the root cause of the blown fuses is unknown. Corrective actions included the continuation of troubleshooting the problems with the inverter and modification to the TBVs controls.
287 | 2871994003 | 1994-08-12 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Oconee 3 | P | BW | PO | 42 | On August 12, 1994, Unit 3 was at approximately 42% full power and returning to full power operation at 3% per hour following a Unit trip. The 3B Main Feedwater (MFDWP) was supplying feedwater and the 3A MFDWP was being warmed in preparation for placing it in service. At 0447 hours, an anticipatory Reactor trip occurred due to the loss of the MFDWP that was in service. The response of the operators and automatic systems brought the unit to stable hot shutdown conditions. An investigation into the cause of the Unit 3 Reactor trip revealed that a gasket connection on the 3B MFDWP Turbine, between the relay valve and the emergency governor lockout valve, had failed resulting in low hydraulic oil pressure. This coincident with low discharge pressure on the 3A MFDWP resulted in the Reactor trip. The root cause is a component failure due to aging. Corrective actions include replacing the valve gasket, revising the maintenance procedure, and contacting the vendor for other operating experience associated with this type equipment.
287 | 2871995002 | 1995-08-14 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | On August 14, 1995, at approximately 0457 hours, Unit 3 tripped from 100% Full Power. Operators stabilized the unit at hot shutdown conditions. The unit post trip response was normal. The transient monitor and events recorder indicated that group 5 control rods had dropped into the core. Approximately three seconds later the Reactor tripped on a Reactor Protective System variable low pressure/temperature trip. An investigation revealed that there was no testing or maintenance being performed at the time of the trip. The investigation into the dropped rods has not determined the cause. The rod group 5 programmer has been sent to the vendor for further analysis. The root cause of the event is Unknown; Possible Equipment Malfunction with the rod group 5 programmer. Corrective actions include replacing the programmer and sending the suspect programmer to the vendor for analysis.
287 | 2871996001 | 1996-03-16 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Oconee 3 | P | BW | PO | 100 | On March 16, 1996, during a Performance Test of the Emergency Power System, an unexpected closure of certain Unit 3 relay contacts occurred due to vibration. This caused a momentary load shed signal that resulted in the loss of several secondary system pumps, which initiated a feedwater transient. At 1318 hours, Unit 3 tripped from 100% full power on a Reactor Protective System (RPS) anticipatory trip due to the loss of Main Feedwater Pumps. All Emergency Feedwater pumps started and supplied the Steam Generators. Unit 3 was powered from the emergency power source and all the Reactor Coolant Pumps (RCP) tripped off, as expected due to the test conditions. The Unit was stabilized on natural circulation. The reactor trip was caused by a condensate system transient resulting from the load shed of 4KV Bus 3TE. The root cause of the event was determined to be Installation Deficiency due to improper assembly of a relay. Subsequently, on March 17, 1996, at Hot Shutdown, a RPS automatic actuation occurred, with no control rods withdrawn, when one of the two operating RCPs was tripped due to high vibration. Corrective actions included replacing and properly installing the relay and revising procedures.
287 | 2871997001 | 1997-03-20 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 3 | P | BW | PO | 73 | On March 20, 1997, Unit 3 was operating at 73% full power, following a refueling outage. Maintenance and Operations personnel were performing a monthly 'Control Rod Drive Breaker Trip and Event Recorder Timing Test.' At approximately 0913 hours, while testing one breaker, the Reactor tripped due to an electrical short in the redundant Control Rod Drive trip confirm breaker circuitry. The trip response was routine with no significant occurrences. The unit was stabilized at Hot Shutdown conditions. The root cause of the event is a manufacturing fabrication deficiency. Corrective actions include repairing the electrical short and revising the CRD breaker trip time test procedure.
287 | 2871998004 | 1998-12-31 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | On December 31, 1998, Unit 3 experienced a reactor trip from 100% Full Power during a Control Rod Drive (CRD) circuit breaker (BKR) trip test. When the test technicians tripped the first BKR per the procedure, the CRD Channel 'B' Trip Confirm Relay actuated unexpectedly. This actuation caused a Generator Lockout, followed immediately by a Main Turbine Trip and Anticipatory Reactor Trip. Unit response was routine and the operators stabilized the unit. A broken wire de-energized an auxiliary relay, which simulated two of the four DC CRD BKRs being open. When the AC BKR under test was opened, the Trip Confirm Relay logic caused the Generator Lockout. Investigation concluded that the wire broke during maintenance on an adjacent circuit during the most recent refueling outage. The trip occurred on the first test at power after the outage. The root cause was a defect dated from manufacture, with a contributing preventative maintenance weakness that allowed a loose fuse holder to cause movement of the wire. Corrective actions include repair of the broken wire, enhancement of maintenance work practices, and enhancement of test methods to allow verification of relay status prior to testing a BKR. The health and safety of the public was not compromised by this event.
287 | 2872000001 | 2000-01-03 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | At approximately 1254 on January 3, 2000, with Unit 3 at approximately 100 percent power, a Stator Cooling runback occurred. Operations verified that plant equipment was responding appropriately. It was observed that Generator MWatts had run back to 0 with Generator MVARs indicating 260 and that the Generator breakers were closed. At approximately 1257, these conditions along with HiHi Generator Stator winding temperatures led Control Room personnel to manually trip the Main Turbine, which resulted in an anticipatory Reactor trip. Reactor Power was approximately 56 percent at the time of the Main Turbine trip. This event involved equipment failures on the secondary side only. Primary and secondary equipment and parameters responded as expected. There were no major problems encountered in placing the plant in Mode 3. Investigations revealed the Stator Cooling runback resulted from high Stator Cooling temperature. This condition was caused by the failure of the temperature controller for the Stator Cooling System proportioning valve. The cause of the reactor trip was inadequate installation of the temperature controller tubing. Corrective actions to prevent recurrence include replacement and analysis of the failed temperature controller. This event is considered of no significance with respect to the health and safety of the public.
287 | 2872002001 | 2002-11-14 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | On November 14, 2002, Oconee Unit 3 was operating in Mode 1 at 100% power. At approximately 0419 hours, Unit 3 experienced a high level in a Moisture Separator Reheater (MSRH). The turbine tripped as a protective feature to prevent water from backing up into the turbine. This caused an anticipatory reactor trip. The high level was caused by three separate equipment failures which resulted in discharge flow paths from the 3A Moisture Separator Drain Tank (MSDT) becoming isolated and water backing up into the MSDT and MSRH. In this event, the plant systems and operators responded as expected. Automatic system responses and operator actions in accordance with procedures were adequate to safely control the reactor following this trip. The corrective action was to repair the three Unit 3 A MSDT level control equipment problems. The health and safety of the public was not compromised by this event.
287 | 2872004001 | 2004-02-26 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | At 11:50:56 on 02-26-2004 Oconee Unit 3 reactor tripped on high Reactor Coolant System pressure approximately three minutes after an Electro-Hydraulic Control (EHC) pump was returned to service following routine maintenance. Post-trip response was normal. Investigation found that a small piece of foreign material, specifically a piece of clear plastic packaging material, inadvertently entered the system during replacement of a discharge filter. The material clogged the hydraulic fluid entry port of a turbine stop valve, causing all four stop valves to close. The root cause was determined to be in attention to detail by two Maintenance technicians performing the task. The material was found and removed. This event is considered to have no significance with respect to the health and safety of the public.
287 | 2872005002 | 2005-08-31 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Oconee 3 | P | BW | PO | 100 | At 1428:27, on 8-31-05, Unit 3 tripped from 100% rated power, Mode 1. The trip transient reduced Reactor Coolant System temperature and pressure, resulting in Engineered Safeguards (ES) actuations of the High Pressure Injection, Containment Isolation (partial), and Emergency Power Systems. Operators took actions per the Emergency Operating Procedure to stabilize the unit in Mode 3. All challenged ES components operated as expected. The causes of the trip and ES actuations were two design deficiencies in a recent (late 2004) modification to the Control Rod Drive system. Redundant power sources were not sufficiently verified nor tested individually in the as-built configuration. Also, a system interface issue was detected both in design review and in testing but was not resolved prior to contributing to the event. Corrective actions include design changes to correct the deficiencies and enhancements to the design change process. This event is considered to have no significance with respect to the health and safety of the public.
287 | 2872008001 | 2008-11-07 | QR8 | Spurious Reactor Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | At 0834 on November 7, 2008 Oconee Unit 3 experienced a reactor trip. The trip was the result of the Control Rod Drive (CRD) processor modules P1 and P2 experiencing a kernel fault caused by an inability to decode a clock signal inputted to the processors with a day value of zero. This resulted in both CRD system processors failing simultaneously, causing a loss of power output from the single rod power supplies and control rods to drop into the core. The processor failure also caused relays to actuate and produce a Reactor Trip Confirm (RTC) signal which in turn initiated a turbine trip and generator lockout signal. The Reactor Protection System (RPS) received a Loss of Main Turbine Anticipatory Trip Signal and tripped the CRD breakers. The unit responded as expected. The Emergency Operating Procedure was entered, subsequent actions completed, and a transfer to the unit shutdown procedure was made without complication. Appropriate post-trip reviews were performed and recovery actions completed per station procedures. The clock signal was disconnected from the CRD system P1 and P2 processors on all units to prevent recurrence of this event. Unit 3 was returned to service on November 9, 2008. This event is considered to have no significance with respect to the health and safety of the public.
287 | 2872009002 | 2009-05-21 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 42 | At 2014 on May 21, 2009, Oconee Nuclear Station Unit 3 experienced a reactor trip as a result of a generator lockout while escalating power following a refueling outage. The X phase differential relay (device 87U) actuated because a relay tap setting was configured incorrectly due to personnel error. This generator lockout resulted in a Reactor Protection System (RPS) actuation due to an anticipatory trip. The RPS received a Loss of Main Turbine Anticipatory Trip Signal and tripped the Control Rod Drive (CRD) breakers. The unit responded as expected. The Emergency Operating Procedure (EOP) was entered, subsequent actions completed, and a transfer to the unit shutdown procedure was made without complication. There were no significant equipment failures. Appropriate post-trip reviews were performed and recovery actions completed per station procedures. The Unit 3 87U differential relays' tap block settings were corrected on all three phases. Unit 3 reached criticality on May 22, 2009, and power escalation resumed. This event is considered to have no significance with respect to the health and safety of the public.
287 | 2872013001 | 2013-10-24 | QR6 | Manual Reactor Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | This revision provides supplemental information, including a revised cause, discovered during the cause evaluation for a similar Unit 3 manual reactor trip on January 31, 2015. <br /><br /> On October 24, 2013, Oconee Unit 3 was at 100% power when Operators observed abnormal Main Feedwater flow oscillations. Manual control was unsuccessful in stabilizing the oscillations. The Control Room supervisor directed a manual trip at 0553 hours. Four main steam relief valves (MSRV) did not fully reseat. Post-trip procedures were used to reseat the MSRVs. All other post trip conditions were normal. The 2013 cause evaluation identified a failure of a bushing seal (o-ring) in the actuator for Main Feedwater Control Valve (MFCV) 3FDW-32 as the cause of the flow oscillations. The 2015 cause evaluation revealed the cause of the 3FDW-32 control problem was a latent defect which produced an intermittent fault in the voltage to pneumatic (E/P) converter. While the o-ring failure was a plausible cause in 2013, given new information from the 2015 event, the faulted E/P converter was determined to be the cause of the 2013 event. The E/P converter was tested in 2013, but due to the intermittent nature of the fault the E/P was refuted after satisfactory testing of 3FDW-32 controls. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of the Reactor Protection System (RPS).
287 | 2872015001 | 2015-01-31 | QR6 | Manual Reactor Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | On January 31, 2015, Oconee Unit 3 was operating at 100% power in MODE 1 when Control Room operators observed that Main Feedwater flow indicators were oscillating outside of normal parameters. The Control Room supervisor made the decision to manually trip Unit 3 at 1431 hours due to erratic feedwater operation and increasing RCS pressure. A subsequent investigation determined the feedwater flow oscillations were caused by a subcomponent failure of the electrical to pneumatic converter (E/P), 3FDW EP 0007, to properly control feedwater flow for Main Feedwater Control Valve (MFCV) 3FDW-32.<br /><br /> This event was reported as a 4-hour notification to the NRC on January 31, 2015, in Event Notification (EN) number 50781 under 10 CFR 50.72(b)(2)(iv)(B) - Reactor Protection System (RPS) Actuation - Critical. The event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the RPS.
287 | 2872017001 | 2017-07-24 | QR5 | Turbine Trip | [45 empty] | Oconee 3 | P | BW | PO | 100 | On 7/24/17, with Oconee Nuclear Station (ONS) Unit 3 operating at 100 percent power, Transmission Department Relay personnel were in the ONS 525kV Switchyard Relay House performing preventive maintenance on a Breaker Failure Relaying device for Power Circuit Breaker PCB-57. This is a nonsafety PCB that isolates a commercial transmission line from the commercial bus in the 525kV switchyard. The maintenance was intended to actuate the protective relaying for PCB-57. The crew inadvertently connected test equipment to the adjacent relaying for PCB-58. The activation of the PCB-58 relay resulted in a Unit 3 separation from the electrical grid and a generator "Lockout." The lockout generates a turbine trip which in turn trips the reactor via the Reactor Protection System (RPS). This actuation of the RPS is reportable per 10 CFR 50.73(a)(2)(iv)(A). <br /><br /> Post trip plant response was normal and plant conditions were controlled and maintained within the allowances of Technical Specifications with no personnel injuries or safety system actuations. <br /><br /> A cause analysis attributed the cause of this event to human error in that test equipment was inadvertently connected to relaying for the incorrect PCB. The cause analysis corrective actions will address the likelihood of comparable human errors from occurring.
287 | 2872020001 | 2020-04-10 | QR6 | Manual Reactor Trip | [45 empty] | Oconee 3 | P | BW | PO | 32 | On April 10, 2020 at 2125 EDT, Oconee Unit 3 was manually tripped from 32% power based on the water level in the 3F1 Feedwater Heater. At the time of the trip, Unit 3 was reducing power as part of a planned shutdown for a refueling outage. The trip was initiated in accordance with procedural guidance that called for tripping the Reactor and Main Turbine if a large Feedwater tube leak exists and any 'F' Feedwater Heater Level indicates >/= 14" while the Reactor is greater than 25% power. At the time of the trip it was thought that there had been a significant tube leak in the 3F1 Feedwater Heater. Subsequent investigation determined there was no tube leak associated with the increased level in the 3F1 heater. <br /><br /> Post-trip plant response was normal and plant conditions were controlled and maintained within the allowances of Technical Specifications with no safety system actuations.<br /><br /> An ongoing cause analysis has determined that the unit trip was due to an overly restrictive heater level limit placed in the operating procedure that did not account for the various heater levels that occur during power reductions.<br /><br /> This event was reported as a 4-hour notification to the NRC on April 11, 2020, in Event Notification (EN) number 54661 under 10 CFR 50.72(b)(2)(iv)(B) - Reactor Protection System (RPS) Actuation - Critical (Manual Reactor Trip). The event is also reportable under 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the RPS.
289 | 2891987004 | 1987-05-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Three Mile Isl 1 | P | BW | PO | 90 | TMI-1 was operating at 90% power with the Integrated Control System (ICS) in full automatic and with no components or systems inoperable. <br /><br />A licensed operator performing the "Power Range Calibration" surveillance on the Reactor Protection System (RPS), accidently transferred the "flow" signal instead of the "flux" signal during the test. The ICS responded to this change as designed by reducing main feedwater flow and withdrawing rods. The RPS responded as designed by tripping the reactor on high pressure at 0751 hours on May 2, 1987. No other safety systems were called upon during this transient. This automatic unplanned RPS actuation is reportable under 10CFR50.73A.2.IV. Root cause was the failure of the operator to recognize that the wrong switch had been selected. <br /><br /> A similar incident occurred May 27, 1976 during Cycle 2 startup physics testing. The "flux" signal to the ICS was selected without placing the proper stations in manual. The ICS withdrew control rods as designed. The RPS tripped the reactor on high flux. <br /><br />Corrective actions are being taken which are to: <br /><br />(1) Improve affected procedures by requiring additional verification that the proper switch has functioned as desired. <br /><br /> (2) Provide guidance and training to all operators to ensure that lessons learned are constructively used to help prevent future occurrences of this nature.
289 | 2891987006 | 1987-06-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Three Mile Isl 1 | P | BW | PO | 10 | On June 12, 1987 at 2157 hours, TMI-1 was at approximately 10% power with the turbine-generator off-line while performing a planned shutdown. The 1B Main Feedwater pump speed was being controlled in hand by the Control Room Operator. As power was being reduced, the speed of the pump was also being reduced to prevent excessive differential pressure across the feedwater regulating valves. At this point, the speed of the pump was inadvertently reduced below that necessary to provide adequate feedwater to the Once Through Steam Generators. The lack of feedwater was recognized and the pump speed was increased but not in time to stop the RCS pressure increase to the RPS trip setpoint. The reactor tripped on high RCS pressure. The Once Through Steam Generators overfed slightly above the normal post trip level control setpoint. RCS temperature and pressure response were normal. The root cause of the event was operator error in not maintaining sufficient feed pump speed to provide adequate feedwater flow to the steam generators. Although this operator error was preventable, its occurrence did not cause a transient that is outside the design basis for the plant. Licensed operators have been directed to maintain acute awareness of main feed pump speed control. Also, feed pump hand control will be emphasized during the 1987-88 training cycle on plant shutdown simulator training exercises.
289 | 2891987008 | 1987-09-16 | QR5 | Turbine Trip | [45 empty] | Three Mile Isl 1 | P | BW | PO | 100 | TMI-1 was operating at 100% power with the Integrated Control System (ICS) in full automatic. No systems or components were inoperable that affected the post trip response. <br /><br />At 1704 hours on September 16, 1987, the turbine tripped on high moisture separator level followed by a reactor trip. The Reactor Protection System (RPS) functioned as designed. The plant post trip response was normal except for a slight feedwater refeed to the steam generator. No other safety systems were actuated. The root cause was the failure of the non-safety related level controller LC77E. LC77E controls the high level dump valve MO-V-2E and did not open the valve far enough to maintain water level. <br /><br />Similar reactor trips resulting from high moisture separator level occurred on January 4, 1986 and May 9, 1975. See the text for more detail. <br /><br />Corrective and preventative actions being taken are: <br /><br />1. High Level Trip Time Delay Relay was replaced. <br /><br /> 2. Dump Valve Level Controller (LC77E) was repaired. <br /><br />3. All six High Level Trip Switches were tested prior to startup. <br /><br />4. All six High Level Dump Valves were tested prior to startup. <br /><br />5. All six High Level Alarm Switches were tested prior to startup. <br /><br />6. Levels of all six Moisture Separators were monitored during startup. <br /><br />7. The Moisture Separator Drain System is being evaluated for improvements. <br /><br />8. The Preventive Maintenance performed on the High Level Dump Valve Controllers and alarm switches will be improved.
289 | 2891988006 | 1988-10-30 | QR5 | Turbine Trip | [45 empty] | Three Mile Isl 1 | P | BW | PO | 100 | At 8:49 a.m. on October 30, 1988 the main turbine tripped to manual with a coincident array of about 8 alarms. Generated megawatts were rapidly decreasing and the main steam safety valves began to lift. Within 4 seconds of the initiation of the event, the reactor tripped on high RCS pressure. The post trip response was normal. Two conditions required operator response. A main steam safety valve did not completely reseat. Operators lowered the steam header pressure control setpoint about 50 psig and the valve reseated. In addition, the main feedwater startup control valve did not control in automatic and required operator action. This second problem has been corrected by retuning the ICS modules. <br /><br />The reactor trip was caused by rapid closure of the main turbine control valves. The closure initiation is attributed to be a result of an erroneous signal being generated within the EHC. Investigation revealed an erratic power supply that required replacement along with a relay in the #4 intercept valve test circuitry within the EHC cabinets. This relay problem was not considered to be related to the root cause of the event. It is believed that the erratic power supply is the most likely initiator of the event.
289 | 2891989003 | 1989-11-29 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Three Mile Isl 1 | P | BW | PO | 100 | At approximately 0806 hours on November 29, 1989, a rapid reduction in turbine load occurred. This rapid reduction in load resulted in increasing temperature and pressure in the Reactor Coolant System causing the reactor to trip on high RCS pressure within about 4 seconds. The Reactor Protection System functioned correctly and operator response was appropriate. The post trip response was normal. Main steam header pressure was reduced to reseat a Main Steam Safety Valve (MS-V-21A). Level control for B OTSG was considered sluggish and the feedwater valve was controlled manually. These actions are in accordance with procedures and training.<br /><br /> The rapid load reduction was the result of EHC action. The power load unbalance circuit that protects the turbine from overspeed and the speed error circuit were suspected since either of these circuits can result in rapid control valve closure. The function and calibration of these circuits were checked. Minor calibration drift was found. The drift was not abnormal and would not have caused the transient. <br /><br /> A loose shield wire was found on the input to the speed error circuit from the turbine primary speed sensor. It is postulated that the loose connection was disturbed by opening and closing the cabinet doors. This was determined to be the probable cause.
289 | 2891991002 | 1991-07-24 | QR3 | Reactivity Control Imbalance | [45 empty] | Three Mile Isl 1 | P | BW | PO | 92 | On July 24, 1991 at 0520 the reactor tripped on low RCS pressure due to control rod Group 7 dropping into the reactor core as a result of personnel error in combination with an equipment failure. During the performance of a weekly Reactor Protection System surveillance procedure, an Instrument and Controls technician failed to follow the procedure which resulted in a failure to re-energize the primary power supply to the rod drive programmer assemblies. Failure of the "A" phase gate drive of the Group 7 control rods on the secondary power supply, resulted in a degradation of that power supply. During restoration of the Integrated Control System to AUTO upon completion of the surveillance, the Group 7 control rods received a command to move. The primary power supply remained in a de-energized state and the programmer cycled through the failed gate drive on the secondary group power supply. Due to the inadequate number of phases on the secondary group power supply to support rod movement, the Group 7 control rods dropped into the core. The Reactor Protection System inserted the remaining rod groups when RCS pressure decreased to 1900 psig.<br /><br /> The event was reported per 10 CFR 50.73(a)(2)(iv).
289 | 2891991003 | 1991-09-27 | QR5 | Turbine Trip | [45 empty] | Three Mile Isl 1 | P | BW | PO | 13 | On September 27, 1991 during plant shutdown for the 9R outage reactor power was stablized at 13% to support completion of turbine valve tightness testing and a special test of the turbine overspeed mechanical trip device. The turbine load limit control was turned to the minimum setting to close the turbine control valves and begin the tightness test while the stop valves remained open. The control valves closed as expected and the turbine decelerated indicating the leak tightness of the valves. After about seven minutes of deceleration, the turbine speed was 1200 rpm. In accordance with procedure, the CRO selected the "FAST" acceleration rate on the turbine control panel and turned the load limit control to maximum setting. The turbine control valves immediately started opening rapidly and OTSG pressure began dropping rapidly. Approximately ten seconds later at 18:37, the turbine tripped on overspeed. Subsequently, main feedwater was isolated to both OTSGs due to low OTSG pressure and both Emergency Feedwater Trains were auto initiated due to the low OTSG levels. The reactor tripped at 18:38 on high pressure. Normal feedwater flow to the OTSG's was re-established and post trip response was considered normal. <br /><br /> The NRC was notified in accordance with 10 CFR 50.72(b)(2)(ii).
289 | 2891992002 | 1992-09-18 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Three Mile Isl 1 | P | BW | PO | 100 | On September 18, 1992 TMI-1 was operating at 100% power. Plant operations and maintenance personnel were in the process of disabling the circulating water (CW) pump trip on high (nominal 42 psig) condenser inlet water box pressure. The basis for removing this trip feature was documented in an Engineering Evaluation which concluded that the automatic trip feature was no longer required. As a result of the current experience with Asiatic clamshell blockage in the main condenser [KE/COND] and the gradual increase in the inlet water box pressure, the CW trip removal was a recognized priority. During the sequence to disable this trip feature, the trip actuated causing the shutdown of three of six CW pumps [KE/P] and the subsequent turbine trip on low vacuum and anticipatory reactor trip. <br /><br /> The root cause was an inadequate review that failed to select the task's least risk solution prior to performing the evolution. Procedures will be revised to provide additional guidance for evolutions of this type and the lessons learned are being widely disseminated. The need to seek the most risk free sequence was addressed with personnel directly involved in the review and performance of the task. <br /><br /> The event was reported per 10CFR50.72(b)(2)(ii).
289 | 2891993003 | 1993-03-12 | QR8 | Spurious Reactor Trip | [45 empty] | Three Mile Isl 1 | P | BW | PO | 100 | On March 12, 1993, TMI-1 was operating at 100% power. During performance of surveillance testing for the Heat Sink Protection System (HSPS) an equipment malfunction in the Reactor Coolant Pump Power Monitor (RCPPM) 1 resulted in sending an erroneous Reactor Coolant Pump Trip signal to the Reactor Protection System (RPS). The RPS functioned normally and tripped the reactor due to a mismatch between Reactor Power and the number of running Reactor Coolant Pumps. <br /><br /> The root cause was electrical equipment failure in the Reactor Coolant Pump Power Monitor 1. The failed equipment was repaired and satisfactorily tested. The remaining RCPPM's shall be inspected and repaired as necessary to improve reliability during testing. Also, procedure enhancements to the surveillance procedure will be made to provide additional checks on equipment status before and after each switching sequence.
289 | 2891997007 | 1997-06-21 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Three Mile Isl 1 | P | BW | PO | 100 | On June 21, 1997 at approximately 1214, while the plant was operating at 100% power, TMI-1 experienced a loss of off site power (LOOP) due to the failure of both generator output breakers located in the site's 230KV substation. The fault detected on the #4 bus (230KV) resulted in the opening of the parallel breaker which suffered a re-strike and caused a fault on the alternate #8 bus. The two faults resulted in breaker action which isolated power to the station and resulted in the LOOP. The LOOP resulted in immediate reactor and turbine trips. Both emergency diesel generators started and loaded on to their respective safeguards buses as designed. Without balance of plant power, the condensate, feed, circulating water and main condenser vacuum pumps were not operable. The once through steam generators were fed through the Emergency Feedwater System via two electric pumps powered by the engineered safeguards buses and a steam driven pump. Heat was removed via the steam generator atmospheric dump valves. Loss of station power also deenergized the reactor coolant pumps which forced the plant into a natural circulation mode. Natural circulation flow was achieved within 19 minutes of the trip. Offsite power was restored within 90 minutes. Systems were restored to enable cooling via the main condenser and subsequent restart of the reactor coolant pumps. The failed breakers were replaced with new ABB model 242 PMG 3000 amp breakers. The plant was back on line at 0202 on June 29, 1997. <br /><br /> The root cause of the plant trip and LOOP was the failure of generator breaker GB-1-02 and the re-strike which occurred during the opening of the parallel breaker caused a fault on the alternate #8 bus in the plant 230KV switch-yard. The fault in the "B" phase of GB-1-02 breaker caused severe overheating and ejection of the bushing and conductor from the breaker. <br /><br /> The event is being reported per 10 CFR 50.73(a)(2)(iv)
289 | 2892006002 | 2006-11-02 | QR5 | Turbine Trip | [45 empty] | Three Mile Isl 1 | P | BW | PO | 100 | On November 2, 2006, at 1334 hours, the Three Mile Island, Unit 1 (TMI-1) reactor tripped from 100% power during a calibration check of the main turbine Digital Turbine Control System (DTCS) condenser pressure instruments. The reactor trip was initiated from Reactor Protection System (RPS) ARTS (Anticipatory Reactor Trip System) due to a main turbine trip initiated from greater than 45% power. The turbine trip resulted from an invalid DTCS protective system actuation. The turbine trip initiated from the two in-service DTCS protective channels not being tested at the time of the event. Both channels received an invalid trip signal. The channel under test at the time of the event was properly bypassed from the trip logic and did not input a trip signal to the DTCS. Plant systems responded properly to the reactor trip transient and the plant was stabilized at hot shutdown conditions. The root cause of the turbine trip is a latent design weakness within the DTCS. Subsequent testing demonstrated that a short circuit of a single milli-amp input to the DTCS signal processing board will affect all of the processor inputs associated with that board and initiate a main turbine trip signal from the in-service trip channels. All online transmitter preventative maintenance activities that provide inputs to the DTCS trip logic circuit have been suspended until the cause for the turbine trip is eliminated. The actuation of the Reactor Protection System was reported to the NRC in accordance with 10CFR 50.72(b)(2)(iv)(B), reference EN# 42957. Submittal of this LER constitutes reporting to the NRC in accordance with 10 CFR 50.73 (a)(2)(iv)(A).
289 | 2892006003 | 2006-12-13 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Three Mile Isl 1 | P | BW | PO | 100 | At 1748 hours on December 13, 2006, the Three Mile Island, Unit 1 (TMI-1) reactor tripped from 100% power following a short duration power disturbance on a 230 kV transmission line located approximately 4 miles from TMI-1. This short duration power disturbance was caused by the failure of a 230 kV transmission line cable splice, which resulted in a single-phase ground fault. This short duration ground fault affected power supplied to the reactor coolant pump motors, which in turn caused actuation of the Reactor Coolant Pump Power Monitors (RCPPM). The RCPPM's actuation sends a signal to the Reactor Protection System (RPS) to trip the unit if a decrease in reactor coolant pump motor power consumption is detected. This reactor trip is designed to protect the fuel rods from overheating upon a sudden loss of Reactor Coolant flow. The RCPPM design includes a time delay to prevent inadvertent reactor trips due to short duration electrical disturbances, which would not affect the reactor coolant pump's ability to maintain adequate Reactor Coolant System flow. The RCPPM time delay has a maximum setting of less than 525 milliseconds. The root cause of the event is a design application deficiency within the RCPPM. The RCPPM circuit design focuses on fuel protection and specifies a maximum time delay, but does not consider the effects of a grid transient of short duration. The RCPPM calibration procedure will be revised to establish a minimum allowed time delay for the Reactor Coolant Pump Power Monitor circuit. A maintenance activity has been scheduled for the next available opportunity, but no later than the October 2007 refueling outage, to calibrate the RCPPM using the revised setpoint tolerance. The actuation of the Reactor Protection System was reported to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B), reference EN #43050. Submittal of this LER constitutes reporting to the NRC in accordance with 10 CFR 50.73 (a)(2)(iv)(A).
289 | 2892012004 | 2012-08-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Three Mile Isl 1 | P | BW | PO | 30 | On Wednesday, August 22, 2012, Three Mile Island, Unit 1, was conducting a Technical Specification required (T.S. 3.1.6.6) plant shutdown to repair a leak on a pressurizer heater bundle. At 8:01:26 AM with the plant at 30% power, the reactor tripped by Reactor Protection System (RPS) actuation on high reactor coolant system (RCS) pressure. The high RCS pressure setpoint was reached due to a loss of suction to the main feedwater pumps when the only operating condensate booster pump tripped. A "counting circuit" relay stuck in the energized position when the number of operating condensate booster pumps was reduced to one, CO-P-2C. The remaining condensate booster pump tripped when one of the two operating condensate pumps was secured. Suction to the main feedwater pumps was severely reduced and produced a loss of feedwater (LOFW) event and caused RCS pressure to rise and RPS to actuate on high pressure. Emergency feedwater (EFW) automatically actuated on low steam generator level (<10"). This LER is being submitted pursuant to the requirements of 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(2)(iv)(B).
289 | 2892012005 | 2012-09-20 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Three Mile Isl 1 | P | BW | PO | 100 | On September 20, 2012, Reactor Coolant Pump RC-P-1C at Three Mile Island (TMI) Unit 1 tripped on an apparent differential overcurrent condition 55 seconds after Vital Bus C was secured in support of inverter maintenance. An automatic runback was initiated, but the Reactor Protection System (RPS) actuated on flux to flow imbalance and the reactor tripped at 14:17:34. The RC-P-1C trip was attributed to the differential overcurrent condition due to a differential overcurrent relay (ITH 87 relay) for the RC-P-1C, "C" phase operational indicator being flagged. Complex troubleshooting was performed with an emphasis on an RC-P-1C Motor or RC-P-1C\87 Differential Relay failure as the probable cause; however, the troubleshooting did not reveal a definitive cause of the initiating RC-P-1C trip. An operational decision evaluation was performed to assess plant restart without identifying the cause of the RC-P-1C trip during the complex troubleshooting. A subsequent investigation was performed to determine why RC-P-1C tripped but could not determine a definitive root cause. The most likely causes were addressed by the replacement of the relay, adjusting the trip setpoint, and eliminating this type of vital bus outage at power. This LER is being submitted pursuant to the requirements of 10 CFR 50.73 (a)(2)(iv)(A).
293 | 2931989011 | 1989-03-04 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Pilgrim | B | GE | PO | 10 | On March 4, 1989 at 1749 hours, an automatic actuation of a portion of the Primary Containment Isolation Control System (PCIS) and the Reactor Protection System (RPS) occurred during Turbine-Generator (T-G) coastdown. Previously, the T-G was manually tripped due to vibration indications of two bearings. The PCIS actuation included the automatic closing of the Main Steam Isolation Valves (MSIVs). The RPS actuation and reactor scram occurred as designed because the MSIVs were closing.<br /><br /> The PCIS actuation occurred because the Main Steam System/Reactor Vessel (RV) low pressure trip setpoint (900 psig) was reached while the reactor mode selector switch was in the RUN position. The pressure decrease was due to the automatic closing and re-opening of the Turbine Bypass Valves that occurred because of a bypass valves vacuum trip and an unexplained reset of the vacuum trip. The cause for the vacuum trip and reset of the trip could not be determined during extensive investigation. Subsequent controlled testing, attempting to duplicate the March 4, 1989 conditions, was performed with satisfactory results. Unrelated to the cause for the event was the failure (spurious upscale trip) of a differential pressure transmitter (Rosemount Incorporated model 1153 DB7RCN0012) that was replaced and sent to the manufacturer for examination.<br /><br /> This event occurred when the reactor power level was 10 percent. The control rods inserted automatically. The RV water temperature was 537 degrees Fahrenheit and the RV pressure was 930 psig just prior to the event. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the health and safety of the public.
293 | 2931989015 | 1989-05-03 | QP5 | Excessive Feedwater Flow | [45 empty] | Pilgrim | B | GE | PO | 24 | On May 3, 1989 at 0326 hours, a high Reactor Vessel (RV) water level occurred that resulted in an automatic Turbine trip, Generator trip, and reactor scram at 24 percent reactor power. The event included a designed automatic transfer of the power source for the 4160 VAC Auxiliary Power Distribution System (APDS). During the event one inboard Main Steam isolation valve (MSIV) and four Sampling System isolation valves closed automatically. The high RV water level was primarily caused while troubleshooting the actuator controls of a Feedwater System regulating valve. The Sampling System isolation valves closed because of a transient voltage decrease (APDS transfer) that de-energized the 120 VAC coils of related relays. A random failure of the DC pilot solenoid coil (125 VDC) for the MSIV, together with the effects of the APDS transfer to the MSIV's AC pilot solenoid control relay, caused the MSIV to close.<br /><br /> Significant corrective actions taken include restricted use of the troubleshooting procedure, replacement of some actuator components for both regulating valves, replacement of the failed DC pilot solenoid assembly, and adjustment of the coil drop out voltage (or coil replacement) for appropriate control relays. The DC pilot solenoid assembly (model 6910-020) was examined by the manufacturer (Automatic Valve Corporation). <br /><br /> This event occurred with the reactor mode selector switch in the RUN position with the Feedwater System in single element (RV water level) control. This report is submitted per 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
293 | 2931989023 | 1989-07-18 | QL7 | Degraded condenser vacuum | [45 empty] | Pilgrim | B | GE | PO | 35 | On July 18, 1989 at 1038 hours, a manually initiated Reactor Protection System (RPS) scram signal and reactor scram occurred. The scram signal resulted in an automatic sequence of expected designed responses that included a Turbine-Generator trip, automatic opening of two 345 KV switchyard air circuit breakers, and an automatic transfer of station electrical loads. <br /><br /> The direct cause for the scram was the deliberate movement of the reactor mode selector switch (RMSS) from the RUN position while at 35 percent reactor power. This conservative action was taken due to decreasing Main Condenser vacuum. The primary cause for the decreasing vacuum was attributed to an inadequacy in the approved procedure that was being used to reconfigure the steam jet air ejectors of the Main Condenser Gas Removal System. <br /><br /> Corrective actions taken included the following: revision of the procedure to include specific steps for interchanging a steam jet air ejector(s) during operation, and cleaning the saltwater portions of the Circulating Water System to remove macro-fouling due to marine organisms. The unit was returned to commercial service on July 26, 1989 at 0936 hours. <br /><br /> This event occurred when the Reactor Vessel (RV) pressure was 980 psig and the RV water temperature was 520 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
293 | 2931989026 | 1989-08-30 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Pilgrim | B | GE | PO | 65 | On August 30, 1989 at 1917 hours, an automatic Reactor Protection System (RPS) scram signal and reactor scram occurred while at 65 percent reactor power. As expected, the scram signal resulted in an automatic sequence of designed responses that included a Turbine-Generator trip, automatic opening of two 345KV switchyard air circuit breakers, and an automatic transfer of station electrical loads. <br /><br /> The direct cause of the scram signal was high Reactor Vessel/Main Steam System pressure of 1069 psig that occurred as a result of an automatic Turbine runback. The Turbine runback was caused by the failure of a nonsafety-related 24KV potential transformer (PT) in conjunction with a nonsafety-related voltage balance relay wired in accordance with an approved architect-engineer (Bechtel) drawing that contained an error since original construction (c. 1971). The PT was manufactured by the Westinghouse Electric Corporation, style EED2553, serial number 70F3376. The cause of the PT failure was a manufacturing defect consisting of a large void within the PT potting (insulating) compound. The PT was replaced, the drawing error was corrected, and the voltage balance relay was rewired in accordance with the revised drawing. The procedure used to functionally test the voltage balance relay was strengthened. Applicable portions of the station electrical system were tested and/or evaluated for impact of overvoltage with satisfactory results. <br /><br /> This event occurred with the reactor mode selector switch in the RUN position. The initial Reactor Vessel pressure was 9 0 psig. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the public health and safety.
293 | 2931989038 | 1989-12-08 | QR8 | Spurious Reactor Trip | [45 empty] | Pilgrim | B | GE | PO | 95 | On December 8, 1989 at 0308 hours, an unplanned automatic Reactor Protection System (RPS) scram signal and reactor scram occurred at 95 percent reactor power. The scram signal resulted in responses that included a Turbine-Generator trip. <br /><br /> The direct cause for the scram signal was a (false) low Reactor Vessel (RV) water level signal that occurred while returning a local RV water level indicator (differential pressure type) to service following a satisfactory calibration performed by a qualified technician. The cause for the event was a minor hydraulic transient that occurred while carefully and slowly opening a low side (active leg) needle type manifold valve in accordance with the approved procedure. The level indicator shares sensing lines common to adjacent RPS level transmitters. Corrective actions taken included the satisfactory calibration of the local level indicator(s) while shutdown on December 8, 1989. Corrective actions being explored are improvements for calibrating the local level indicators including possible change of the manifold valve handle(s) or replacement of the related needle type manifold valves with metering type valves. The calibration procedure is being revised to be performed while shutdown. <br /><br /> This event occurred during power operation with the reactor mode selector switch in the RUN position. The RV pressure was 1027 psig with the RV water temperature at 547 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
293 | 2931990008 | 1990-05-13 | QR5 | Turbine Trip | [45 empty] | Pilgrim | B | GE | PO | 100 | On May 13, 1990 at 1603 hours, an automatic scram resulting from a load rejection occurred while at 100 percent reactor power. The load rejection included a trip of the Generator Field Breaker, actuation of the Turbine mechanical hydraulic control speed governor, closure of the four Turbine Control Valves and opening of the three Bypass Valves, and the brief actuation of the Main Steam/Target Rock two-stage relief valves at approximately 1100 psig (low end of the 1115 psig setpoint range including tolerance).<br /><br /> The load rejection was caused by a momentary fault on the offsite 345 KV transmission system. The Generator's loss-of-field relay (240) detected the fault and immediately tripped the Generator without an expected (inherent) 15 cycle time delay because one of it's components, the telephone relay ('X') coil, was defective. The relay (240) was last calibrated and functionally tested on October 26, 1989. At that time, the operation of the ('X') coil was tested in accordance with the vendor manual. The relay's time delay was built-in and not adjustable, and was not required to be timed. The relay was installed during plant construction (c. 1972). The cause for the open coil is being investigated but is believed to be random or age related failure. The relay is the only one of its type (Westinghouse type KLF-1) installed at Pilgrim Station and was replaced with another KLF-1 relay having an adjustable time delay. The (240) relay's calibration sheet was revised to include a calibration of the adjustable time delay. <br /><br /> This event occurred with the reactor mode selector switch in the RUN position. The Reactor Vessel (RV) pressure was initially at 1035 psig with RV water temperature at 548 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
293 | 2931990013 | 1990-09-02 | QP5 | Excessive Feedwater Flow | [45 empty] | Pilgrim | B | GE | PO | 60 | On September 2, 1990 at 2233 hours, an unplanned manual reactor scram was initiated with reactor power at 60 percent. The operators manually scrammed the reactor due to difficulties experienced in controlling reactor vessel (RV) water level. A fuse blew in a feedwater control circuit power supply causing both Feedwater Regulating Valves (FRVs) to lockup without control room indication. A modification was implemented while shutdown which improves the reliability of the power supply and provides Control Room indication of a FRV lockup from a loss of control power. <br /><br /> After the shutdown other equipment problems were experienced. The startup FRV failed open due to air leaks and failure of its air booster relay that was later replaced. The Reactor Core Isolation Cooling System (RCICS) was declared inoperable due to the turbine tripping on three start attempts. The turbine trips were attributed to an improper manual start sequence specified in the RCICS operating procedure and/or looseness of the mechanical overspeed trip linkage. The RCICS operating procedure was revised and repairs were made to the mechanical overspeed trip linkage. The RCICS suction piping experienced a pressure transient due to the injection check valve not fully seating after the second start attempt. The check valve was modified to prevent recurrence. The High Pressure Coolant Injection System (HPCIS) was operable; however, the turbine oversped and automatically reset on both starts. An exact cause of the overspeed trips could not be determined; however, corrective actions were taken for probable causes and the HPCIS was tested satisfactorily. A Residual Heat Removal System/Shutdown Cooling suction isolation valve would not open normally. The cause was contact failure on the valve's seal-in relay (General Electric type CR120A) that was replaced. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
293 | 2931992016 | 1992-12-13 | QR5 | Turbine Trip | [45 empty] | Pilgrim | B | GE | PO | 48 | On December 13, 1992, at 1723 hours, an automatic scram resulting from a load rejection occurred while at 48 percent reactor power. The load rejection included a trip of the Main Turbine, closure of the Turbine Control Valves and opening of the Bypass Valves, and automatic transfer of the Auxiliary Power Distribution System.<br /><br /> The load rejection was most likely caused by 345 KV switchyard flashovers due to salt deposited during a severe coastal storm. Corrective actions taken included a washdown of the switchyard after the storm winds subsided and repairing of damaged insulation on a conductor from the current transformer. The unit returned to commercial service on December 18, 1992, at 1350 hours. <br /><br /> This event occurred during power operation while at 48 percent reactor power. The reactor mode selector switch in the RUN position. The Reactor Vessel (RV) pressure was 955 psig with RV water temperature at 540 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
293 | 2931992018 | 1992-12-20 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Pilgrim | B | GE | PO | 75 | On December 20, 1992, at 0233 hours, an automatic Reactor Protection System (RPS) scram signal and scram, together with the closing of the Main Steam Isolation Valves, occurred while at 75 percent reactor power. Automatic responses included a transfer of electrical loads, Turbine-Generator trip, and closing of applicable isolation valves. <br /><br /> The root cause of the event was utility non-licensed Instrumentation and Control technician error. The technician incorrectly adjusted the trip settings of the Main Steam Radiation Monitors during power ascension on December 19, 1992. Hydrogen injection began on December 20, 1992, and the resulting increase in main steam radiation exceeded the trip settings that were too low for hydrogen injection radiation levels. Contributing to the error was the format of the settings identified in the trip setting procedure. The required settings were identified in a whole number format (e.g., 14,900) while the radiation monitors display the settings in a scientific notation format (e.g., 1.49E4). Corrective action taken included revising the procedure to identify the trip settings in scientific notation format and improved verification. The unit returned to commercial service on December 23, 1992, at 0622 hours. This event occurred during power operation with the reactor mode selector switch in the RUN position. The Reactor Vessel (RV) pressure was 1005 psig with the RV water temperature at approximately 545 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and this event posed no threat to the public health and safety.
293 | 2931993004 | 1993-03-13 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Pilgrim | B | GE | PO | 100 | On March 13, 1993 at 1628 hours, an automatic scram resulting from a load rejection occurred during a severe coastal storm while at 100 percent reactor power. The load rejection included a trip of the Turbine-Generator, transfer of station electrical loads, and brief opening of one Main Steam relief valve. The 120 VAC safeguards Buses 'A' and 'B' de-energized. The Reactor Vessel (RV) pressure-temperature (P-T) limit was exceeded during subsequent cooldown. <br /><br /> The load rejection was caused by 345 KV switchyard insulator flashovers due to wind packed snow deposited during blizzard conditions. Corrective actions taken included an inspection of the switchyard and insulators. The cause of exceeding the P-T limit was a RV pressure increase that occurred after the HPCI System, that was being used for RV pressure control, was removed from service due to high Suppression Pool water level. The P-T condition was evaluated. The evaluation concluded the RV did not exceed the allowable limits of ASME sections III and XI. The cause of the de-energized safeguards buses was trip settings that were too low. The trip settings were subsequently increased. Other corrective or preventive actions were taken or are planned. The unit returned to commercial service at 0459 hours on March 17, 1993. <br /><br /> This event occurred near the end of the fuel cycle during power operation with the reactor mode selector switch in the RUN position. The RV pressure was 1025 psig with RV water temperature at 525 degrees Fahrenheit.
293 | 2931993014 | 1993-05-31 | QR5 | Turbine Trip | [45 empty] | Pilgrim | B | GE | PO | 24 | On May 31, 1993, at 1921 hours, an automatic scram occurred while at 24 percent reactor power. The event included a trip of the Turbine-Generator and transfer of the Auxiliary Power Distribution System. The scram was the result of the closing of the Turbine Stop Valves while the Turbine first stage pressure was greater than the scram bypass pressure. The Turbine Stop Valves were closing as a result of the Turbine trip. The Turbine-Generator trip was initiated by the operation of a Unit Auxiliary Transformer differential relay. <br /><br /> The operation of the relay was investigated for cause. The investigation included relay calibration, differential circuit wiring checks, Unit Auxiliary Transformer insulation resistance testing and oil sample analysis, cable insulation resistance testing, breaker testing, and performance of a test approximating the conditions existing at the time of the event. The investigation could not determine the cause for the operation of the relay. The unit returned to commercial service on June 3, 1993.<br /><br /> This event occurred during power ascension from a refueling outage with the reactor mode selector switch in the RUN position. The Reactor Vessel (RV) pressure was 940 psig with RV water temperature at 540 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the public health and safety.
293 | 2931993022 | 1993-09-10 | B1 | Loss of Offsite Power (LOOP) |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Pilgrim | B | GE | PO | 100 | On September 10, 1993, at 1134 hours, a simultaneous loss of preferred offsite power and an automatic scram resulting from a load rejection occurred during a fast moving electrical storm while at 100 percent reactor power. The loss of preferred offsite power included an automatic start of Emergency Diesel Generator (EDG) 'B'. EDG 'A', in service for surveillance testing and loaded on its safety related bus, remained in service. The load rejection included a trip of the Turbine-Generator and opening of three Main Steam relief valves. <br /><br /> The loss of preferred offsite power and load rejection was caused by separate lightning strikes that caused the opening of switchyard breakers. One of the 345 KV switchyard air type circuit breakers (ACB 105) was struck by lightning. Corrective actions taken included a walkdown of the switchyard. Except for the replacement of an ACB 105 pressure reducing valve solenoid and surge suppression circuit, no corrective action was necessary as a result of the walkdown. The unit returned to commercial service at 0718 hours on September 12, 1993. <br /><br /> This event occurred during power operation with the reactor mode selector switch in the RUN position. The RV pressure was 1035 psig with RV water temperature at 550 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). This event posed no threat to the public health and safety.
293 | 2931994005 | 1994-08-29 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Pilgrim | B | GE | PO | 100 | On August 29, 1994, at 0732 hours, an automatic scram occurred while at 100 percent reactor power. The scram was the result of a load rejection that was automatically initiated by a Main Generator faulted condition. Responses included automatic transfer of the plant's auxiliary power system and the brief, automatic opening of three of the Main Steam relief valves for pressure relief. The Reactor Core Isolation Cooling System was operated manually for Reactor Vessel level control for approximately three minutes. Two in-series secondary containment dampers did not fully close (i.e., approximately 90-95 percent closed) as designed but the secondary containment design basis was evaluated as being met with the dampers in the as-found position. <br /><br /> The cause of the main generator fault was the partial blockage of cooling water through one of the generator stator bars that was caused by foreign material, i.e, pieces of gasket, inadvertently introduced into the main generator stator cooling water system oulet header. Corrective action taken included completely rewinding the generator stator, completely rewinding the generator rotor, and inspecting and flushing the generator stator cooling water system. The cause of the two dampers not fully closing was an accumulation of damper lubricant and dirt along the dampers' side seals and a buildup of degraded lubrication in the dampers' actuators. Corrective action taken included cleaning the dampers, modifying the preventive maintenance program to inspect the secondary containment dampers more frequently, and to periodically rebuild the dampers' actuators. The event posed no threat to public health and safety.
293 | 2931995003 | 1995-03-24 | QR6 | Manual Reactor Trip | [45 empty] | Pilgrim | B | GE | PO | 60 | On March 24, 1995 at 0750 hours, a manually initiated Reactor Protection System (RPS) scram signal and scram occurred while at 60 percent reactor power. The signal resulted in an automatic sequence of expected designed responses that included a Turbine-Generator trip and an automatic transfer of station electrical loads. <br /><br /> The direct cause for the scram signal was the deliberate movement of the reactor mode selector switch from the RUN position while at 60 percent reactor power. This action was taken due to increasing Main Generator stator cooling water (SCW) temperature and conductivity, increasing generator stator temperatures, and a generator field ground alarm. The root cause for the event was a failure of the mechanical linkage of the SCW temperature control valve controller. Corrective action planned includes replacement of the temperature control valve controller and linkage. <br /><br /> This event occurred during power operation. The Reactor Vessel (RV) pressure was 982 psig with the RV water temperature at approximately 544 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) and the event posed no threat to the public health and safety.
293 | 2931996005 | 1996-04-19 | QR5 | Turbine Trip | [45 empty] | Pilgrim | B | GE | PO | 22 | On April 19, 1996, at 1016 hours, an automatic scram occurred at 22 percent reactor power while reducing power for a planned outage. The scram was initiated by vibration in the low pressure portion of the main turbine-generator. At 1018 hours, a high water level isolation occurred during scram recovery. <br /><br /> The cause of the scram was vibration in a portion of the new low pressure turbine. The low pressure turbine rotors have a monoblock design. The clearances between the new low pressure turbine rotor blades and turbine casing diaphragm are smaller than the previous low pressure turbine. The smaller clearances introduced different rub characteristics than the previous low pressure turbine. The high water level isolation was caused, in part, by decreasing reactor pressure that was due to a leak in a turbine steam sealing system valve downstream of the main steam isolation valves. <br /><br /> Scram-related corrective action taken included increasing the vibration trip setting for the low pressure portion of the turbine and revision of related procedures. The high water level isolation-related corrective actions included valve repair. <br /><br /> This scram occurred with the reactor mode selector switch in the RUN position. The reactor vessel pressure was 944 psig with the reactor water temperature at the saturation temperature for the reactor pressure. The events posed no threat to the public health and safety.
293 | 2931997003 | 1997-02-15 | QP5 | Excessive Feedwater Flow | [45 empty] | Pilgrim | B | GE | PO | 20 | On February 15, 1997, at 0038 hours, a manual scram was initiated at approximately 20 percent reactor power. The scram was intentionally initiated as a result of increasing reactor water level experienced while reducing power for the scheduled 1997 refueling outage. The scram resulted in the insertion of the control rods, transfer of the source of power to the auxiliary power distribution system, and trip of the turbine-generator. <br /><br /> The direct cause was greater than normal feedwater flow past the nonsafety-related feedwater system train 'A' and 'B' regulating valves at low steaming rates. Degradation of the actuator of FV-642A in conjunction with the inability of the valve's plug to travel to its lower seat was the primary root cause of the event. Corrective action taken included disassembly and repair of FV-642A and its actuator and positioner. The positioner of FV-642B was repaired and calibrated. The preventive maintenance program was modified for the train 'A' and 'B' regulating valves and startup feedwater regulating valve. <br /><br /> The scram was initiated when the reactor mode selector switch was moved from the RUN position to the SHUTDOWN position. The reactor vessel pressure was 954 psig with the reactor water temperature at the saturation temperature for the reactor pressure. The event posed no threat to public health and safety.
293 | 2931997026 | 1997-12-06 | QP5 | Excessive Feedwater Flow | [45 empty] | Pilgrim | B | GE | PO | 75 | On December 6, 1997, at 0907 hours, an automatic scram occurred at approximately 75 percent reactor power. The scram was initiated as a result of a turbine trip due to high reactor water level (>45 inches) experienced during power ascension following an outage. The turbine trip/reactor scram resulted in the insertion of the control rods and transfer of power to the startup transformer. <br /><br /> The cause of the scram was the failure of the "A" feedwater regulating valve (FRV) in the full open position due to the misalignment of the valve clip inside the pilot valve assembly of the positioner. Corrective action taken included replacing the valve positioner and performing calibration adjustments. <br /><br /> The scram occurred while the reactor mode selector switch was in the RUN position. The reactor vessel pressure was approximately 1004 psig with the reactor water temperature at the saturation temperature for the reactor pressure. The event posed no threat to public health and safety.
293 | 2931999008 | 1999-08-05 | QR5 | Turbine Trip | [45 empty] | Pilgrim | B | GE | PO | 100 | On August 5, 1999, an automatic scram occurred while at 100 percent power. The scram resulted from a turbine trip initiated by a high water level in turbine steam moisture separator tank 'A'. Automatic responses included the brief opening of the main steam relief valves for pressure relief. The cause of the trip was a malfunction of moisture separator drain tank 'A' drain valve controller and incorrect setting of the drain tank's dump valve controller. The root cause determined that a lack of knowledge in understanding how this type of moisture separator level controller operated existed in the Engineering and Maintenance disciplines. This lack of knowledge led to inappropriate changes to the associated calibration procedure and improper field adjustments to the controllers themselves resulting in the high water level condition. Corrective actions taken prior to plant restart included replacement and calibration of the level controllers. Corrective actions taken after plant restart included additional training for the Instrumentation & Calibration Technicians and Engineering Support Personnel and revision to plant procedures dealing with the calibration of controllers. The event posed no threat to public health and safety.
293 | 2931999009 | 1999-09-13 | QL7 | Degraded condenser vacuum | [45 empty] | Pilgrim | B | GE | PO | 27 | On September 13, 1999, at 1825 hours, an unplanned scram was manually initiated while at 27 percent reactor power. This action was taken because of degrading vacuum in the main condenser. The root cause of the event was the failure of the augmented offgas (AOG) system train 'B' condenser level control system in conjunction with AOG air purge flow, that overcame the capacity of the main condenser air ejector system. The AOG system bypass procedure requires the air purge. Corrective actions taken included the cleaning of a plugged level control sensing line, replacement of a level control instrument root valve and level transmitter, and loop calibrations of the AOG train 'B' condenser level control system. Other corrective actions are planned. The event occurred during power operation while at about 27 percent reactor power. The reactor vessel pressure was about 952 psig with the reactor vessel water temperature at the saturation temperature for that pressure. The event posed no threat to public health and safety.
293 | 2932001006 | 2001-08-13 | C2 | Loss of Vital Low Voltage ac Bus (<600 V) |  |  | X | [14 empty] | X | [27 empty] | Pilgrim | B | GE | PO | 49 | On August 13, 2001, during a transient that began at 100 percent power, an automatic scram occurred at 49 percent reactor power. The scram included automatic insertion of the control rods. About 40 minutes after the scram, safety-related reactor water level instrumentation began to trend anomalously from actual water level and caused level instrumentation to be inoperable for approximately 36 minutes. The root cause of the scram was concurrent trip of RPS channels "A" and "B". Channel "A" tripped due to a loss of Bus "A" power resulting from a surveillance procedure error. Channel "B" tripped due to high neutron flux resulting from a trip of both recirculation MG sets/pumps. The root cause of the anomalous water level indication was unique hydraulic conditions that allowed water to drain from reference legs "A" and "B". Corrective action taken included the replacement of a fuse in the recirculation MG set field circuit, and isolating the reference leg backfill system. Corrective action planned includes revising the surveillance procedure, and evaluating options to preclude reference leg water draining. The events posed no threat to public health and safety.
293 | 2932001007 | 2001-12-27 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Pilgrim | B | GE | PO | 53 | On December 27, 2001 at 1321 hours, an automatic Reactor Protection System scram signal and scram occurred during a surveillance test performed while at 100 percent reactor power. The scram resulted in the automatic insertion of all control rods. The direct cause of the scram was an automatic trip of both Recirculation System motor-generator sets that caused decreased core flow resulting in a trip signal from the neutron monitoring system flow control trip reference circuits. The root cause of the scram was an internal failure, during the required surveillance test, of an analog trip system calibrating unit that was not reproducible. Circuit analysis identified the most likely failed component within the unit was an intermittent micro-switch. A failed micro-switch would apply a voltage from the calibrating unit to a selected master trip unit while rotating the same rotary selector switch between channels. Corrective action taken included replacement of the suspect calibrating unit. The event posed no threat to public health and safety.
293 | 2932003001 | 2003-02-21 | QR6 | Manual Reactor Trip | [45 empty] | Pilgrim | B | GE | PO | 22 | On February 21, 2003 an unplanned manual reactor scram was initiated during a controlled shutdown while at 22% reactor power. The resulting scram was the completion of a required shutdown that was initiated as a result of a trip of the recirculation loop 'A' motor-generator (MG) set/pump on February 20, 2003. The direct cause of the shutdown was the trip and lockout of the recirculation loop 'A' MG set/pump that was due to a mechanical-type failure of one of two rotor field slip ring copper studs on the generator portion of the MG set. The root cause was improper installation of the generator collector slip ring assembly in the 1991 timeframe. Corrective action taken included replacement of the loop 'A' MG set generator rotor and inspection and testing of the loop 'B' MG set generator. The manual scram was directed as a result of a runback of the recirculation loop 'B' MG set/pump on February 21, 2003. The root cause of the runback was a difference between the actual total feedwater flow and the conditioned signal sent to the feedwater level control system. Corrective action taken included adjustments to improve the response of the feedwater regulating valves, and tuning the overall gain of the feedwater level control system. The events posed no threat to public health and safety.
293 | 2932003002 | 2003-05-19 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Pilgrim | B | GE | SU | 2 | On May 19, 2003 an unplanned automatic closing of the main steam isolation valves (MSIVs) occurred while at about 2.5% reactor power, during startup from the 2003 refueling outage. The closing of the MSIVs resulted in a designed automatic scram signal and scram. The scram resulted in the insertion of the control rods and consequent isolation signals due to an expected decrease in the reactor water level. The root cause was licensed operator error. In response to an alarm, the operator operated a control switch that opened the turbine steam bypass valves instead of operating a switch to increase the steam pressure setting. The opening of the bypass valves resulted in decreased pressure in the reactor vessel and main steam lines. The pressure decrease resulted in a reactor water level increase that resulted in the closing of the MSIVs per design. Corrective action taken Included an Operations human performance stand down and an INPO Assist visit. Corrective actions planned include coaching the responsible operator in the proper use of human performance tools, and implementation of an Operations Human Performance improvement action plan. The event posed no threat to public health and safety.
293 | 2932003003 | 2003-06-01 | QR5 | Turbine Trip | [45 empty] | Pilgrim | B | GE | PO | 100 | On June 1, 2003 an unplanned automatic scram occurred while at 100% reactor power. The scram was the result of a load rejection. Automatic responses included the insertion of all withdrawn control rods, transfer of the source of electrical power for Pilgrim's 4.16 kV auxiliary power distribution system (APDS), closure of the turbine steam control and stop valves, trip of the turbine, opening of the turbine steam bypass valves, and opening of main steam relief valves for pressure relief. The direct cause of the scram was the automatic closing of the turbine control valves. The direct cause of the event was an electrical fault in the unit auxiliary transformer (UAT) that was powering the APDS at the time of the event. The fault was the result of the failure of a conductor within the low voltage portion of the UAT (X-winding). Corrective actions taken included a temporary alteration for powering the APDS during power operation. Corrective actions planned include the repair or replacement of the unit auxiliary transformer. The event posed no threat to public health and safety.
293 | 2932006001 | 2006-03-13 | QR6 | Manual Reactor Trip | [45 empty] | Pilgrim | B | GE | PO | 43 | On March 13, 2006, at 1808 hours, an unplanned scram was manually initiated while at 43 percent reactor power. This procedurally required action was taken because of high temperature in the Augmented Offgas (AOG) system recombiner. There were no complications encountered during the response to the scram. The root cause of the event was the failure of the controller of a pressure control valve (PCV) that supplies steam dilution flow PCV and steam heating to the recombiners preheater. The failure was due to inadequate preventive maintenance of the controller. Corrective action taken included replacement of the pressure control valve controller and repair of a hand operated valve that enables steam to bypass the pressure control valve. Corrective action planned includes developing preventive maintenance for the AOG pressure controllers, training, and evaluating changes to procedures. The event occurred during power operation. The reactor vessel pressure was about 967 psig with the reactor vessel water temperature at the saturation temperature for that pressure. The event posed no threat to public health and safety.
293 | 2932007005 | 2007-07-10 | QR5 | Turbine Trip | [45 empty] | Pilgrim | B | GE | PO | 50 | On July 10, 2007 at 1954 hours, an automatic scram occurred with the plant operating at approximately 48 percent reactor power. The automatic scram initiated from a valid Reactor Protection System (RPS) signal resulting from fast closure of the turbine steam control valves. The turbine steam control valves closed in response to an unexpected turbine on low vacuum. The low vacuum signal resulted from a calibration error on the low vacuum turbine trip low vacuum trip mechanism (VTS-1). The trip mechanism was calibrated and set incorrectly during the April/May 2007 Refueling Outage. Corrective action taken included calibrating the vacuum pressure trip mechanism. Additional corrective actions planned include training improvements relative to calibrating the turbine vacuum pressure alarm and trip setpoints and procedure enhancements. The automatic scram occurred while the reactor mode selector switch was in the "RUN" position. Reactor vessel pressure was approximately 957 psig. The event occurred during a scheduled thermal backwash of the main condensers. The event posed no threat to public health and safety.
293 | 2932008006 | 2008-12-19 | QR5 | Turbine Trip | [45 empty] | Pilgrim | B | GE | PO | 100 | On December 19, 2008 at 1831 hours during a severe winter storm an automatic reactor scram occurred with the plant operating at 100% power. The automatic scram initiated from a valid Reactor Protection (RPS) Signal resulting from fast closure of the turbine control valves due to actuation of the main transformer bus differential relay (87B/MT). Automatic response from the main transformer protective relay scheme included opening 345 kV circuit breakers ACB-104 and ACB-105; main turbine trip; and fast transfer of 4.16 kV power from the Unit Auxiliary Transformer (UAT) to the Startup transformer (SUT). The 120 V ac safeguards panels (Y3/31 and Y4/41) de-energized after the UAT to SUT power transfer. The direct cause of the event was an electrical fault resulting from conductive snow and ice build-up on the nonconductive porcelain surfaces of the ACB-105 "A" phase generator side bushing. The direct cause of power loss to the safeguards panels was high in-rush current and transformer (X55) input breaker trip to Y3/31; and transformer (X56) tap control board malfunction to Y4/41. Corrective actions were taken to evaluate and assess switchyard circuit breaker and main transformer equipment damage. The bushing on the "A" phase generator side feed on ACB-105 was replaced. The input breaker to X55 and the tap control board to X56 were replaced. Corrective actions planned include analysis of equipment design modifications to reduce flashover and ground fault events in the switchyard. In addition, the input breakers to X55 and X56 will be modified and replaced, and a vendor evaluation of the X56 tap control board will be completed. The event posed no threat to public health and safety.
293 | 2932011003 | 2011-05-10 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Pilgrim | B | GE | SU | 2 | On May 10, 2011, during STARTUP Mode with reactor thermal power at approximately 1.7 percent, Pilgrim Nuclear Power Station(PNPS) experienced an automatic reactor scram while raising reactor temperature and pressure. The reactor scrammed on intermediate range monitor (IRM) hi-hi flux on both reactor protection system channels. Prior to the scram, operators took the reactor critical, reached the point of adding heat, and established a heatup rate. During the heatup, operators observed a high heatup rate and in response, the shift manager directed operators to insert control rods to reduce the heatup rate. The number of rods or number of notches to insert was not specified. Power began to lower as expected; however, operators did not recognize that inserting control rods to reduce heatup rate with rising moderator temperature caused the reactor to become subcritical. After achieving a temperature change from the power reduction, operators withdrew the same control rods before evaluating the core condition. The resultant reactor response was a faster power ascension rate than expected, which led to an automatic intermediate-range high-flux reactor trip. All systems operated as expected, in accordance with design. The root cause of this event was determined to be the failure to adhere to established standards and expectations due to a lack of consistent supervisory and management enforcement. Investigation into the event revealed several examples of inconsistent enforcement of administrative procedure requirements and management expectations for command and control, roles and responsibilities, reactivity manipulations, clear communications, proper briefings, and proper turnovers. Numerous corrective actions have been taken or are planned to reinforce standards and retrain crew members on the fundamentals of criticality and heating range operation. This event had no impact on the health and/ or safety of the public.
293 | 2932012002 | 2012-05-22 | QL7 | Degraded condenser vacuum | [45 empty] | Pilgrim | B | GE | PO | 32 | On Tuesday, May 22, 2012 at 1311 hours, with the reactor at approximately 35% core thermal power, during a planned power reduction to support thermal backwash of the main condenser, a manual reactor scram was inserted due to degrading main condenser vacuum. The direct cause of the degraded vacuum is attributed to loss of the Steam Jet Air Ejector (SJAE) inter-condenser loop seal due to a partially open SJAE steam supply valve (1-HO-163). The root cause of the 1-HO-163 valve being partially open was due to inadequate processing of an emergent work order related to the reach rod position indication versus the actual valve position. Following the reactor scram, all rods were verified to be fully inserted and the Primary Containment Isolation System Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. Standby Gas Treatment System Train 'B,' which is designed to shutdown 65 seconds after the Group II signal is received if the Standby Gas Treatment Train 'A' is inservice, continued to operate until manually secured. With this exception all other plant systems responded as designed. This event had no impact on the health and/or safety of the public because emergency core cooling systems were operable and available to perform their required safety functions.
293 | 2932013001 | 2013-01-10 | QR6 | Manual Reactor Trip | [45 empty] | Pilgrim | B | GE | PO | 100 | On Thursday, January 10, 2013 at 1534 hour [EST], with the reactor at 100% core thermal power, both reactor recirculation pumps unexpectedly tripped and a manual reactor scram was inserted as required by station procedures. Following the reactor scram, all rods were verified to be fully inserted and the Primary Containment Isolation System Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. All other plant systems responded as designed. The scram was uncomplicated and decay heat was released to the main condenser via the turbine by-pass valves. The cause of the two reactor recirculation pumps tripping was due to the inadvertent seal-in of a relay (pump trip interlock) in the Low Pressure Coolant Injection (LPCI) Loop Select Logic circuitry within the Residual Heat Removal (RHR) System during surveillance testing. When the logic was reset at completion of testing, a normally open relay contact (which was inadvertently closed) interlocked with the recirculation pumps circuit, sent a trip signal to their drive motor breakers. Corrective action has been taken to revise the subject surveillance procedure with steps to reinstall relay covers and added a verifier to observe relay status/ state prior to resetting the relay logic circuit. This event had no impact on the health and/or safety of the public.
293 | 2932013003 | 2013-02-08 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Pilgrim | B | GE | PO | 85 | On Friday February 8, 2013, at 2117 hours with the reactor initially at 85% core thermal power, Pilgrim Nuclear Power Station (PNPS) experienced a loss of off-site power (LOOP) resulting in a load reject and a reactor scram. All rods fully inserted and the Emergency Diesel Generators automatically started and powered safety-related buses A5 and A6. All other safety systems functioned as required. The plant stabilized in Hot Shutdown. At the time of the event a significant winter storm (Nemo) was buffeting Southern New England. At 2200 hours PNPS in conjunction with the local grid operator determined off-site power sources were not reliable and efforts to restore off-site power were temporarily suspended. At 2200 hours, PNPS declared a Notification of Unusual Event. On February 10, at 1055 hours, one of two off-site power supplies was restored, all safety buses were powered from the startup transformer and the Unusual Event was exited. Later on February 10, at 1402 hours with the plant in Cold Shutdown, ice bridging on a startup transformer insulator caused its 345 KV supply breaker to open resulting in a second LOOP. Again the EDG's started and powered safety-related buses. All other safety systems functioned as required. Shutdown cooling was restored at 1426 hours. On February 10, at 2020 hours, this occurrence was reported to the USNRC as documented in EN# 48739.<br><br> The severe winter storm which caused extensive generalized geographical damage to the electrical distribution network was root cause of the LOOP events.<br><br> These events posed no threat to public health and safety.
293 | 2932013008 | 2013-08-22 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Pilgrim | B | GE | PO | 100 | On Thursday, August 22, 2013 at 0755 [EDT] with the reactor critical at 98% core thermal power (CTP), and the mode switch in RUN, the Pilgrim Nuclear Power Station (PNPS) was manually scrammed due to lowering reactor water level resulting from a trip of the reactor feed pumps. The reactor feed pumps tripped due to a loss of power to the pump seal cooling water flow switch relays and resultant automatic actuation of the feed pump trip circuit.<br /><br /> The direct cause of the reactor feed pump trip was an automatic actuation of the feed pump trip circuitry. The feed pump trip circuits actuated as designed in response to a loss of power to the pump seal cooling water flow switch relays. The seal cooling water flow switch relays lost power as a result of a 120V AC breaker trip resulting from a short-to-ground fault in the associated circuits fed by the breaker. Corrective action was taken to repair the ground fault in the associated circuits fed by the 120V AC breaker and to revise reactor feed pump trip circuit design to remove the loss of seal water trip function.
293 | 2932013009 | 2013-10-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Pilgrim | B | GE | PO | 100 | On Monday October 14, 2013 at 2121 hours [EDT], with the reactor critical at 100% core thermal power, the mode switch in RUN, and offsite power 345KV Line 342 out of service for a scheduled upgrade, a loss of offsite power (LOOP) occurred due to the loss of the second 345KV Line 355. All control rods fully inserted, main steam isolation valves closed on the loss of power to the reactor protection system, and the emergency diesel generators automatically started supplying power to both 4160V safety buses. Following the scram, reactor water level lowered to +12 inches initiating the Primary Containment Isolation System (Group II, Reactor Building Isolation System (RBIS); and Group VI - Reactor Water Cleanup System) automatically per design. A plant cool down commenced with reactor water level being maintained in the normal post-scram band of +12 inches to +45 inches utilizing the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems.<br /><br /> The cause of Line 355 loss was due to a failure of an offsite substation tower support. The offsite tower was repaired and Line 355 was energized at 2023 hours on October 15, 2013.<br /><br /> These events posed no threat to public health and safety.
293 | 2932015001 | 2015-01-27 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Pilgrim | B | GE | PO | 52 | On Tuesday January 27, 2015, at 0402 hours, while in the process of lowering reactor power, with the reactor in the RUN mode at 52 percent core thermal power, Pilgrim Nuclear Power Station (PNPS) experienced a loss of 345KV power resulting in a load reject and an automatic reactor scram. The loss of 345KV power was due to faults from flashovers in the PNPS switchyard. All control rods fully inserted. The Emergency Diesel Generators had been previously started and were powering safety-related buses A5 and A6. The plant stabilized in Hot Shutdown. At the time of the event a significant winter storm (Juno) was buffeting Southern New England.<br /><br /> The root cause of the event is that the design of the PNPS switchyard does not prevent flashover when impacted by certain weather conditions experienced during severe winter storms. A modification of the switchyard is planned to address the susceptibility of the PNPS switchyard to flashovers during severe winter storms.<br /><br /> This event posed no threat to public health and safety.
293 | 2932015005 | 2015-05-22 | QL7 | Degraded condenser vacuum | [45 empty] | Pilgrim | B | GE | SU | 4 | On Friday, May 22, 2015 at 10:02 hours EDT, with the Reactor Mode Select Switch in the Start-Up position and the reactor at approximately 4 Percent core thermal power, a manual reactor scram was inserted due to degrading Main Condenser vacuum due to high air in-leakage from a crack on a feedwater heater expansion bellows and plant conditions caused by extended operation on the Main Turbine bypass valves. <br /><br /> Following the reactor scram, all rods were verified to be fully inserted and no Emergency Operating Procedure entry conditions existed. All plant systems responded as designed. <br /><br /> The cause of the event is that the design limitations of the Offgas System were exceeded by the unusual combination of plant conditions resulting in degrading main condenser vacuum. Corrective action was taken to mitigate the air in-leakage from the crack on a feedwater heater expansion bellows. In addition, guidance and limitations have been provided for operation with elevated air in-leakage conditions.<br /><br /> This event posed no threat to public health and safety.
293 | 2932015007 | 2015-08-22 | QL5 | Partial Closure of MSIVs | [45 empty] | Pilgrim | B | GE | PO | 100 | On Saturday, August 22, 2015, at 1628 [EDT], with the reactor at 100% core thermal power the Pilgrim Nuclear Power Station experienced an automatic reactor scram due to Average Power Range Monitor High Flux signal from the rapid closure of one main steam isolation valve (MSIV). All plant systems responded as designed. <br /><br /> The Root Cause of this event is inadequate worker practices resulting in an excessive load being applied to the unistrut enclosed pneumatic line (during or prior to 2001) causing it to lay on a Main Steam Line subject to vibration. The excessive load caused an initiating crack in the nipple threads that over time resulted in a shear of the line. <br /><br /> The pneumatic supply line nipple was replaced and the line was re-supported. <br /><br /> This event posed no threat to public health and safety.
293 | 2932016007 | 2016-09-06 | QP5 | Excessive Feedwater Flow | [45 empty] | Pilgrim | B | GE | PO | 91 | On September 6, 2016 at 0827 EDT, with the reactor at approximately 91 percent core thermal power, operators manually scrammed the reactor when the benchmark for a reactor water level of +42 inches increasing was reached. Following the scram, all rods fully inserted and the Average Power Range Monitors were downscale, indicating the reactor was shut down. The Main Steam Isolation Valves closed on a Primary Containment Isolation Signal Group 1 isolation and were subsequently reopened to maintain reactor pressure.<br /><br /> The reason for the increasing reactor water level was the malfunction of Feedwater Regulating Valve 'A' (FRV 'A'). The reactor operator at the control panel placed FRV 'A' in remote manual in an attempt to stabilize the feedwater flow oscillations. This had no effect on the performance of FRV 'A'. The operators experienced feedwater flow oscillations from FRV 'A' that resulted in reactor water level high and low level alarms on the control panel. Shortly after this, the benchmark reactor water level of +42 inches increasing was reached and operators manually scrammed the reactor. <br /><br /> There was no impact to public health and safety.
293 | 2932018001 | 2018-01-04 | QR6 | Manual Reactor Trip | [45 empty] | Pilgrim | B | GE | PO | 81 | On January 4, 2018 at approximately 1400 EST, with the reactor at approximately 100 percent core thermal power, Air Circuit Breakers 103 and 104 automatically opened due to a fault condition on 345KV Line 342. The sustained loss of one incoming 345KV line due to weather related conditions requires a plant shut down. While assessing plant conditions, the operating crew reduced reactor power to approximately 81 percent core thermal power. Following these actions, it was determined that the loss of 345KV Line 342 was due to weather and a manual scram was initiated at 1409 hours. <br /><br /> This event is reportable per the requirements of Title 10 Code of Federal Regulations 50.73(a)(2)(iv)(A) due to a manual actuation of the Reactor Protection System and automatic isolation signals affecting containment isolation valves in more than one system. <br /><br /> There was no impact to public health and safety.
293 | 2932018006 | 2018-10-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Pilgrim | B | GE | PO | 100 | On October 5, 2018 at 1209 hours, with the reactor operating at 100% power, an automatic reactor scram occurred due to a reactor water level perturbation and receipt of a low reactor water level Reactor Protection System signal caused by a malfunction of the 'A' Feedwater Regulating Valve (FRV). <br /><br /> The Failure Modes Analysis attributed the probable cause to be an intermittent signal in the stepper motor and encoder control loop, which is the system that manipulates the pneumatic spool to operate the FRV's Double- Acting Piston Actuator. The as-found condition of the stepper motor and encoder electrical connectors showed that several pin sockets were not properly seated within their connector housings. Proper seating of the FRV stepper motor and encoder electrical connections is critical in ensuring error free operation of the FRVs. <br /><br /> There were no radiological releases due to this event. All control rods inserted fully. All other plant systems responded as designed. This event had no impact on the health and/or safety of the public. <br /><br /> This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A).
293 | 2932019004 | 2019-05-17 | QL7 | Degraded condenser vacuum | [45 empty] | Pilgrim | B | GE | PO | 70 | On Friday, May 17, 2019 at 2303 [EDT], with the reactor at approximately 70% core thermal power, Pilgrim Nuclear Power Station initiated a manual reactor scram due to degrading condenser vacuum as a result of the trip of Seawater Pump B. Investigation into the cause identified the Seawater Pump B breaker ground sensing relay in the tripped state. <br /><br /> Following the Seawater Pump B trip and reactor scram, Main Condenser parameters responded as expected to a loss of seawater pump transient, no anomalies were noted. There were no radiological releases due to this event. All control rods inserted fully. All other plant systems responded as designed. <br /><br /> This event had no impact on the health and/or safety of the public. <br /><br /> This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A).
295 | 2951988005 | 1988-02-24 | QP5 | Excessive Feedwater Flow | [45 empty] | Zion 1 | P | WE | PO | 49 | At approximately 1000 hours on February 24, 1988, Zion Unit 1 tripped from 49% power. The technical staff had been performing low pressure steam poppet testing on 1B Feedwater (FW) pump per Tech Staff Special Procedure (TSSP) 87-29. The immediate cause of the trip was high steam generator level caused by slow response of the 1C Feed Regulating Valve and its inability to follow the swing in FW header pressure when 1B FW pump was tripped off as part of the poppet test. Contributing factors were failure of TSSP 87-29 to anticipate the magnitude of the effect of FW pump speed on FW flow to the steam generators, false alarms on the annunciator panel due to a short circuit which diverted the operator's attention from the rising S/G level, and failure of the chart recorder for control room S/G level during the event. The reactor protection system functioned properly in tripping the unit, minimizing safety significance. Corrective actions include repairs to the FW regulating valve and revisions to FW pump poppet testing procedures.
295 | 2951988011 | 1988-05-07 | QR5 | Turbine Trip | [45 empty] | Zion 1 | P | WE | PO | 6 | On 05/07/88 at 1701 hours, while attempting to synchronize the generator, the Nuclear Station Operator noticed zero voltage for the generator excitation. While attempting to raise the excitation voltage, a generator trip was received which caused a turbine trip. At 1706 hours, the resulting transient caused a reactor trip to occur due to a low-low level in steam generator 1B. Subsequent investigation revealed that the operator was "fooled" into seeing zero excitation due to corrosion on phase B in the primary of the potential transformer circuit. Specifically, the corrosion took place in the series resistors used to limit fault current should the potential transformer fail. The SV (overvoltage) relay, which monitors phase A & C voltages, tripped the unit due to over excitation. <br /><br />All safety related equipment functioned per design. <br /><br /> Surveillance of the series resistors will be added to the preventive maintenance schedule to prevent recurrence of this type of event.
295 | 2951988013 | 1988-07-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Zion 1 | P | WE | PO | 99 | On July 13, 1988 Unit 1 was operating at 99% power when a reactor trip occurred on steam flow/feedwater flow mismatch with low (25%) steam generator level. Investigation into the event revealed that feedwater square root extractor 1FM-530B, which supplies a signal to steam generator D level control when the feedwater flow channel selector switch is selected to the 1F-530 position, had failed high. This caused the steam generator loop D feedwater regulating valve to shut. A reactor trip occurred on steam flow/feedwater flow mismatch with low steam generator level. The cause of the event was failure of square root extractor 1FM-530B. The cause of the module failure was a bad amplifier. The module was replaced with a spare module.
295 | 2951988017 | 1988-07-23 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Zion 1 | P | WE | PO | 10 | On July 23, 1988, Unit 1 was being shutdown per Plant Shutdown General Operating Procedure (GOP) 4. Turbine and reactor power were both at approximately 5%, steam generator levels were at the low point of a diverging oscillation, and reactor coolant average temperature was approximately stable at 549 degrees F. Feedwater flow was also oscillating in an attempt to maintain steam generator level. The point in the plant shutdown procedure for tripping the turbine had been reached. <br /><br />Over a three minute period, all four steam generator levels increased rapidly, which caused reactor coolant average temperature to decrease to approximately 542 degrees F. This reduction in reactor coolant temperature caused reactor power to increase from approximately 5% to approximately 10%, due to the negative moderator temperature coefficient. <br /><br /> When the turbine was manually tripped, the reactor tripped when reactor power increased to the Power Range Permissive P-10 setpoint (two out of four power range channels above 10% power). All plant systems responded normally following the reactor trip. <br /><br />The two contributing root causes to this event were personnel error and procedure deficiency. The personnel error included the manual turbine trip while reactor power was increasing to the P-10 setpoint (turbine trip/reactor trip not blocked), and poor control of feedwater flow which caused reactor power to increase from 5% to 10% in 2 minutes. <br /><br />A procedure deficiency also contributed to the personnel error. Due to the instability of feedwater flow, power should be monitored more closely while taking the turbine off line. Currently, the unit operator is required to verify reactor power below P-10 only once, and then perform a number of intermediate steps prior to tripping the turbine. Therefore, a significant time delay could occur between verifying P-10 and actually tripping the turbine.
295 | 2951989002 | 1989-01-27 | QR5 | Turbine Trip | [45 empty] | Zion 1 | P | WE | PO | 99 | While investigating failure of a safeguards test light to light, the Unit 1 turbine tripped which resulted in a reactor trip. All safety related equipment operated as expected. As the operator was holding a test pushbutton and depressing the test light, a technician placed leads across two adjacent terminals in the circuit to simulate the coil of the circuit. When the test leads were placed in the circuit, a turbine trip signal was developed and tripped the turbine. Investigation indicated that the most likely cause of the event was the technician placing the leads across incorrect terminal points. The cause of the test light failing to light was a blown bulb and faulty socket. The bulb and faulty socket were replaced. The circuit was tested and verified operating correctly prior to startup of the reactor. The Electrical Maintenance Department will review this event and stress the importance of awareness during troubleshooting.
295 | 2951990004 | 1990-01-27 | QP5 | Excessive Feedwater Flow | [45 empty] | Zion 1 | P | WE | PO | 39 | Unit 1 was in Mode 1 at approximately 39 percent power. The Nuclear Station Operator (NSO) placed the level control valve for the 1D Steam Generator (S/G) into manual control for troubleshooting on the controlling S/G level channel. The NSO continued to perform other duties, including a 50 gallon dilution of the Reactor Coolant System (RCS) boron concentration, and withdrawal of control rods one half step for temperature control.<br /><br /> Approximately 35 minutes after placing the ID S/G level control valve into manual, at 0816, Unit 1 experienced a Turbine Trip/Reactor Trip resulting from high water level on ID S/G. <br /><br /> The cause of the event was personnel error. <br /><br /> There was no safety significance to this event, as all safeguards and reactor protection equipment operated as designed. Standing Order 90-04 was issued which requires a NSO to be stationed continuously at the S/G control panel whenever a main feedwater regulating valve is in manual control.
295 | 2951990017 | 1990-08-13 | QR5 | Turbine Trip | [45 empty] | Zion 1 | P | WE | PO | 95 | Unit 1 was at steady state at 1030 MWe. Unit 2 was in Hot Shutdown, with Periodic Test (PT)-5A, "Reactor Protection Logic Reactor at Hot Shutdown" in progress. Due to difficulties encountered in testing, the need arose to trip Unit 2 locally. An extra Nuclear Station Operator rushed out of the Control Room, went to the wrong Unit, and tripped Unit 1. <br /><br /> The cause of this event was personnel error. <br /><br /> All safety systems operated as designed. There was therefore no safety significance to this event. <br /><br /> Corrective actions include tailgate sessions, better labeling at the turbine pedestals, repairing the turbine stop valve bypass valves, and an investigation to determine the feasibility of bypassing the turbine bearing lift oil pump speed switch trip at low turbine speed. 1066D
295 | 2951991016 | 1991-11-07 | QC4 | Loss of ac Instrumentation and Control Bus. | [10 empty] | X | [28 empty] | X | [5 empty] | Zion 1 | P | WE | PO | 100 | At 0434 on November 7, 1991, with the Unit at 100% power and steady state conditions, A.C. Instrument Inverter 114 failed, causing the 'Low Steam Generator Level' and 'Low Steam Generator Pressure' bistables to trip. Six seconds later a Steam Flow/Feed Flow mismatch signal was generated due to 1C Feed Pump flow reduction causing a Reactor Trip. The reactor trip signal caused the High Steam Flow Program to reset as designed, resulting in a High Steam Flow signal. The High Steam Flow signal combined with the 'Low Steam Generator Pressure' bistables previously tripped to establish the coincidence necessary to actuate Safety Injection and Main Steamline Isolation. <br /><br /> The cause of the inverter failure was a component failure. A Silicon Controlled Rectifier (SCR) in the Master section of Inverter 114 misgated causing a reduction in the inverter output voltage. This voltage reduction was sufficient enough to trip the channels of Reactor Protection and Safeguards instrumentation fed from this inverter.<br /><br /> During this event all safety related equipment operated as designed and there was minimal safety significance to this event. <br /><br /> Corrective actions included replacing all Unit 1 inverter SCRs prior to startup, including the SCRs in the preventative maintenance program and ensuring all Unit 2 SCRs will be replaced during the next Unit 2 refueling outage. <br /><br /> Previous events (LERS 1-91-005 and 1-91-008) documented A.C. Instrument Inverter failures that occurred on April 27 and May 10, 1991 on Inverters 111 and 112 respectively. The corrective actions from these LERs would not have prevented this event.
295 | 2951993007 | 1993-07-07 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Zion 1 | P | WE | PO | 100 | On July 7, 1993 at 0851 during the performance of Periodic Test (PT)-5, "Reactor Protection Logic Testing". on train A, the Reactor Protection test panel pushbutton was depressed, inadvertently causing the 1B Reactor Coolant Pump (RCP) AB! breaker to trip open and Unit 1 Reactor to trip.<br /><br /> The cause of the Unit 1 Reactor Trip was component failure. Troubleshooting identified that the stem mounted limit switch for Loop Stop Isolation Valve (LSIV) 1MOV-RC8001D had a shorted lug on the limit switch contact. The safety significance of this event was minimal. <br /><br /> Corrective actions include repairing the shorted lug, verifying the state of each LSIV relay for both units, and successfully reperforming PT-5. 93007.ler1
295 | 2951994005 | 1994-04-03 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Zion 1 | P | WE | PO | 25 | On 04/03/94, at 0430, Unit 1 was synchronized to the electrical distribution system following refueling outage Z1R13. At 0618, a loud noise was heard in the control room, and a subsequent generator trip and reactor trip occurred. At 0619, operating personnel reported that a fire was emanating from the main generator lead box. The Generating Site Emergency Plan (GSEP) was activated and the appropriate notifications were made. At 0905, the fire was extinguished and the GSEP was terminated. At 1456, during isolation of the main generator, incorrect fuses were pulled creating a two of four reactor coolant pump bus undervoltage signal and the 1A turbine driven auxiliary feedwater (AFW) pump autostarted. The fuses were reinstalled and the 1A AFW pump was secured. <br /><br /> The cause of the main generator fire was the inner ceramic surface inside the main generator C phase bushing had been contaminated with an oily substance during initial manufacturing. The cause of the 1A AFW pump autostart was an inadequate out of service. All reactor protection, engineered safeguards, and auxiliary power systems functioned normally throughout this event. <br /><br /> Corrective actions were replacing the Unit 1 west main transformer, inspecting and repairing the Unit 1 main generator and inspecting the Unit 2 main generator. <br /><br /> This supplementary report provides generator failure information as committed to in the original report.
295 | 2951994010 | 1994-07-02 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Zion 1 | P | WE | PO | 100 | On July 2, 1994, at approximately 1144 hours, a firewatch contacted the control room and reported smoke on the Unit 1 turbine deck between the generator and the exciter. The Shift Engineer confirmed that all three bus duct phases were on fire and the Station fire alarm was initiated. A unit shutdown of 5% per minute was initiated. At approximately 1152 hours the fire brigade had completed discharging portable CO sub 2 units on the fire and was in the process of discharging the first dry chemical unit on the fire when the Unit 1 Reactor tripped. The control room entered Emergency Operating Procedure E-0, "Reactor Trip or Safety Injection". All systems functioned as designed and no abnormalities were noted in responding to the reactor trip other than control rod M-8 did not indicate fully inserted. <br /><br /> The cause of the reactor trip most likely was due to ionization of the dry chemical from fire fighting efforts resulting in a main generator neutral ground trip. The cause of the bus duct fire was most likely inadequate design and vendor recommendations which did not ensure a sufficient connection during operation. The bus duct jumper cable connections, as designed, use threaded stainless steel inserts into the aluminum bus duct. Some of these connections loosened, apparently from the vibration and temperature changes of unit operation despite being tightened to vendor recommendations. The conductivity of the loosened cables decreased increasing the current flow in the other cables, causing cable insulation to overheat and ignite. Corrective actions include developing guidelines for improved installation with a revised design. <br /><br /> This supplemental report provides additional information concerning the root cause and corrective actions for the event.
295 | 2951996010 | 1996-03-16 | QP5 | Excessive Feedwater Flow | [45 empty] | Zion 1 | P | WE | PO | 20 | On March 16, 1996, Unit 1 was returning to service. At approximately 20% reactor power, Steam Generator (S/G) feedwater (FW) control was being transferred from the FW Bypass Regulating Valves to the Main FW Regulating valves. After the transfer, 1C S/G level continued to increase despite efforts to close the 1C Main FW Regulating valve (1LCV-FW520). The reactor subsequently tripped on 1C S/G Level High High although closed valve indication was observed prior to reaching 70% level. <br /><br /> The cause of this event was a new but defective pneumatic volume booster on the valve. The booster spring seat was found to be stuck in a position that would prevent the venting function. <br /><br /> Corrective actions include response time testing the Unit 2 Main FW Regulating valves and conducting a bench test break in period on similar components prior to issuing them for use. <br /><br /> The safety significance of this event is minimal.
295 | 2951996015 | 1996-04-17 | QR8 | Spurious Reactor Trip | [45 empty] | Zion 1 | P | WE | PO | 100 | While performing PT-20-ST, 'Centrifugal Charging and Letdown System Power Operated Valve Tests,' a reactor trip occurred at 0206 on April 17, 1996 in response to a 2-out-of-3 channel low flow coincident logic in the 1C reactor coolant loop. The third bistable also tripped coincident with the reactor trip signal. All rods fully inserted on reactor trip and auxiliary feedwater and steam dumps operated to remove excess reactor heat load. <br /><br /> The cause of the event is entrained gas in the sensing lines on loop 1C resulting from insufficient procedural guidance. During a previous forced outage, the reactor coolant system (RCS) loops 1A, 1B, and 1C were drained. It is believed that air entered the sensing lines on loop 1C during this maintenance. The reactor trip occurred following the first performance of PT-20-ST following this' maintenance outage. <br /><br /> Corrective actions include reviewing and revising, as necessary, certain operating procedures for filling and venting of the RCS. Additionally, maintenance practices and procedures will be reviewed and revised, as necessary, to ensure that instrument sensing lines are backfilled or vented following maintenance activities which could impact fill of the instrument lines. <br /><br /> The safety significance of this event is minimal.
295 | 2951996021 | 1996-08-18 | QL5 | Partial Closure of MSIVs | [45 empty] | Zion 1 | P | WE | PO | 100 | At approximately 1127 hours on August 18, 1996, the Unit 1 Nuclear Station Operator (NSO) tested the 1D Main Steam Isolation Valve (MSIV) in accordance with the Periodic Test (PT)-3D, 'Main Steam Isolation Valves Quarterly Check.' This test partially closes the MSIVs to prove operability. After the NSO placed the 1D MSIV test switch in the closed position the externally mounted MSIV limit switch failed to stop MSIV motion.<br /><br /> The NSO released the switch, opening the MSIV. The 1D MSIV partial closure malfunction caused the 1D Steam Generator Level to decrease rapidly to the 10% low-low Steam Generator Level protective setpoint. The Reactor Protection System sensed the low-low steam generator level and functioned to cause a reactor trip. A reactor trip occurred at 1133 hours on August 18, 1996. <br /><br /> The Intermediate MSIV Position Limit Switch (IMPLS) on the 1D MSIV failed. A formal failure analysis revealed that the internal moving components of the IMPLS were not operating freely due to lubricant that had become dried and highly viscous. The cause of this event was an inadequate Preventive Maintenance program due to Managerial Methods in that management did not apply lessons learned from industry experience to prevent the limit switch failure. <br /><br /> Corrective actions include: The IMPLS was replaced, the MSIV was successfully tested, and the operation of the new IMPLS was verified acceptable. In addition, the station replaced all Unit 1 IMPLSs and all Unit 2 IMPLSs will be replaced in the next outage. station will include the Unit 1 and Unit 2 IMPLS in the PM program, and PT-3D will be revised to include mitigating actions. Zion Station will apply lessons learned from industry experience to limit switches in critical applications.
296 | 2961996001 | 1996-02-29 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On February 29, 1996, at 0158 hours, Browns Ferry Unit 3 was operating at 99.9 percent power and Unit 2 at approximately 94 percent power when the Unit 3 reactor scrammed after receiving a high APRM neutron flux signal. The reactor scram followed a pressure transient when the output of the Electric Hydraulic Control (EHC) frequency/voltage converter (FVC) card associated with the speed control drifted to a setting that created a demand to ramp down the turbine control valves. These conditions resulted in engineered safety feature (ESF) actuations. Therefore, this event is reportable pursuant to 10 CFR 50.73(a)(2)(iv), as any event or condition that resulted in manual or automatic actuation of any ESF including the reactor protection system. The cause of this event resulted from a faulty turbine speed control EHC FVC card. The immediate corrective action was to bring the reactor to a stable condition. The faulty card was replaced. TVA plans to send the faulty card to the vendor for further investigation. Any additional corrective actions that are developed as a result of the vendor's investigation will be implemented in accordance with TVA's corrective action process. There was a previous LER (260/94005) that resulted from an EHC system malfunction; however, corrective actions taken in LER 260/94005 would not have precluded this event.
296 | 2961996002 | 1996-04-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On April 21, 1996, at 0351 hours, a low reactor water level scram occurred on Unit 3. The event was initiated by the loss of reactor feedwater pump (RFP) 3C while aligning RFP 3C's oil tank to the oil purification system. The discharge check valve on RFP 3C was damaged during the pump trip transient and was not full seated. This allowed back flow from he discharge of the two operable RFPs through RFP line 3C. Thus, RFPs 3A and 3B were unable to maintain vessel water level and the unit scrammed. The High Pressure Coolant Injection (HPCI) system and the Reactor Core Isolation Cooling system auto-started on low reactor water level and restored vessel level. All automatic Engineered Safeguard Features and all automatic isolations or actuations of primary and secondary containment group logic systems functioned as expected.<br /><br /> The RFP trip was caused by personnel error. An Assistant Unit Operator improperly aligned oil valves resulting in draining the RFP 3C oil tank. Appropriate personnel corrective action was taken. A human performance evaluation is also being performed to determine if additional actions are needed. Due to the nature of the pump trip, RFP 3C experienced a faster than normal closure of the discharge check valve which damaged the valve. Inspection of the valve also showed operational wear was present. Engineering is performing a failure evaluation on the valve wear to determine what modifications are needed to improve the performance of the valves.
296 | 2961996003 | 1996-05-01 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On May 1, 1996, at approximately 1110 hours, a full reactor scram on low reactor water level occurred. At 1109 hours, a "Condensate Booster Pump Suction Pressure Low" alarm was received in the Unit 3 Main Control Room. This alarm resulted from the closure of the Steam Packing Exhauster Condensate Bypass Valve. At 1110 hours, the "A" reactor feedwater pump tripped. The reactor automatically scrammed when the vessel level reached +11.2 inches. At -45 inches the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems auto initiated and injected into the vessel. The automatic Engineered Safeguard Features and automatic isolation or actuations occurred as expected. The cause of the valve failure was a material defect in the valve shaft. Specifically, the shaft contained a material defect in a notch sensitive area when subjected to transients that caused rapid valve position changes, resulted in high stresses being placed on the shaft, causing the shaft to fail. Additionally, personnel involved in disposition of a crack in the shaft inappropriately determined the condition acceptable.<br /><br /> The valve and pneumatic operator was replaced with a manual operator. This operator will remain in place until disposition of the system design. TVA is evaluating the design of the Steam Packing Exhauster Condensate Bypass Valve to see if design enhancements can be made that could prevent recurrence of this type of event. The Engineering individuals involved in the event received personnel corrective actions. TVA will provide information to the applicable personnel on management's expectations for evaluating plant conditions.
296 | 2961996005 | 1996-09-15 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On September 14, 1996, at 2047 hours, Reactor Recirculation Motor Generator (MG) Set 3A tripped on loss of generator field. This resulted in tripping Reactor Recirculation Pump 3A. Power operation continued at a reduced level in single recirculation pump mode with Reactor Recirculation Pump 3B in service. BFN Technical Specifications (TS) require that the reactor be placed in hot shutdown within 24 hours if operating with only one recirculation loop. Therefore, reactor power was subsequently reduced to approximately 40 percent and the reactor manually scrammed at 1724 hours on September 15, 1996. This event is being reported in accordance with 10 CFR 50.73 (a) (2) (ii) (A) as a completion of a plant shutdown required by TS. <br /><br /> Inspection of the MG set showed a bus bar in the generator armature circuit had failed. The companion bus bar was severely cracked in the same corresponding area and metallurgical tests determined high cycle fatigue was the failure mechanism. Both bus bars showed a pronounced bend inward toward the rotational axis. It is believed these bends, in conjunction with the rotational dynamics of the assembly, was the cause of the high cycle fatigue. affected and high cycle fatigue over a long period of time ultimately led to electrical failure of the bus bar. Pronounced bends were not observed on the five remaining recirculation system MG set bus bar pairs on the Unit 1 and 2 MG sets, and MG Set 3B. Since none of the other MG set bus bars were found to be significantly bent, these MG sets are not considered susceptible to a similar failure. The exact cause of the large bends in the MG Set 3A bus bars could not be determined though the condition may have been caused by improper rigging during a past lift of the generator rotor assembly.<br /><br /> The MG Set 3A bus bars and generator collector rings were replaced, and the MG set and Reactor Recirculation returned to service on September 17, 1996.
296 | 2961998003 | 1998-04-07 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On April 7, 1998, while performing a constructibility survey for DCN W40629A, Recirculation System Upgrade, a corporate engineer inadvertently shorted a recirculation pump control circuit, causing breaker 603 to trip. The resultant loss of power to critical circuits caused both recirculation pumps to runback to minimum speed. The associated reduction in core flow caused the unit to enter Potential Instability Region I on the power to flow map, which necessitated that the reactor be manually scrammed, as required by Technical Specifications. Corrective actions will consist of strengthening the controls associated with walkdowns in NEDP-11, "Design Input Walkdown Controls," and briefing appropriate personnel on the additional requirements. In addition, appropriate personnel corrective actions were taken. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(i), as the completion of any nuclear plant shutdown required by the plant's technical specifications and 10 CFR 50.73 (a)(2)(iv) an event that resulted in a manual or automatic actuation of an engineered safety feature, including the reactor protection system.
296 | 2962000001 | 2000-04-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Browns Ferry 3 | B | GE | PO | 70 | On April 15, 2000, with Unit 3 in operation at 70% power, a low reactor water level scram occurred following a reactor feedpump 3C flow reduction. The feedpump 3C flow reduction was caused by a drop in control oil pressure due to a clogged control oil filter. Safety systems responded as expected. All control rods scrammed and fully inserted. The event evaluation determined that recent maintenance activities on feedpump 3C, which involved an atypically large number of feedpump trips and resets, had increased the particulate concentration in the control oil. This caused the filter to clog at a much faster rate than experienced in the past. Corrective actions include installing control oil filter differential pressure indicators to provide online oil pressure monitoring capability. Additional operational guidance has been added to the Alarm Response Procedures for feed pump control oil system problems. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in an actuation of an engineered safety feature, including the reactor protection system.
296 | 2962000005 | 2000-05-24 | QR8 | Spurious Reactor Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On May 24, 2000, with Unit 3 operating at 100 percent power, an invalid low reactor water level scram signal was generated while returning a feedwater level transmitter to service following scheduled calibration. The reactor scram caused reactor water level to decrease below the low level (level 3) and low-low level (level 2) setpoints. All emergency systems operated as expected in response to the scram, including insertion of all control rods. This event did not result in loss of the normal heat removal path as described in NEI 99-02, Revision 0, since the condenser remained available throughout the event and was used for decay heat removal. The root cause of this event was determined to be lack of specific proceduralized valving sequences for this level transmitter based on the current design and procedural guidance. The scram was the result of a pressure perturbation in the common variable sensing line shared with both channels of reactor protection system level transmitters. Corrective actions include revising the applicable procedure. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in an actuation of an engineered safety feature, including the reactor protection system.
296 | 2962004002 | 2004-11-23 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On November 23, 2004, while Unit 3 was in steady state operation at 100% power, a main turbine trip and subsequent reactor scram occurred. All expected system responses occurred. A lightning strike occurred on the TVA 500-kV system approximately 40 miles distant from Browns Ferry. This strike resulted in a phase-to-ground fault on all three phases of the transmission line, and the electrical power transient caused speed perturbations on both the Unit 2 and Unit 3 main turbines. The rate of speed change seen on Unit 3 was slightly greater than the maximum rate anticipated by the turbine control system logic, and therefore the turbine speed feedback signals, while valid, were designated as invalid by the logic. With all turbine speed feedback signals designated as invalid, a main turbine trip on loss of speed feedback occurred in accordance with the system design, and a reactor scram occurred due to the turbine trip. The event cause was that actual turbine speed changes exceeded those anticipated as possible by the turbine control logic, causing valid speed signals to be designated as invalid. Corrective actions included the adjustment of the affected logic settings, evaluation of the turbine speed response, and consideration of modifying the speed control and turbine trip logic.
296 | 2962005001 | 2005-02-11 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | At 1629 hours Central Standard Time on February 11, 2005, the Unit 3 reactor scrammed from 100% power. The scram was caused by a simultaneous false trip signal generated to the main generator circuit breaker 234, switchyard circuit breakers 5264 and 5268, and a main generator trip. This signal was generated when a PK block (disconnect device 26W), which had been pulled as par t of a clearance for breaker 5264, was re-inserted as part of a switching order from the Load Dispatcher for returning the breaker to service. When the PK block 26W was inserted (out of sequence of the switching order), the associated current transformer (CT) circuit was momentarily grounded resulting in a false differential. T he correct sequence of the switching order was to actuate the trip cutout switches for the differential trip functions prior to inserting any of the PK blocks. The generator trip resulted in a turbine trip and opening of the output breakers caused a power-load unbalance trip. The control valve (CV) fast closure caused the reactor to SCRAM. All rods inserted. Reactor water level lowered, as expected, and was recovered by normal feed water flow. All expected Primary Containment Isolation System (PCIS) isolations were received along with the auto start of Control Room Emergency Ventilation (CREV), and the three Standby Gas Treatment (SGT) trains. The root cause of this event was determined to be personnel error, in that the Operator (Utility Licensed) failed to follow the task sequence identified in the switching order.
296 | 2962005002 | 2005-09-17 | QL7 | Degraded condenser vacuum | [45 empty] | Browns Ferry 3 | B | GE | PO | 73 | On 9/17/05 Unit 3 was in steady state operation at approximately 73% power. A maintenance activity was in progress to repair a level control valve on a high pressure feedwater heater. During the work on the valve, an air-leakage pathway to the main condenser was created, and due to an unanticipated mechanical failure of the valve internals, the valve could not be readily reassembled to isolate the in-leakage path. Over a period of approximately 10 minutes, the main condenser vacuum decreased to the low vacuum trip setpoint for the main turbine, and a main turbine trip and subsequent reactor scram occurred at 1129 hours CDT. All expected system responses occurred. Actuation of primary containment isolation system Groups 2, 3, 6, and 8 occurred due to the expected temporary lowering of reactor water level below the actuation setpoint. This logic isolates shutdown cooling (if in service), isolates the reactor water cleanup system, isolates the normal reactor building ventilation,initiates the standby gas treatment system, initiates the control room emergency ventilation system, and retracts traversing in core probes (if inserted). The normal heat rejection path (from the reactor to the main condenser via the steam lines with reactor water make-up provided by the condensate/feedwater systems remained in service.Neither the high pressure coolant injection nor reactor core isolation cooling systems were used during this event.No safety-relief valve (SRV) operation occurred during the trip transient, and post-trip review confirmed that peak reactor pressures remained below the nominal SRV lift setpoints. The event was caused by the unanticipated failure mode of the valves internals, and the work control process was not effectively managed to assess all possible failure modes. Corrective actions include revisions to operating procedures and the provision of training to managers/supervisors on effective operational decision making.
296 | 2962005003 | 2005-10-31 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On October 31, 2005, while Unit 3 was in steady state operation at 100% power, a main turbine trip and resultant reactor scram occurred. At the time, operators were in the process of returning 500-kV switchyard Bus-2, Section 2 to service using a switching order. When the Power Circuit Breaker (PCB) to the 500-kV Trinity 2 transmission line was closed, the PCB immediately tripped back open. The post-scram investigation subsequently determined that this was due to a closed ground switch at an offsite substation on this transmission line. The PCB properly tripped open to clear the Trinity 2 line ground; however, the electrical power transient resulting from the ground and its clearing caused speed perturbations on the Unit 3 main turbine. The rate of speed change seen on the turbine was slightly greater than the maximum rate anticipated by the turbine control system logic and, therefore, the turbine speed feedback signals were designated as invalid by the turbine control logic. With all turbine speed feedback signals designated as invalid, a main turbine trip on loss of speed feedback occurred in accordance with the system design and a reactor scram occurred due to the turbine trip. This event was an uncomplicated plant scram with major plant safety systems responding as expected and in accordance with the plant design. The event cause was that actual turbine speed change exceeded that anticipated as possible by the turbine control logic, causing valid speed signals to be designated as invalid. Additionally, the switching order was deficient in that instructions to open the closed ground switch were in a separate switching order and were not performed. Corrective actions include modifying the Unit 3 turbine control logic and strengthening the process used by the transmission system organization for switching activities.
296 | 2962006002 | 2006-08-19 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On August 19, 2006, at 1105 hours central daylight time, Unit 3 was manually scrammed following a loss of both the 3A and 3B Reactor Recirculation pumps. Just prior to the event, the Unit 3 Unit Operator (UO) received alarms indicating low reactor water level, reactor feedwater level control system failure, and failure of the input/output modules for both the 3A and 3B Reactor Recirculation pumps. The UO also reported that main generator load was approximately 730 megawatts electrical (approximately 64 percent of full power output) and lowering. Based on these indications, the UO scrammed the reactor. The immediate cause of the manual scram was the loss of both the 3A and 3B Reactor Recirculation pumps. The manual scram was required by the conditions presented to the Unit 3 operator following the loss of recirculation flow. The initial investigation into the trip found the Variable Frequency Drive (VFD)microprocessors non-responsive. The root cause of the event was the VFD controls malfunctioned due to excessive traffic on the connected plant Integrated Control System (ICS) network. Corrective actions include developing a network firewall device that limits the connections and traffic to any potentially susceptible devices on the plant ICS network and installing a network firewall device on each Unit's VFD controller.
296 | 2962006003 | 2006-08-29 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On August 29, 2006, while in steady state operation at 100% power, control room annunciation was received at 2210 hours CDT of a low level in the main turbine electro-hydraulic control (EHC) fluid reservoir. Local inspection of the tank confirmed an actual low level and also that the tank level was continuing to drop. At 2223 hours, reactor power was reduced to approximately 78% via reactor recirculation pump speed reduction, and, at 2225 hours, a manual scram was initiated in accordance with plant procedures. All control rods fully inserted and expected system responses were received. Actuation of primary containment isolation system groups 2, 3, 6, and 8 occurred due to the expected temporary lowering of reactor water level below the actuation setpoint. Valve realignment as part of the main turbine trip which followed the scram isolated the location of the EHC fluid leak from the rest of the system. The normal heat rejection path (from the reactor to the main condenser via the main steam lines with reactor water make-up provided by the condensate/feedwater systems) remained in service. Reactor water level was recovered to the normal operating range by the normal reactor water level control system. Neither the high pressure coolant injection nor reactor core isolation cooling systems were used during this event. The root cause of the EHC fluid leak was determined to be inadequate O-ring compression on a solenoid valve mounting due to the use of device mounting bolts which were too long. The bolts and the valve were supplied as a kit by the vendor. Plant procedures will be revised to verify bolt length and mounting hole depth in future activities involving EHC components.
296 | 2962007001 | 2007-02-09 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | At 1208 Central Standard Time, on February 9, 2007, Unit 3 received an automatic reactor scram on low water level following the loss of condensate flow. Just prior to the scram, operations attempted to establish manual operation of the condensate and demineralizer system. Personnel were in the process of modifying the control logic for the condensate and demineralized water system backwash controller. With the primary controller in run mode and the secondary controller in the program mode, personnel were loading new software into the secondary controller. The personnel involved were experiencing difficulties loading the software onto the secondary controller, so they attempted to load software onto the primary controller. They placed primary controller, which was previously in the run mode, into the program mode. However, the secondary controller was not returned to the run mode. With neither controller the run mode the condensate and demineralizer water system demineralizers isolated. This resulted in a decrease in reactor water level and an automatic reactor scram. The root cause of this event was the individuals involved in the planning and implementation of the work order did not fully understand manual operation of the system. Additionally, there is inadequate guidance or limitations on the use of in-field decision making. TVA is revising the operating instructions for the condensate demineralizer system. TVA is revising trouble shooting guidance to eliminate trouble shooting under the direction of the system engineer or other individuals except under tightly controlled circumstances.
296 | 2962007005 | 2007-12-31 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On December 31, 2007, at 2140 hours Central Standard Time (CST), Unit 3 reactor received an automatic scram signal following a main generator load reject. The reactor scram from the generator load reject was expected. All systems responded to the scram as expected. All control rods inserted. During the initial pressure transient, which peaked at 1141 psig, six of the main steam system relief valves opened. The reactor pressure was subsequently controlled with the main steam system bypass valves. The reactor water level was controlled by the Feedwater system, the normal heat removal path through the main condenser was maintained during the event. The reactor scram was reset December 31, 2007, by 2146 hours CST. TVA is submitting this report according to 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in a manual or automatic actuation of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B) (i.e., reactor protection system including reactor scram of trip, and general containment isolation signals affecting containment isolation valves in more than one system.)
296 | 2962009001 | 2009-08-24 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | At 1850 Central Standard Time (CST), on August 24, 2009, Unit 3 operators inserted a manual scram due to lowering reactor vessel water level. Prior to the manual scram, Condensate Booster Pump 3A tripped on low suction pressure followed by a trip of Condensate Booster Pump 3B. The Reactor Feedwater Pump Turbine (RFPT) suction header experienced low suction pressure, but feedwater pump 3A did not trip as expected. Feedwater pump 3B tripped as expected. The condensate flow path through the demineralizers is the only path with sufficient capacity to provide an adequate source of feedwater to the reactor vessel at 100 percent power. Loss of the flowpath through the condensate demineralizers caused lowering reactor water level which resulted in a control room operator inserting a manual reactor scram. Reactor vessel water level decreased to -47 inches and was recovered by High Pressure Coolant Injection (HPCI) system and Reactor Core Isolation Cooling (RCIC) system initiation. The communication adapter for Condensate Demineralizer Programmable Logic Controller Remote Chassis 10 (which is associated with condensate demineralizer;vessel 3H) was found with status lights indicating a communications failure had occurred, This failure caused an apparent loss of communication with the remote chassis associated with the other condensate demineralizer vessels. The root cause of this event was determined to be less than adequate functional testing of the condensate demineralizer system valve lock-up devices. TVA is developing a more robust testing methodology and frequency (preventative maintenance work orders) for ensuring the condensate demineralizers effluent lockup devices work properly.
296 | 2962010004 | 2010-12-26 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On December 26, 2010, at 1615 hours Central Standard Time, an alarm for Main Turbine Vibration High 3-VA-47-15 was received in the Unit 3 control room on annunciator panel 3-XA-55-7B Window 32. Control room operators responded using Unit 3 Alarm Response Procedure (ARP) 3-ARP-9-7B. Exciter rotor inboard journal bearing vibration level indicated 8.0 mils and rising, and the outboard journal bearing indicated 5.5 mils and rising. At 1617 hours, an Upper Power Runback was initiated per the ARP. It was noted that vibration levels initially lowered then continued rising. At 1620 hours, control room operators initiated a manual reactor scram. The direct cause of this event was an exciter rotor-deflector rub resulting from a combination of high differential air exit temperatures and existing decreased clearances on the rotor. The root cause was inadequate procedural guidance for monitoring the exciter air cooling system and prescribing mitigation actions to be taken based on differential temperature limits. The rub was corrected during the forced outage. Corrective actions include installation of cooler vents for use in minimizing air binding, establishment of a cooler venting process, increased controls and documentation of manual "balancing" valve manipulation, increased system monitoring process rigor and oversight, and performance of a training analysis for inclusion of relevant aspects of this root cause into the Operations and Engineering training materials.
296 | 2592011001 | 2011-04-27 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Browns Ferry 3 | B | GE | PO | 75 | On April 27, 2011, severe weather in the Tennessee Valley Service Area caused grid instability and loss of all 500-kV offsite power sources that resulted in automatic scrams of all three units. All three units were in Mode 1 at the time of the event. All scram systems were actuated, all actuations were complete, and required systems started and functioned successfully with the exception of an indeterminate position indication for the Unit 3 B Inboard Main Steam Isolation Valve. All onsite safe shutdown equipment was available with the exception of the 3B Emergency Diesel Generator (EDG), which was inoperable and unavailable due to planned maintenance. After the event, only one 161-kV line remained available for offsite power - all (seven) 500-kV lines and one (of two) 161-kV line were lost. All three units immediately entered Mode 3 (Hot Shutdown) with their respective 4-kV busses supplied by the onsite EDGs. On April 27, 2011, at 1701 hours, a Notification of Unusual Event (NOUE) was declared due to the loss of normal and alternate supply voltage to all unit-specific 4-kV shutdown boards for greater than 15 minutes and at least two EDGs supplying power to unit-specific 4-kV shutdown boards. On May 2, 2011, at 2050 hours, the NOUE was terminated following restoration of qualified offsite power sources.
296 | 2962012003 | 2012-05-22 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Browns Ferry 3 | B | GE | PO | 19 | On May 22, 2012, at 0249 Central Daylight Time, the BFN, Unit 3, reactor was automatically scrammed due to de-energization of the Reactor Protection System from actuation of the 3A Unit Station Service Transformer (USST) differential relay 387SA, which resulted in a loss of 500 kilovolt (kV) power to BFN, Unit 3. All safety systems responded as expected to the loss of 500kV power. No Emergency Core Cooling System or Reactor Core Isolation Cooling (RCIC) System reactor water level initiation set points were reached. The RCIC System was manually started to control reactor water level. Primary Containment Isolation System initiation signals for groups 1, 2, 3, 6 and 8 were received as expected due to loss of power. The immediate cause of this event was the 3A USST differential relay was installed with incorrect design calculation settings which resulted in the BFN, Unit 3, scram. The root cause of this condition was inadequate procedural guidance within NEDP-5, Design Document Reviews, for the types of review required by engineering. The corrective action to prevent recurrence is to revise NEDP-5, Design Document Reviews, to establish the definition and requirements for each type of review.
296 | 2962012004 | 2012-05-24 | QR6 | Manual Reactor Trip | [45 empty] | Browns Ferry 3 | B | GE | SU | 1 | On May 24, 2012, at approximately 0638 Central Daylight Time, Operations personnel inadvertently ranged 3H intermediate range monitor (IRM) down instead of up resulting in a half scram from the 3B reactor protection system (RPS) trip channel. Subsequently, the IRM was properly ranged and Operations personnel responded in accordance with procedures to reset the half scram. Coincident with Operations personnel placing the scram reset switch in the Group 2/3 position, an electrical spike was received on 3A IRM of the 3A RPS trip channel resulting in control rod insertion for the Groups 1 and 4 control rods. Operations personnel identified the unexpected control rod motion and initiated a manual reactor scram in accordance with Browns Ferry Nuclear Plant (BFN) Abnormal Operating Instructions. The root cause was determined to be high impedance of the BFN, Unit 3, Main Control Room (MCR) common ground to station ground that exposed the 3A IRM to noise feedback. The corrective action to prevent recurrence is to verify that BFN, Unit 3, MCR common ground connections to station ground are as shown in the applicable system drawings. If any ground connections are identified that require repair, work orders will be initiated and repairs performed. Following repairs, the high impedance connection of BFN, Unit 3, MCR common ground to station ground will be confirmed to have been resolved by documenting the results of validation testing.
296 | 2962012005 | 2012-05-29 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 76 | On May 29, 2012, at 0331 Central Daylight Time, the Browns Ferry Nuclear Plant (BFN), Unit 3, reactor automatically scrammed due to fast closure of turbine control valves, initiated by a load reject signal on the Main Generator. The cause of the load reject signal was actuation of newly installed main transformer differential relay 387T, which caused the scram. All systems responded as expected to the load reject signal. Main steam isolation valves remained open and reactor pressure was controlled by the main turbine bypass valves. No Emergency Core Cooling System or Reactor Core Isolation Cooling System reactor water level initiation set points were reached. Primary Containment Isolation System isolations from Groups 2, 3, 6, and 8 were received, and reactor water level was controlled by the Feedwater System. Three root causes were identified: 1) inadequate procedure, instructions, and testing methodology/equipment used for current transformer (CT) bench testing; 2) inadequate acceptance review by Tennessee Valley Authority (TVA) Engineering of a vendor prepared design change; and 3) inadequate management, oversight, and accountability by the BFN Maintenance organization for work performed by the Protective Relay Group. The corrective actions to prevent recurrence include: 1) revise the CT bench test procedure; 2) revise the human performance procedure to incorporate technical conscience principles, focus technical task risk factors, mitigating strategies, and decision making; and 3) using the Nuclear Operating Model, utilize the TVA's strategic performance management process to ensure management alignment in the ownership and accountability for leadership expectations at BFN.
296 | 2962013003 | 2013-02-25 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [28 empty] | X | X |  |  |  |  | Browns Ferry 3 | B | GE | PO | 92 | On February 25, 2013, at approximately 1313 hours Central Standard Time, the Browns Ferry Nuclear Plant (BFN), Unit 3, reactor automatically scrammed due to an actuation of the Reactor Protection System from a turbine trip. The turbine tripped on low condenser vacuum due to a reactor feedwater piping separation. The Main Steam Isolation Valves were manually closed. There was one Safety Relief Valve that was manually operated to maintain reactor pressure due to the unavailability of the Main Turbine Bypass Valves upon loss of condenser vacuum. All systems responded as expected to the turbine trip. No Emergency Core Cooling System or Reactor Core Isolation Cooling (RCIC) system reactor water level initiation set points were reached. Reactor water level was controlled with the RCIC system and reactor pressure was controlled with the High Pressure Coolant Injection system.<br /><br /> The root cause for this event is that the system design for BFN, Unit 3, Feedwater Long Cycle line does not account for flashing of water to steam due to isolation valve leakage.<br /><br /> The corrective action to prevent recurrence is to redesign Feed Water Long Cycle lines downstream of each Feed Water Long Cycle isolation valve and upstream of the Miscellaneous Drain Header with a valve and piping configuration appropriately designed for the specified application.
296 | 2962014001 | 2014-03-18 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 35 | On March 18, 2014, the Browns Ferry Nuclear Plant (BFN) Unit 3 reactor automatically scrammed due to a turbine trip from a high main turbine moisture separator level. Initial indications show the level controller for 3B2 Moisture Separator failed to maintain level in automatic. Additionally, local manual control attempts failed to restore moisture separator level. Following the turbine trip Main Steam Isolation Valves remained open with main turbine bypass valves controlling reactor pressure.<br /><br /> At approximately 2232, Central Daylight Time (CDT) the 3B2 Moisture Separator Level High Alarm was received and an operator was dispatched to investigate. In accordance with the alarm response procedure the 3B2 Moisture Separator Water Level Controller was placed in manual. Attempts to control the Moisture Separator Reservoir 3B2 High Level Dump Valve manually were ineffective. At approximately 2252 CDT, the Unit 3 reactor automatically scrammed due to a turbine trip from a high moisture separator level.<br /><br /> The root cause was a failure to prevent the introduction of foreign material during the manufacturing process of the Moisture Separator Level Controller. The manufacturing defect was a legacy issue dating back to 1971 when the controller body was originally machined. The corrective actions to prevent recurrence requires the removal, cleaning of air passages, replacement of control relays, for similar controllers and upgrading the calibration procedure to include cleaning guidance.
296 | 2962014002 | 2014-05-06 | QR8 | Spurious Reactor Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 100 | On May 6, 2014, at approximately 0830 Central Daylight Time (CDT), the Browns Ferry Nuclear Plant (BFN) Unit 3 reactor automatically scrammed as a result of an Anticipated Transient Without Scram/Alternate Rod Insertion (ATWS/ARI) signal generated during functional testing of reactor water level instrumentation. The scram air header was depressurized through the ATWS/ARI valves causing all rods to insert into the core. The ATWS/ARI signal also simultaneously opened the Recirculation Pump Trip (RPT) breakers, tripping both Recirculation pumps. The loss of both pumps along with reduced core flow caused a reactor water level transient that lowered level below the Reactor Protection System (RPS) trip setpoint (+2 inches), resulting in a full reactor scram signal. Prior to this event, reactor power was 2.1 percent as all control rods were inserted by the ATWS/ARI initiation ten seconds earlier. Following receipt of the ATWS/ARI signal, all plant systems performed as required.<br /><br /> The root cause of the event was that the ATWS low reactor water level Automatic Trip Unit (ATU) cards initiated a voltage transient that actuated the ATWS high reactor pressure trip due to a design anomaly.<br /><br /> The corrective action to prevent recurrence includes installing time delay relays in association with the Unit 3 reactor pressure ATWS circuit.
296 | 2962018001 | 2018-01-10 | QR5 | Turbine Trip | [45 empty] | Browns Ferry 3 | B | GE | PO | 74 | On January 10, 2018, at approximately 0926 Central Standard Time (CST), with Unit 3 at 74 percent power, Browns Ferry Nuclear Plant (BFN) received an automatic scram on Reactor Protection System (RPS) Turbine Control Valve (TCV) fast closure trip. The support bracket for Unit 3 TCV #2 Electro- Hydraulic Control (EHC) pressure switch separated from TCV #2 allowing the mass of the pressure switch to break the hydraulic sense line. As a result, the EHC pressure switch sensed low pressure and triggered a half scram. With a half-scram previously in place due to an unrelated issue from closure of TCV #3, the additional half-scram resulted in an automatic scram on Unit 3 which is a reportable condition. Safety systems responded as designed and the reactor scram was uncomplicated. <br /><br /> The apparent cause of this event was determined to be high cycle fatigue failure of the Unit 3 TCV #2 EHC pressure switch support bracket. <br /><br /> This failure was corrected by replacing the failed mounting bracket with a newly designed mounting bracket. The corrective action to reduce the probability of recurrence is to install viscoelastic dampeners on the steam piping to reduce the overall piping vibration on the area components. The dampeners are expected to reduce overall piping vibration and the probability of future vibration induced failures of various components in the moisture separator rooms.
296 | 2962019001 | 2019-03-09 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Browns Ferry 3 | B | GE | PO | 100 | On March 9, 2019, at approximately 2259 Central Standard Time (CST), Browns Ferry Unit 3 received an automatic Reactor SCRAM from 100 percent power as a result of a Turbine Load Reject. Browns Ferry Unit 3 declared a Notification of Unusual Event due to loss of the 500kV offsite source. The automatic SCRAM occurred as a Licensed Reactor Operator (LRO) made adjustments to lower incoming reactive power on Unit 3 at the request of the Balancing Authority. The LRO incorrectly operated a hand switch and changed the automatic voltage regulator (AVR) from auto to manual. In this mode of operation, the dynamic limiter is removed, which allows Operations personnel to adjust Mega Volt Amps Reactive (MVAR) beyond the Under Excitation Limiter (UEL) protection setting. As a result, the generator circuit breaker tripped causing a Turbine Load reject and an automatic SCRAM. All safety systems actuated as designed. <br /><br /> The root cause for this event was determined to be that Operations department leaders have allowed continued negative human performance (HU) behaviors by inconsistently providing coaching or reinforcing the use of appropriate HU barriers. The corrective action to prevent recurrence is to revise the Operations Excellence Program, BFN-ODM-4.28, to require use of a dynamic learning environment to develop Operations Department Leaders' skills in coaching and reinforcing the use of appropriate HU barriers. Training will be required prior to assuming shift following initial qualification as Nuclear Unit Senior Operators (NUSO) and Shift Managers (SM). The currently qualified NUSOs and SMs have received training. <br /><br /> A plastic cover was placed over the manual/auto select voltage regulator hand switch on all three Units to mitigate unintentional operation of the AVR from automatic to manual control. The Operating Instruction procedure for the Turbine Generator System was revised to prompt Operations personnel to validate the initial status of the AVR prior to adjusting MVAR.
298 | 2981987002 | 1987-01-04 | QP5 | Excessive Feedwater Flow | [45 empty] | Cooper | B | GE | SU | 5 | While conducting a plant heatup with the reactor critical and power in the upper end of the Intermediate Range, a reactor scram occurred as a result of a rapid injection of feedwater and resulting high neutron flux. The feedwater injection was caused by a valving error in the Main Feedwater System. At the time of this event, a plant startup with associated Reactor Coolant System (RCS) pressurization was in progress. <br /><br />The cause of this event is considered to be a result of a personnel error on the part of the licensed operator in the Control Room. In attempting to establish and maintain feedwater flow to the reactor vessel using the Reactor Feedwater pumps, an improper initial valve lineup and subsequent correction of this error after a Reactor Feedwater Pump was placed in service resulted in substantial feedwater addition and an ensuing decrease in RCS temperature. <br /><br />Corrective action to be taken includes discussion of this event by the Operations Supervisor with all licensed shift operating personnel, a review (and revision, where applicable) of startup and system operating procedures in an effort to prevent a recurrence of events such as this, incorporation of this event and lessons learned in licensed operator continuing training, and consideration of this event in the evaluation of enhancements scheduled to be made to this panel as part of the Detailed Control Room Design Review project.
298 | 2981987003 | 1987-01-07 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Cooper | B | GE | PO | 30 | On January 7, 1987 during power escalation following the 1986 refueling/major maintenance outage, it became apparent that the input leads to the Steam and Feedwater Flow Recorder (RFC-RF-96) may have been reversed during Detailed Control Room Design Review (DCRDR) implementation. While troubleshooting the apparent lead reversal, the flow signal to the recorder and to the Reactor Water Level Control System was lost. The loss of signal caused the operating Reactor Feedwater Pump speed and flow to increase substantially, exceeding the capacity of the operating Condensate and Condensate Booster Pumps. Consequently, the Reactor Feed Pump tripped due to low suction pressure. Upon loss of feedwater, the reactor water level decreased until, at 1945, a Reactor Scram and Group Isolations 2, 3 and 6 occurred. All safety systems operated as designed, control of reactor vessel level was reestablished, and normal scram recovery procedures were followed. <br /><br /> Upon investigation, it was determined that the recorder RFC-RF-96 input lead terminals had not been fully tightened during performance of the aforementioned DCRDR project. Hence, when a voltmeter was connected to verify the apparent lead reversal, the circuit continuity was interrupted and the feed flow signal lost, initiating the feedwater transient. Therefore, the root cause of the event has been determined to be due to an apparent insufficient acceptance test of the Steam and Feedwater Flow Recorder (RFC-RF-96) during and following completion of the DCRDR design change activity. Corrective action taken following the scram and prior to restart included a verification of terminal connections on Panel 9-5 and in the Feedwater and High Pressure Coolant Injection (HPCI) control systems to ensure tightness. No other discrepancies were noted. Further corrective action to be taken includes a review of this event with all licensed operators and a review of the acceptance testing and quality control program for this particular Design Change.
298 | 2981987005 | 1987-01-10 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Cooper | B | GE | PO | 22 | At 1027 on January 10, 1987, a reactor scram occurred due to closure of the Main Steam Isolation Valves (MSIVs). MSIV closure occurred as a result of low primary containment pneumatic header pressure supplied from the Main Nitrogen System. Primary Containment inerting was in progress. During the inerting process, at a flow rate of 800 cfm, the Drywell Pneumatic Pressure Low alarm (set at 90 psig) was annunciated. The nitrogen supply header pressure was checked and determined to be 77 psig and stable. The licensed operators, upon verifying conditions to be stable, allowed inerting to continue. However, just prior to the scram, the inerting flow was increased to approximately 1000 cfm without consideration of the low drywell nitrogen supply pressure. The increased flow rate caused the pneumatic header pressure to be reduced to the point where sufficient pressure was not available to maintain the MSIVs fully open. The MSIVs began to drift closed, resulting in the reactor scram. <br /><br /> The cause of this event is considered to be the result of inadequate procedural guidance. In a recent procedure revision, the Primary Containment Pneumatic Header backup air supply valve position was changed from normally open to normally closed to achieve compliance with the combustible gas control issue. However, in making this change, the potential impact on pneumatic header pressure during Primary Containment inerting was not known and, therefore, not adequately addressed. <br /><br />Corrective action taken includes revisions to CNS operating procedures to address primary containment pneumatic header pressure concerns while inerting, as well as a revision to the appropriate alarm procedure to open the pneumatic header backup air supply valve upon receipt of the Drywell Pneumatic Pressure Low alarm. Additionally, this event will be reviewed with all licensed operators.
298 | 2981987009 | 1987-02-18 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Cooper | B | GE | PO | 50 | At 1350, a reactor scram occurred accompanied by Group II, III, and VI Isolations when the operating Reactor Feed Pump was mistakenly tripped by a Station Operator from the local control station. The Station Operator (unlicensed operator) had been dispatched, subsequent to discussions and review with licensed Control Room operators of the procedural requirements, to conduct a local trip test of the standby Reactor Feed Pump turbine which was in the initial stages of being placed in service. Upon entering the Feed Pump Room, he apparently became disoriented with respect to north-south direction and pump location and tripped the operating pump. At the time of this event, power level was approximately 50 percent and preparations were being made to increase power to 100 percent. <br /><br /> The cause of this event was personnel error on the part of the Station Operator dispatched to conduct a local trip test of the Reactor Feed Pump turbine being placed in service, in accordance with the operating procedure. A contributing cause is considered to be the lack of human factors in component/equipment markings. <br /><br /> Corrective action taken included establishing stable plant conditions and implementing normal scram recovery procedures. The operating crew involved subsequently met with the Station Operations Review Committee (SORC) to critique the event and to identify measures which could be taken to aid in preventing future occurrences of this nature. A meeting was held by the Division Manager of Nuclear Operations with Operations Department supervisory personnel. Further meetings are planned by the Operations Supervisor with all shift operating personnel. Additionally, a comprehensive review of equipment identification and marking will be undertaken, and action implemented to resolve deficiencies identified.
298 | 2981987011 | 1987-05-17 | QR5 | Turbine Trip | [45 empty] | Cooper | B | GE | PO | 75 | At 0131, while conducting monthly turbine valve testing, a reactor scram occurred due to Turbine Control Valve Fast Closure. The ensuing Reactor Vessel water level shrink was of such a magnitude that the low water level trip setpoint was reached, causing isolation of Groups 2, 3, and 6 Containment Isolation Valves. Sensing the low water level condition, Reactor Feed Pump speed increased, resulting in an excessive feedwater addition to the vessel and, soon thereafter, Reactor Feed Pump trip. With the Main Steam Isolation Valves (MSIVs) still open and steam loads necessary to maintain condenser vacuum still in service, Reactor Vessel water level began to decrease. Efforts to re-establish a source of feedwater were initiated, but not completed before the Reactor Vessel Low Water Level setpoint was reached. Consequently at 0207, another scram occurred and Engineered Safety Features previously noted were actuated. <br /><br />Following the second low water level trip, control of Reactor Vessel water level was established and normal scram recovery procedures were initiated. <br /><br />The primary cause of the event was due to personnel error while conducting surveillance testing. A contributing cause of the event is considered to be the lack of Turbine Trip System status information displayed to surveillance testing personnel at the Turbine Front Standard. Corrective actions being taken include revising the surveillance test procedure to provide more specific guidance regarding turbine trip testing and investigating the possibility of making changes at the Turbine Front Standard to improve Turbine Trip System status information.
298 | 2981987014 | 1987-05-18 | QR6 | Manual Reactor Trip | [45 empty] | Cooper | B | GE | PO | 20 | During plant startup following an unscheduled shutdown, condenser hotwell and reactor water conductivity, which had been trending upward and evaluated as not being unusual for normal startup activities, began to increase rapidly. Although immediate actions were taken to locate and isolate condenser tube leakage, when reactor water conductivity was determined at 7:50 PM to have exceeded 10 micromho/cm, a plant shutdown was commenced. At 10:57 PM, with load at approximately 100 MWe, the reactor was manually scrammed. The ensuing Reactor Vessel Water Level shrink reached the low water level trip setpoint causing actuation of Groups 2, 3, and 6 Containment Isolation Valves. <br /><br />The cause of the initiating event was determined to be main condenser tube leakage. Prior to conducting a successful restart of the plant, a total of four (4) tubes were found to be leaking and were plugged. General Electric Company (GE) was consulted regarding the potential deleterious effect of the conductivity excursion on the Reactor Coolant System pressure boundary and associated vessel internals. GE concluded that the excursion would not be expected to impact the integrity of the pressure boundary or be of any consequence to the internals.
298 | 2981988002 | 1988-01-28 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Cooper | B | GE | PO | 35 | On January 28, 1988 at 7:12 P.M., a reactor scram occurred during startup of the 1B Reactor Recirculation (RR) Pump due to Average Power Range Monitor (APRM) High flux. During the pump startup sequence, the 1B Reactor Recirculation Motor Generator (RRMG) speed control system malfunctioned, resulting in a core flow increase greater than expected when the 1B Recirculation Loop Discharge Valve automatically jogged open. Consequently, reactor power increased to the APRM High flux scram setting (approximately 66 percent power) for the existing reactor flow condition. During the ensuing Reactor Vessel water level transient, water level decreased to the point where actuation of Groups 2, 3, and 6 Isolations occurred. Additionally, upon transfer of 4160V AC power, both Diesel Generators automatically started. <br /><br /> At the time of this event, the plant was in operation at approximately 35 percent power (275 MWe). The flow control system malfunction occurred as a result of a locking screw, used to secure a disc that actuates high and low travel stops, which had loosened and vibrated off. The disc dropped into the low limit switch and, due to its actuation, scoop tube drive in the lower direction was electrically stopped. Therefore, the expected runback of the RRMG to minimum speed following pump breakaway was prevented. <br /><br />A thorough inspection of both 1A and 1B RRMGs and calibration of the RRMG control loops was performed. The previously noted deficiency on the 1B RRMG was discovered and corrected. In addition, deficiencies found during calibration of the control loops were resolved. Preventive maintenance requirements will be upgraded to incorporate the lessons learned from this event.
298 | 2981988019 | 1988-07-15 | QR6 | Manual Reactor Trip | [45 empty] | Cooper | B | GE | PO | 100 | On July 15, 1988, at 9:58 A.M., the reactor was manually scrammed subsequent to discovery of electrical arcing at a bolted connection between the removable covers of the "A" Phase Isolated Phase Bus Duct. Prior to inserting a manual scram, power level was reduced from approximately 100 percent to 50 percent power by reducing recirculation flow. In addition, Reactor Vessel water level was increased eight to ten inches above the normal control point in anticipation of the expected water level "shrink". Nevertheless, upon inserting the manual scram, the level transient was of sufficient magnitude that the isolation logic circuits for Groups 2, 3, and 6 Isolations were actuated. <br /><br />The cause of the arcing was due to a broken ground strap on the "A" Phase bus duct. An additional factor was the cork-neoprene gasket between the bus duct housing and the top removable cover which had degraded to the point where the cover contacted the bus duct housing on the generator side. As a result, a ground path was established through the ungrounded bus duct cover, resulting in the observed arcing. <br /><br /> Immediate corrective action taken included the necessary scram recovery actions to establish stable plant conditions and restoration of systems to service that had been automatically isolated. The Isolated Phase bus duct components were inspected and all necessary gaskets and ground straps replaced. Further corrective action to be taken includes establishing and implementing appropriate preventive maintenance actions to assure the continued integrity of the bus duct grounding and gasketing system.
298 | 2981988021 | 1988-08-25 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Cooper | B | GE | PO | 100 | At approximately 12:40 A.M. on August 25, 1988, a reactor scram, and Group 1 and 7 Isolations occurred as a result of signal spikes on all four Main Steam Line Radiation Monitors. The resulting water level "shrink" caused Group 2, 3, and 6 Isolations, and the automatic start of the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems. The HPCI and RCIC systems were used to restore and maintain reactor water level, while the designated safety/relief valves operated in the low-low set mode to control reactor pressure. <br /><br />Reactor water samples taken following the scram indicated normal chemistry and radioactivity levels. Radiation levels in the main steam lines, off-gas system, drywell, and main turbine area were normal and steady prior to the event. The signal spikes were attributed to electrical noise. <br /><br />Immediate corrective actions taken were to respond to the scram and group isolations to stabilize the plant. A troubleshooting effort was unable to exactly duplicate the signal spikes, therefore no specific cause could be positively identified. To minimize the chance for recurrence, a separate chassis ground was added to each Main Steam Line Radiation Monitor. In addition, the station directive stipulating control over portable radios was expanded to include stricter requirements in certain areas of the plant. Furthermore, the adequacy of the instrument and cable shielding for the Main Steam Line Radiation Monitors will be verified during the 1989 Maintenance and Refueling Outage.
298 | 2981989001 | 1989-01-25 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Cooper | B | GE | PO | 100 | On January 25, 1989, at 6:53 A.M., an automatic reactor scram due to high neutron flux occurred while at 100 percent power under normal steady state conditions. The ensuing Reactor Pressure Vessel water level transient resulted in actuation of Groups 2, 3, and 6 Isolations (Primary Containment, Reactor Water Cleanup, and Secondary Containment including Standby Gas Treatment System initiation). Water level was immediately restored and maintained by the Condensate/Feedwater System; no automatic or manual ECCS System actuations were required. <br /><br /> It was initially theorized, based on available plant data, that the neutron flux transient was due either to electronic noise in the Neutron Monitoring System or a pressure spike as a result of a main turbine pressure control system malfunction. Subsequently, problems were experienced when attempting to equalize through the inboard Main Steam Isolation Valve (MSIV) on the "A" Main Steam Line. Upon disassembly of the inboard valve, it was determined that the stem disc had separated from the stem during operation, and that the main disc seated, causing a pressure spike and the resulting flux transient. <br /><br /> The safety significance of this event is considered to be minimal. The transient response of the plant was very similar to the response recorded for an overseas BWR which suffered a similar failure. The reactor response was consistent with predicted results provided in the Transient Analysis Design Report. Corrective actions taken included refurbishment of both the inboard and outboard MSIVs on the "A" MSL using stem and disc assemblies of an upgraded design. Further action to be taken includes upgrading the remaining six MSIVs with the new design stem and disc assemblies.
298 | 2981989025 | 1989-09-28 | QR5 | Turbine Trip | [45 empty] | Cooper | B | GE | PO | 100 | On September 28, 1989, at 11:36 AM, a main turbine trip occurred, followed immediately by a reactor scram. The Reactor vessel water level transient that resulted from the scram caused containment isolation Groups 2 (Primary Containment) 3 (Reactor Water Cleanup) and 6 (Secondary Containment) to occur. The turbine trip signal that initiated the event was turbine hydraulic control oil reservoir low level, which occurred approximately two minutes after the control oil pumps were shifted. It was later verified that reservoir level had remained in the normal range throughout the event. <br /><br /> The exact cause for the turbine hydraulic control oil reservoir low level trip signal could not be positively identified. It was concluded the trip signal was caused by spurious actuation of the level switch due to equipment vibration as a result of shifting control oil pumps. <br /><br /> The immediate actions taken were to stabilize the plant following the scram. To minimize the possibility of recurrence, a temporary instruction was issued to limit control oil pump shifting, and a control oil system flush was scheduled for the next outage. Additionally, several system reliability improvements will be evaluated.
298 | 2981989026 | 1989-11-25 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Cooper | B | GE | PO | 100 | On November 25, 1989, at 10:15 P.M., with the plant at full power, a reactor scram occurred when the outboard Main Steam Isolation Valves (MSIVs) closed as a result of depressurization of the Instrument Air (IA) System. The decrease in IA System pressure occurred when the "B" Air Dryer Post Filter assembly ruptured. Investigation revealed that the Post Filter media (paper cartridges) had been ignited by either hot air or hot particles from the dryer. The burning cartridges resulted in overheating of the filter assembly housing. The associated heat induced stress, coupled with internal (system) air pressure, caused the housing to deform and rupture. <br /><br /> Corrective actions taken included complete disassembly, inspection and refurbishment of the "B" Air Dryer, including replacement of the Post Filter assembly, as well as an extensive inspection of the "A" Air Dryer. Filter cartridges capable of withstanding high temperature conditions were installed in both Post Filter assemblies. Approximately fifteen feet of piping downsteam of the Post Filter was replaced due to concerns about the possible effects of overheating. Checks were made of the IA System downstream of the Post Filters to verify system cleanliness. Additionally, components in the vicinity of the ruptured Post Filter assembly were inspected to ensure that debris from the event was not present. <br /><br /> Further corrective action includes upgrading the Air Dryer training programs, performance of a design review of the Air Dryer trains, and implementation of upgraded Air Dryer operational checks and preventive maintenance activities.
298 | 2981990011 | 1990-10-17 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Cooper | B | GE | PO | 100 | On October 17, 1990, at 1:49 PM, with the plant in operation at full power, a reactor scram and several ESF actuations, including Group Isolations and Emergency Core Cooling System actuations, occurred due to a ground fault on the 345 kV Phase A transmission line, causing the 345 kV output breakers to open. The ground fault occurred when gusting wind conditions caused a power cable (5/C-#10) to a temporary construction elevator which was installed to facilitate refurbishment of the Reactor Building roof, to come into contact with the 345 kV A Phase transmission line and the transmission tower shield line. Power to the station was immediately restored through the Startup Transformer. This power source, however, was interrupted within three seconds of the initial ground fault when a piece of the power cable made contact between the 345 kV Phase C transmission line and the 161 kV Phase A transmission line. Upon sensing loss of voltage on the 4160 VAC Critical buses, supply breakers from the Emergency Transformer closed, repowering the 4160 VAC Critical Switchgear.<br /><br /> The root cause of this event is failure to establish and implement sufficient work control measures for the Reactor Building roof refurbishment activity, considering the location selected for staging of the work. <br /><br /> Corrective actions taken included verification of proper transmission system protective relay operations; transmission line inspections; and inspections and testing of the Normal, Startup and Main power transformers. The temporary construction elevator was relocated, and the materials on the roof that could be dislodged by high winds were removed. Extensive work control measures were established in preparation for completion of the refurbishment effort. This event and the corrective measures taken will be disseminated to appropriate NPG personnel.
298 | 2981993038 | 1993-12-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cooper | B | GE | PO | 100 | On December 14, 1993, at 1:34 am, with the plant in operation at full power, an automatic reactor scram occurred due to low reactor vessel water level. The cause of the low water level was determined to be a failure of the Reactor Feedwater Pump (RFP) master controller. Upon receipt of annunciators associated with the feedwater system, reactor power was lowered by reducing the speed of the Reactor Recirculation (RR) Pumps. As water level continued to decrease, the B RR Pump was tripped in an effort to reduce power more rapidly, however, an automatic reactor scram occurred due to low reactor vessel water level. <br /><br /> The plant response to the transient was normal. All control rods inserted, the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) Systems initiated, and Groups 2 (Reactor Coolant System), 3 (Reactor Water Clean Up System), and 6 (Primary and Secondary Containment) Isolations occurred. Normal reactor vessel water level was restored and HPCI, RCIC, and RFP B were subsequently secured. <br /><br /> The malfunction of the RFP master controller was caused by the failure of a normally energized 1/2 watt voltage dropping resistor. The most probable root cause for its failure is age related degradation. The failed master controller was replaced with a spare controller. Prior to its installation, the spare unit was visually inspected for degraded components and bench tested. Additionally, other similar GEMAC controllers in the HPCI, RCIC and Reactor Feedwater Systems were inspected for visual signs of degradation of resistors and other components. No deficiencies were found. Further corrective action to be taken includes an evaluation of GEMAC controllers for age related concerns.
298 | 2981994004 | 1994-03-02 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Cooper | B | GE | PO | 97 | POWER LEVEL - 097%. On March 2, 1994, at 5:45 pm, a reactor scram from 97 percent power occurred as a result of Average Power Range Monitor (APRM) high neutron flux trip. The cause of the event was partial closure of turbine governor valves caused by a turbine digital electro-hydraulic (DEH) control system malfunction resulting in a momentary reactor pressure increase. This pressure increase caused a reduction in reactor core void fraction, resulting in reactor power reaching the APRM high flux scram setpoint. Immediately following the reactor scram, vessel inventory shrink due to void collapse resulted in reactor water level reaching the nominal Level 3 trip setting of >/= +4.5 inches with Instrument 0 being approximately 165 inches above the top of active fuel. Reactor water level was restored by the reactor feed system in combination with short term operation of both the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems. The plant was stabilized in a safe condition following the transient and later placed in cold shutdown. <br /><br /> Through extensive failure analysis, the most likely component failure was determined to be a transistor relay on the DEH Valve Transfer Control Card. The card was replaced. During the plant startup, conducted March 12, erratic bypass valve operation occurred resulting in a small pressure spike and associated power increase. The DEH System 24 volt power supplies were determined to be the cause of the problem. Both power supplies were replaced.
298 | 2982000011 | 2000-10-14 | QR5 | Turbine Trip | [45 empty] | Cooper | B | GE | PO | 100 | On October 14, 2000 at approximately 3:24 Central Daylight Time (CDT), a phase 'C' differential current trip (87/GT relay) [EIIS:87] resulted in a Main Generator [EIIS:GEN] trip and automatic reactor scram. All rods inserted. Reactor Pressure Vessel (RPV) pressure initially rose to 1068 psig which is below the lowest Safety Relief Valve setpoint of 1080 psig and then was controlled by the Digital Electro-Hydraulic control system. RPV level initially lowered due to shrink and caused Group 2 (Primary Containment), Group 3 (Reactor Water Cleanup), and Group 6 (Secondary Containment) isolations. The Alternate Rod Insertion (ARI) signal initiated on low RPV level; however, level recovered prior to ARI tripping the Reactor Recirculation Motor Generator field breakers. Reactor Feed Pump turbines tripped on high RPV water level swell following the scram. The RPV swell dampened the RPV pressure transient. A normal cooldown was commenced and the plant was placed in Mode 4, Cold Shutdown, at 17:48 CDT on October 14, 2000. The cause of the event was vibration induced insulation wear in a current transformer (CT) [EIIS:XCTI lead wire [EIIS:CBL2] associated with the main power transformer [EIIS:XFMR] which resulted in a short to ground. The worn insulation has been repaired, and a spare CT in the transformer has been used to replace the CT with the damaged leads. The CT with the damaged leads has been spared in place.
298 | 2982003004 | 2003-05-26 | QR6 | Manual Reactor Trip | [45 empty] | Cooper | B | GE | PO | 89 | On May 26, 2003, at 1321 hours, there was a step change in main turbine vibration indication from less than 4 mils to 10.2 mils. A manual reactor scram was initiated from 89% power. Subsequent to the scram, reactor vessel water level dropped to approximately 30 inches below instrument zero, resulting in Primary Containment Isolation System Group 2, 3, and 6 isolations, start of High Pressure Coolant Injection and Reactor Core Isolation Cooling systems, and trip of the Reactor Recirculation pumps. An evaluation of plant response determined all control rods fully inserted and systems controlling reactor pressure and level responded as designed. The most probable cause for the turbine blade failure in the low pressure turbine is material condition. The failure mechanism is consistent with age-related/end-of-life type failures. Long term corrective action will be to replace the low pressure turbine rotors with new rotors during the next refueling outage. Immediate actions taken were to manually scram the reactor, trip the main turbine, and place the unit in a cold shutdown condition. An initial visual exam of the turbine blade root specimen was obtained, which concluded the crack is consistent with high cycle fatigue. Magnetic particle and eddy current testing were performed on both faces of the last four rows on both LP1 and LP2 spare rotors. Blades with crack indications on the spare rotors were replaced. The in-service LP1 and LP2 rotors were replaced with the spare rotors.
298 | 2982003006 | 2003-10-28 | QR6 | Manual Reactor Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Cooper | B | GE | PO | 75 | On October 28, 2003, at 0130 hours, a fire occurred on a wooden transmission structure located between the main generator output and the 345KV switchyard. Due to the imminent loss of the main generator output line to the switchyard, a manual scram was performed at 0200 hours. All control rods inserted and Primary Containment Isolation System Group Isolations for Primary Containment, Reactor Water Cleanup and Secondary Containment initiated as expected due to vessel level shrink. The Emergency Core Cooling Systems did not initiate. During water level recovery an overfeed condition caused the operating Reactor Feedwater pump to trip and a second manual scram was inserted in anticipation of a low level scram signal. Normal shutdown procedures were entered at 0300 hours and a vessel cool-down was initiated. The transmission structure fire was reported out at 0647 hours. The fire occurred when dust accumulation on the insulators and structure became wetted and created a path for stray electrical currents from phase to phase, or phase to ground across the wooden cross arm. The cause of this event is the failure to properly ground the insulator strings on the wooden structure. The damaged wooden structure and associated line disconnect switch were removed on October 30, 2003. Grounding cables were installed on a similar structure on November 24, 2003.
298 | 2982003007 | 2003-11-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cooper | B | GE | PO | 100 | On November 28, 2003, "B" Reactor Feed Pump (RFP) transferred to manual and lowered to approximately 3100 revolutions per minute causing the reactor to automatically scram on low reactor vessel water level at 2202 hours. Subsequent to the scram, reactor vessel water level dropped to approximately 47 inches below instrument zero resulting in Primary Containment Isolation System Group 2, 3, and 6 isolations, start of High Pressure Coolant Injection and Reactor Core Isolation Cooling systems, and automatic trip of the Reactor Recirculation pumps. An evaluation of plant response determined all control rods fully inserted and systems controlling reactor pressure and level responded as designed. The approximate root cause of this event is a spurious signal entered the reactor feed pump turbine controller. Immediate action was taken to place the plant in a safe shutdown condition in Mode 3 (Hot Shutdown). Prior to plant startup, 1) operators were trained on the event, 2) radio frequency interference suppression, to attenuate frequencies greater than one mega hertz, was installed on the reactor feed control input signals, 3) a modification was completed that added annunciation for a RFP in manual and provided additional signal monitoring, and 4) installed ground wires from feedwater control station cases to cabinet ground bus. Subsequent to startup and still to be completed is a modification that will attenuate frequencies greater than one kilohertz. This will prevent spurious signals in the reactor feed pump turbine controller, dampen noise on the master controller, and filter noise.
298 | 2982005001 | 2005-04-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cooper | B | GE | PO | 100 | On April 15, 2005 at 0436 Central Daylight Time, from 100 percent power, steady state, Cooper Nuclear Station (CNS) had a feedwater and reactor level transient followed by a low level alarm and scram. Level reached 70 inches below Instrument Zero, all control rods inserted, and reactor pressure was controlled by turbine bypass valves. High pressure coolant injection (HPCI) and reactor core isolation cooling (RCIC) automatically injected. All automatic actuations functioned as required. Level recovered with HPCI and RCIC injecting. After stopping the level drop, HPCI was rendered inoperable by erroneously positioning its auxiliary oil pump switch to PULL-TO-LOCK (PTL) . It was repositioned to AUTO twenty seconds later. Cause of the level transient was a manufacturing deficiency in the installed feedwater master level controller obtained as an equivalent part from a different manufacturer to replace the previous unit. The master controller was replaced with the previous unit. The cause of the operator error was inadequate management of change for a revision to the HPCI operating procedure versus ingrained practice of placing HPCI in PTL. HPCI procedure was enhanced. Additional actions are planned to obtain a spare master level controller and to provide simulator training to operators. CNS started up and returned to power on April 17, 2005.
298 | 2982005004 | 2005-09-23 | QL7 | Degraded condenser vacuum | [45 empty] | Cooper | B | GE | PO | 76 | On September 23, 2005, at 0022, Operations noted condenser vacuum degrading and Steam Jet Air Ejector air flow rising. The decline occurred after starting a backwash of Condenser B-2 Waterbox. Operations performed actions per Abnormal Procedures,and reduced power. Condenser vacuum continued to decline. By 0040, condenser vacuum had dropped to 23.1 inches of Mercury. The minimum acceptable value for vacuum is 23 inches of Mercury. Operators manually scrammed the reactor due to degrading condenser vacuum which was caused by significant air in leakage. The air leak was through a turbine bearing slop (waste oil and water) drain line that failed due to high-cycle fatigue. Inadequate support of slop drain lines in the Main Condenser led to piping vibration induced by Low Pressure (LP) Turbine exhaust steam flow. An evaluation of plant response determined that all control rods were fully inserted, and systems controlling reactor pressure and level responded as designed. Condenser vacuum was maintained to support Bypass Valve operation during the event. The interim corrective action to address the Root Cause was to remove the slop drain lines from the condenser and to plug the condenser penetration holes. This was completed prior to unit restart.
298 | 2982006001 | 2006-02-26 | QR6 | Manual Reactor Trip | [45 empty] | Cooper | B | GE | PO | 70 | On February 26, 2006, at 0250 Central Standard Time, Reheat Valve 1B did not re-open after the valve was closed during conduct of a surveillance test on the main turbine reheat/intercept valves. This occurred concurrent with a high level alarm in Moisture Separator D. Per procedure, the plant was manually scrammed. All control rods fully inserted and a Primary Containment Isolation System Group 2 isolation occurred. Reactor power, vessel pressure and level response were as expected. The cause of the event was contamination of the electro-hydraulic fluid in the turbine control system from inadvertent introduction of waste fluid to the control system fluid reservoir on August 14, 2005. Feed and bleed actions to reduce the contamination did not eliminate particulate contamination in normally stagnant lines associated with the reheat/intercept test solenoid valves resulting in a stuck reheat valve. Immediate actions were to cycle all intercept and reheat stop valves via the test solenoids several times to verify flushing of the electro-hydraulic fluid through the valves. Corrective actions to prevent recurrence include replacing the test solenoid valves for the turbine reheat/intercept and main stop valves and flushing and replacing the electro-hydraulic fluid in the turbine generator control system.
298 | 2982006004 | 2006-05-22 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Cooper | B | GE | PO | 100 | At 0651 on May 22, 2006, Service Air (SA) pressure began lowering for an unknown reason. Additional Service Air Compressors (SACs) could not be started in time to recover SA pressure. Following a rapid power reduction the reactor was manually scrammed at 0701 as a mitigating action. All automatic systems functioned as expected, and the plant entered and remained in Mode 3, Hot Shutdown. This event was not risk significant. Analysis revealed the most likely cause to be the SAC automatic control system failed to respond to system pressure changes. SACs were placed in local control mode to operate independently based on individual start-stop-unload setpoints. The plant subsequently started up on May 24, 2006. The cause was a single point failure mode introduced into the newly installed SAC compressor controller that was unrecognized in the design process. A standing order now prevents SACs from operation in other than local control until an evaluation of failure modes on the automatic control system has been performed. Action remaining includes revising applicable plant configuration change procedures to perform failure mode evaluation for Maintenance Rule (MR) Risk Significant control systems; revising the SAC operating procedure to normally operate in local mode, except when controlled methods retain at least two SACs to supply plant air; determining which of the past three years plant modifications require a failure mode evaluation; and performing evaluations for those modifications.
298 | 2982007004 | 2007-05-19 | QR6 | Manual Reactor Trip | [45 empty] | Cooper | B | GE | PO | 50 | On 5/19/2007 at 00:25 CDT, Cooper Nuclear Station (CNS) was in Mode 1 at 50%Power in Single Loop Operation when a small water leak developed from a Control Rod Drive Hydraulic Control Unit (HCU) directional control valve (DCV) during maintenance. The leak degraded to the point of a visible steam plume, and prompted a precautionary Reactor Building evacuation. After several unsuccessful attempts to isolate the leak operators made the conservative decision to remove the unit from service. At 02:12 CDT, the operators manually scrammed the reactor. Control rods inserted normally. A Group 2 Primary Containment isolation signal isolated required systems. The scram was uncomplicated with systems functioning as required. No off-site releases occurred due to the HCU valve leak which stopped after the scram. The manual scram and controlled shutdown were not nuclear risk significant. Leakage past a manual isolation valve is the most probable direct cause of the DCV internal pressure. The cause of the leak was that tag-out implementation and acceptance for maintenance did not require verification that HCU was de-pressurized, nor were contingencies in place if it was not. Corrective actions are being tracked in CNSs corrective action program.
298 | 2982008001 | 2008-08-09 | QR6 | Manual Reactor Trip | [45 empty] | Cooper | B | GE | PO | 69 | At 0025 Central Daylight Time (CDT) on August 9, 2008, reactor power was lowered from 85% to 69% to perform main turbine stop valve closure and steam valve functional testing. At 0156 CDT, during the first reheat/stop valve (1A) test, while reheat/stop valve had failed to reopen, a Moisture Separator (MSR) 'C' high level alarm occurred. In accordance with the alarm procedure for MSR high level, the plant was manually scrammed. Control rods fully inserted, and a Primary Containment Isolation System Group 2 isolation occurred. Plant and mitigating system responses were as expected. Risk significance was negligible. The event was caused from a manufacturing defect that caused the reheat/stop valve test solenoid to jam. The root cause was attributed to a practice of performing reheat/stop valve testing at a power level which could result in a MSR high level condition should a reheat/stop valve test solenoid malfunction. Action was taken to prevent recurrence by deleting sections in the functional test procedure for energizing the reheat/stop valve test solenoids.
298 | 2982009002 | 2009-11-06 | QR6 | Manual Reactor Trip | [45 empty] | Cooper | B | GE | PO | 20 | On November 6, 2009, at 19:30 Central Standard Time, Cooper Nuclear Station (CNS) control room operators inserted a manual reactor scram when vessel water level lowered quickly after a turbine trip. The turbine had been tripped after a hydraulic fluid leak developed in the digital electro-hydraulic (DEH) turbine control system that could not be isolated and repaired with the turbine on-line. After the scram, all control rods inserted and automatic systems responded as expected. A Group 2 isolation occurred due to reactor low water level conditions. Vessel water level was subsequently recovered and the Group 2 isolation was reset. The leak was caused by higher than normal vibration of the DEH supply line for governor valve #3 (GV-3) at low power. CNS repaired the leak by replacing the swaged joint connection that had fractured with a modified fitting. Additionally, a missing stop bolt for the actuator bracket on GV-3, that would have restrained the DEH supply line, was replaced. The root cause was deficient workmanship. CNS will add a step in the applicable preventive maintenance plans for the governor valves to ensure that the support bolting for the valve actuator bracket is installed. This event was not risk significant.
298 | 2982009004 | 2009-11-11 | QR6 | Manual Reactor Trip | [45 empty] | Cooper | B | GE | PO | 15 | On November 11, 2009, at 17:43 Central Standard Time, Cooper Nuclear Station (CNS) control room operators inserted a manual reactor scram after a non-isolable digital electro-hydraulic (DEH) fluid leak developed. This was the same governor valve (GV) and fitting location that had leaked November 6, 2009, and required a forced plant shutdown. After the scram, all control rods inserted and automatic systems responded as expected. Inspection of the governor valve fitting found that the face O-ring installed five days earlier was not the correct size for the application and did not seal appropriately. This O-ring was acquired from a turbine generator tool box and was not added to the work order to document its use. CNS maintenance replaced the O-rings on all electro-hydraulic fittings for GVs with new ones from warehouse inventory. The root causes were a failure to follow the material control and warehouse issuing processes and ineffective management of the initial repair to the DEH fluid leak five days prior. CNS will use management processes to reinforce expectations for procedure compliance and will implement case study training on this event. CNS will also inventory the turbine generator tool box and remove any materials that are not in compliance with the procedure for in-process material control. This event was not risk significant.
298 | 2982020003 | 2020-11-01 | QR6 | Manual Reactor Trip | [45 empty] | Cooper | B | GE | PO | 100 | On November 1, 2020, at 0534, Cooper Nuclear Station (CNS) Control Room Operators inserted a manual reactor scram due to low Digital Electro-Hydraulic (DEH) tank level. Further investigation revealed that a leak had developed at governor valve (GV) 1, and a pencil-sized stream of EH fluid was discovered leaking out of the lower, outboard inspection port on the GV1 actuator. <br /><br /> Investigation revealed one bolt on the actuator inspection port cover plate was bottomed-out and prevented appropriate tightening for an adequate seal. The o-ring on this cover plate was ruptured, allowing excessive leakage. <br /><br /> The causes were on-site vendor craftsmanship was unsatisfactory in the failure to recognize the bottomed-out bolt during actuator installation and inspector port cover plate holes on the new GV1 actuator body were not threaded deep enough to meet vendor specifications. CNS will appropriately classify cntical Turbine Generator Fluid connections that are subject to additional verification of bolting and torqueing performance. In addition, CNS will review the final vendor evaluation of the actuator manufacturing defects/field craftsmanship and determine if additional actions are warranted. <br /><br /> This event was not risk significant.
301 | 3011987002 | 1987-08-16 | QR5 | Turbine Trip | [10 empty] | X | [29 empty] | X |  |  |  |  | Point Beach 2 | P | WE | PO | 100 | A Unit 2 reactor trip occurred from 100% power at 1855 hours on August 16, 1987. The trip was caused by a loss of electrical load. The Unit 2 generator breaker opened due to a lightning strike near the plant causing a flashover between the ground and "B" and possibly the "C" phases of the 345 kV line for the Unit 2 X01 transformers. As a result a turbine trip and reactor trip occurred. Due to the nature of the transient, an auto bus transfer of non-vital buses to offsite power did not occur resulting in the reactor coolant pumps, circulating water pumps, main feed pumps, condensate pumps and turbine auxiliaries being deenergized. Condenser vacuum was quickly lost. A few minutes after the trip, the main steam isolation valves were closed manually from the control room to stop the flow of steam to the turbine hall. The "B" main steam isolation valve closed to within 1 inch of the full closed position but was easily seated by manual operator action. All other equipment operated as designed during this transient. This incident was classified as an Unusual Event. <br /><br /> The "B" and "C" phase 19 kV/345 kV transformers were inspected and tested as well as the fast bus transfer circuitry response and were verified operable prior to Unit 2 startup. The reactor was critical by 2138 hours on August 17, 1987.
301 | 3011988001 | 1988-04-07 | QR8 | Spurious Reactor Trip | [45 empty] | Point Beach 2 | P | WE | PO | 100 | At 0904 hours on April 7, 1988, a reactor trip occurred from 100% power. The trip was caused by a low pressurizer pressure signal. Safety injection also initiated due to a low pressurizer pressure signal. These and other anomalies were caused by red instrument bus voltage fluctuations resulting from the primary and alternate inverters feeding the red instrument bus with the inverters connected in parallel. The inverter parallel operation occurred due to the failure of the mechanical interlock, which is designed to prevent the simultaneous connection of the inverters to the load. <br /><br />During the recovery, with primary pressure near the safety injection set point and safety injection reset, safety injection occurred a second time due to cooling of the primary coolant system when steam was restored to the turbine hall. <br /><br />All systems operated as expected during the transient with the exception of one of the two source range nuclear instrumentation channels. This channel failed to energize after the trip. This channel remains out of service and was placed in the trip blocked condition as allowed by Point Beach Technical Specifications. <br /><br /> Immediate corrective action included the posting of an operator aid at the location of the instrument bus breaker cabinets, which provides instructions to reduce the probability of this type of occurrence in the future. The plant returned to power operation on April 12, 1988.
301 | 3011989002 | 1989-03-29 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Point Beach 2 | P | WE | PO | 100 | On March 29, 1989, at 0843 hours, Unit 2 experienced a main step-up transformer lockout main generator breaker trip and concurrent turbine and reactor trips. The unit had been operating at 100% power. The lockout occurred shortly after the spurious actuation of the Unit 2 X01C phase fire deluge spray system. The deluge spray apparently induced a flashover from the transformer to ground, which was detected by transformer differential protective relays. The spray system actuated while troubleshooting a wiring problem discovered during modification work which replaced the transformer deluge heat actuation devices with new electronic detectors. <br /><br /> The emergency diesels automatically started because of bus undervoltage. The undervoltage condition was the result of the premature actuation of the generator stuck breaker protection relay, which isolated a Unit 1 bus section cross-connection. The voltage decreased on the remaining transmission line to Unit 2 due to a maintenance outage at a nearby plant and the line losses associated with transmission from other distant supplies. <br /><br /> An Unusual Event was declared at 0854 hours. The event was terminated at 1205 hours. Repairs were effected and the unit returned to service on April 2.
301 | 3011989004 | 1989-08-20 | QR5 | Turbine Trip | [45 empty] | Point Beach 2 | P | WE | PO | 100 | On August 20, 1989, at 1631, Unit 2 experienced a main step-up transformer lockout, main generator breaker trip, and concurrent turbine and reactor trips. The unit had been operating at 100% power. The lockout occurred shortly after water spray had been initiated to the transformer oil coolers to reduce temperatures on the X01 transformers. The unit transformer lockout was initiated by the apparently random actuation of the 2X01 "B" phase "sudden pressure" trip system. The unit responded in a normal manner to the trip with several minor problems. An Unusual Event was declared at 1644 due to loss of electrical load. The Unusual Event was terminated at 1856. After extensive investigation and thorough checkout and testing of the 2X02 "B" phase transformer, the unit was returned to service on August 21, 1989.
301 | 3011991006 | 1991-12-17 | QR8 | Spurious Reactor Trip | [45 empty] | Point Beach 2 | P | WE | PO | 100 | At 1008 on December 17, 1991, Point Beach Nuclear Plant Unit 2 experienced a reactor trip during modification work on DC distribution panel D11. While a cable was being pulled from panel D11 as part of the modification, a cable connected to breaker 32 was displaced by the cable being removed. This movement caused the termination in breaker 32 to loosen and allow its associated cable to become disconnected. This cable supplies power to DC distribution panel D22. Panel D22 supplies power to the Unit 2 "A" train reactor protection circuitry. Panel D22 became deenergized, resulting in a reactor trip on Unit 2 and actuation of the crossover steam dumps on Units 1 and 2. The Unit 1 turbine was manually run back to 73% power to allow closure of the Unit 1 crossover steam dump without exceeding reactor power limitations. The Unit 2 condenser steam dumps were not enabled because of the loss of DC power to the arming circuit. Panel D22 was reenergized at 1037. Unit 1 was returned to full power at 1350. After the electrical connections in panels D11 and D13 were check-tightened, Unit 2 was placed back on line at 0346 on December 18. Unit 2 reached full power at 2245 on December 18, 1991. This event is an actuation of the Reactor Protection System (RPS). Therefore, a four-hour notification to the NRC was made in accordance with 10 CFR 50.72(b)(2)(ii).
301 | 3011993002 | 1993-03-28 | QR5 | Turbine Trip | [45 empty] | Point Beach 2 | P | WE | PO | 100 | At 0145 CST on March 28, 1993, while Unit 1 was shut down for its Cycle 20 annual refueling outage and Unit 2 was operating at 100% power, a Unit 2 reactor trip occurred during performance of Technical Specification Test TS-4A, "Turbine Trip Test (Monthly), Unit 2." A Duty Operating Supervisor (DOS) was directed by the Duty Shift Superintendent (DSS) to conduct Test TS-4A. The DOS then assigned one Licensed Auxiliary Operator (LAO) to assist him in performing the evolution. Test TS-4A cautions the operator to hold the turbine test handle in the "TEST" position during the entire test to prevent an actual trip from the mechanical trip block devices. However, due to valve operation difficulties and subsequent follow-up actions, the LAO commenced opening thrust bearing Hand Valve 2EH-00065 before the DOS was able to hold the turbine test handle in "TEST." Pressure in the test line increased to the turbine trip setpoint and, because the test handle was not in the "TEST" position, the turbine stop valves shut and the turbine tripped, resulting in a reactor trip. The test was immediately terminated. Operations personnel entered Emergency Operating Procedure EOP-0, "Reactor Trip or Safety Injection." Unit 2 was subsequently returned to full power at 2220 CST on March 29, 1993. A 4-hour notification to the NRC was made at 0401 CST in accordance with 10 CFR 50.72 (b) (2) (ii).
301 | 3011995003 | 1995-03-07 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Point Beach 2 | P | WE | PO | 98 | At 2159 on March 7, 1995, Point Beach Nuclear Plant (PBNP) Unit 2 experienced an automatic turbine runback and subsequent reactor trip from 98% power. The turbine runback and reactor trip resulted from an oil leak and subsequent pressure loss in the Unit 2 turbine generator electrohydraulic (EH) control system. The pressure loss caused one of the two turbine stop valves to shut, which led to an overtemperature differential temperature (OT [symbol omitted] T) turbine runback and reactor trip. The leak originated from a union joint in the EH oil piping supplying the left turbine stop valve. All reactor protection features operated as designed. The response of the secondary plant is being evaluated. The exact cause of the leaking union joint could not be determined. However, this is considered an isolated event. A 4-hour Emergency Notification System (ENS) notification was made in accordance with 10 CFR 50.72(b)(2)(ii). The NRC Resident Inspector was also notified.
301 | 3011996001 | 1996-05-18 | QR5 | Turbine Trip | [45 empty] | Point Beach 2 | P | WE | PO | 90 | At 1130 on May 18, 1996 PBNP Unit 2 experienced a spurious turbine trip and subsequent automatic reactor trip from 90% power. The turbine trip was initiated by closure of both turbine stop valves, as indicated by the first-out annunciation of "2-of-2 Turbine Stop Valves Closed". All reactor protection features operated as designed. Post-trip troubleshooting isolated the cause of the turbine trip to a spurious loss of pressure in the turbine high- pressure emergency-trip line of the Electro-Hydraulic Control (EHC) System, without a coincident Auto Stop Trip (AST) depressurization. Although there was no physical evidence of valve degradation, the EHC Emergency Trip Solenoid Valve (20ET) was identified as a likely component to have failed. The valve was removed and replaced with an identical component. The suspect valve will be subjected to testing and further evaluation to replicate its failure mechanism, if possible. A 4-hour Emergency Notification System (ENS) notification was made in accordance with 10 CFR 50.72(b)(2)(ii). The NRC Resident Inspector was also notified.
301 | 3012000007 | 2000-12-20 | QR5 | Turbine Trip | [45 empty] | Point Beach 2 | P | WE | PO | 63 | On December 20, 2000, the Point Beach Nuclear Plant (PBNP) Unit 2 experienced a turbine generator and reactor trip while raising power following completion of the unit's refueling outage. The trip occurred with reactor power at approximately 63% power. The cause of the trip was initially identified as a ground overcurrent relay actuation on the main step up transformer. Subsequent investigation determined the trip was due to the 2-51N neutral overcurrent relay detecting a phase current imbalance; however, no evidence of an actual overcurrent condition was identified. Further investigation determined that the trip resulted from the opening of the current transformer circuit for the "C" phase input to the 2-51N relay. The open circuit occurred due to the failure of a manufacturer's crimp connection. The circuit was repaired and the connections in the current transformer for the other phases were checked and found to be satisfactory. The unit was returned to service on December 21st.
301 | 3012001001 | 2001-02-06 | QR5 | Turbine Trip | [10 empty] | X | [29 empty] | X |  |  |  |  | Point Beach 2 | P | WE | PO | 100 | On February 6, 2001, at approximately 2150, the Point Beach Nuclear Plant (PBNP) Unit 2 tripped from 100% power. The trip was the result of a turbine generator lockout apparently caused by one of the generator stator neutral ground fault detection devices (27/59N relay). System and components required to perform following the reactor trip operated as designed with the possible exception of the cross over steam dump system. This system actuated as expected to minimize the turbine over speed; however, main condenser vacuum was lost when the dump valves apparently failed to reseat promptly. The reactor coolant system was maintained in hot standby following the trip with temperature maintained via the steam generator atmospheric steam dump valves. Following extensive trouble shooting and a thorough incident investigation, PBNP Unit 2 was restarted on February 8th. Since the exact cause for the actuation of the 27/59N relay could not be determined, the plant was returned to operation after completing a temporary modification to change the relay circuit from a generator lock out actuation to a common alarm function. Prior to 1987, the PBNP units had operated without these relays. Other installed protective relaying is available to minimize the risk of faulting due to a stator ground. The NRC was notified of this event via the ENS at 2244 on February 6, 2001. The safety and welfare of the public and the plant staff was not impacted by this event.
301 | 3012001002 | 2001-06-27 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Point Beach 2 | P | WE | PO | 70 | On June 27, 2001, at approximately 18:20, the Point Beach Nuclear Plant (PBNP) Unit 2 reactor was manually tripped with reactor power at approximately 70%. This trip was directed by procedure (AOP-13A) when the water level in the Circulating Water (CW) System pump bay decreased to less than -11 feet (normal pump bay level with four CW pumps in service is about -7 feet). The Service Water (SW) pumps also take a suction from the pump bays and -11 feet is a conservative minimum water level to assure that components serviced by the SW system will remain capable of performing their safety functions. The decrease in pump bay water level was attributed to the influx of a large number of small forage fish (Alewives) on the Unit 2 traveling water screens. This influx caused a high differential water level across the screens and ultimately resulted in the disabling of the traveling screen drive mechanism. Following the trip one of the two running Unit 2 CW pumps was secured. This action; in conjunction, we believe, with a screen failure that permitted increased water flow into the pump bay; resulted in a rapid recovery of the pump bay level. The preliminary root cause report has identified the following causal factors: ineffective implementation of previously identified corrective actions from related events, delays in operator response while in the AOP, and problems with the sequence of action steps within the procedure. With the exception of two minor equipment problems identified in the report, the operator and equipment responses to the transient were as expected and the unit was stabilized in the hot shutdown condition. Unit 2 returned to normal operation on July 1, 2001.
301 | 3012003004 | 2003-07-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Point Beach 2 | P | WE | PO | 100 | On July 10, 2003, at approximately 1340 CDT, while operating at 100% power, the Point Beach Nuclear Plant (PBNP) Unit 2 experienced the failure of the “B" Main Feedwater Pump (MFP) due to an electrical fault within the motor. The loss of the MFP resulted in an automatic Unit 2 reactor trip at approximately 1341 CDT. The trip was due to a feed flow/steam flow mismatch coincident with low steam generator level. The auxiliary feedwater system also actuated as expected due to the initial low steam generator water levels. The reactor protection and safety systems responded as required and the unit was stabilized in Mode 3. A four hour event notification was made to the NRC at 1455 CDT. The apparent cause for the failure of the "B" MFP motor failure has been preliminarily determined to be failure of the stator winding Insulation due to age related degradation. Additional inspection and testing will be performed by the vendor that is contracted to rewind the motor to determine the validity of this failure mode assessment. Unit 2 was taken critical at 2306 CDT on July 12 and operated with a single MFP and a nominal 50% power limit until the "B" MFP motor was replaced. Unit 2 returned to full power operation on July 16, 2003. Systems and equipment necessary to mitigate the consequences of this motor failure and subsequent reactor trip functioned as designed and the plant was maintained in a stable hot shutdown condition until the restart on July 12, 2003. The safety and welfare of the public and the plant staff was not impacted by this event and the safety significance was minimal.
301 | 3012004002 | 2004-05-05 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Point Beach 2 | P | WE | PO | 100 | On May 15, 2004, a manual trip of the Point Beach Nuclear Plant (PBNP) Unit 2 was initiated when the control room was notified that a diver had become entangled in the intake structure for the circulating water (CW) system. While inspecting the intake structure for winter damage, the diver's tether, air and communication line became snagged. The diver's line tender, together with the assistance of a rescue diver, were unable to clear the lines. When communications with the diver were lost, the NMC diving liaison on the boat requested that the Unit 2 CW pumps be secured in order to facilitate removing the diver from the water. Securing the CW pumps requires that the reactor first be tripped. After the reactor trip and securing the CW pumps, both divers exited the water uninjured. Plant systems functioned as expected during the reactor trip transient, including the reactor protection and auxiliary feedwater systems. Since the circulating water system was secured, the main condensers were unavailable for decay heat removal. The steam generator atmospheric steam dump valves were used to remove decay heat. An incident investigation and root cause evaluation were conducted. The primary causes of this event were determined to be unclear and inconsistent communications and inadequate supervisory oversight. Process and procedural corrective actions are being completed. PBNP Unit 2 was returned to full load operations on May 20, 2004.
301 | 3012010001 | 2010-06-19 | QR6 | Manual Reactor Trip | [45 empty] | Point Beach 2 | P | WE | SU | 1 | On June 19, 2010 at 06:36 CDT control room personnel initiated a manual reactor trip of Unit 2 from MODE 2 at 0% power. Prior to the manual reactor trip, an automatic turbine trip occurred due to receipt of a generator lockout signal. Prior to automatic turbine trip, power reduction to 44% had been completed and the unit was being maintained in a stable condition in MODE 1. Following the trip, all safety systems and equipment operated as expected. All rods fully inserted into the core. The generator lockout was due to incorrectly calculated generator protection third harmonic stator ground trip relay setpoints. The incorrect setpoints were based on data taken during Unit 2 startup following the fall 2009 refueling outage. The installation of the relay setpoints occurred on February 24, 2010, when Unit 2 was at 100% power. The setpoints were not correct for the new plant configuration across the full range of power operation. The third harmonic function relays were removed from service on June 20, 2010, pending resolution of appropriate setpoint values. Unit 2 was returned to service on June 21, 2010. Immediate corrective actions included disabling the affected relay functions until new setpoints are calculated or the trip function is converted to an alarm function.
301 | 3012010002 | 2010-07-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Point Beach 2 | P | WE | PO | 64 | On 7/9/10 at 06:47 CDT, control room personnel initiated a manual reactor trip of Unit 2 from approximately 64% power as a result of a failure of the range diaphragm assembly in the 'A' feedwater regulating valve (FRV) [FCV] positioner. Safety systems functioned as expected. Control rods fully inserted into the core. Unit 2 was returned to full power on 7/11/10 at 07:57. Corrective actions included rebuilding the failed 2CS-466 'A' FRV positioner and the 2CS-476 'B' FRV positioner. This 60-day licensee event report is being submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(iv)(A).
301 | 3012012001 | 2012-06-27 | QR6 | Manual Reactor Trip | [45 empty] | Point Beach 2 | P | WE | PO | 100 | On June 27, 2012 at 2046, a Point Beach Nuclear Plant (PBNP) Unit 2 manual reactor trip was actuated due to indications of a loss of load to the main turbine. At approximately 2045 alarms were received in the control room indicating reduced PBNP Unit 2 turbine first stage pressure and generator megawatts, indicative of a significant reduction in turbine load. Control rods were responding as designed by inserting into the reactor to reduce reactor power. Operations noted that the turbine speed indication on the EH control panel was reading high with the generator output breaker closed, indicating a control system failure. Based on these indications, the Shift Manager directed that the reactor be shutdown by manually actuating the reactor protection system. No automatic reactor protection setpoints were exceeded and an automatic shutdown was not actuated or required. Based on troubleshooting, NextEra determined that the loss of turbine load was due to a failure of the speed channel card in the EH system. The speed channel card was replaced. Pursuant to 10 CFR 50.73 (a)(2)(iv)(A), the event is reportable as an event or condition that resulted in manual actuation of the reactor protection system.
302 | 3021987009 | 1987-07-02 | QR8 | Spurious Reactor Trip | [45 empty] | Crystal River 3 | P | BW | PO | 88 | On July 2, 1987, Crystal River Unit 3 was operating at 88.4% Rated Thermal Power, generating 771 MWe. Surveillance testing on Channel B of the Reactor Protection System was in progress. The B Control Rod Drive Mechanism (CRDM) circuit breaker opened normally when the shunt trip device was tested, but would not reclose after testing. <br /><br />While investigation into the B CRDM breaker problem was in progress, the inverter supplying power to the A vital bus failed. The A vital bus automatically transferred to its alternate power source. During the transfer the bus experienced a sligh voltage dip which caused the A CRDM breaker to open. Since both breakers were open simultaneously, all power was removed from the control rod drive mechnaisms. This caused all control rods to fall to the fully inserted position and shut down the reactor. The CRDM breaker that would not close has been replaced. The inverter has been repaired and a modification has been prepared to lower the undervoltage setpoint.
302 | 3021987011 | 1987-07-10 | QR8 | Spurious Reactor Trip | [45 empty] | Crystal River 3 | P | BW | PO | 64 | On July 10, 1987, Crystal River Unit 3 was operating at 64% power and 523 MWe. The "C" reactor coolant pump had previously been secured, so the plant was operating with only 3 of 4 reactor coolant pumps in service. At 0537 a reactor trip occurred due to the reactor coolant pump power monitors. All 4 RPS channels indicated a loss of more than one RCP, even though the 3 RPC's remained in operation. Upon receiving the reactor trip, control room operators realized that the main turbine did not automatically trip, and they manually tripped the turbine. <br /><br />The cause was due to a failed relay for the "B" RCP power monitor circuit. The failed relay caused a power fuse to open, which led to all 4 RPS channels sensing more than 1 RCP off. The cause of the turbine not tripping was the failure of the reactor trip lockout relay. <br /><br />The plant was maintained in a stable condition following the trip. The failed RCP power monitor relay and open fuse were replaced. The failed reactor trip lockout relay was replaced. Both circuits were subsequently tested satisfactorily.
302 | 3021988006 | 1988-02-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Crystal River 3 | P | BW | PO | 56 | On February 28, 1988, Crystal River Unit 3 experienced a reactor trip during a power decrease from 99 percent to approximately 40 percent power. The trip was due to a Feedwater transient which resulted in high Reactor Coolant System pressure. The main turbine failed to automatically or remotely trip after the reactor trip, and operators manually opened the generator output breakers and manually shut the Main Steam Isolation Valves. <br /><br />The cause of the Feedwater transient was a broken stem nut in the yoke of the "B" Feedwater main block valve. The cause of the failure of the turbine to automatically or remotely trip was a failed turbine trip solenoid, and a potential contributing factor was corrosion of the trip circuit power fuse and fuse holder. <br /><br />The stem nut has been replaced with a nut manufactured on site in accordance with vendor instructions. The turbine trip solenoid and circuit fuse have been replaced, and the fuse holders have been cleaned. All new components were satisfactorily tested, as was the "A" Feedwater main block valve. Failure analyses have been performed on the stem nut and on the turbine trip solenoid.
302 | 3021988024 | 1988-10-28 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Crystal River 3 | P | BW | PO | 21 | Crystal River Unit 3 (CR-3) was in Mode 1, Power Operation, during the early morning hours of October 28, 1988. The reactor was producing 21% full power. Operators were preparing to close the generator output breakers. At 0328, output breakers were closed. Forty-four seconds after breaker closure, the reactor tripped. <br /><br />Reactor trip ultimately resulted from an increased control setting for the Main Turbine Governor Valves (GV's). The increased setting caused steam pressure to decrease more than expected, resulting in Main Steam and Main Feedwater isolation. As designed, Main Feedwater Pumps (MFWP's) tripped as part of the isolation. The Reactor Protection System tripped the reactor due to loss of MFWP's at greater than 20% full power. <br /><br />The GV position limit setting was reduced before restart following the trip. Operating procedures have been revised to include instructions regarding steam header pressure decrease following output breaker closure, and actions to be taken if pressure drops excessively.
302 | 3021989023 | 1989-06-16 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Crystal River 3 | P | BW | PO | 12 | On June 16, 1989 CRystal River Unit #3 was MODE 1 ( Power Operation) at 12% reactor power within the main turbine latched and rolling. At 1325, the Unit #3 Start-up Transformer became de-energized which resulted in a reactor/turbine trip. Both emergency diesel generators started due to the under voltage condition sensed on both 4160 V. buses. The diesel generators re-energized their respective buses. A loss of main feedwater occurred due to the loss of Unit #3 Start-up Transformer. The Emergency Feedwater Initiation and Control system actuated to supply feedwater to both Once Through Steam Generators. However, the motor driven emergency feedwater pump did not automatically start and was manually started. The cause of the degradation of off-site power was inadvertent actuation of a 230 KV feeder test trip circuit coincident with failure of a fault detector relay. The cause of the start failure of the emergency feedwater pump was a failed relay and a loose connection to a second relay in the automatic start circuit. Florida Power Corporation is evaluating the continued need for the test trip circuit pushbuttons in the off-site power supply cabinets. A testing program for the relays which initiate Emergency Feedwater on a loss of off-site power will be developed.
302 | 3021991003 | 1991-04-20 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Crystal River 3 | P | BW | PO | 47 | On April 20, 1991, Crystal River Unit 3 was operating in MODE 1, at 47% rated thermal power, performing Main Condenser (COND) water box and Circulating Water Pump (CWP) maintenance. Two of the four COND water boxes were out of service. At 0650, CWP-1A tripped, removing cooling from the A COND and the Secondary Services Closed Cycle Cooling Water System (SC) which provides cooling to turbine and generator equipment. CWP-1D continued to supply its main COND with cooling water. <br /><br /> The operators began reducing power to take the turbine off line, then tripped the turbine as many turbine temperature alarms were received. The turbine trip was below the Anticipatory Reactor Trip System bypass setpoint so no automatic reactor trip resulted. After the turbine trip automatic control systems and plant systems responded as designed; however, the configuration resulted in the Anticipated Transient Without Scram Mitigation System Actuation Circuitry (AMSAC) logic detecting Main Feedwater and Reactor Power input signals which met actuation setpoints. AMSAC initiated Emergency Feed Water (EFW) and the operator manually tripped the reactor due to initiation of EFW at power.<br /><br /> This event was caused by water intrusion into the CWP motor during a severe rainstorm. Corrective action will be to provide additional rain protection for the CWPs.
302 | 3021991014 | 1991-11-25 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Crystal River 3 | P | BW | PO | 20 | On the evening of November 25,1991, Crystal River Unit 3 was operating in Mode 1, power operation, at approximately 20 percent power. Plant startup was in progress. The output breakers were closed at 1716. Just after breaker closure, operators noticed the deaerator level was high and increasing. Efforts to restore proper deareator level were unsuccessful. At 1720 the 'B' Main Feedwater Booster Pump tripped, causing the Main Feedwater Pumps to trip. This caused an anticipatory reactor trip and initiation of Emergency Feedwater. <br /><br /> The Feedwater Booster Pump trip was caused by a false low level signal from the deareator level switch. The false signal resulted from age related failure of two gaskets on two other level switches sharing common sensing lines. Technicians replaced the gaskets with a different type gasket. Technicians also investigated the response of a deareator dump valve which had not operated properly as part of the level control scheme. Instruments were installed to monitor operation of condensate pumps and associated controls during subsequent startup to assure they controlled properly. <br /><br /> Guidance and training is being provided to the operations crew on startup evolutions to assure consistency.
302 | 3021991017 | 1991-12-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Crystal River 3 | P | BW | PO | 50 | On December 2, 1991 at 2000, Crystal River Unit 3 (CR-3) was commencing a shutdown from 100 percent Rated Thermal Power (RTP) to allow trouble shooting Power Range Nuclear Instrumentation (NI) Channel NI-8, which had previously gone to zero indicated power and tripped Reactor Protection System (RPS) Channel "D". As power was reduced, a pre-existing Quadrant Power Tilt (QPT) began to increase. At 2315, QPT exceeded steady state limit of Technical Specifications and reduction of the nuclear overpower trip setpoint was required. At 0200 on December 3, power was stabilized at 50 percent RTP to allow adjustment of the nuclear overpower trip setpoint. Technicians placed Channel "A" of RPS in bypass and began reducing the overpower trip setpoint. During adjustment of the overpower trip setpoint, an erroneous reactor power signal was sent to the Integrated Control System (ICS), due to NI-8 indicating zero, resulting in feedwater flow decrease to the steam generators and control rod withdrawal. The reactor tripped on high pressure in approximately 30 seconds. Several factors contributed to this event including incorrect operator training on the NI power averager/auctioneer circuit, and lack of cautions in the procedure regarding setpoint adjustment with a failed NI. Plant procedures are being revised to provide cautions and operators will receive training on operation of the averager/auctioneer.
302 | 3021991018 | 1991-12-08 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | Crystal River 3 | P | BW | PO | 15 | On December 8, 1991, Crystal River Unit 3 was being returned to power operation. As reactor power was being increased from 11% RATED THERMAL POWER (RTP) to 15% RTP, Reactor Coolant System (RCS) pressure increased to the open setpoint for the Pressurizer Spray Valve, RCV-14. RCV-14 opened; however, the "closed" indicating lamp did not extinguish. On decreasing RCS pressure, RCV-14 did not close, resulting in a continued slow decrease in RCS pressure. Prior to RCS pressure reaching the Engineered Safeguards (ES) actuation setpoint, an operator inappropriately bypassed ES. Shift supervision directed ES out of bypass and ES actuation was initiated. After ES was reset, a plan was implemented which bypassed ES and used High Pressure Injection to raise RCS pressure. RCV-14 was manually isolated, terminating the event. The plant was placed in MODE 5 (COLD SHUTDOWN) and RCV-14 was repaired and tested satisfactorily. Plant Maintenance Procedures are being revised to preclude recurrence of this type of Motor Operated Valve failure. Administrative guidance has been developed on the bypassing of ES actuation signals.
302 | 3021992001 | 1992-03-27 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Crystal River 3 | P | BW | PO | 98 | On March 27, 1992, Crystal River Unit 3 was operating in MODE 1 at 98% Rated Thermal Power. Maintenance was in progress on the 'C' Vital Bus inverter. The inverter was malfunctioning and troubleshooting was in progress to determine the root cause of the problem. Leads had been lifted to partially isolate a constant voltage transformer internal to the inverter. At 1308, with the inverter output isolated, it was connected to the DC system input. This imposed a 350 volt peak-to-peak AC feedback signal on the DC system. This caused two relays which receive control power from the DC system to actuate, opening the feeder breakers and isolating the 230 KV Offsite Power Transformer. This de-energized the 4160 volt Engineered Safeguards (ES) busses, causing a reactor trip and an Emergency Diesel Generator start. A four hour report was made as required by 10CFR50.72(b)(2)(ii). This event is reportable under 10 CFR 50.73(a)(2)(iv). The relays, which are used for normal operation of the transformer feeder breakers and do not perform any protective relaying function, were disabled prior to restart to preclude future spurious trips.
302 | 3021992027 | 1992-12-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Crystal River 3 | P | BW | PO | 100 | On December 29, 1992, Crystal River Unit 3 was operating in MODE 1 (POWER OPERATION) at 100% of RATED THERMAL POWER. At 04:16:16, the plant tripped due to high Reactor Coolant System (RCS) pressure caused by inadequate Main Feedwater (MFW) flow to the 'B' Once Through Steam Generator. Binding of the 'B' MFW Pump (MFWP) turbine control actuator caused the pump speed to decrease, resulting in a reduction in MFW flow on the affected side. RCS pressure increased to the high pressure trip setpoint due to inadequate primary-to-secondary heat transfer. <br /><br /> Internal binding was caused by a buildup of deposits in the pump control actuator combined with normal wear of internal parts. External binding was the result of rubbing between two actuator components. The MFWP oil accumulators were purged several times. Control oil filters were replaced. The MFWP actuator was replaced and the linkage arm was cleaned and reassembled. Florida Power Corporation (FPC) is establishing a preventive maintenance (PM) program to replace the MFWP turbine control actuators and rebuild the actuator linkage every six years. FPC is also evaluating the need for a PM program to clean the associated oil systems on a periodic basis.
302 | 3021993009 | 1993-09-18 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Crystal River 3 | P | BW | PO | 100 | On September 18, 1993, Crystal River Unit 3 was in MODE 1 (POWER OPERATION) at 100% power. At 2348, a high differential current alarm On September 18, 1993, Crystal River Unit 3 was in MODE 1 (POWER OPERATION) at 100% power. At 2348, a high differential current alarm for the "D" Reactor Coolant Pump (RCP) was received in the control room. Almost immediately, the "D" RCP tripped on high differential current. The Integrated Control System responded by beginning an automatic plant runback to 75% power. Approximately eight seconds later, the Reactor Protection System tripped the reactor on flux/flow/imbalance. <br /><br /> One of the Main Steam Safety Valves did not fully reseat following the trip. Personnel dispatched to the valve discovered that a non-captive release nut had rotated slightly, preventing the valve from fully seating. The valve was returned to the fully seated position following a re-adjustment and locking of the release nut. FPC determined that the RCP trip was caused by a shorted "B" phase surge capacitor, which was replaced. Several other minor plant anomalies were experienced coincident with the reactor trip and were subsequently corrected. <br /><br /> FPC is considering additional evaluations and corrective actions.
302 | 3021996017 | 1996-05-31 | QR5 | Turbine Trip | [45 empty] | Crystal River 3 | P | BW | PO | 100 | On May 31, 1996, Florida Power Corporation's Crystal River Unit 3 was operating at 100% power generating 879 megawatts. While testing the turbine trip devices, an unexpected isolation of the steam flow path to the Main Turbine resulted in a reactor trip due to high Reactor Coolant System pressure. The Reactor Protection System performed as designed and operators responded properly per Emergency Operating Procedures. Several anomalies were noted during the event: a Turbine Bypass Valve did not control properly; two Main Steam Safety Valves (MSSV) did not reseat properly; Emergency Feedwater Initiation and Control (EFIC) actuated on low steam generator level limits; and steam was noted coming from the inboard seal on Emergency Feedwater Pump EFP-1. The cause of the event was debris in a manual isolation valve preventing it from fully seating thus allowing Electro-Hydraulic Control (EHC) fluid to drain. A post-trip analysis addressed completion of main feedwater/ICS trip data reviews, EHC fluid flushes on all Turbine Trip Solenoid Valves, concerns regarding EFP-1 seal leakage and verification of lift setpoints for the MSSV's. Other actions will include enhancements to the EHC post-maintenance and turbine check procedures, a detailed evaluation of ICS response to low steam generator levels, and possible changes to turbine bypass and MSSV's.
302 | 3021998003 | 1998-02-11 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Crystal River 3 | P | BW | PO | 100 | On February 11, 1998, at approximately 0030, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) experienced a loss of power to the Integrated Control System (ICS), which eventually caused a reactor top. The ICS was in AUTO when a loss of power caused the Main Feedwater pumps to run back to minimum speed. This caused the ATWS (Anticipated Transient Without SCRAM) Mitigating System Actuation Circuitry (AMSAC) to initiate the Emergency Feedwater System (EFW) and trip the turbine. The AMSAC is designed to actuate when indicated feedwater flow is less than 17 percent and reactor power is greater than 50 percent. The turbine trip Anticipatory Reactor Trip System (ARTS) is designed to trip the reactor automatically when the turbine trips and reactor power is greater than 45 percent. The plant responded as designed to a loss of power to the ICS. The root cause of the loss of power to the ICS was a zener diode not adequately soldered to the printed circuit board trace for the power supply monitor. FPC performed an evaluation of the reactor trip in accordance with Administrative Instruction (AI) AI-704, Reactor Trip Review and Analysis. The evaluation determined the plant responded as expected with minor equipment anomalies. The equipment anomalies were evaluated by FPC and corrected as appropriate. FPC replaced the ICS power supply monitor. FPC will perform a visual inspection of similar circuit boards installed in the plant during the next available outage.
302 | 3021998009 | 1998-08-27 | QL5 | Partial Closure of MSIVs | [45 empty] | Crystal River 3 | P | BW | PO | 100 | At 2348, on August 27, 1998, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. While troubleshooting a half trip signal on Emergency Feedwater Initiation and Control (EFIC) System Channel A Main Steam Line Isolation (MSLI), both Main Steam Isolation Valves (MSIVs) from the "A" Once Through Steam Generator (OTSG) closed. The reactor operator initiated a manual reactor trip upon closure of the two MSIVs. The reactor protection system performed as expected and reactor operators responded properly per Emergency Operating Procedures (EOPs). The cause for the MSIVs closing was personnel error during the EFIC troubleshooting activity. The cause for the manual reactor trip has been reviewed with Maintenance Department personnel and Operations Department Nuclear Shift Managers. Since 1990, FPC has submitted three Licensee Event Reports involving plant equipment troubleshooting activities that resulted in a reactor trip.
302 | 3022002002 | 2002-11-07 | QR5 | Turbine Trip | [45 empty] | Crystal River 3 | P | BW | PO | 100 | On November 7, 2002, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER (RTP). One of two 500 kilovolt (KV) substation generator output breakers (breaker 1662) was closed. The other 500KV substation generator output breaker (breaker 1661) was out of service for scheduled maintenance. At 14:39, a main turbine trip and subsequent anticipatory reactor trip occurred when breaker 1662 opened. The cause for opening of breaker 1662 was mis-operation of an Agastat 7024AC time delay relay contact used to remove power from phase-to-phase fault relay 39E and phase-to-ground fault relay 39F. Upon removal of the supply power to the Agastat relay, the relay contact created a voltage spike of the 39E relay power supply. Reactor Protection System actuation is reportable under 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. The Agastat relay has been replaced by a multi-function programmable relay to block the trip signal from the 39E and 39F relays when applying or removing control power and prior to de-energizing the relays. No previous similar occurrences have been reported to the NRC by CR-3.
302 | 3022003005 | 2003-11-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Crystal River 3 | P | BW | PO | 37 | At 17:34, on November 5, 2003, Progress Energy Florida, Inc., (PEF) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at approximately 37 percent RATED THERMAL POWER. While troubleshooting problems with the "B" Main Feedwater Pump (FWP-2B) control circuits, a feedwater transient occurred that resulted in an automatic reactor trip. When FWP-2B was placed in automatic, the control signal to the pump decreased significantly. This caused a loss of feedwater flow to both Once Through Steam Generators (OTSGs). Operators attempted to restore feedwater flow by placing FWP-2B back in manual and raising the set point of both feedwater pump controllers. As OTSG level continued to decrease, Reactor Coolant System (RCS) pressure and temperature increased. An automatic reactor trip occurred on high RCS pressure. An automatic Emergency Feedwater (EFW) System actuation occurred on low OTSG levels. The cause for this event was human error associated with not verifying the correct circuit cards were installed in the Integrated Control System (ICS) during the recent refueling outage. The correct circuit cards were installed in the ICS to correct the problem. Reactor Protection System and EFW System actuation are reportable under 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported to the NRC by CR-3.
302 | 3022004001 | 2004-03-24 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Crystal River 3 | P | BW | PO | 100 | At 03:31, on March 24, 2004, Progress Energy Florida, Inc., (PEF) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. While in steady state operation, a large decrease in the reactor demand and Main Feedwater flow demand signals occurred within the Integrated Control System (ICS). The Main Feedwater pumps ran back until discharge pressure was less than steam generator pressure, at which time the Main Feedwater flow reduced to zero. Upon sensing less than 17 percent Main Feedwater flow, the Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuitry (AMSAC) initiated a turbine trip and actuated the Emergency Feedwater System (EFW). The Reactor Protection System (RPS) sensed the turbine trip above 45 percent reactor power and initiated an anticipatory reactor trip. The cause for this event was age-related failure of the zener diodes in the +15 volt regulator circuit for a Bailey 820 Control Module in the Main Feedwater Integrated Control System. The circuit board was replaced. RPS and EFW valid actuations are reportable under 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported to the NRC by CR-3.
302 | 3022004003 | 2004-09-06 | QC5 | Loss of Non-safety-Related Bus | [13 empty] | X | [30 empty] | X | Crystal River 3 | P | BW | PO | 97 | At 11:51, on September 6, 2004, Progress Energy Florida, Inc., Crystal River Unit 3, was in MODE 1 (POWER OPERATION) at 97 percent RATED THERMAL POWER. During Tropical Storm Frances, phase-to-ground faults occurred concurrently on a 230 kilovolt transmission line and a 230 kilovolt switchyard south bus breaker. Loss of power to the Startup transformer resulted in opening the reactor trip breakers, tripping of the reactor coolant pumps and main feedwater pumps, and loss of power to the Main Turbine Lube Oil System. A main turbine trip and subsequent actuation of the Reactor Protection System occurred. The Emergency Feedwater Initiation and Control System actuated to feed the Once Through Steam Generators. The transmission line fault was caused by mechanical failure of a carbon steel pin in a vertical string of insulators due to high wind conditions. The breaker fault was caused by flash over due to contamination from wind and salt spray. The insulator string was replaced. The breaker was tested, inspected, washed down and returned to service. Actuation of the Reactor Protection System and Emergency Feedwater System are reportable to the NRC. This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported.
302 | 3022005003 | 2005-10-29 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Crystal River 3 | P | BW | PO | 16 | At approximately 01:26, on October 29, 2005, Progress Energy Florida, Inc., Crystal River Unit 3, was in MODE 1 (POWER OPERATION) at approximately sixteen percent RATED THERMAL POWER when a manual reactor trip was initiated in anticipation of an Emergency Feedwater System actuation. The plant was being shutdown for a refueling outage when the only operating Condensate Pump motor tripped on electrical overload and resulted in a loss of both Underwater Pumps. The second Condensate Pump had been shutdown by procedure and removed from service for maintenance. The cause for loss of the operating Condensate Pump was insufficient guidance and information available to the Reactor Operators to prevent operation at critical speeds. The Condensate Pump motor/magnetic coupling/pump assembly has been replaced. Procedural guidance is being developed to ensure operation at critical speeds is avoided. This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A). The Reactor Protection System and Emergency Feedwater System performed as designed. This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported to the NRC.
302 | 3022007002 | 2007-02-21 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Crystal River 3 | P | BW | PO | 71 | At 19:14, on February 21, 2007, Crystal River Unit 3 (CR-3), operated by Florida Power Corporation (FPC) doing business as Progress Energy Florida, Inc., was in MODE 1 (POWER OPERATION) at approximately 71 percent RATED THERMAL POWER. CR-3 was at reduced power for planned maintenance on one of four main condenser water boxes when the Integrated Control System (ICS) for Main Feedwater (FW) became erratic causing actual FW flow to drop to zero in both FW trains which underfed the Once-Through Steam Generators. The Reactor Protection System (RPS) actuated on high Reactor Coolant System (RCS) Pressure causing a reactor trip. Emergency Feedwater Initiation and Control (EFIC) actuated on low steam generator levels. The cause for this event was inadequate human performance in the implementation of the ICS circuit card refurbishment program which resulted in an age-related failure of the zener diodes in the +15 volt regulator circuit for a Bailey 820 Control Module in the ICS. RPS and Emergency Feedwater System valid actuations are reportable under 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. LER 50-302/2004-001-00 documents a previous similar event at CR-3.
302 | 3022008003 | 2008-08-24 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Crystal River 3 | P | BW | PO | 60 | At 15:53 on August 24, 2008, Progress Energy Florida, Inc. (PEF), Crystal River Unit 3 (CR-3) was operating in MODE 1 (POWER OPERATION) at approximately 60 percent RATED THERMAL POWER, when the reactor was manually tripped. At 15:37, the Condensate Pump CDP-1A magnetic coupling became uncoupled. Delays in rapid power reduction led to a low Deaerator (FWHE-1) level and eventual cavitation of the Main Feedwater (FW) System booster pumps and Main FW pumps. The cavitation caused a loss of FW flow control to the Once-Through Steam Generators. This loss of flow control led to the decision to manually trip the reactor. The root cause for this event was original plant design failing to provide adequate alarms to the operating crews to promptly identify Condensate Pump failures. Required equipment operated as designed during the manual reactor trip. Loss of FW is an analyzed event bounded by the CR-3 Final Safety Analysis Report accident analysis. This condition does not represent a reduction in the public health and safety. Operating crews were trained on this event. Compensatory measures to alert the operating crew of a loss of a Condensate Pump were established. Design options are being evaluated to alert the operating crew of Condensate Pump failures. A previous similar occurrence has not occurred or been reported to the NRC.
302 | 3022009001 | 2009-01-27 | QR6 | Manual Reactor Trip | [45 empty] | Crystal River 3 | P | BW | PO | 100 | At 10:17, on January 27, 2009, Progress Energy Florida, Inc. (PEF), Crystal River Unit 3 (CR-3), was operating in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER when the Reactor Coolant System pressure was observed rising toward the automatic reactor trip setpoint and the reactor was manually tripped. Prior to this event, technicians were performing preventive maintenance on the 'A' 4160 volt Unit Bus indication located in the Main Control Board. Doble Relay Test Set leads were incorrectly connected in place of the Fluke MultiMeter leads during a voltage check. This resulted in a path to ground that blew the 'A' and 'B' Secondary Side potential transformer fuses, resulting in a loss of voltage indication on the 'A' 4160 volt Unit Bus and tripping loads. The Reactor Protection System responded as expected to the manual trip signal, control rods fully inserted and safety systems functioned' as required. No reduction in the public health and safety was created. The causes for the manual reactor trip were improper use of human performance tools and inadequate closure of corrective actions for a previous similar event. All relay work was immediately stopped and a Human Performance Review Board Meeting was held. This report is submitted pursuant to 10CFR50.73(a)(2)(iv)(A). A previous similar occurrence was documented in Nuclear Condition Report (NCR) 133661.
302 | 3022009003 | 2009-08-24 | QR6 | Manual Reactor Trip | [45 empty] | Crystal River 3 | P | BW | PO | 100 | At 11:00, on August 24, 2009, Progress Energy Florida, Inc. (PEF), Crystal River Unit 3 (CR-3) was operating in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER when the Control Room staff received multiple alarms and observed the Group 7 control rods fully insert into the reactor core. The reactor was manually tripped prior to automatic actuation of the Reactor Protection System (RPS). Prior to this event, electricians were implementing Preventive Maintenance procedure PM-126, "Electrical Checks of CRD [Control Rod Drive] Power Train." When the Integrated Control System was placed in Automatic, the output driver within the Group 7 programmer caused an erroneous phase sequence to the control rod drive stators, culminating in inadequate magnetic force to restrain the rods from dropping during movement. The RPS responded as expected to the manual trip signal, control rods fully inserted and safety systems functioned as required. No reduction in the public health and safety was created. The programmer failure was caused by inadvertent test jumper contact while using an improperly fused test jumper. This caused an over-current failure of the output driver within the programmer. The programmer was replaced and PM-126 was placed on administrative hold. This report is submitted under 10CFR50.73(a)(2)(iv)(A). No previous similar occurrence has been reported to the NRC.
304 | 3041988007 | 1988-10-08 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Zion 2 | P | WE | PO | 56 | On 10/08/88, Unit 2 operators were performing Periodic Test (PT)-1, "Rod Control Cluster Exercise" AA!. This test involves stepping each bank of control rods into and out of the core in order to verify proper rod operation. When the unit operators received an Urgent Failure Alarm from the control rod circuitry, investigation found a blown fuse indicator in the SCD cabinet, When the operators attempted to replace this fuse, the Unit 2 reactor tripped. <br /><br /> The cause of the reactor trip was procedural deficiency. The cause of the Rod Control System Urgent Failure annunciator was component failure. All safety systems responded as designed. <br /><br />Corrective actions included analyzing all failed components to determine the mode of failure, and revising Operating procedures to require System Engineering concurrence before removing fuses from rod control cabinets.
304 | 3041988009 | 1988-10-12 | QR5 | Turbine Trip | [45 empty] | Zion 2 | P | WE | PO | 94 | October 12, 1988 at 1336 hours the reactor tripped due to a turbine trip while an Instrument Maintenance (IM) Technician was attempting to calibrate the Control Room alarm switch for the Condenser Low Vacuum alarm accordance with procedure 2PS-TSS63LV. <br /><br />The IM Technician disconnected the pneumatic sensing line to the alarm switch, which is connected to the vacuum Trip section of the Turbine Protection Block. This action caused the Trip Block to sense a Low Vacuum condition and subsequently trip the Main Turbine TA!. All systems functioned as designed to place the unit the Hot Shutdown mode automatically. The health and safety of the public were not compromised. <br /><br />The root cause of the event has been determined to be the lack of an adequate procedure to perform the task. The procedure in question is being changed to provide the proper direction to perform the task without affecting the unit. <br /><br />The Labelling Department will correctly label the alarm switch and isolation valve in the HP Turbine closure. <br /><br /> The IMs will continue the ongoing effort to upgrade the IM procedures.
304 | 3041990001 | 1990-01-18 | QR6 | Manual Reactor Trip | [45 empty] | Zion 2 | P | WE | PO | 40 | On January 18, 1989, at approximately 0235, Zion Unit 2 was operating in a steady configuration at approximately 40% power. A condenser tube leak test was being performed. Due to a deficiency in the procedure for this test and subsequent corrective action, a condenser vacuum excursion was experienced. This caused the turbine control system to oscillate governor valves #2 and #3 over a 5% range. The unit operator attempted to alleviate this oscillation condition by switching alternatively between turbine manual and turbine automatic control. Due to continued oscillation of the governor valves, the operator believed that the turbine control system was unable to control the turbine and therefore initiated a manual reactor trip. The governor oscillation was primarily introduced into the turbine control system from the condenser vacuum excursion through the impulse pressure feedback circuit. There were no safety consequences as a result of this event. The test procedure was rewritten to change the order of the valve line-up preventing future condenser vacuum excursions.
304 | 3041990010 | 1990-09-07 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Zion 2 | P | WE | PO | 98 | On 9/7/90 Zion Unit 2 tripped on a sudden loss of condenser vacuum. Inspections found a failed condenser expansion boot in the A-bay of the condenser, a failed low pressure turbine rupture disc, and that both of the feed water pumps' rupture discs had been deformed. Internal inspection of the condenser determined that the initiating event had been a failure of the boot. The root cause analysis determined that the condenser expansion boot had a life expectancy of 5 to 7 years but had been in service for 9 years. Aggravating the aged condition was improper torquing and exposure to excessive temperature. All safety systems responded as designed. Corrective action included replacement of the damaged components, adding the boots to the Preventive Maintenance program to ensure that they are replaced at 5 year intervals, and to follow vendor installation recommendations.
304 | 3041990011 | 1990-09-22 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Zion 2 | P | WE | PO | 39 | On September 22, 1990, at approximately 2151, Unit 2 was at 39% and ramping up in power when the 2W main power transformer experienced an internal fault. A major oil fire resulted from the 2W transformer explosion. The fire was successfully contained by the deluge system and was extinguished by the Fire Brigade. Neither the 2E main power, station auxiliary, or unit auxiliary transformers were damaged during the event. The NSS and secondary systems shutdown response was normal. <br /><br /> The 2W main power transformer experienced heavy mechanical damage due to the pressure spike resulting from the fault. Additionally, the isolated phase bus duct was significantly damaged by mechanical displacement from the transformer explosion and bus duct flashovers that occurred after the initial fault. No damage was found to the main generator.<br /><br /> The transformer was disassembled for the root cause investigation. The transformer expert determined that static electrification was not present and contamination could not be found. The expert concluded that the transformer experienced a primary to secondary fault. The most probable cause of the fault was nitrogen breakout. When the transformer was energized nitrogen bubbles in the oil were pushed upward within the transformer and an arc was developed. <br /><br /> The transformer was replaced with a spare unit, and the bus ducts and associated equipment were repaired. Additional precautionary measures being pursued include transformer cooler bank sequencing, addition of bus duct lighting arresters, and addition of a separate bus duct ground cable.
304 | 3041990013 | 1990-11-11 | QR5 | Turbine Trip | [45 empty] | Zion 2 | P | WE | PO | 99 | On 11-11-90 at 1014 Zion Unit 2 tripped due to a sensed loss of Main Turbine bearing oil pressure. The diaphragm in the bearing oil section of the Turbine Trip Device (TTD) had ruptured. This sensed loss of bearing oil pressure actuated the TTD which tripped the turbine. The turbine bearings were not damaged, as they did not lose oil pressure. <br /><br /> The root cause analysis determined that the diaphragm had been in service past its service life expectancy. Signs of cracking and hardness were visible. <br /><br /> Following verification of the new diaphragm shelf life, it was placed into the TTD. After performing PT-101 "Main Turbine Protective Device Trip Test", Section 5.2 "Low Bearing Oil Pressure Trip Test", the unit was returned to service. Currently a Preventive Maintenance procedure is being created to ensure that the TTD is properly maintained at each refuel outage.
304 | 3041991002 | 1991-03-21 | QP2 | Partial Loss of Feedwater Flow |  | X | [13 empty] | X | [29 empty] | Zion 2 | P | WE | PO | 99 | At 0930, during the performance of Operating Periodic Test (PT)-211, Wet Pipe Sprinkler System Test, the Unit 2 Unit Auxiliary Transformer (UAT) and the Main Power Transformer (MPT) were inadvertently deluged. At 1309, another deluge occurred on the System Auxiliary Transformer (SAT) causing the SAT to trip. The buses fed from the SAT automatically transferred to the UAT. The 2A feedwater pump tripped when the SAT tripped causing a Reactor Trip on Lo-Lo Steam Generator Level. When the main generator tripped, one diesel generator (DG) was Out of Service (OOS) for maintenance so an essential bus was not automatically re-energized. A Generating Station Emergency Plan (GSEP) Unusual Event (EAL 3D) was declared at 1335 and both units were started toward Cold Shutdown. The event was caused by spurious actuation of the Unit 2 transformer's Fire Protection deluge system and the improper positioning of the Fire Protection deluge nozzles. During this event all failures and actions taken were within the bounds of the Technical Specification limiting conditions for operation. Various corrective actions were developed and implemented to address the concerns that were raised as a result of this event.
304 | 3041991004 | 1991-06-11 | QP5 | Excessive Feedwater Flow | [45 empty] | Zion 2 | P | WE | PO | 17 | On June 11 1991, during Unit 2 plant startup, several unsuccessful attempts were made to use the bypass Feedwater Regulating Valves (FRV) SJ! in the automatic mode to control steam generator (S/G) level JO! while the unit operators were aligning the main feedwater pumps. The main feedwater system SJ! was successfully aligned with the bypass FRVs in the manual mode and the main turbine speed was increased to 1800 rpm. After the main generator was synchronized to the grid, the unit operators attempted to place the main FRVs in automatic and to close the bypass FRVs in manual. The main FRVs filled the S/Gs to 70% which then generated a turbine trip signal which then generated a reactor trip because reactor power was greater than 10%. <br /><br /> This event was caused by a failed capacitor in the power supply circuitry of the S/G level controller. Contributing to this event was a history of problems with leaking bypass FRVs. This lead to the incorrect diagnosis by the unit operators that the leaking bypass FRVs were causing the S/G level control problems. During this event all actions taken were within the bounds of the Technical Specification Limiting Conditions for Operation and there was no safety significance to this event. Corrective actions included determining the root cause of the capacitor failure, reviewing the S/G level control system to determine what information should be provided to the unit operators, identifying recurring Feedwater System problems, and verifying the calibration of the bypass FRV controller.
305 | 3051987008 | 1987-06-26 | QR5 | Turbine Trip | [45 empty] | Kewaunee | P | WE | PO | 100 | On June 26, 1987, at 1115, with the plant at 100% power, a plant electrician pulled out the drawer of the upper phase B Main Generator Potential Transformer cabinet. This caused a loss-of-excitation signal to the Main Generator resulting in a generator trip, followed by a turbine/reactor trip. <br /><br />Information was needed on the electrical size of the Potential Transformers located in the Emergency Diesel Generator Control and Excitation Cabinet. A plant electrician was asked to collect this information by opening the cabinet door and reading the nameplate data. The electrician misunderstood the instructions and pulled out the Main Generator Potential Transformer Cabinet drawer. When the Potential Transformer was pulled out an open circuit resulted, and the voltage signal to the loss-of-excitation relay was disconnected. This loss of input caused the loss-of-excitation relay to be energized, resulting in a loss-of-excitation generator trip. <br /><br />The root cause of the event was personnel error. The electrician misunderstood his job task. To prevent recurrence, the Main Generator Potential Transformer cabinet will be locked and a caution sign will be placed on the front of the drawer. <br /><br /> The plant systems responded as designed and the operators followed appropriate procedures for plant stabilization. <br /><br /> This event is being reported as required by 10 CFR 50.73(a)(2)(iv).
305 | 3051987009 | 1987-07-10 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Kewaunee | P | WE | PO | 100 | At 1143 CDT on July 10, 1987, with the plant at full power, a reactor/turbine trip occurred due to an undervoltage (UV) transient on the 4160 volt electrical buses, designated as 1-1 and 1-2, which supply the Reactor Coolant Pumps and Main Feedwater Pumps. <br /><br /> During normal power operation, the Main Auxiliary Transformer (MAT) powers the 4160 volt buses 1-1 and 1-2 from its "Y" windings and 4160 volt buses 1-3 and 1-4 was badly damaged due to insulation failure and a subsequent ground fault. The fault on the "X" windings caused the voltage on the "Y" windings to decrease resulting in a coincident undervoltage condition of less than 77% of rated voltage for greater than 0.1 seconds on buses 1-1 and 1-2, causing a reactor trip. <br /><br />Immediately after the trip, operators implemented the appropriate Emergency Operating Procedures and stabilized the plant at Hot Shutdown. Plant systems performed as designed. <br /><br /> Prior to start-up, the damaged section of the Bus Bar was isolated. Buses 1-3 and 1-4 are currently being powered from the Reserve Auxiliary Transformer (RAT), while the MAT continues to feed Buses 1-1 and 1-2. Additional corrective actions included contacting the manufacturer to provide an in-depth analysis and a consultant for an independent assessment. The damaged section of the Bus Bar will be replaced. There was no other equipment damage as a result of this event. <br /><br /> This event is being reported per 50.73(a)(2)(iv) as an actuation of the Reactor Protection System and actuation of Engineered Safety Features.
305 | 3051988001 | 1988-03-02 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Kewaunee | P | WE | PO | 93 | At 1348 on March 2, 1988, with the plant at 93.3% power due to the end of life coastdown prior to the annual refueling outage, a reactor/turbine trip occurred due to an undervoltage (UV) condition on 4160 volt electrical buses 1-1 and 1-2. These buses supply power to the reactor coolant pumps (RXCP) and the main feedwater pumps (FWP). <br /><br />During normal power operation, the main auxiliary transformer (MAT) supplies power to the 4160 volt buses 1-1 and 1-2 from its "Y" windings. A section of the bus bar running from the MAT to the bus switchgear was badly damaged due to insulation failure and a subsequent fault. The fault on the bus bar caused an undervoltage condition of less than 77% of rated voltage on buses 1-1 and 1-2, resulting in a reactor trip. The reserve auxiliary transformer (RAT) assumed the loads for buses 1-1 and 1-2. Based on the amount of smoke present in the turbine building the Shift Supervisor activated the plant's emergency siren which required all on-site personnel to assemble for accountability. The differential current protection functioned as designed and opened all breakers on the affected protection zone. This de-energized the affected bus and terminated the fire. The fire team was dispatched to control the situation. Immediately after the trip, operators implemented the appropriate Operating Procedures and stabilized the plant at hot shutdown. Plant systems performed as designed. <br /><br />The plant then entered its scheduled refueling shutdown. Corrective actions included a complete investigation by the manufacturer of the bus bars, a private consultant, and an independent laboratory. They will provide an independent analysis of the failure. The damaged section of the bus bar and the insulation on the entire bus from the MAT to the bus 1-1 and 1-2 switchgear will be replaced during the refueling outage with a different type insulation.
305 | 3051988004 | 1988-04-12 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Kewaunee | P | WE | PO | 23 | At 0215 on 4/12/88 while the plant was at 23% reactor power in a startup following the cycle XIII-XIV refueling outage, a low condenser hotwell level of approximately 5% caused a condensate pump trip, an associated feedwater pump trip, and then a turbine/reactor trip. These actuations occurred during a secondary plant flushing evolution. This is a post-outage special procedure which flushes contaminants from secondary plant piping and the condenser that may have been introduced into the secondary system during the refueling outage. <br /><br />The secondary plant piping was flushed twice, and then the condenser was flushed 5 times. During the final condenser flush at 23% power, the hotwell level decreased to approximately 5%. At approximately 5% level the condensate pump tripped due to the low hotwell level. This pump trip ensures adequate net positive suction head is maintained for the condensate pump. <br /><br /> The cause of the event was a combination of the procedure requiring local valve manipulations outside of the control room, communication difficulties, and the rapid rate of decrease in the hotwell level. This combination resulted in the hotwell level decreasing to below the condensate pump trip setpoint. The condensate pump trip resulted in an associated feedwater pump trip followed by a turbine/reactor trip. <br /><br /> As a corrective action potential hardware changes which would limit the number of remote valve manipulations required to be performed outside of the control room are being evaluated.
305 | 3051988006 | 1988-05-02 | QR8 | Spurious Reactor Trip | [45 empty] | Kewaunee | P | WE | PO | 100 | At 1124 on May 2, 1988, with the plant operating at 100% power the plant experienced a reactor/turbine trip. A spurious trip signal on the Channel IV Overtemperature Delta Temperature (OT DELTA T) trip circuitry in conjunction with the OT DELTA T function for channel I being tripped for performance of a monthly instrument check caused the reactor/turbine trip. <br /><br />The monthly surveillance procedure SP 48-003E, Nuclear Power Range N41 Instrument Channel Test at >10% Power, requires that the reactor protection related to N41 be placed in a tripped condition. This included the Channel I OT DELTA T reactor trip. Faulty wires in the Channel IV OT DELTA T setpoint calculator made an intermittent connection causing the setpoint to spike. When the setpoint dropped below the Channel IV DELTA T value, which had remained constant, the 2 of 4 logic for OT DELTA T trip was made. This resulted in a reactor/turbine trip. <br /><br />The root cause of the event was an equipment failure. The Foxboro box for the Channel IV OT DELTA T setpoint calculator had an intermittent connection between its connector plug and an internal circuit board due to faulty wires. Had other reactor protection system testing not been in progress this failure would not have resulted in a reactor trip. <br /><br /> The wires identified as faulty were replaced and the setpoint calculator was reinstalled. A strip chart recorder was mounted locally and was checked periodically for several days following the plant's restart to verify the box was functioning correctly. <br /><br />This event is being reported as required by 10 CFR 50.73(a)(2)(iv).
305 | 3051989016 | 1989-12-27 | QR5 | Turbine Trip | [45 empty] | Kewaunee | P | WE | PO | 100 | At 1658 CST on December 27, 1989, with the reactor at 100% power, the plant experienced a turbine/reactor trip. The reactor trip was caused by both turbine stop valves closing coincident with the plant power level greater than 10%.<br /><br /> The turbine stop valves closed as a result of a decrease in electro-hydraulic (EH) trip fluid header pressure. The decrease in EH pressure could be caused by either of two valves opening in response to signals allowing the EH fluid to be dumped. <br /><br /> The root cause of the decrease in EH trip fluid header pressure could not be determined. A multi-disciplined committee was formed to review the event using formal root cause analysis techniques. Based on the review of all applicable plant parameter data, the team generated several possible scenarios that may have occurred. A specific scenario which was the initiating event could not be conclusively determined. The report generated by the committee included several recommendations for follow-up inspections and maintenance during the next refueling outage (scheduled for March of 1990).<br /><br /> The plant was stabilized in the hot shutdown condition. As expected, the auxiliary feedwater pumps started, which is an ESF actuation, in response to the trip. This event is being reported as required by 10 CFR 50.73(a)(2)(iv).
305 | 3051991010 | 1991-10-12 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Kewaunee | P | WE | PO | 99 | At 1400 CDT on October 12, 1991, with the plant at full power, a reactor/ turbine trip occurred returning equipment to service during the implementation of Preventive Maintenance Procedure (PMP) 38-10, "DC Supply and Distribution (EDC) 20 KVA Inverter Maintenance." During this process 125 VDC Distribution Cabinet BRD-103 was de-energized as a result of inadequate non-safeguard breaker coordination. This de-energization caused the feedwater regulating valves (FW-7A and B) to close, resulting in a trip signal from the subsequent steam flow-feedwater flow mismatch coincident with low water level in steam generator A. As expected, the auxiliary feedwater pumps started, which was an ESF actuation, in response to plant conditions.<br /><br /> A main contributor to this event was inadequate coordination between the 300 amp breaker which supplies 125 VDC Distribution Cabinet BRD-103 and the 200 amp breaker from BRD-103 to a non-safeguard inverter. To prevent recurrence the magnetic trip settings of the respective breakers were adjusted accordingly. In addition, any modifications necessary to further ensure proper coordination of non-safeguard DC breakers will be scheduled for the 1992 refueling outage. <br /><br /> The plant safety systems responded as designed and the operators followed appropriate recovery procedures for plant stabilization. In addition to the plant trip and corresponding ESF actuation, a Technical Specification required instrument channel check was not performed during recovery activities on the shift immediately following the plant trip. <br /><br /> This event is being reported as required by 10 CFR 50.73(a)(2)(iv) and 10 CFR 50.73(a)(2)(i).
305 | 3051992017 | 1992-09-15 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Kewaunee | P | WE | PO | 100 | This report describes an event that resulted in a reactor trip from 100 percent power. The trip occurred at 0243 CDT on September 15,1992 and was caused by a failure of the number 4 bushing on the main generator output breaker (G-1 OCB). The bushing failure resulted in a generator lockout, a turbine trip, a reactor trip, and isolated the 345 kilovolt offsite power supplies to the substation. Offsite power continued to be supplied to the plant through the two 138 kilovolt substation power supplies. G-1 OCB is an off circuit breaker and is located in the substation, which is outside of the protected area of the plant. Since the bushing is oil filled, the failed bushing resulted in a fire. The fire was isolated to G-1 OCB and was extinguished at 0400 hours. <br /><br /> The cause of the bushing failure could not be determined. The breaker had been overhauled during the 1992 refueling outage. In addition to the scheduled overhaul, annual predictive maintenance is performed. Neither indicated any degradation of the bushing; however, the inability to predict a bushing failure is not uncommon. <br /><br /> Prior to returning the plant to service, the bushing was replaced and the breaker was tested. Oil samples taken from the main transformer were analyzed to ensure that the fault on G-1 OCB did not damage the transformers. After repairs were completed, the plant was reconnected to the grid at 2050 hours on September 17, 1992.
305 | 3051992020 | 1992-11-01 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Kewaunee | P | WE | PO | 100 | This report describes the events that led to the initiation of a manual reactor trip from 100 percent power, and the post-trip plant response. The manual reactor trip was initiated at 2340 hours on November 1, 1992 in response to low forebay level, the failure of all four traveling water screens, decreasing condenser vacuum, and dips in electrical generator output. Following the manual trip, plant systems responded as designed with the following two exceptions: <br /><br /> 1 . A non-safety related circuit breaker, 1-407, which connects an alternate supply of power to electrical bus 4 from the reserve auxiliary transformer did not automatically close on a loss of power to the main auxiliary transformer. <br /> 2. Feedwater control valve, FW-7A, failed to close completely. <br /><br /> The event was initiated by a buildup of debris on the traveling water screens which resulted in a low forebay level and subsequent failure of the screens. Sustained strong easterly winds had resulted in increased amounts of debris being deposited on the screens.<br /><br /> Prior to returning the plant to service, a post-trip review was performed to determine and correct the causes of the equipment malfunctions. Breaker 1-407 and FW-7A were tested and shown to operate correctly. Additional testing of each component is scheduled for the 1993 refueling outage. The plant was connected to the grid at 1121 on November 3, 1992.
305 | 3051993001 | 1993-01-28 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Kewaunee | P | WE | PO | 100 | On January 28, 1993, at 0443 hours, with the plant operating at 100% power, a large fault on main feedwater pump B motor caused an undervoltage condition on Bus 1 and Bus 2. The bus voltage dropped below the undervoltage reactor trip setpoint and initiated an automatic reactor trip. The voltage on both buses quickly recovered once the fault was isolated. <br /><br /> On January 29, 1993, during the subsequent plant startup, another reactor trip occurred at 1516 hours from 5% power. reached the low-low level reactor trip setpoint of 17% while steam generator level was being manually controlled. Problems with steam dump valve SD-11A1 (to the condenser) contributed to the difficulty in controlling steam generator level. <br /><br /> During both trips, all plant systems responded as designed. <br /><br /> Corrective actions included replacing main feedwater pump B motor with a spare and using the steam generator power operated relief valves during subsequent plant startups until the steam dump valve is repaired. Steam dump valve SD-11A1 will be repaired during the 1993 refueling outage which is scheduled to start March 5.
305 | 3051993001 | 1993-01-29 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Kewaunee | P | WE | SU | 5 | On January 28, 1993, at 0443 hours, with the plant operating at 100% power, a large fault on main feedwater pump B motor caused an undervoltage condition on Bus 1 and Bus 2. The bus voltage dropped below the undervoltage reactor trip setpoint and initiated an automatic reactor trip. The voltage on both buses quickly recovered once the fault was isolated. <br /><br /> On January 29, 1993, during the subsequent plant startup, another reactor trip occurred at 1516 hours from 5% power. reached the low-low level reactor trip setpoint of 17% while steam generator level was being manually controlled. Problems with steam dump valve SD-11A1 (to the condenser) contributed to the difficulty in controlling steam generator level. <br /><br /> During both trips, all plant systems responded as designed. <br /><br /> Corrective actions included replacing main feedwater pump B motor with a spare and using the steam generator power operated relief valves during subsequent plant startups until the steam dump valve is repaired. Steam dump valve SD-11A1 will be repaired during the 1993 refueling outage which is scheduled to start March 5.
305 | 3051995003 | 1995-05-16 | QR5 | Turbine Trip | [45 empty] | Kewaunee | P | WE | SU | 5 | On May 16, 1995 with the reactor at approximately 5 percent power, Surveillance Procedure (SP) 54-064, 'Turbine Overspeed Trip Test,' was being performed. SP 54-064 is required once per operating cycle and was being performed in preparation for plant startup after the 1995 Refueling Outage. During the performance of the procedure, the Nuclear Control Operator (NCO) mispositioned the Overspeed Protection Control (OPC) key switch, which caused the turbine control valves to close. When the NCO and operations personnel attempted to recover from the mispositioning event, the reactor tripped due to steam flow greater than feedwater flow coincident with steam generator low level in the B train steam generator. <br /><br /> The cause of this event was determined to be the failure to adequately assess the consequences of returning the OPC key switch to the 'OFF' position. It was determined that the lack of self checking when manipulating the OPC key switch and a heightened sense of urgency to regain and control turbine speed after the misposition of the OPC key switch were contributing factors to this event. <br /><br /> The NCO was reminded as to the importance of self checking. An evaluation will be performed to determine the need to change the OPC key switch labels to reduce the probability of reoccurrence of this event. SP 54-064 is being revised to give generic guidance to address unusual circumstances encountered during the performance of the SP. Additional training will be provided during the next Operations Training Requalification cycle on the turbine control system.
305 | 3051995005 | 1995-09-05 | QR8 | Spurious Reactor Trip | [45 empty] | Kewaunee | P | WE | PO | 96 | On September 5, 1995 with the reactor at 96 percent power, Surveillance Procedure (SP) 47-010A, 'Channel 1 (Red) Reactor Coolant Temperature and Pressurizer Pressure Instrument Channel Test,' was being performed. SP 47-010A is performed monthly. During performance of the procedure, a spurious reactor trip occurred. With the exception of erratic indication on one of the two source range nuclear instruments, the plant response to the trip was as expected. <br /><br /> The cause of the trip is suspected to have been a misaligned contact on a trip relay which completed the two out of four trip logic when one channel of the Pressurizer (PZR) Low Pressure trip logic was tripped in as part of the SP test sequence. This is a suspected condition since inspections, testing, and computer and sequential event recorder printout reviews did not confirm that a trip signal from low pressure was initiated. <br /><br /> Subsequent to the trip, a repeat performance of the SP could not reproduce a trip condition. Subsequent to performing a test of the reactor protection logic relays on the train suspected to have caused the trip, and all four of the reactor coolant temperature and PZR pressure channels, the plant was returned to power and placed on-line. The testing performed confirmed that no trip signals existed to prevent a start-up and or result in a similar occurrence.
305 | 3051996002 | 1996-03-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Kewaunee | P | WE | PO | 70 | This report describes two events which caused reactor protection system actuations. The first event occurred with the plant at 70 percent power on March 31, 1996. The actuation occurred during the performance of Special Test Procedure TB-54-1, 'Turbine Reheat Stop Valve - Test and Trouble Shooting.' A spring loaded piston check valve failed allowing the emergency trip fluid header to depressurize, which caused the turbine stop valves to close resulting in a reactor trip. The second event occurred on April 1, 1996, with the plant in the hot shutdown mode. The operating crew was performing Surveillance Procedure 49-074A, 'Control Rod Drop Time Test - Startup Measurements,' and mistakenly allowed Steam Generator level to decrease to the reactor protection actuation setpoint of 17 percent. <br /><br /> The cause of the first event was the failure of a spring loaded check valve. The second event was caused by the operating crew failing to recognize the impact of changing plant conditions. <br /><br /> The spring loaded check valve was replaced and the reheat stop valve was successfully tested on April 1, 1996. Operations training will continue to stress the importance of recognizing and assessing the impact of changing plant conditions. A training module, incorporating operating experience, will be developed to address operation of the plant during the varying conditions that can exist following a reactor trip.
305 | 3051996003 | 1996-04-02 | QR8 | Spurious Reactor Trip | [45 empty] | Kewaunee | P | WE | PO | 98 | On April 2, 1996, with the reactor at 98 percent powers Surveillance Procedure (SP) 48-003F, 'Nuclear Power Range Channel 2 (White) N-42 Monthly Test,' was being performed. During the performance of the procedure, a spurious reactor trip occurred. The plant response to the trip was as expected. <br /><br /> The cause of the trip was a set of electrically open contacts located on the Train A Positive Rate trip matrix. The open contacts completed the two out of four trip logic when a test signal was injected into Channel 2 (White) N-42 as part of SP 48-003F. closed, they were found by measuring the voltage across the contacts. [Redline: A root cause could not be conclusively determined; however, two potential causes for the open contracts are debris being lodged between the contact surfaces or oxidation of the contact surfaces.]<br /><br /> The relay causing the reactor trip was replaced. The new relay was tested using the appropriate sections of SP 47-062A, 'Reactor Protection Logic Train A Test.' This test confirmed the new relay was working properly. After the plant was returned to power, SP 47-062A, 'Reactor Protection Logic Train A Test,' and SP 47-062B, 'Reactor Protection Logic Train B Test,' were performed with acceptable results.
305 | 3051998005 | 1998-02-24 | QP2 | Partial Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Kewaunee | P | WE | PO | 97 | On February 24, 1998, while operating at 97% power, an inadvertent reactor trip occurred. The trip occurred during surveillance testing of the B train Engineered Safeguards Features (ESF) actuation logic circuits. While conducting the logic tests, the B train feedwater isolation relay actuated. The relay actuation initiated a turbine trip, a reactor trip, a trip of both main feedwater pumps, and closed the main feedwater flow control and isolation valves to the B steam generator. The feedwater isolation relay actuated when a reduced voltage was applied to the relay. This is done as part of the testing to verify circuit continuity following actuation logic tests. The reduced voltage normally does not result in actuation of the relay. The event was caused by failing to set the relay armature coil tension when the relay was replaced on February 12, 1998. The plant response to the trip was normal. No abnormal or unexpected conditions other than the initiation source of the trip were noted. There were some ESF equipment actuations; however, they were consistent with the originating trip signal and normal trip response. Subsequent to the trip the feedwater isolation relay armature coil tension was adjusted and a plant restart was conducted.
305 | 3052000009 | 2000-06-06 | QR6 | Manual Reactor Trip | [45 empty] | Kewaunee | P | WE | PO | 37 | On June 6, 2000, while operating at 37% power, a manual trip was initiated in response to an abnormal high temperature indication of the A Reactor Coolant Pump (RXCP). At the time of the trip, the plant was in a chemistry hold at reduced power following a recently completed refueling outage. The indicated increased temperature was on the RXCP bearing water outlet temperature that would be indicative of a RXCP radial bearing related problem. Plant procedures prohibit operating the RXCP with bearing temperature indication in excess of 225 degrees F. Subsequent to the Operators noting temperature indication exceeding 225 degrees, the reactor and affected pump were tripped. The cause of the increased temperature indication was a failed resistance temperature detector (RTD). The plant response to the trip was normal. All systems operated as designed.
305 | 3052001004 | 2001-06-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Kewaunee | P | WE | PO | 96 | On 6/20/01 at 0011 CDT, while the plant was operating at ninety-six percent power, a Reactor Protection System (RPS) actuation occurred when the feedwater (FW) regulating valve (FW-7B) to the "B" steam generator failed to the closed position. All other safety-related equipment operated as expected. Feedwater is regulated by 12-inch air-operated valves (AOV) (FW-7A and FW-7B). An Air Volume Booster is in line with each valve actuator to assist in air bleed off during a feedwater isolation signal. During the post-trip recovery, plant personnel inspected the Air Volume Booster for FW-7B and identified a tear in the diaphragm. The root cause of this event is the "running to failure" maintenance schedule for FW Regulating Valve Volume Booster Relays. This event was reported in accordance with 10CFR50.72(b)(1)(iv)(B) as a valid RPS actuation. This event was analyzed from a Probabilistic Risk Assessment (PRA) perspective. The incremental core damage probability (ICDP) and incremental large early release probability (ILERP) were 4.66E-09 and 5.26E-12, respectively. Thus, this event was of negligible safety significance. The Air Volume Boosters for both FW-7A and FW-7B were replaced. Following repairs, the reactor became critical on June 21 at 0225 CDT, and the plant output breaker was closed at 1205 CDT. Full power was reached on June 22, 2001 at 1050 CDT.
305 | 3052005016 | 2005-11-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Kewaunee | P | WE | PO | 100 | On November 28, 2005 at 2219 central standard time (CST), while the plant was operating at 100 percent power with no abnormal indications, the 'B' main feedwater pump tripped on a bus 2 feeder breaker trip (overcurrent trip on a 4160 volt bus). During the transient, 'B' steam generator reached its low-low level setpoint actuating a reactor protection system reactor trip at 2220 CST. All systems responded as designed. Subsequent inspection of the 'B' main feedwater pump identified a short to ground in all three phases of the motor. This event was reported as a non-emergency in accordance with 10 CFR 50.72(b)(2)(iv)(B) for actuation of the reactor protection system when the reactor is critical and 10 CFR 50.72(b)(3)(iv)(A) for valid actuation of the auxiliary feedwater system. Since all safety systems operated as expected, this event is considered to have negligible safety significance. This is not considered a safety system functional failure. The 'B' main feedwater pump motor was replaced and the reactor startup was completed on November 29, 2005 at 2236 CST with the plant output breaker being closed on November 30, 2005 at 0335 CST. Full power was reached on December 2, 2005 at 1938 CST.
305 | 3052006001 | 2006-04-26 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Kewaunee | P | WE | PO | 35 | On April 26, 2006 at 2043 Central Standard Time (CST) the operating crew manually initiated a reactor trip.This trip was initiated with the plant at approximately 35 percent power, as it was being shutdown to repair an unisolable service water pipe leak. The operating crew had stopped one of the two operating condensate pumps when the single running main feedwater pump tripped unexpectedly. The operating crew recognized the turbine had not automatically tripped with no feedwater pumps running. Therefore, the operating crew manually initiated a reactor trip. With loss of main feedwater pumps, level in both steam generators decreased to the automatic actuation setpoint starting all auxiliary feedwater pumps. All safety systems functioned as expected following the manual reactor trip. Because the reactor did not automatically trip upon the loss of the main feedwater pump, the Shift Manager declared an Alert at 2049 CST based on failure of the reactor protection system to initiate and complete a reactor trip. Upon further investigation, the declaration of an Alert was not required, since the conditions to generate a reactor trip signal did not exist at the time the operators manually tripped the reactor. The Alert was terminated at 0024 CST on April 27, 2006. This event was reported in accordance with 10 CFR 50.72(a)(1)(i) for declaration of an emergency classification, 10 CFR 50.72(b)(2)(iv)(B) for actuation of the reactor protection system when the reactor is critical, and 10 CFR 50.72(b)(3)(iv)(B)(6) for valid actuation of the auxiliary feedwater system.
305 | 3052006012 | 2006-10-30 | QP2 | Partial Loss of Feedwater Flow | [10 empty] | X | [29 empty] | X |  |  |  |  | Kewaunee | P | WE | PO | 93 | At 8:48 CST on 10/30/2006, Kewaunee Power Station tripped from approximately 92% full power due to steam generator B steam flow feedwater flow mismatch coincident with low water level on steam generator B. The cause of the plant transient that led to the reactor trip was a loss of the red instrument bus. The bus deenergized due to component failure during the performance of maintenance on its inverter. Following the reactor trip; - The auxiliary feedwater pumps automatically started, as designed, due to low-low level in the steam generators. No other safeguards systems actuated during the transient. - Non-safety related valve MS-201 B1, steam supply to reheater 1B reheater inlet valve, did not fully close. This resulted in pressurizing high pressure feedwater heater (15B) causing relief valve HD-130B, 15B headwater heater relief valve, to lift. - After the turbine trip, during bus transfer, non-safety related 4160V reserve auxiliary transformer breaker failed to close resulting in bus 4 losing power. This resulted in a loss of circulating water flow, which, in turn, caused a loss of condenser vacuum and condenser steam dump valves. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in automatic actuation of the reactor protection system and the auxiliary feedwater system.
305 | 3052006013 | 2006-11-10 | QR8 | Spurious Reactor Trip | [45 empty] | Kewaunee | P | WE | PO | 10 | On 11/10/2006 at 14:20 CST, Kewaunee Power Station experienced a reactor trip while reducing power at 1/2 percent per minute during a planned shutdown to investigate abnormal temperature and vibration indications on the turbine number nine bearing at the turbine generator exciter. At approximately 10 percent reactor power as permissive P-10 cleared, a spurious reactor protection system actuation occurred due to failed open relay contacts on the B train associated with power range nuclear instrumentation N-41. The bistable for power range nuclear instrumentation N-42 was in a tripped condition due to an unrelated failure on 11/09/2006. When P-10 automatically unblocked, the power range nuclear instrumentation low range-high flux trip was generated. Following the trip, steam supply to reheater B1 inlet valve, MS-201B1, did not fully close and had to be isolated to limit the plant cool down. Main steam isolation valves remained open and the normal condenser heat sink remained available. Main feedwater regulating valve, FW-7A, did not automatically close on the reactor trip coincident with low Tave (554 deg F). The valve did not respond to manual closure actions. Level in A steam generator rose to 67 percent which initiated a feedwater isolation signal. The feedwater isolation signal tripped the running A main feedwater pump and main feedwater valves isolated. The A and B motor driven auxiliary feedwater pumps started as designed.
305 | 3052007001 | 2007-01-12 | QR5 | Turbine Trip | [45 empty] | Kewaunee | P | WE | PO | 94 | At 10:39 on 1/12/2007, with the reactor at 1660MWt (93.7%), while performing a turbine mechanical trip test, the turbine and reactor tripped due to low auto stop oil pressure. MS-201B1, Reheat Steam to MSR B1 failed to close, which resulted in additional RCS cooldown to 536 degrees F. Per contingency procedures, action was taken to isolate the reheat steam, which halted the cooldown, and Tave was restored to 547 degrees F. The additional cooldown resulted in letdown isolation on low pressurizer level. Feedwater isolated and auxiliary feedwater initiated, as designed, due to low-low level in the steam generators. No other safeguards systems actuated during the transient. The direct cause was a loss of auto stop oil pressure to the interface valve that resulted in a turbine-reactor trip. The probable cause of this pressure loss was either the overspeed trip test valve linkage out of adjustment, undetected test valve lever movement on the part of the operator, or a combination of the two. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in automatic actuation of the reactor protection system and the auxiliary feedwater system. This event was originally reported in LER 2007-001-00. This supplemental report updates the cause and corrective action.
305 | 3052007004 | 2007-02-27 | QR8 | Spurious Reactor Trip | [45 empty] | Kewaunee | P | WE | PO | 100 | On 2/27/2007 at 23:33 CST, with the reactor at approximately 100% power, while performing a quarterly channel calibration on nuclear instrument channel N-43, the reactor tripped. MS-201 B1, Reheat Steam to MSRBl, failed to close, (a repeat occurrence), which resulted in a reactor coolant system cooldown to 537 degrees F. Per contingency procedures, action was taken to manually isolate the turbine moisture separator reheat steam, which halted the cooldown, and Tave was restored to 547 degrees F. The additional cooldown resulted in a chemical and volume control system letdown isolation on low pressurizer level. Main feedwater isolated and auxiliary feedwater initiated, as designed, due to low-low level in the steam generators. No other safeguards systems actuated during the transient. The direct cause of the event appears to have been a Westinghouse BF66 relay contact failure in the reactor protection system trip matrix associated with nuclear instrumentation. The specific relay could not be determined. The most probable root cause has been determined to be blind contact relay failures due to a combination of relay contact sulfidation caused by poor circuit design, manufacturing defects in some installed relays, and installation practices from the original installation 30 years ago being inconsistent with current standards and practices. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in automatic actuation of the reactor protection system and the auxiliary feedwater system.
306 | 3061989002 | 1989-05-26 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | On May 26, 1989, Unit 2 was at 100% power. At 0605 Unit 2 tripped on steam generator low level. Investigation of plant data revealed that the turbine control valves had closed just prior to the trip. Investigation of the turbine control system led to the power supply drawers, where failed components were found on a speed error amplifier card. The failed components were an electrolytic capacitor and an inductor. The speed error amplifier card was replaced and inspection of all other circuit cards was completed. The speed error amplifier was tested and the control system returned to service. Unit 2 was returned to service at 0353 on May 27, 1989. <br /><br /> Cause of the event was failure of an electrolytic capacitor. The capacitor failure shorted the control system power supply to ground, causing loss of electronic control power to the turbine control valves. This caused the control valves to close. The short circuit cleared about 7 seconds later, allowing the control valves to reopen, but the low steam generator level trip setpoint had been reached and Unit 2 tripped. <br /><br /> The speed error amplifier card was replaced. Other circuit cards were inspected.
306 | 3061989004 | 1989-12-21 | QR3 | Reactivity Control Imbalance | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | Unit 2 tripped on December 21, 1989, from what appeared to be faulty voltage regulation by one of the control rod drive mechanism motor-generator sets. One substation circuit breaker did not operate properly and power was lost to non-safeguards 4KV buses, which supply the reactor coolant pumps. The reactor was cooled by natural circulation for about 3 hours. The voltage regulator for the MG set was replaced and tested. Since the outdoor temperature at the time of the trip was -22 degrees F, the cold was blamed for the breaker malfunction. Heating was applied to the substation breakers and testing showed proper operation. The unit was restarted. On December 26, 1989, a nearly identical trip and loss of non-safeguards 4KV buses occurred. Extensive investigation uncovered malfunctions in the MG sets, in the rod control system, and in the substation breaker control system. After repairs and extensive testing, Unit 2 was returned to service on January 10, 1990.
306 | 3061989004 | 1989-12-26 | QR3 | Reactivity Control Imbalance | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | Unit 2 tripped on December 21, 1989, from what appeared to be faulty voltage regulation by one of the control rod drive mechanism motor-generator sets. One substation circuit breaker did not operate properly and power was lost to non-safeguards 4KV buses, which supply the reactor coolant pumps. The reactor was cooled by natural circulation for about 3 hours. The voltage regulator for the MG set was replaced and tested. Since the outdoor temperature at the time of the trip was -22 degrees F, the cold was blamed for the breaker malfunction. Heating was applied to the substation breakers and testing showed proper operation. The unit was restarted. On December 26, 1989, a nearly identical trip and loss of non-safeguards 4KV buses occurred. Extensive investigation uncovered malfunctions in the MG sets, in the rod control system, and in the substation breaker control system. After repairs and extensive testing, Unit 2 was returned to service on January 10, 1990.
306 | 3061990001 | 1990-03-08 | QR5 | Turbine Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | On March 8, 1990, Unit 2 was at 100% power. An Operations Instructor and a trainee were making operator rounds in the Turbine Building. The bus duct cooler local panel test was to be demonstrated to the trainee. When the test button was depressed, a relay failed to operate properly and a generator lockout signal was produced, resulting in a turbine trip and reactor trip at 1104. Plant response to the trip was as expected for a secondary-side initiated reactor trip; some water hammer occurred in secondary side piping. After the circumstances of the trip were reviewed and corrective action taken, the unit was restarted. <br /><br /> Cause of the event was failure of a test relay to operate properly, allowing a trip signal to be generated. The circuit is designed so that when the test button is depressed, relay K3 deenergizes, removing the trip relay (23-X) from the circuit prior to simulating a high temperature condition. The K3 relay contacts failed to open as designed. Thus, when the high temperature condition was simulated, a trip signal was generated, producing a generator lockout and resulting in a turbine trip and reactor trip.
306 | 3061990002 | 1990-03-09 | QR8 | Spurious Reactor Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 6 | On March 9, 1990, Unit 2 was being restarted following the unit trip on March 8 (Unit 2 LER 90-001). Reactor power was about 6% and the turbine had just been tripped as part of turbine control system testing that is performed at each startup. When the turbine was relatched, at 0128, the reactor tripped. Cause of the trip was determined to be a failed relay, which was then replaced. Logic testing then took place to prove operability of the new relay. After the logic testing, visual observation of some permissive relays showed that two relays, one in each train, were not in their proper positions. These two relays were replaced and tested for proper operation. The Unit was restarted and returned to service at 0928 on March 10, 1990. <br /><br /> Cause of the event was failure of a Westinghouse NBFD relay. The failed relays were replaced.
306 | 3061990003 | 1990-03-16 | QR3 | Reactivity Control Imbalance | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | On March 16, 1990, Unit 2 was operating at 100% power. At 0921 a reactor trip occurred following the resetting of a Rod Control System Urgent Failure alarm which had been generated by connecting test equipment to the Rod Control System. <br /><br /> Electronic noise had been observed on temporary monitoring equipment installed on Unit 2 Rod Control System. In an attempt to identify or eliminate possible sources of this noise, an I&C technician planned to disconnect and reconnect various inputs to a recorder. The technician connected an oscilloscope to a point in the Rod Control System. When the oscilloscope was connected, the "V-ref" control signal was forced to a low value by the low input impedance of the oscilloscope. The "V-ref" signal for only two rods, E-03 and I-11, was affected and they dropped approximately 10 steps into the core as the Urgent Failure circuitry responded to prevent rod motion by applying "hold" current to the rod mechanisms. Approximately 10 seconds later, the Urgent Failure alarm was reset. While the Reset pushbutton was depressed, the "hold" current was removed from rods E-03 and I-11, and they began to drop into the core, resulting in a high negative flux rate reactor trip. Response to the trip was normal and correct. After evaluation of the event, the unit was returned to service at 0128 the next day.
306 | 3061990012 | 1990-12-29 | QR3 | Reactivity Control Imbalance | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | On December 29, 1990, Unit 2 was at 100% power. At 2234, Unit 2 tripped. Control room annunciators, and the sequence of events generated by the plant process computer, indicated that the cause of the reactor trip was a negative flux rate trip from the reactor protection system. <br /><br /> An investigation into the cause of the negative flux rate trip revealed that two circuit cards in the rod control system power cabinet 1BD had failed. The first failure was of a transistor in the urgent failure alarm circuit. The second failure was the opening of a solder connection on the stationary gripper regulation card, causing the reference voltage to go to zero. In response to the reference voltage going to zero, the urgent failure alarm circuit should have generated an urgent failure alarm and a "hold" current that would be applied to the stationary grippers for all the rods supplied by that power cabinet. This hold current would have prevented the rods from dropping into the reactor. But since the Urgent Failure alarm circuit had also failed, no current was supplied to the stationary grippers in control rod Bank D and they fell into the core, causing the negative flux rate trip. <br /><br /> The failed cards in the rod control system were replaced. Unit 2 was returned to service at 1330 on December 30, 1990.
306 | 3061994002 | 1994-07-21 | QR5 | Turbine Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | On July 21, 1994, Unit 2 was at 100% power. A wet pipe sprinkler system had been recently installed at the turbine-generator to provide protection against lube oil fires. On the morning of July 21, a hydrostatic test of the fire protection piping was begun. After the system had been at test pressure for about 1 3/4 hours, a sprinkler head activating device failed and water was sprayed on the main generator bushings, establishing a current path from B phase bushing to ground. The generator ground relay actuated the 86 generator lockout relay, which caused a reactor trip at 1019 hours. The unit responded as expected to the automatic trip, including automatic start of the auxiliary feedwater pumps on low steam generator level. Leaking feedwater isolation valves contributed to an RCS cooldown, and the resulting low pressurizer level caused letdown isolation. Cause of the trip was determined; the bushing enclosure, neutral connection, isophase bus, and vertical link box were disassembled, inspected, cleaned, and tested; and the determination was made that there was no electrical damage. The unit was returned to service at 0703 on July 22. The turbine-generator wet pipe sprinkler system on both Units 1 and 2 has been isolated until further system evaluation can be completed.
306 | 3061996001 | 1996-03-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | At approximately 0011 hours on March 19, 1996, while operating at 100 percent reactor power, Unit 2 experienced a reactor trip generated by a protective signal received from Low Low Steam Generator Water Level. Significant observations by Control Room personnel included indication of 100 percent demand signal on CV-31135 and indications of decreasing water level in 21 Steam Generator with no feedwater flow in Loop A. Additionally, a lock-in trouble annunciation for the feedwater control system was received. Also heard and felt by Operations personnel immediately preceding this event was a loud thud which was probably water hammer. <br /><br /> After the plant was in a stable condition, an investigation was begun and the cause of the trip was determined. CV-31135, Loop A Feedwater Regulating Valve, was isolated and stroked with no externally visible impairment of operation. But because of observed indications and plant response, it was decided to disassemble CV-31135 as it was the most likely candidate to initiate this event. During disassembly of CV-31135 it was observed that the valve plug had separated from the valve stem. <br /><br /> The valve stem/valve plug separation resulted in the valve plug dropping completely into the valve cage obstructing all Loop A feedwater flow to 21 Steam Generator. This ultimately resulted in the loss of the unit on a Low Low Steam Generator Water Level reactor trip.
306 | 3061996002 | 1996-04-18 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Prairie Island 2 | P | WE | PO | 100 | At approximately 1916 hours on April 18, 1996, while operating at 100% reactor power, Unit 2 experienced a reactor trip generated by a protective signal received from a Low Steam Generator Water Level signal. Significant observations by Control Room personnel prior to the trip included annunciators indicating Instrument Air low header pressure and a problem in the Instrument Air Dryers. The Unit 2 instrument air header indicated zero flow and header pressure was decreasing. Steam generator levels decreased as their feedwater regulating valves drifted shut due to the loss of air. About one minute after the feedwater regulating valves began to close, 22 Steam Generator reached the Low level trip setpoint resulting in a reactor trip. <br /><br /> The plant response to the reactor trip was normal with the following exceptions: <br /><br /> 1) The orifice isolation valve failed closed due to low air pressure, isolating letdown. <br /><br /> 2) The following fans tripped: 21 CRDM Fan, 11 Aux Bldg Exh Fan, 21 Aux Bldg Exh Fan and 21 Aux Bldg M/U Fan. <br /><br /> The cause of the trip was failure of a 122 Air Dryer purge exhaust valve to close during a drying cycle. Failure of an air inlet or exhaust purge valve to close during dryer operation causes a loss of air header pressure through the 1-1/2 inch purge exhaust line. A manual valve is installed on this line which can be used to isolate the leak during this type of event. Operators were dispatched to the air dryer during the course of this event but had insufficient time to isolate the air dryer manually
306 | 2821996012 | 1996-06-29 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Prairie Island 2 | P | WE | PO | 100 | On June 29, 1996, both Units 1 and 2 were operating at 100% power. In summary, both reactors tripped following the loss of three of four 345 KV offsite transmission lines to the plant substation, due to high winds. The plant safeguards busses were supplied power by the four safeguards diesel generators for several hours. <br /><br /> All safeguards diesel generators provided the needed electrical power throughout the duration of the event. In addition, all cooling water (essential service water) pumps functioned as required. The event was mitigated by the proper functioning of the safety related equipment and the proper management of the event by operators.
306 | 3061998005 | 1998-11-09 | QR5 | Turbine Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 22 | On November 9, 1998, Unit 2 was undergoing an orderly shutdown in preparation for refueling. During the course of the shutdown, at approximately 0048, the unit unexpectedly tripped from 22% power. The reactor trip was initiated by a turbine trip. The unit remains shutdown for refueling.
306 | 3062000001 | 2000-04-28 | QR5 | Turbine Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 22 | On April 28, 2000, Unit 2 was undergoing an orderly shutdown in preparation for refueling. During the course of the shutdown, at approximately 2240, the unit tripped from 22% power. The reactor trip was initiated by a turbine trip which was initiated by a Hi Hi Level signal from 23B Feedwater Heater. The unit remains shutdown for refueling.
306 | 3062001004 | 2001-05-09 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Prairie Island 2 | P | WE | PO | 12 | On May 9, 2001, Unit 2 was undergoing an orderly shutdown as a result of the declared inoperability of D5 and D6 Diesel Generators (Unit 2 LER 01-03). At about 2006, with the reactor at 12% power, the turbine was manually tripped when 2A/2B Condenser differential pressure reached 2.5" Hg. The reactor tripped automatically as a result of the turbine trip. After the trip, vacuum continued to decrease in both condensers until vacuum was completely lost by 2047. After the vacuum loss, water was observed coming from the condenser air ejector discharge to atmosphere. Additional operator checks of the air ejectors noted water in the air ejector flowmeter, and that the 2B Condenser air ejector suction piping was hot while 2A Condenser piping was at ambient temperature. Actions were taken to drain the water from the air ejector discharge. At approximately 2243, condenser vacuum began a slow recovery without any significant operator intervention other than draining the discharge line. Vacuum was fully recovered by approximately 0945 on May 10.
306 | 3062001005 | 2001-10-31 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [28 empty] | X | X |  |  |  |  | Prairie Island 2 | P | WE | PO | 100 | On October 31, 2001, at approximately 1409, Unit 2 Reactor was manually tripped from 100% power when 2A/2B Condenser differential pressure reached 2.5 inches Hg. A steam leak on the body of 21 air ejector main steam supply control valve had been identified on October 24, 2001. Plans were made to temporarily repair the steam leak by installing an enclosure box around the valve and its proximate piping and injecting leak sealant. As part of this planning a contingency action plan was developed to isolate the leak if further degradation of the valve occurred. On October 31, 2001, temporary repairs to stop the leak were started by installing an enclosure box and injecting leak sealant. While preparing to inject the last stick of sealant, the enclosure box unexpectedly shifted. Due to a concern that the valve may have degraded further, with a potential for a steam release, the Shift Supervisor made a conservative decision and ordered an immediate evacuation of the Unit 2 Turbine Building. While performing the steps of the contingency action plan to isolate and bypass the control valve, vacuum was lost faster in 2A condenser than in 2B condenser. When the vacuum differential pressure between the condensers reached 2.5 inches Hg the reactor/turbine was manually tripped as required by procedure. The post-trip recovery was normal.
306 | 3062007001 | 2007-04-05 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | On April 5, 2007, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 was operating at 100% power. At approximately 0908 CDT, during surveillance testing of Unit 2 Train A safeguards logic at power, a spurious Train A Safety Injection (SI) actuation occurred resulting in Reactor Protection System (RPS) actuation. Train A SI was in "Test" at the time and should not have caused the RPS trip. At approximately 0913 the operating crew manually actuated Train B SI as required by emergency operating procedures. Reactor Coolant System (RCS) pressure momentarily decreased below the shutoff head of the high head Emergency Core Cooling System (ECCS) pumps during the transient, resulting in ECCS discharge to the RCS. At approximately 0920 safety injection was terminated per emergency operating procedures. All systems operated as expected and operator response and recovery actions were as expected. Initial investigation of the cause of the automatic reactor trip was determined to be a deficiency with the safety injection relay equipment. Instrument and Control technicians discovered a safety injection relay with high contact resistance. The high resistance contact caused the relay to not reset when exiting the safeguards logic test. With the relay not reset, and safeguards logic not in test, a spurious SI actuation occurred. The defective relay was replaced and tested to verify proper operation prior to Unit 2 reactor startup.
306 | 3062008002 | 2008-10-30 | QR6 | Manual Reactor Trip | [45 empty] | Prairie Island 2 | P | WE | SU | 1 | On October 30, 2008, at 1414 CDT during reactor physics testing following a Unit 2 outage, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 was just above the point of adding heat (POAH) when an urgent failure alarm was received while moving Bank A control rods inward. It was noted that Group 1 control rods in Power Cabinet 21AC unexpectedly stopped moving while Group 2 control rods in Power Cabinet 22AC continued inward rod motion. Operators stopped Group 2 control rods and initiated a manual reactor trip. All systems operated as expected following the trip and operator response and recovery actions were as expected. Subsequent troubleshooting identified that a Phase C fuse in the 21AC Moveable Gripper bus duct disconnect switch had blown. Troubleshooting also identified that the blown fuse was not fault related and likely due to a random failure. All 21AC moveable gripper bus duct disconnect switch fuses were replaced on October 31st, 2008 at approximately 0031 CDT thereby restoring full functionality of bank A control rods. In addition, all of the moveable gripper bus duct disconnect-switch fuses for the other two power cabinets (22AC and 21BD) in Unit 2 were replaced to ensure that the extent of condition was corrected. Reactor startup and physics testing were resumed on October 31, 2008 at 1115 and Unit 2 reactor was returned to criticality on October 31, 2008 at 1311 CDT.
306 | 3062010001 | 2010-04-16 | QR5 | Turbine Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 13 | On April 16, 2010, the Prairie Island Nuclear Generating Plant's (PINGP) Unit 2 reactor down power began in preparation for 2R26 refueling outage. At approximately 13% power the turbine automatically tripped due to a greater than 2.5 inch Hg pressure differential between the A and B condensers. The steam plant and reactor protection system responded as expected to the initial event. After the reactor trip, operators responded in accordance with procedures, recovered vacuum, and continued with the Unit 2 shutdown.
306 | 3062010002 | 2010-05-25 | QR5 | Turbine Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 32 | On May 25, 2010, Prairie Island Nuclear Generating Plant's (PINGP) Unit 2 Reactor was increasing power following the 2R26 Refueling Outage. At approximately 32% power the turbine automatically tripped due to a trip of the 21 Main Feed Water Pump (FWP). The turbine trip resulted in an automatic Unit 2 Reactor trip. The 21 FWP trip was due to the failure of the FWP suction pressure switch. The steam plant and reactor protection system responded as expected to the initial event. After the reactor trip, operators responded utilizing emergency operating procedures for reactor trip and reactor trip recovery and transitioned into a normal shutdown procedure.
306 | 3062011002 | 2011-05-09 | QR5 | Turbine Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | On May 9, 2011, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 tripped from approximately 100% steady-state power as a result of a turbine trip from a generator lockout signal. At the time of the trip Unit 1 was in a planned refueling outage in Mode 6 Operation and thunderstorms were in the vicinity of the plant. Post event diagnostics determined that the relay ground potential circuit had a missing link (wire) between substation panels which resulted in the loss of the reference ground potential to the associated protective relaying in the Switchyard panels. This resulted in the improper operation of the breaker protection relays. The causal evaluation determined that the proximate cause of the relaying scheme failure was inadequate ground wire installation during a modification to the substation equipment. The evaluation also determined that NSPM (Transmission and Nuclear) did not establish the appropriate standard for procedure quality with respect to work under System Control Center jurisdiction in the PINGP substation such that a means of effectively utilizing human performance tools to minimize errors during work, which directly impacts the safe and reliable operation of nuclear plants, was not in place.
306 | 3062012001 | 2012-02-21 | QR6 | Manual Reactor Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 11 | On February 21, 2012, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 was performing a normal shutdown in preparation for refueling outage 2R27. With Unit 2 at approximately 11.42% power, the reactor was manually tripped in accordance with the 21/22/23 Feedwater Heater Hi-Hi alarm response procedure. There were no other unusual /not understood events associated with the shutdown. The Equipment Cause Evaluation (ECE) determined that the third stage low-pressure FWH bypass line to the condenser is potentially restricting flow to the dump valve. The ECE also determined that the Moisture Separator Reheater Control valves are ramped closed earlier than necessary and are fully closed by approximately 20% reactor power. This causes excessive moisture in the extraction steam at low power and results in more water accumulating in the low-pressure feedwater heaters. "The RCE determined that station implementation of the Corrective Action Program (CAP) and Equipment Reliability processes have not minimized risk of event recurrence while implementing long-term corrective actions by requiring interim/mitigating actions be taken prior to the next potential opportunity for recurrence."
306 | 3062013001 | 2013-02-21 | QR6 | Manual Reactor Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 11 | NULL
306 | 3062015002 | 2015-04-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | On April 3, 2015, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 was operating at 100 percent power, when at 0652 CDT, an unexpected annunciator, 47510-0104 21 FEEDWATER PUMP LOCKED OUT was received. The reactor was manually tripped as required by the annunciator response procedure. This also resulted in a turbine trip as designed. The Operations crew entered the reactor trip emergency operating procedures and stabilized the unit in Mode 3, at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. The Auxiliary Feedwater Pumps actuated as designed on low narrow range steam generator level. Steam Generator levels were returned to normal. <br /><br /> This event is reportable under 10 CFR 50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation, and 10 CFR 50.72(b)(3)(iv)(A), any event or condition that results in valid actuation of any of the systems listed in paragraph 10 CFR 50.72(b)(3)(iv)(B)(6), PWR auxiliary or emergency Feedwater system. <br /><br /> The cause evaluation determined that the event was caused by pressure fluctuation within the system which resulted in the bourdon tube movement at a high frequency causing wear of the internal components of the pressure switch. Corrective actions: Pressure Switch (PS-16012) was replaced immediately on April 3, 2015, and to install snubbers to reduce process flow fluctuations experienced by Feedwater Pump pressure switches.
306 | 3062015003 | 2015-06-07 | QR5 | Turbine Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | On June 7, 2015, at 0735, the Unit 2 Reactor automatically tripped while operating at 100 percent power due to an automatic Turbine trip due to low bearing oil pressure. The crew entered the reactor trip emergency operating procedure and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the trip. All safety functions operated as designed. The automatic reactor trip is reportable per 10 CFR 50.72(b)(2)(iv)(B). The Auxiliary Feedwater System actuated to start the auxiliary feedwater pumps as designed on low narrow range steam generator level and provided makeup flow to the steam generators. The auxiliary feedwater actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A). Steam generator levels returned to normal. There was no effect on Unit 1 as a result of this trip. <br /><br /> Normal bearing oil discharge pressure is approximately 19 psi when the turbine is at 1800 rpm and oil is being supplied from the main oil pump. The turbine will trip when 2 out of 3 bearing oil pressure instruments reach 6 psi. Troubleshooting performed in support of the event identified a cracked and broken weld on a reducing flange for the line that supplies high pressure oil to the Seal Oil skid and Auto Stop Oil. This was the component that failed and resulted in the loss of pressure to the turbine oil bearings. Corrective actions taken included repairing the broken weld, restoring the oil skid to operation, performing an extent of condition evaluation, and entering separate corrective actions to inspect piping connections in the Unit 1 and Unit 2 turbine oil reservoirs.
306 | 3062016001 | 2015-12-17 | QR5 | Turbine Trip | [45 empty] | Prairie Island 2 | P | WE | PO | 100 | On 12/17/2015 at 1234 Central Standard Time (CST) with Unit 2 (U2) in Mode 1 at 100 percent power, the U2 electric generator tripped due to a ground overvoltage protection relay (59/2G) actuation, which resulted in an automatic reactor trip and expected Auxiliary Feedwater System actuation. At 1307 CST a fire alarm was received in the U2 containment. Personnel were unable to verify the status within 15 minutes and the site declared an Unusual Event, HU2.1, at 1318 CST. The licensee notified the NRC Resident Inspector, state and local authorities and made an Event Notification to the NRC for the Unusual Event and the U2 reactor trip as required under 10 CFR 50.72(a)(1)(i) and 10 CFR 50.72(b)(2)(iv)(B). Subsequently, the Unusual Event was terminated on 12/17/2015 at 1450 CST after a containment entry determined there was no smoke or fire. The original Event Notification was updated to cancel the Unusual Event and to add reporting under 10 CFR 50.72(b)(3)(iv)(A) for the expected Auxiliary Feedwater system actuation. Decay heat removal was via forced circulation with Auxiliary Feed and Steam Dumps providing secondary cooling. Offsite power remained available. The health and safety of the public was not at risk.<br /><br /> A troubleshooting plan was initiated which determined an actual ground fault existed internal to the new U2 electric generator, installed during the Fall 2015 U2 refueling outage, causing a U2 reactor trip and the expected Auxiliary Feedwater actuation. The cause of the ground fault of the U2 electric generator was determined to be foreign material, specifically a hex socket and hex key introduced at the vendor's manufacturing facility during installation of a temporary dust cover on collector end of the generator rotor.
309 | 3091987006 | 1987-06-27 | QP5 | Excessive Feedwater Flow | [45 empty] | Maine Yankee | P | CE | PO | 53 | On June 27, 1987, a manual reactor trip was initiated due to an uncontrollable increase in steam generator # 3 level. <br /><br /> The increase in steam generator level occurred when an Instrument and Controls technician was replacing a component in the feedwater control cabinet. The technician removed output leads from the failed time lag unit and interrupted the control signal to the # 3 main feedwater regulating valve. The valve failed open causing a rapid rise in steam generator level. The reactor was manually tripped as steam generator level approached the automatic turbine trip setpoint. <br /><br />All systems responded properly following the plant trip. <br /><br /> The root cause of this event is personnel error. The importance of performing thorough circuit investigations before conducting troubleshooting or maintenance will be emphasized to all I & C personnel. <br /><br />A good work practices guide will be developed to provide guidance for investigating discrepancies between drawings and as-built conditions and documentation of the status of ongoing jobs.
309 | 3091987007 | 1987-07-01 | QR5 | Turbine Trip | [45 empty] | Maine Yankee | P | CE | PO | 25 | On July 1, 1987, while operating at 25% power, the main turbine was manually tripped due to high vibrations at #5 bearing. The administrative limit for turbine vibrations is 14.0 mils, as recommended by Westinghouse, the manufacturer. <br /><br /> During the 1987 refueling outage, the low pressure main turbines were disassembled for inspection and maintenance repairs. <br /><br />The root cause of the turbine vibrational problems has not yet been determined.
309 | 3091988001 | 1988-01-05 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Maine Yankee | P | CE | PO | 100 | On January 5, 1988, an unscheduled reactor trip occurred on Loss of Load due to a main turbine trip. The main turbine tripped automatically when the turbine driven main feedwater pump tripped on low suction pressure. <br /><br />The low turbine-driven feedwater pump suction pressure was the result of loss of flow from the Heater Drain Pumps. The operating Heater Drain Pump was tripped and its standby pump was prevented from starting because the Heater Drain Tank low level switch failed. <br /><br />The low level switch failure was due to corrosion of the switch float, which leaked and sank, locking in a low Heater Drain Tank level signal. The low level switch and float was replaced on January 5, 1988.
309 | 3091988006 | 1988-08-13 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Maine Yankee | P | CE | PO | 98 | On August 13, 1988, an unscheduled reactor trip occurred on Loss of Load due to a main turbine trip. The main turbine tripped automatically due to an electrical fault in one of the unit's two output transformers. <br /><br />The faulted transformer caused a momentary low voltage condition on the reserve power supply which inhibited the automatic transfer of electrical power from the station service to reserve transformers. Both emergency diesel generators started and picked up loads on the emergency buses. All buses were repowered by manually closing the reserve power circuit breakers. <br /><br /> An investigation determined that the reserve power circuit breakers' autoclosure relaying functioned as designed. <br /><br />The root cause of the unit transformer high voltage phase to ground short is indeterminate pending further transformer inspection.
309 | 3091988010 | 1988-12-16 | QR5 | Turbine Trip | [45 empty] | Maine Yankee | P | CE | PO | 18 | On 16 December, 1988, during the initial startup from refueling outage, a reactor trip occurred on Loss of Load due to turbine trip. The main turbine auto trip was caused by high level in the Heater Drain Receiver Tank (HDT). <br /><br />HDT pumps and normal level control valve were not yet in service. HDT level was being limited by unexpected leakage from a flange on an incoming line from a feedwater heater. When the flange was isolated to stop the leakage, HDT level began increasing. The high level dump valve failed to open on high level, and level further increased to the turbine trip setpoint. <br /><br />Pneumatic controls for the high level dump valve were found not to be properly aligned, preventing valve opening. Bolting on the leaking flange was found to be improperly torqued. A Heater Drain system alignment, including pneumatic controls, was performed prior to restart. The flange bolts were properly torqued prior to restart.
309 | 3091989001 | 1989-01-10 | QR5 | Turbine Trip | [45 empty] | Maine Yankee | P | CE | PO | 100 | At 2019 on January 10, 1989, the reactor automatically tripped from 100% power on loss of load due to a turbine trip. The turbine tripped due to a spurious low voltage condition on a control power bus for the Electro-Hydraulic Control (EHC) system. <br /><br /> The EHC system positions the turbine control valves. Control power for EHC is provided from five DC power busses. Loss of voltage on any one of these busses actuates a relay that trips the main turbine.<br /><br /> A Westinghouse technical representative (the EHC system vendor) physically inspected the power distribution panel and electronically tested the system. The system was found functioning properly. The root cause of the spurious loss of voltage could not be identified.<br /><br /> As a precautionary measure, several potentially suspect electronic components were replaced. A temporary strip chart recorder was connected to three of the busses to assist further troubleshooting efforts in the event of a repeat occurrence. The other two busses are not externally accessible for recording.
309 | 3091989003 | 1989-04-05 | QR5 | Turbine Trip | [45 empty] | Maine Yankee | P | CE | PO | 100 | On April 5, 1989, a plant trip occurred when generator protective relays 86P and 86BU actuated on a loss of load condition to trip the reactor and turbine. The cause of the plant trip was attributed to a Central Maine Power Company (CMP) relay inspector returning a 345 KV breaker failure relay to service. After testing the relay, the inspector did not close the relay input switches before closing the output (trip) switches. With all output switches closed, a charged input cable was reconnected to the relay, causing it to actuate. The relay in turn tripped unit tie breakers which isolated the plant from the grid resulting in the loss of load condition.<br /><br /> All plant systems responded normally to the plant trip. <br /><br /> A caution has been added to the associated CMP Test Instruction ensuring the output (trip) switches are closed last when restoring the relay to service.
309 | 3091991005 | 1991-04-29 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | X | [10 empty] | Maine Yankee | P | CE | PO | 100 | On April 29, 1991, Maine Yankee tripped from 100% power when one of the two main output transformers developed an internal fault. The electrical fault in the main transformer X-1A resulted in a generator primary relay trip of the main turbine. The Reactor Protective System tripped the reactor on Loss of Load. Protective relaying and the automatic transfer to reserve power performed as designed. <br /><br /> The transformer fault caused arcing at the neutral bus beneath the main generator. The arcing damaged hydrogen lines and the neutral leads bushings and resulted in a hydrogen fire beneath the main generator. The plant declared an Unusual Event due to the fire, which was allowed to burn itself out over a 3 hour period. <br /><br /> The damaged transformer has been replaced with an on-site spare (X-1S). The main generator repairs were completed and the plant resumed operation on May 31, 1991. <br /><br /> Two transformer failures (without fires) occurred previously at Maine Yankee on August 13, 1988 (X-1A) (LER-88-006), and on August 31, 1978 (X-1B). <br /><br /> The root cause of the transformer fault was an internal fault to ground. The transformer (X-1A) had been rebuilt following the fault in 1988 and had been in service for approximately 9 months.
309 | 3091991006 | 1991-05-30 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Maine Yankee | P | CE | PO | 12 | At 1754 on May 30, 1991, with the reactor at 12% power, an automatic reactor trip occurred due to actuation of the Reactor Protective system. Level in steam generator number one dropped below the low steam generator water level trip setpoint when main feedwater pump (P-2A) tripped on low suction header pressure. The feedwater pump tripped when the main feedwater regulating valves had been opened an excessive amount allowing a large inflow of feedwater. <br /><br /> During this event, standby main feedwater pump P2B did not run and standby condensate pump P27C did not automatically start when they should have. Subsequent testing and evaluation found pressure switch PS 1305B, which provides an auto trip signal to P2B, to be defective. A replacement pressure switch was installed and tested. <br /><br /> Pressure sensing switches associated with main feedwater pump auto start and auto trip functions were tested and calibrated. Pressure sensing lines were blown down. Pressure sensing equipment and circuitry associated with P27C auto start functions were inspected and functionally checked. <br /><br /> An attachment providing enhanced guidance for operating the feedwater station during plant startup at low power will be added to the plant startup procedure. During the next refueling outage, February 1992, a modification to the main feedwater regulating system will include installing new main feedwater regulating valve controllers.
309 | 3091991010 | 1991-10-05 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Maine Yankee | P | CE | PO | 100 | At 0237 on October 5, 1991, an automatic reactor trip from 100% power occurred due to actuation of the Reactor Protective System from a loss of load trip when the main turbine tripped. The turbine trip occurred when the steam driven feedwater pump (P-2C) tripped after a condensate pump (P-27C) breaker tripped due to a phase to phase short at the motor leads connection. <br /><br /> The generator primary relay (86P) actuation was delayed due to the slow closure of a main turbine stop valve; the backup relay (86BU) actuated and transferred station service to offsite power as designed. All safety systems performed as expected.
309 | 3091991012 | 1991-11-22 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Maine Yankee | P | CE | PO | 100 | A reactor trip from 100% power occurred on November 22, 1991 at 0957 due to the failure of a condensate pump motor (P-27B). Internal motor lead arcing caused a drop in voltage on the bus. The condensate pump motor breaker tripped on overcurrent. The transient resulted in a trip of the steam turbine driven feedwater pump. This action tripped the main turbine. The reactor protective system tripped the reactor on loss of load. <br /><br /> All safety systems performed as expected. <br /><br /> This LER is similar to number 91-010, however, the cause of the LER 91-010 motor failure is not identical to this LER.
309 | 3091992001 | 1992-02-08 | QR5 | Turbine Trip | [45 empty] | Maine Yankee | P | CE | PO | 79 | On February 8, 1992 at 2224, a manual plant trip was initiated due to a loss of the main turbine electro-hydraulic control system (EHC) pressure. The plant was in a coastdown mode in preparation for the 1992 Refueling Outage. <br /><br /> Normally each of the two EHC pumps is independently powered. The two motor control centers (MCCs) that supply power to the EHC pump motors were cross-connected to perform maintenance. The feeder breaker from the bus supplying the MCCs tripped, de-energizing the EHC pumps, causing the loss of the EHC system pressure. The operating crew assessed the problem and decided to manually trip the plant.<br /><br /> All safety systems performed as expected. The post trip evaluation determined that the MCC feeder breaker was slightly overloaded in the cross-connected configuration due to cyclical loads. <br /><br /> To prevent recurrence of a similar event, bus PMs will be upgraded to require determination of bus loading prior to cross-connection. Revised preventative maintenance requirements are scheduled to be complete by September 1, 1992.
309 | 3091994008 | 1994-05-18 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Maine Yankee | P | CE | PO | 100 | On May 18,1994, the reactor tripped from 100% power on loss of load due to a main turbine trip. The main turbine tripped due to a trip of the turbine-driven feedwater pump (TDFP). The TDFP tripped on overspeed when high pressure (HP) steam was manually aligned to the TDFP. <br /><br /> Earlier, an air leak on a 345 KV switchyard breaker required decreasing power to 600 MWE (70% rated power) to allow breaker isolation. Reactor power was maintained at 100% while the main turbine load was being reduced. At 80% rated output, the main turbine extraction steam did not have sufficient pressure to run the TDFP and therefore HP steam had to be aligned. The control room recognized that the HP governor valve was cycling and dispatched an operator to open the HP isolation valve. Since the HP governor valve already had a high open demand signal, the pump tripped on overspeed. <br /><br /> The root cause of the plant trip was inadequate procedural guidance. Changes have been made to the procedure to prevent recurrence.
309 | 3091994011 | 1994-07-16 | QR6 | Manual Reactor Trip | [45 empty] | Maine Yankee | P | CE | HS | 1 | At 0207 on July 16, 1994, during a plant shutdown, with the plant in Hot Standby (Condition 6), operators manually actuated the Reactor Protective System (RPS) to trip the reactor in accordance with plant procedures, after receiving a high vibration alarm and observing abnormal vibration indications for the #2 Reactor Coolant Pump (RCP). The #2 RCP was shut down at 0210 pending an engineering evaluation of the indicated vibration amplitudes. <br /><br /> Subsequent investigation determined the cause of the increased vibration indication to be a faulty vibration monitoring instrument.
309 | 3091995001 | 1995-01-14 | QR6 | Manual Reactor Trip | [45 empty] | Maine Yankee | P | CE | PO | 99 | On January 14, 1995, Maine Yankee was in the process was in the process of returning to full power following a shutdown to repair a leak in the feedwater system. At 0802, with the plant operating at 99 percent power, the Control Room received an alarm indicating a ground in the main electrical generator. The crew had approximately 50 minutes to determine the cause of the ground before a time delay relay would automatically trip the plant. <br /><br /> Following further investigation by Operations personnel and Maintenance workers, other indications of a main generator ground were found and the unit was manually tripped at 0839. <br /><br /> Plant systems responded normally during the plant trip. <br /><br /> An investigation of the ground by plant personnel with guidance from the generator manufacturer's representatives revealed the ground occurred in the A phase of the generator stator. An evaluation to determine the exact nature of the failure is continuing.<br /><br /> The anticipated corrective action is to repair or replace a damaged coil in the generator stator.
309 | 3091996003 | 1996-02-13 | QP5 | Excessive Feedwater Flow | [45 empty] | Maine Yankee | P | CE | PO | 90 | On 2/13/96 at 2228, Maine Yankee was operating at 2440 MWt (90.3% power) when the reactor automatically scrammed due a loss of load trip from a high steam generator #3 water level. The high water level was due to a faulty positioner on the steam generator #3 Main Feedwater Regulating Valve(MFRV). The faulty positioner caused the main feedwater regulating valve to go to the full open position which resulted in overfeeding the #3 steam generator and the resultant trip on high water level. <br /><br /> The faulty positioner on #3 MFRV has been replaced. The positioner on #2 MFRV was also replaced as a precautionary measure, since it had been in service since July 1992. The positioner on #1 MFRV had been replaced in January 1996. The air filter of the positioner on #3 MFRV was inspected and found to be clean. <br /><br /> Planned long term actions are to (1) have the manufacturer perform a failure analysis on the positioner, (2) evaluate equipment history to include MFRV positioners; in a Preventative Maintenance program, (3) evaluate securing the air supply to the MFRV during plant shutdowns, and (4) evaluate new types of control systems which would relocate the instruments off the MFRV actuator.
309 | 3091996031 | 1996-10-09 | QR8 | Spurious Reactor Trip | [45 empty] | Maine Yankee | P | CE | PO | 90 | On October 9, 1996, Maine Yankee was operating at 2440 MWt (90.3% power) when the reactor scrammed. The reactor trip breakers opened without any initiating trip signals having been received. At the time of the trip, the logic trip relay surveillance was in progress and reactor trip breakers #3 and #7 were open as part of the surveillance. All safety related systems responded correctly upon the plant trip. <br /><br /> The exact cause of the trip has not been determined. The apparent cause of the trip was voltage transient in the logic circuitry being tested during the surveillance. Additional testing and analysis are being performed to attempt to determine the exact cause of the trip, including bench testing o the circuit to identify any potential design deficiencies which might have contributed to the event. Also being considered is additional monitoring of the circuit during the next surveillance. <br /><br /> The following logic matrix components which were undergoing testing at the time of the trip were replaced prior to plant restart: the test power supply and the Matrix Relay Hold push-button. Also, the circuitry was thoroughly tested (with no problems found) and the logic trip relay surveillance was completed before a plant restart.
311 | 3111987002 | 1987-01-18 | QR8 | Spurious Reactor Trip | [45 empty] | Salem 2 | P | WE | SU | 3 | On January 18, 1987, a Reactor Trip occurred while performing troubleshooting on Nuclear Instrument System Intermediate Range (IR) Channel N36. The Reactor was at three percent (3%) power and the P10 Interlock which blocks trips from Intermediate Range indication, was not in effect when the Technician pulled the control power fuse for the channel, resulting in an erroneous "High Neutron Flux" signal and subsequent Reactor Trip. The "root cause" has been determined to be personnel error compounded by an I&C Technician Training inadequacy. He was not aware, that pulling the control power fuse in that condition would result in a Reactor Trip. Signs have been placed on the IR (drawer) control power fuses to caution personnel regarding pulling the fuses. This occurrence was reviewed with the I&C Technicians. This occurrence will be reviewed by the Nuclear Training Center for additional improvements to the I&C Technician Training Program. Additionally, the procedures will be reviewed for improvements from a "Human Factors" point of view.
311 | 3111987004 | 1987-03-12 | QR5 | Turbine Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON MARCH 12, 1987, AT 0930 HOURS, FOLLOWING A LOAD INCREASE TO 1160 MWE AND 530 MVAR, SALEM UNIT NO. 2 EXPERIENCED A GENERATOR-TURBINE/REACTOR TRIP. THE 'ROOT CAUSE' OF THE GENERATOR FIELD LOSS RESULTING IN THE TRIP COULD NOT BE DETERMINED. THE INVESTIGATION RESULTS SUGGEST THAT THE LOSS OF GENERATOR EXCITATION OCCURRED DUE TO A BUMPED TRANSFER WHEN THE VOLTAGE REGULATOR WAS SHIFTED FROM AUTO TO MANUAL. WHEN THIS OCCURRED, GENERATOR FIELD-CURRENT WAS OBSERVED TO DROP FROM 5500 AMPS TO APPROXIMATELY 3000 AMPS. IN ACCORDANCE WITH DESIGN, THE SHIFT OF THE VOLTAGE REGULATOR WAS INITIATED BY THE EXCITER OVERCURRENT PROTECTION. THE RELAYS POTENTIALLY RESPONSIBLE FOR THE OCCURRENCE WERE CHECKED; NO ADJUSTMENTS WERE REQUIRED. THE VOLTAGE REGULATOR WAS EXTENSIVELY FUNCTIONALLY TESTED. THIS OCCURRENCE WAS DISCUSSED WITH THE GENERATOR VENDOR. NEW OPERATING CURVES WERE ISSUED WITH A LIMIT OF 400 MVAR.
311 | 3111987005 | 1987-04-07 | QR5 | Turbine Trip | [45 empty] | Salem 2 | P | WE | PO | 85 | On April 7, 1987, during trouble shooting of No. 22 Main Turbine Governor Valve controls, a Reactor Trip was generated from a Turbine Trip with Reactor Power greater than the setpoint of the P-7 Interlock. The "root cause" of this occurrence has been determined to be an equipment failure. The Turbine trip was initiated from an Electro Hydraulic Control (EHC) System DC power failure which occurred when a new servo card was inserted in the governor valve position control circuit. The new servo card had an undetected failed capacitor which shorted the DC control power to ground, resulting in a Turbine Trip and a direct Reactor Trip. The failed servo card was replaced and the system was tested with satisfactory results. Although this is considered to be an isolated occurrence, in the future, spare servo cards will be calibrated for each Main Turbine Governor Valve during a convenient shutdown period. No further corrective action is deemed necessary.
311 | 3111987011 | 1987-08-06 | QP5 | Excessive Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 100 | On August 6, 1987 at 0912 hours, a Turbine Trip/Reactor Trip occurred due to No. 24 Steam Generator (S/G) High-High Level. At the time of the trip, a No. 24 S/G Level Channel II functional test was in progress. Other than the trip, no abnormal events were identified. The root cause of the trip has been attributed to personnel error. The Nuclear Control Operator during the functional test did not correct a feed-steam flow deviation. A performance review of the Nuclear Control Operator has been completed. Appropriate corrective discipline has been initiated. A discussion of this event will be included in the next cycle of Operator Requalification Training and will be considered for inclusion in initial Operator Training for the S/G water Level Control System. Additionally, a copy of this LER will be incorporated into the Operations Department Newsletter.
311 | 3111988006 | 1988-04-21 | QR8 | Spurious Reactor Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | On April 21, 1988 at 1533 hours, during routine power operation, a reactor trip occurred. The trip was a result of No. 23 Reactor Coolant (RC) Loop Low Flow with the reactor greater than or equal to 36% power (P-8). At the time of the event, a Maintenance technician was repairing a leak on the low pressure side of No. 23 RC Loop Flow transmitter. The root cause of this event has been attributed to personnel error. This event has been reviewed by Maintenance Department management. Appropriate corrective discipline with the individual(s) involved has been completed. Also, this event has been reviewed with Maintenance Department personnel during a "work shop" type session. The need to use established procedures for work was stressed. A sign (e.g., lamacoid) will be posted by the reactor coolant flow transmitters valving cautioning personnel about the sensitivity of this equipment to isolation valve manipulation. A Human Performance Evaluation System (HPES) investigation has been initiated.
311 | 3111988007 | 1988-04-22 | QR5 | Turbine Trip | [45 empty] | Salem 2 | P | WE | PO | 18 | On April 22, 1988 at 1418 hours, a Turbine Trip occurred as a result of No. 23 Steam Generator (S/G) High-High Level (67%). Following the Turbine Trip, a Reactor Trip occurred due to the plant being above 10% power (permissive P-7). A review of the event revealed that just prior to the Turbine Trip reactor power increased from approximately 12% to 18%. This power increase apparently caused level in No. 23 S/G to increase (swell) rapidly peaking at approximately 67%. The apparent cause of this event has been attributed to Electro-Hydraulic Control (EHC) equipment problems. The EHC Rate Amplifier Card was replaced and the EHC was successfully tested. Operations Management has reviewed this event. Discussions with the individuals involved have been completed. Operating Department procedures will be reviewed to ensure appropriate guidance is provided for EHC operation. Engineering investigations of the EHC control concerns during plant startup are continuing. A License Change Request (No. 87-09) has been submitted to the NRC modifying the logic for a Reactor Trip subsequent to a Turbine Trip. Presently, a Turbine Trip/Reactor Trip will occur when reactor power is greater than or equal to 10% (P-7). The change will require a Turbine Trip/Reactor Trip to occur when reactor power is greater than or equal to 50% (P-9).
311 | 3111988009 | 1988-05-13 | QR3 | Reactivity Control Imbalance | [45 empty] | Salem 2 | P | WE | PO | 97 | On May 13, 1988 at 2349 hours, a reactor trip occurred. The first out indication was "Power Range Negative Flux Trip". At the time of the trip, reactor power was being reduced to between 85% and 90%, via rod insertion, to support performance of Technical Specification Surveillance 4.3.4.2. Investigations revealed it is highly probable that Control Rod No. 1D3 had dropped resulting in the negative rate trip. Testing to determine why the control rod dropped was inconclusive. The 21BD Power Cabinet Alarm Circuitry Card was replaced. The Unit was returned to service on May 15, 1988. No further problems or concerns associated with the Control Rods have been identified.
311 | 3111988014 | 1988-06-22 | QR8 | Spurious Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Salem 2 | P | WE | PO | 100 | On 6/22/88, during routine power operation, a reactor trip and safety injection (SI) occurred. The reactor trip occurred when the Solid State Protection System (SSPS) (JC) sensed No. 23 reactor coolant pump (RCP) breaker open. A reactor trip will occur when one of the four RCP breakers opens with power above P-8 (36%). The SI was the result of a combination of the indication of Nos. 22 and 23 Steamline Low Pressure (less than 500 psig) and Nos. 21 and 22 High Steamline Flow. The Unit was stabilized in Mode 3 (Hot Standby). The apparent root cause of this event has been attributed to the failure of the "C" Vital Instrument Bus inverter. Valve 2PR2 and the Nos. 23 and 2 CFCUs (which failed to function as designed during the event) were tested to ensure operability. No problems were identified. The "C" Vital Instrument Bus Inverter was repaired. The Unit was returned to service on June 25, 1988. A design change has been initiated (2EC-2245) to delete the reactor trip logic which occurs when "one out of four RCP breakers open" is met. This design change will be implemented during the upcoming fourth refueling outage pending approval by the NRC of a submitted license change request. A similar design change for Salem Unit 1 will be implemented during its next refueling outage. A design change is being prepared to replace the inverters with state of the art equipment.
311 | 3111988016 | 1988-07-30 | QR8 | Spurious Reactor Trip | [45 empty] | Salem 2 | P | WE | PO | 80 | On 7/30/88, during power reduction operations, a reactor trip occurred. The "first out" overhead annunciation was "Turbine Trip - P-7". The root cause of this event has been attributed to equipment problems associated with the "C" Vital Instrument Bus (VIB) inverter. Just prior to the trip, a "C" VIB inverter failure indication was received in the Control Room. The failure did not cause a reactor trip since the VIB voltage loss lasted for less than 10 milliseconds. To prevent a reactor trip from occurring, power reduction to less than 36% (P-8) at 1%/minute was initiated. When power reached 80%, a reactor trip occurred as the "C" VIB voltage dropped to a value low enough for relay operation for 67 milliseconds. The first out annunciation indication of No. 23 RCP breaker open was not received since the signal mustlast for at least 250 milliseconds to actuate the alarm. However, the reactor trip would generate a turbine trip causing the first out annunciator to lock in on "Turbine Trip - P-7". The "C" VIB Inverter has been repaired. The Unit was returned to service on 7/31/88. A design change has been initiated to delete the reactor trip logic which occurs when "one out of four RCP breakers open" is met. It will be implemented during the upcoming fourth refueling outage. A similar design change for Salem Unit 1 will be implemented during its next refueling outage. Both Salem Unit 1 and Salem Unit 2 inverters will be replaced with state of the art equipment during their respective 8th and 5th refueling outages.
311 | 3111988017 | 1988-08-31 | QP5 | Excessive Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 72 | On 8/31/88 at 0553 hours, a Turbine Trip occurred as a result of No. 23 Steam Generator (SIG) High-High Level (67%). Following the Turbine Trip a Reactor Trip occurred due to the plant being above 10% power (Permissive P-7). The unit was in the process of a power coast down as the start of the fourth refueling outage approached. Prior to the event, the Nuclear Control Operator (NCO) received an alarm indicating that steam flow was significantly less than feed flow for No. 23 S/G. Feed flow was at 100% with steam flow at 70%. The NCO attempted to manually close the 23BF19 valve (Feedwater Control Valve), however, the valve could not be closed resulting in the SIG level rising to the Turbine Trip setpoint. The apparent cause of this occurrence has been attributed to a design/equipment problem associated with the 23BF19 valve. Investigation of the 23BF19 valve revealed that its positioner linkage had disconnected due to vibration. The linkage had pulled itself away from the lower turn buckle as evidenced by the damaged rod threads. Since the Unit was very near the end of its fuel cycle, the scheduled fourth refueling outage was initiated. The "star" type lockwasher will be replaced with an "overlap" type lockwasher for all BF19 and BF40 valves. Also, "locktight" will be applied to the rod threads. The preventive maintenance requirements for the BF19 valves will be modified to require inspection of the turnbuckles and tightness of the rod nuts every 18 months.
311 | 3111988024 | 1988-11-28 | QP5 | Excessive Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 25 | On 11/28/88, during turbine startup, No. 23 Steam Generator (S/G) level increased to 67% resulting in a Turbine Trip. Following the Turbine Trip, a Reactor Trip occurred as a result of No. 22 S/G low-low level. The root cause of this event has been attributed to inadequate procedural guidance. Maintenance procedures do not adequately define how to set the regulator for the BF19 Feedwater Control valve positioner. Subsequently, the 23BF19 positioner regulator was set high. Investigations revealed that level was oscillating on all four S/Gs prior to the turbine trip. These oscillations coupled with the high setting of the regulator led to failure of the positioner causing the valve to lock open momentarily. This led to the Turbine Trip on high-high S/G level. Upon receipt of the trip signal, the Steam Generator Feed Pumps (SGFPs) tripped, by design. With the SGFPs tripped, S/G level began to decrease in all four S/Gs. Operations personnel initiated AFW System flow to the S/Gs. However, the AFW System is designed to maintain reactor power to 5%. Reactor power could not be reduced below 5% (from 25%) quickly enough to prevent the reactor trip on No. 22 S/G low-low level. The 23BF19 positioner has been repaired. The valve was successfully stroke tested. The other BF19 valve positioners were checked and the other BF19 valves were successfully stroke tested. The procedures for setting the BF19 positioner regulator will be revised to ensure consistent results. Startup of the Unit was successfully completed on 12/2/88. This event will be reviewed for incorporation into applicable training programs.
311 | 3111989003 | 1989-02-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 60 | On 2/5/89, following power reduction from 90% to 60%, the Unit experienced a Rx. Trip on No. 23 Steam Generator (S/G) Low Level concurrent with Steam Flow/Feed Flow mismatch. At the time of the event, Nos. 23a and 23b Circulating Water Pumps and No. 23 Heater Drain Pump were out of service. Four minutes prior to the unit trip, No. 22 S/G Feed Pump (SGFP) had tripped due to low suction pressure. It was found that the low suction trip set point for the #22 SGFP responded high due to failure of the low suction pressure switch. The root cause of this event has been attributed to inadequate procedures associated with operating the plant with Circ. Water System reduced capacity concurrant with an inoperable Heater Drain Pump. Procedure AOP-COND-2 has been revised to clarify operator actions with inoperable Circ. Pumps and Heater Drain Pumps. The SGFP low suction pressure first out annunciator relay was installed and tested. The speed control and electric overspeed were also checked for both SGFPs. The No. 22 SGFP low suction pressure switch was repaired and the No. 21 SGFP switch was checked and found satisfactory. The #21 SGFP mechanical overspeed device was checked and the pump was operated to simulate a transient prior to it being placed in service. The 23MS15 valve was adjusted and tested successfully. Investigation of the 23MS167 Control Room indication problem revealed that the "close" limit switch was not making proper contact. The switch was repaired and the valve tested satisfactorily. This event has been reviewed by Operations management and will be reviewed with applicable personnel. This event will be incorporated into applicable training programs.
311 | 3111989005 | 1989-03-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 100 | On 3/12/89, both Steam Generator Feed Pumps (SGFPs) reduced their turbine speed to idle. The reactor subsequently tripped on No. 23 Steam Generator (S/G) Feed Flow/Steam Flow Mismatch with Low S/G Level. After the reactor tripped, a Safety Injection (SI) occurred on High Steamline Flow coincident with Low Steamline Pressure. The root cause of this event has been attributed to an equipment failure. A control power fuse, in the "D" Vital Instrument Inverter low voltage power source, came out of its fuse holder resulting in inverter failure and deenergization of "D" Vital Instrument Bus. Investigations concluded the fuse more than likely had come out of the fuse holder due to improper installation at some point in the past. The fuse assembly did not show any sign of damage or impairment which would cause the fuse to dislodge. Subsequently, the inverter fuse was reinstalled and successfully checked for continuity and tightness. The static inverter was started, tested satisfactorily and returned to service. Engineering is investigating the feasibility of separating the pressure channels to other vital inverters thereby eliminating the possibility of the occurrence of a similarly caused SI. New Vital Inverters are scheduled to be installed during the next Unit 2 refueling outage. These inverters have a fast transfer feature. Engineering is evaluating the possibility of moving the inverter's alternate power source to the same bus as the normal supply. This coupled with the high speed transfer feature of the new Vital Inverters should prevent recurrence of this event.
311 | 3111989008 | 1989-04-11 | QL5 | Partial Closure of MSIVs | [45 empty] | Salem 2 | P | WE | PO | 100 | On April 11, 1989 at 2043 hours, a reactor trip on No. 24 Steam Generator (S/G) "Low-Low Level" occurred. The No. 24 main steamline isolation valve, 24MS167, had closed. At the time of the event, the required Technical Specification Surveillance 4.0.5-V for the 21MS18 Main Steamline Bypass Stop Valve was in progress. The root cause of this event has been attributed to an equipment failure. An "operate reset" latching relay (74-4A), associated with the Solid State Protection System (SSPS), failed during the 21MS18 surveillance resulting in closure of the 24MS167 valve. The failed "74-4A" relay was replaced. The circuit was then tested satisfactorily. An inspection of the other 74-4A and 3-3B MS167 relays will be conducted to determine if similar mechanical defects are present. Following the reactor trip, the 24MS15, Main Steamline Safety Valve, lifted twice. The valve remained partially open for approximately one hour. Investigation revealed that the as found lift set pressure was 901 psig (after the second lift). A proper lift setpoint of 1070 psig could not be achieved. The valve was subsequently replaced with a spare valve. It appears that the valve seating surface during the first lift became damaged allowing increased leakage. The replaced 24MS15 valve has been shipped to Crosby Valve & Gage Co. for inspection and repair.
311 | 3111989013 | 1989-06-10 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X | X |  |  |  | Salem 2 | P | WE | PO | 100 | On 6/10/89, a reactor trip was manually initiated from 15% reactor power due to the loss of the main condenser on high back pressure. At 2306 hours the "Screenwash Trouble" overhead annunciator in the Control Room alarmed due to high diff. level (dl) across several Circulating Water System (CWS) screens. A power runback was initiated. Within five minutes of the alarm, five of the six circulating pumps tripped on high dl across their associated screens. The Turbine was manually tripped with the reactor at 48% power. Subsequently, the functional turbine bypass valves (steam dumps) were armed and opened. Condenser back pressure increased to where the permissive to use the steam dumps was exceeded. The steam dump valves closed and the first main steam safety valve in each steamline lifted. Direction was given to manually trip the reactor. The root cause of this event has been attributed to external causes and inadequate corrective action from a similar prior event. Large accumulations of grass and debris on the screens caused the high dl. On 8/11/83, a similar event occurred. The corrective action from the prior event did not require any long term actions. A review of the preventive maintenance (PM) history for cleaning the trash racks was conducted. It was found that no specific PM requirement existed. The racks were last cleaned three years ago. Therefore, a PM task to require special cleaning of the trash racks every refueling outage has been established. The trash racks were cleaned of the grasses and debris and the Unit was returned to power on 6/14/89. The failed 21A Circulating Water Pump Struthers Dunn relay which prevented it from tripping was replaced.
311 | 3111990029 | 1990-06-28 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Salem 2 | P | WE | PO | 75 | At 0032 hours on 6/28/90, during Salem Unit 2 power ascension operations, a reactor trip occurred following the loss of both Steam Generator Feedwater Pumps (SGFPs) resulting from failure of 2F 4160-480/277 Volt Transformer. Due to the loss of both SGFP's "Low Steam Generator Level Coincident with Steam Flow/Feed Flow Mismatch" had occurred causing the reactor trip. A main steamline isolation was manually initiated to reduce an excessive cooldown rate following the reactor trip. Main Steam Isolation Valves (MSIVs) 21 and 24MS167 did not close on the initial attempt; however, the operator again depressed the Main Steamline Isolation pushbuttons (this time for an extended period) and the valves closed. The unit was stabilized in Mode 3 (Hot Standby). The root cause of the transformer failure was inadequate preventive maintenance. The preventive maintenance program is being revised to provide routine, documented inspection and cleaning of transformer coils. Also, the routine electrical transformer testing is being revised to include low frequency-induced test and corona detection to better check insulation and integrity for incipient failures. Investigation of the MSIV closure concern revealed the MSIV isolation logic did not meet design basis as per IEEE Standard 279. The MSIV circuitry was modified on Salem Units 1 and 2 to resolve the identified concerns. The MSIV design change concerns, addressed in this LER, have been reviewed by E&PB management and will be reviewed with applicable E&PB supervision stressing the importance of cross-disciplinary reviews of design changes.
311 | 3111990036 | 1990-09-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 60 | On 9/4/90 at 0226 hours, during normal power operation, No. 21 Steam Generator Feed Pump (SGFP) tripped on Low Suction Pressure. A turbine runback to 60% power at 15%/min was initiated. At the completion of the runback, Steam Generator (S/G) level began increasing. As per procedure, the four BF19 valves (S/G Feedwater Control Valves) were placed in manual mode to gain control of S/G level. However, just after the 24BF19 valve was put in manual control, No. 24 S/G reached its high level setpoint initiating a Turbine Trip at 0231 hours on 9/4/90. With reactor power above permissive P-9 (50 power), a reactor trip followed. The root cause of the reactor trip is attributed to equipment failure. The 21BF19 Auto/Man controller failed, causing valve closure during the recovery operation after the No. 21 SGFP had tripped. The setpoint for the suction pressure switch had drifted high. When the 23HD15 valve (Heater Drain Pump Discharge Control Valve) failed closed (ruptured diaphragm) a significant SGFP suction pressure drop occurred. This coupled with the high setpoint resulted in the No. 21 SGFP trip. Preceeding the rupture of the valve diaphragm, the valve controller failed. The failed pressure switch, the 23HD15 valve diaphragm, and the 23HD15 valve controller's pneumatic relay were replaced. The 21BF19 valve Auto/Man controller was replaced. The preventive maintenance program for the HD15 valves will be reviewed. The secondary plant process controls will be evaluated to ensure optimum reliability with minimal operator required intervention. A review of existing procedural guidance for actions, following a loss of a SGFP during full power operation has been initiated.
311 | 3111991017 | 1991-11-09 | QR5 | Turbine Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | On 11/9/91, a Reactor Trip event occurred during performance of the monthly Auto Stop Oil System protection device testing. After the generator breaker opened (per design), a turbine overspeed condition developed resulting in failure of the turbine/generator. The reactor trip initiated while the Auto Stop Oil (AST) System test/normal lever was still in the "test" position. Following the initial drop in AST System header pressure, pressure returned. Once the AST bistable reset setpoint was reached, the turbine relatched allowing the turbine valves to reopen. Within 15 seconds of the generator output breakers' opening, the main stop valves fluctuated at the 90% open limit. Within the following 6 seconds the 4 main stop valves had gone full open. The governor valves then opened due to failure of the 63-3 AST turbine protection pressure switch to lock in the turbine trip signal in conjunction with the failure of 3 overspeed protection EHC solenoid valves (20/ET, 20-1/OPC and 20-2/OPC) to open. The operators at the front standard heard several highly unusual sounds from the turbine and manually tripped the turbine causing closure of the turbine valves. The trip cause was blockage of the AST pressure reduction orifice. Investigation to identify the source of the foreign material is continuing. Several causal factors of the turbine failure have been identified (see main report). Corrective actions have been taken or are in the process of implementation to address these causal factors.
311 | 3111992007 | 1992-04-26 | QP5 | Excessive Feedwater Flow | [45 empty] | Salem 2 | P | WE | SU | 4 | On 4/26/92, at 0219 hours, during plant startup, a Reactor Trip occurred on No. 24 Steam Generator (S/G) Low-Low Level during startup following the sixth refueling outage. Prior to the trip, at 0153 hours, with reactor power at 3%, a Turbine Trip signal and Main Feedwater isolation on No. 23 S/G high-high level occurred. Assessment of the cause of the High-High Level turbine trip signal, by the Senior Nuclear Shift Supervisor (SNSS), was that the Nuclear Control Operator (NCO) overfed No. 23 S/G. Approximately 12 minutes later the startup resumed. Reactor power remained at approximately 4%. A second NCO was assigned to assist in placing Main Feedwater in service. While placing No. 23 S/G onto Main Feedwater, No. 24 S/G level started decreasing below 25%. At 0220 hours, a reactor trip occurred on No. 24 S/G Low-Low Level. Following the trip, Auxiliary Feedwater was reduced and a main steamline isolation was manually initiated to curtail a reactor cooldown following the trip. The cause of the No. 23 S/G High-High level signal and the reactor trip was Management/Quality Assurance Deficiency as related to maintenance activities on the No. 23BF19 valve (#23 S/G Feedwater Control Valve) during the recent refueling outage. Debris from maintenance activities was not removed from the inlet pipe to the valve. This debris kept the valve open during the startup. Corrective action included 23BF19 valve disassembly, cleaning and inspection; procedure modifications, positive disciplinary action, and management review of event with applicable personnel.
311 | 3111992009 | 1992-05-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 15 | On 5/14/92, at 1801 hours, during a plant startup, a reactor trip on No. 23 Steam Generator (S/G) Low-Low Level occurred from 15% reactor power. Prior to the trip, the No. 23 S/G had experienced level control problems.<br /><br /> Two control modules required replacement. To support replacement of the modules, the No. 23 S/G main feedwater control valve (23BF19) was closed leaving mass inventory control via the No. 23 S/G feedwater control valve bypass valve (23BF40). However, contrary to this understanding, the 23BF19 valve remains open approximately 0.25" when at 20% reactor power; therefore, when the module replacement work was initiated and the 23BF19 valve demand was reduced to 0%, in preparation of 23BF19 valve control return, it fully closed. This eventually lead to the reduction of S/G mass inventory to below the reactor trip setpoint (16%). The root cause of this event is "Management/Quality Assurance Deficiency". Operations personnel understanding of the BF40 valve (4" Globe Valves) capability for maintaining S/G mass inventory (independent of the BF19 valves) was not correct. Operations procedure, "Hot Standby to Minimum Load" has been revised. The circumstances surrounding this event will be reviewed with applicable Operations Department personnel and will be reviewed by the Nuclear Training Center. PSE&G will review its past response to INPO Significant Operating Experience Report No. 84-4. The BF19 and BF40 valves position indication will be reviewed by engineering.
311 | 3111992014 | 1992-09-03 | QR8 | Spurious Reactor Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | On 9/3/92, at 0917 hours a reactor trip occurred due to the 'A' Reactor Trip Breaker (RTB) opening. Following the reactor trip, a cooldown occurred. Auxiliary Feedwater was reduced and the MS10 valves (atmospheric relief valves) were verified closed. However, the cooldown continued and manual Main Steamline Isolation (MSI) was initiated stopping the cooldown. After the MSI, Reactor Coolant System (RCS) pressure and temperature reached maximum levels of 2280 psig and 552 degrees F. The Pressurizer Master Controller was taken to manual. Pressurizer spray was initiated and pressure reduced and stabilized at 2235 psig. At 0936 hours, the 21MS15 and 22MS15 main steam safety valves lifted. The 21MS10 and 22MS10 valves had not opened. At 1005 hours, an 'Unusual Event' was declared for, 'SG Safety Failure to Reseat'. The Unusual Event was terminated with the plant in Mode 3. Investigation of this event included testing of the '2A' RTB which did not identify any RTB problems. The cause of the reactor trip is attributed to personnel error. An NEO exhibited poor judgement resulting in a sequence of events leading to the trip. Appropriate disciplinary action has been taken with the individual involved. The reactor trip and events following the trip will be reviewed by the Nuclear Training Center. Investigation of a Pressurizer pressure master controller concern is continuing. The MS10 control concerns have been investigated by engineering and design changes are planned. The breaker in the '2A' RTB cabinet is being sent to Westinghouse to verify that it functions per design.
311 | 3111993002 | 1993-01-28 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Salem 2 | P | WE | PO | 100 | POWER LEVEL - 100%. On 1/28/93, the low suction pressure alarm for both Steam Generator Feedwater Pumps (SGFPS) was received. Both pumps tripped on low suction pressure. A manual reactor trip was then initiated. The Unit was stabilized in Hot Standby. Prior to the loss of the SGFPS, a technician was connecting a brush recorder to the inputs and output of the Steam Generator Feed Pump (SGFP) Master Controller to troubleshoot observed spikes on all 4 Steam Generator feed flow instrument channels. The root cause of this event is equipment failure. The SGFP master controller module test jack was sufficiently loose to allow the weight of the troubleshooting lead to bring the threads of the troubleshooting test lead into contact with the module chassis. This created an electrical short between the controller signal common and chassis ground, which produced an erroneous maximum speed demand signal. Flow through the pumps then increased resulting in the low suction pressure and the pump trips. The loose SGFP master controller test jack was repaired and other jacks in the SGFP speed control loop circuitry were inspected and repaired as required. The other Hagan protection channel test connections (both Salem Units) are being checked during the protection channel monthly functional surveillance. The Hagan process channel test connections, both Salem Units, will be checked for looseness. Engineering is reviewing whether changes to the test jacks are needed to prevent event recurrence.
311 | 3111993005 | 1993-03-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 100 | On 3/16/93, at 1106 hour , subsequent to a 22 Steam Generator Feedwater Pump (SGFP) trip on low suction pressure, a reactor trip occurred on 24 Steam Generator (SG) low-low level. Condensate Polisher (CP) vessel regeneration was in progress. Following the reactor trip, 24 SG level increased rapidly (due to the 24BF19 valve failing open) and feedwater isolation initiated upon 24 SG level reaching the high-high level setpoint. 24 SG was then isolated. The root cause of the reactor trip is "Management/Quality Assurance Deficiency". Less than timely actions to correct a leaking CPS valve packing and failure to mitigate increasing leakage resulted in failure of a differential pressure switch. This led to the 22 SGFP trip and subsequent Reactor Trip. The failed differential pressure switch was causing premature opening of 24CP2 (Feed and Condensate Inlet Valve). A pressure transient occurred resulting in a sudden drop of SGFP pump suction pressure sufficient to actuate one of the SGFP suction pressure trips. The differential pressure switch failed due to water intrusion. An aggressive leak reduction program is in place. The circumstances surrounding the events in this LER will be reviewed with applicable station personnel for increased sensitivity to mitigation of leaks. The planning effort in support of the 24CP14 valve repair will be reviewed. Additional corrective action will be taken based on the results of this review. The failed CP System differential pressure switch and its flex conduit were replaced. The 24CP14 packing leakage will be repaired .
311 | 3111994008 | 1994-06-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 6 | At 0439 hours on 6/29/94, an automatic Reactor Protection System trip from 14% power occurred due to 23 Steam Generator (SG) lo-lo level, resulting from the tripping of 21 SG Feed Pump (SGFP), caused by 22 SG hi-hi level. Emergency operating procedures were entered and the Unit was stabilized in Mode 3. This event is attributed to the design of the feedwater control system, which exhibits sensitivity at low power levels, that was strongly affected by normal closing of the 21 SGFP recirculation valve, 21BF32. When 21BF32 closed, a greater level increase occurred in 22 SG than in the other SGs. Operability checks and troubleshooting verified proper SG level control response. To eliminate the effect of BF32 closure upon SG level control during Startup, procedure revisions on both Units have been implemented which ensure the valves remain open during Startup. To provide additional margin of SG level control to better cope with feedwater control system transients during Startup and at low power, a license change request will be submitted in order to lower the current SG lo-lo setpoint of 16% to less than 10%. Design changes, currently scheduled for installation on Unit 1 during 1R12 and on Unit 2 during 2R9, utilize digital equipment technology that will reduce the exhibited sensitivity of the feedwater control system at low power levels.
311 | 3111994011 | 1994-09-29 | QL5 | Partial Closure of MSIVs | [45 empty] | Salem 2 | P | WE | PO | 28 | The Nuclear Control Operator (NCO) with balance of plant (BOP) responsibilities mistakenly-closed main steam line isolation valves 21 and 22MS167. The other operating crew NCOs recognized this mistake however, they had insufficient time to intervene in order to avoid an automatic protective response. The BOP NCO, realizing the mistake, immediately initiated a manual reactor trip signal, at 0232 hours on 9/29/94. Expected plant response occurred and Emergency Operating Procedures were entered. Main steam was isolated to limit Reactor Coolant System cooldown and the Unit was stabilized in HOT STANDBY at 0317 hours (same day). This event is attributed to personnel error by the BOP NCO, as a result of inadequate self-checking and inattention to detail. A Human Performance Enhancement System evaluation of this event has been conducted. Appropriate personnel corrective actions have been taken. Observations of operations personnel are ongoing to ensure adequacy of self verification techniques. During the trip recovery, an incorrect attempt was made to reset the Safeguards Equipment Controllers (SECs) and Technical Specification (TS) 3.0.3 was entered. Two SECs were reset and TS 3.0.3 was exited. Subsequent review showed the TS 3.0.3 entry was invalid and the involved overhead alarm (OHA) response procedure was inadequate. Appropriate procedure changes will be made regarding the attempt to reset the SECs.
311 | 3111995004 | 1995-06-07 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Salem 2 | P | WE | PO | 100 | On 6/7/95, at 1828 hours, a Unit 2 controlled shutdown from Mode 1 was initiated in accordance with the requirements of Technical Specification (TS) 3.0.3 due to the inoperability of both Residual Heat Removal (RHR) trains. The inoperability was caused by the failure of the 21RHR pump recirculation valve (21RH29) to automatically open when the 21RHR pump was started and the inability to ensure operability of the 22RHR pump recirculation valve (22RH29). With both RHR trains inoperable, the Unit was operating in a condition not covered by the TSs and the requirements of TS 3.0.3 were initiated. The Unit was reducing load with the group buses already transferred to the 21 and 22 Station Power Transformers. When the Unit load was below 50 MW (14% reactor power), the Nuclear Control Operator manually tripped the turbine. 500KV Bus Section breakers, BS 1-9 and BS 9-10, both opened; however, BS 1-9 breaker failure protection circuitry actuated unexpectedly causing loss of Bus Section 1 which represents the loss of one source of off-site power to both Salem Units. This caused the loss of 4KV group buses 2F and 2G which caused the trip of 23 and 24 reactor coolant pumps, followed by an automatic reactor trip on low flow in two of four reactor coolant loops (> 10 % reactor power) at 2301 hours on 6/7/95.
311 | 3111997014 | 1997-10-02 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Salem 2 | P | WE | PO | 100 | On October 2, 1997 Salem Unit 2 was manually tripped from 100% power following the loss of both operating Steam Generator Feed Pumps (SGFP). The event was caused by a failed analog circuit card in the Westrac Data Acquisition System (DAS). The DAS is a temporary system that was connected to the Advanced Digital Feedwater Control System (ADFCS) to monitor ADFCS performance in support of modification acceptance testing. The component failure produced a false signal in the ADFCS representative of low feedwater header pressure. The differential between this signal and main steam header pressure is compared to a programmed differential pressure set point to determine SGFP speed. In response to this condition, SGFP speed increased, raising feedwater flow to 120% of the full flow value. This reduced SGFP suction pressure to the SGFP Low Suction Pressure trip setpoint, tripping both operating SGFPs. Operations personnel promptly responded to this condition by manually tripping the reactor. Following the event, the DAS was disconnected from the ADFCS.
311 | 3112001008 | 2001-12-31 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Salem 2 | P | WE | PO | 100 | On December 31, 2001, at approximately 0009 hours, with Salem Unit 2 operating at 100 percent power, an automatic reactor trip followed by a safety injection (SI) actuation occurred. Earlier, the Reactor Coolant System Pressurizer "low pressure/heaters on" alarm had annunciated and the operators observed Pressurizer pressure decreasing. The Pressurizer master controller called for no sprays and more heaters. Both spray valve controllers demanded closing. Spray valve 2PS1 indicated full closed (green light), but 2PS3 indicated mid-position (no red or green lights). The control room operator attempted to manually close the 2PS3 spray valve from the control console, but the valve failed to respond. The control room supervisor (CRS) directed the reactor operator to take the master controller to manual and attempt to close the valve, but the valve still did not respond. The CRS entered the abnormal operating procedure (AOP) for Pressurizer pressure malfunction and the operations superintendent recommended initiation of a manual reactor trip and stopping No. 23 reactor coolant pump (RCP). As the CRS was acknowledging the recommendation, the unit tripped on over-temperature delta-T (OTDT) followed shortly thereafter by a safety injection on low Pressurizer pressure signal. The cause of this event was the Pressurizer spray valve 2PS3 failing to an open position. The valve failed to this open position because of a broken position feedback linkage. The position feedback linkage was replaced on both Unit 2 Pressurizer spray valves and Unit 2 returned to service. This event is reportable in accordance with 10CFR50.73 (a)(2)(iv)(A).
311 | 3112003001 | 2003-03-29 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Salem 2 | P | WE | PO | 80 | A manual reactor trip was initiated at 0442 on March 29, 2003, with reactor power level at approximately 80%. The manual reactor trip was initiated in response to degradation of the normal plant heat sink when three of six Circulating Water (CW) pumps were emergency tripped due to loss of the CW traveling screens, with a fourth pump already out of service for condenser water box cleaning. All safety systems operated as designed following the reactor trip. The unit was stabilized in Mode 3 with the reactor at normal operating temperature and pressure with core cooling being provided by the auxiliary feedwater system and main steam dumps to the condenser. The cause of manual reactor trip is attributed to the inability of the Unit 2 Circulating Water (CW) system to handle the excessively high river debris (detritus, hydroids, trash, etc.) levels in the Delaware River due to the design capability of the CW traveling screens. The CW traveling screen shear pins were replaced, the condenser water boxes were cleaned and Operations procedures were reviewed and modified as appropriate to assist plant operators in actions to take during high detritus levels. An ongoing CW improvement project is developing CW traveling screen improvements to increase the reliability of the CW system. This report is being made in accordance with 1 OCFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the system listed in paragraph (a)(2)(iv)(B)."
311 | 3112004006 | 2004-07-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 100 | On Tuesday July 13, Salem Unit 2 tripped due to a malfunction of the 21BF19 valve, while Maintenance/l&C personnel were in the process of testing the Digital Feedwater System. Specifically, the Steam Generator Feed Pump differential pressure input to the feedwater system (PT508) was being tested in accordance with plant procedures. Initially, all the feedwater regulating valves (21-24BF19s) responded as expected. At approximately 1300 hours, the 21BF19 valve stopped responding. The Licensed Nuclear Control Operator placed the controller for the 21BF19 valve in manual and attempted to open the valve. The valve did not respond and the reactor automatically tripped on low steam generator level within approximately 45 seconds of the valve going to 31% open. The failure of the 21BF19 valve positioner (Bailey model number AV2320200) was due to the failure of the I/P that resulted in a sudden drop from 60% to 30% valve position. Some of the corrective actions taken were: (1) The 21BF19 positioner was replaced, (2) The digital feed QAM card was replaced, (3) The bezel control for the 21BF19 was removed and the contacts cleaned, and (4) An air operated valve diagnostic test was satisfactorily performed. This report is being made in accordance with10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
311 | 3112004007 | 2004-07-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 8 | On Thursday July 15, 2004, Salem Unit 2 was manually tripped while returning to power following the July 13, 2004 automatic reactor trip (LER 311/2004-006, dated September 13, 2004). During start-up, at approximately 8% power, feedwater flow was automatically transitioning from the feedwater bypass valve (BF40) to the main feedwater regulating valves (BF19). As the demand for the main feedwater regulating valves increased the demand for the BF40s decreased, as designed. However, the actual position of the number 23 loop main feedwater regulating valve (23BF19) did not move in response to the increasing demand. As the level in 23 Steam Generator continued to decrease due to the lack of response from 23BF19, the control room operator manually initiated a reactor trip with 23 Steam Generator level at approximately 16%. The failure of the valve was determined to be a positioner failure (Bailey model number AV2320200) due to sticking of the positioner pilot stem because of poor/ineffective vendor quality control allowing uneven surface finishing and dimensions that cause sticking of the positioner pilot stem. Some of the corrective actions taken were: (1) The 23BF19 positioner, as well as all Unit 2 feedwater regulating valves (21, 22, and 24BF19s), were replaced and calibrated under direction of the manufacturer, (2) The overshoot condition for the Unit 2 BF19s positioners was corrected prior to Unit restart, (3) A rollout was performed with appropriate PSEG personnel with specific recommendations to test each positioner pilot spool. Some longer term corrective actions being considered include: (1) Replacing the positioners with a different design and (2) Installing in line air filters (in parallel) at the redundant air panels for the BF19s. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
311 | 3112004008 | 2004-09-09 | QR5 | Turbine Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | On September 9, 2004 at 0106 hours Salem Unit 2 automatically tripped off line as a result of a Main Turbine Trip which initiated a Reactor Trip. The turbine tripped on Generator Differential and Loss of Field. All control rods fully inserted and all safety related systems were available and functioned as designed. The direct cause of this event was exciter brush/collector flash over. The root causes of this event were that the Generator/Exciter vendors recommended inspections were not implemented and the lessons learned from a 1993 Hope Creek brush failure were not applied to Salem Unit 2. (Salem Unit 1 is a different Generator/Exciter). Corrective actions taken include replacing the Salem Unit 2 exciter brushes, repair to the collector ring damaged in the brush failure event, incorporation of vend or recommended inspections and guidance into plant procedures. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B), specifically (B)(1)reactor trip.
311 | 3112006003 | 2006-09-26 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Salem 2 | P | WE | PO | 94 | On September 26, 2006 at 1513, with Salem Unit 2 in an end of cycle (EOC) coast down at 94% power, a manual reactor trip was performed due to elevated seal leak-off flows on 21 Reactor Coolant Pump (RCP). The 21 RCP number one seal leak-off flow exceeded the pump trip criteria of greater than 6 gpm. The reactor trip actions and plant recovery were performed without complications. A root cause team determined that the most probable cause is the combination of dissolved oxygen being introduced into a low boron and low lithium Reactor Coolant System which caused corrosion products to become dislodged from the system and deposited onto the RCP seals. Corrective actions are to improve procedures to better cope with EOC chemistry conditions. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
311 | 3112007002 | 2007-05-24 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Salem 2 | P | WE | PO | 100 | On May 24, 2007 at 0232, Salem Unit 2 tripped due to 22 Steam Generator (SG) low-low level. The cause of the low SG level trip was the failure of the 24 Demineralizer Vessel (DMV) upper sight glass, which resulted in a loss of condensate inventory and suction pressure and ultimately the trip of 21 Steam Generator Feedwater Pump (SGFP). The 21 SGFP trip resulted in a turbine runback signal and level decrease in the 22 SG. An automatic reactor trip occurred when 2 of 3 channels reached the low-low level set point on the 22 SG. The root cause for failure of the 24 DMV upper sight glass is attributed to the latent failure to control vendor documents pertaining to the installation and maintenance of these sight glass windows. Corrective actions included replacing all Unit 2 sight glass windows prior to placing the DMVs back into service and the replacement of Unit 1 sight glass windows as the DMVs were removed from service during routine operation. All DMV sight glasses have been replaced. This event is reportable in accordance with 10CFR50.73 (a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section."
311 | 3112007003 | 2007-08-06 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Salem 2 | P | WE | PO | 100 | On August 6, 2007, the Salem Unit 2 reactor tripped due to 22 Steam Generator water level reaching its low low level set point. The cause of steam generator low low level was a faulty Solid State Protection System (SSPS) output driver card A517 that initiated a spurious feedwater interlock signal and resulted in the closure of the feedwater regulating valves. It was determined that the failed circuit card was due to a defective solder joint. The root cause was attributed to inadequate post soldering test practices. The failed circuit card was replaced and the system tested satisfactorily. The test and inspection procedure for refurbished SSPS safety related circuit cards will be revised to include: (1) the use of soldering standards with inspections of both sides of the circuit card and (2) a manual test of the circuit card with agitation. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
311 | 3112008002 | 2008-05-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 25 | On May 9, 2008, Salem Unit 2 was at approximately 47% power and ramping up to 100% following its sixteenth (2R16) refueling outage. At 09:44 the Salem Unit 2 control room observed that there was no power to the circulating water traveling screens. A power reduction was initiated in accordance with operating procedures. Shortly following the removal of the main turbine from service, at approximately 25% power, control room personnel noticed the main feedwater regulating valve (23BF19) had swapped to manual and 23 Steam Generator level was increasing. With the regulating valve in manual control and level in the Steam Generator rising, the Unit 2 reactor was ordered tripped at 10:59. The cause for the 23BF19 swapping to manual shortly after the turbine trip was determined to be the result of the 23 Steam Generator steam flow input signals decreasing (spiking) to below the low sensor limit. The steam flow signal spike was caused by a pressure wave initiated from the main turbine stop valves closing as a result of the manually initiated turbine trip. Corrective actions included restoring power to the circulating water screens, and PSEG will revise the Unit 1 and 2 ADCFS low sensor limits (for DP transmitters) to consider the lowest possible output that can be experienced. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)...."
311 | 3112010001 | 2010-01-03 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Salem 2 | P | WE | PO | 80 | On January 3, 2010, at approximately 0804, a manual reactor trip was initiated with reactor power level at approximately 80%. The manual reactor trip was initiated in response to a degraded Circulating Water (CW) system and in accordance with operating procedures. The CW system degradation was due to heavy ice loading that affected the ability of CW traveling water screens (TWS) to operate, which resulted in the loss of four out of six CW pumps. The unit was returned to service on January 4, 2010, at 1831 after ice was cleared from the screens, condenser water boxes were cleaned and demonstrated to operate properly. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)
311 | 3112010002 | 2010-01-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 78 | On January 21, 2010, at 1818 hours, the 21 Steam Generator Feedwater Pump (SGFP) tripped. A turbine runback automatically initiated as expected and steam generator level in all four Steam Generators (SG) continued to lower. The 22 SG reached the SG low level reactor trip setpoint at 1820 hours resulting in an automatic reactor trip. All control rods fully inserted on the trip. All three Auxiliary Feedwater (AFW) pumps started in response to the low SG water level and decay heat was removed by the steam dumps to the main condenser. Operators entered the emergency procedures for the plant trip and stabilized the plant in Mode 3 (HOT STANDBY). The cause of the 21 SGFP trip was an internal wiring short in the SGFP trip control circuit that resulted in a false low suction pressure trip signal. The cause for the wiring short was the result of poor work practices. The reactor tripped on low water level in the 22 SG as designed. Corrective actions consist of lug inspections, document changes, training analysis, and evaluation of the integrated plant response to a SGFP trip from full power and implementing changes as appropriate. This report is made in accordance with 10CFR50.73 (a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
311 | 3112010003 | 2010-10-17 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Salem 2 | P | WE | PO | 100 | On October 17, 2010, at approximately 0512 hours, Salem Unit 2 automatically tripped due to bus undervoltage for the 21 through 24 Reactor Coolant Pumps (RCPs). The non-safety related group buses which power the RCPs were being fed from the Unit 2 Auxiliary Power Transformer (APT). The APT is directly powered from the Unit 2 main generator. At the time of the trip the main generator voltage regulator was in manual control and was being transferred to automatic control. During the voltage regulator transfer to automatic, a loss of excitation occurred. This loss of excitation led to the undervoltage condition on the group buses. The 22 through 24 RCPs tripped following the reactor trip when their respective breakers opened on undervoltage, the 21 RCP continued to run through the event. The 21 and 22 Auxiliary Feedwater (AFW) pumps started as a result of the trip of both main feedwater pumps. The 23 AFW pump started as a result of low steam generator levels in all four steam generators. Unit 2 was stabilized in Mode 3 with a reactor coolant temperature of 547°F and a reactor coolant pressure of 2235 psig. The cause of the automatic reactor trip was an undervoltage condition on the non-safety related group buses which power the RCPs. The undervoltage condition was the result of a loss of main generator excitation during the transfer of the voltage regulator from manual to automatic. Troubleshooting determined that loss of excitation was the result of a degraded 43A transfer relay that failed to transfer excitation control from the manual voltage regulator to the automatic voltage regulator. Corrective actions included replacement of the 43A transfer relay. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)...".
311 | 3112011004 | 2011-06-26 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Salem 2 | P | WE | PO | 100 | This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed paragraph (a)(2)(iv)(B)." At approximately 1800 hours on June 26, 2011, the 23 Reactor Coolant Pump (RCP) tripped resulting in an automatic reactor trip on low flow in one reactor coolant loop above the P-8 permissive (36% power permissive). As expected, the 21, 22 and 23 Auxiliary Feedwater (AFW) pumps started on low steam generator level following the unit trip. Unit 2 was stabilized in Mode 3 at normal operating temperature and pressure with the 21, 22 and 24 RCPs in-service. Salem Unit 2 tripped on low reactor coolant flow in the 23 reactor coolant loop. The low flow condition was the result of the trip of the 23 RCP due to two separate phase to ground faults. Both ground faults occurred at the termination to the motor where the cable shield interfaces with the stress tube of the termination kit. The insulation at this location was found to be brittle. Existing cable testing practices performed in accordance with industry standards would not detect this cable condition. Failure analysis determined that a partial discharge test or potentially destructive testing would have to be performed to detect the cable insulation degradation. The 23 RCP motor was tested satisfactorily. The damaged sections of the RCP motor leads were removed and new terminations were made. Megger testing and visual examination of the 21, 22, and 24 RCP motor leads was performed. The post maintenance testing procedure will be revised. The RCP motor feeder cables for the Unit 1 and 2 RCPs will be replaced.
311 | 3112012001 | 2012-03-23 | QR5 | Turbine Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | On March 23, 2012, at approximately 1428 hrs. Salem Unit 2 experienced an automatic reactor trip due to a turbine trip. The cause of the turbine trip was the spurious, simultaneous spiking of all three 103% overspeed inputs to the turbine Digital Electro Hydraulic Controller. At the time of the trip, the 22 Station Power Transformer was tagged out of service for maintenance. Upon unit trip and non-vital bus transfer from the Auxiliary to the Station Power Transformers, power to the F and G group buses was lost due to unavailability of the 22 Station Power Transformer. The 23 and 24 Reactor Coolant Pumps tripped as a result of the F and G busses being de-energized. This report is being made in accordance with 10CFR 50.73(a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)..."
311 | 3112012005 | 2012-11-25 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 92 | On November 25, 2012, Salem Unit 2 was in Mode 1 operating at 92% reactor thermal power. At approximately 1128 hours, operators received an Advanced Digital Feedwater Control System (ADFCS) trouble alarm and entered the abnormal operating procedure in response to indications of a lowering level in the 24 Steam Generator (SG){SJ}. The Reactor Operator (RO) took action to recover SG level by taking manual control of the 24 SG Feedwater Control Valve 24BF19 {SJ/LCV}, but was unsuccessful in recovering 24 SG level control. At 1130 hours while operators were proceeding to manually trip the reactor, an automatic reactor trip occurred due to a Lo Lo Level in the 24 SG. The cause of the trip was the failure of the 24BF19 valve due to debris inside the valve positioner current to pneumatic (I/P) converter. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A), for actuation of the Reactor Protection and Auxiliary Feedwater systems.
311 | 3112014002 | 2014-01-31 | QR6 | Manual Reactor Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | On January 31, 2014 at 0805, Salem Unit 2 experienced a partially dropped rod, identified as Control Bank D, Group B, Rod 1D2, while performing monthly rod surveillance testing. Rod 1D2 indicated 166 steps with the remainder of Control Bank D, Group B rods at 220 steps withdrawn. Operators entered Technical Specification (TS) 3.1.3.1, Action c. for the misaligned control rod, requiring a reduction in thermal power to less than 75 percent Rated Thermal Power (RTP) within one hour. A load reduction using boration and turbine load adjustments was commenced at 0812.<br /><br /> At 0904, at approximately 70 percent RTP, the plant entered the Action for TS 3.1.1.1, Shutdown Margin (SDM), which requires a continuous boration rate of equal to or greater than 33 gpm until the required SDM is restored. At approximately 20% RTP, the reactor was manually tripped due to a lack of available turbine load to continue to maintain Tave on program. All control rods inserted on the reactor trip. Corrective actions will be based on the cause of the rod 1D2 cable failure and possible enhancements to the SDM calculation procedure.<br /><br /> This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an "...event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)..."
311 | 3112015002 | 2015-08-05 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Salem 2 | P | WE | PO | 100 | On 8/05/15, at 1539, Salem Unit 2 experienced an automatic reactor trip. The cause of the reactor trip was due to a trip of the 21 Reactor Coolant Pump (RCP) causing a 21 Reactor Coolant Loop low flow condition. The 21 RCP breaker tripped as designed when the 2B Auxiliary Power Transformer (APT) infeed breaker to the 2H 4 kilovolt (kV) Non-Vital Bus opened. The root cause evaluation did not identify a definitive cause. However the most probable cause of the 2H 4 kV Non-Vital Bus trip was due to a ground fault on the 21 Heater Drain Pump (HDP) motor that was not isolated by its associated neutral overcurrent relay. An automatic start of the Auxiliary Feedwater (AFW) system occurred as expected following the reactor trip due to low steam generator water levels. <br /><br /> Corrective actions include replacement of the 21 HDP motor and its neutral overcurrent relay. <br /><br /> This event is reportable under 10 CFR 50.73 (a)(2)(iv)(A) as an event that resulted in an automatic actuation of the reactor protection system and actuation of the AFW system.
311 | 3112016002 | 2016-02-04 | QR5 | Turbine Trip | [45 empty] | Salem 2 | P | WE | PO | 74 | On 2/4/16 at 11:21, Salem Unit 2 automatically tripped from approximately 74% power. Power had been reduced at the beginning of dayshift to support a 500 KV transmission line outage. The reactor trip was due to a Main Turbine trip caused by a Main Generator Protection signal initiated by a main generator automatic voltage regulator (AVR) volts/hertz over excitation protection relay. All emergency core cooling systems and emergency safeguards feature systems functioned as expected. As found calibration data for the generator protection logic relay were found out of specification low. An evaluation determined the cause of the event to be that the organization failed to develop and implement corrective actions to resolve the previously identified cause of poor manufacturing/vendor quality identified in the causal evaluation following a similar Unit 1 trip on 12/21/2012 trip due to STV-1 relay setpoint drift. <br /><br /> This report is being made in accordance with 10 CFR 50.73 (a)(2)(iv)(A.), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," specifically automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System for this event.
311 | 3112016003 | 2016-02-14 | QR5 | Turbine Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | On 2/14/16 at 20:58 Salem Unit 2 automatically tripped from 100% power on Generator Protection. The trip was initiated due to a Main Turbine trip caused by a Main Generator Protection signal. All emergency core cooling systems and emergency safeguards feature systems functioned as expected. The motor driven and steam driven auxiliary feed pumps started as expected on steam generator low level. Operators stabilized the plant in Mode 3 with decay heat removal via the main steam dump valves and auxiliary feed water system. Condenser vacuum remained available for the duration of the event. Operators also ensured a normal offsite electrical power lineup. Investigation identified a Stator Water Cooling valve leak dripping onto a relay, shorting the relay wiring terminations. This caused the turbine generator trip. <br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the Reactor Protection System and the Auxiliary Feedwater System.
311 | 3112016005 | 2016-06-28 | QR5 | Turbine Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | On 6/28/16 at 04:22 Salem Unit 2 automatically tripped from 100% power on Generator Protection. The reactor trip was initiated due to a Main Turbine (MT) trip caused by a Main Generator Protection signal. All emergency core cooling systems and emergency safeguards feature systems functioned as expected. The motor driven and steam driven auxiliary feedwater pumps started as expected on steam generator low level. Operators stabilized the plant in Mode 3 with decay heat removal via the main steam dump valves and auxiliary feedwater system. <br /><br /> Investigation identified that a broken current transformer core ground wire internal to the A Main Power Transformer (MPT) was intermittently touching the X1 and X2 low voltage connections inside the transformer bushing compartment causing a ground fault. This caused the turbine generator trip. <br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the Reactor Protection System (RPS) and the Auxiliary Feedwater System (AF).
311 | 3112016006 | 2016-08-31 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Salem 2 | P | WE | PO | 100 | At approximately 1500 hours on August 31, 2016, the 21 Reactor Coolant Pump (RCP) tripped resulting in an automatic reactor trip on low flow in one reactor coolant loop above the P-8 permissive (36% power permissive). As expected, the 21, 22 and 23 Auxiliary Feedwater (AFW) pumps started on low steam generator level following the unit trip. Unit 2 was stabilized in Mode 3 at normal operating temperature and pressure with the 22, 23 and 24 RCPs in-service. <br /><br /> The trip of the 21 RCP was caused by a Service Water (SW) leak that developed on the 22 Containment Fan Coil Unit (CFCU) motor cooler. The SW leaked on to the 21 RCP motor lead containment penetration and the motor leads in the termination box. This caused the A and C phase instantaneous overload relays to actuate causing the trip of the RCP and the subsequent reactor trip on low flow in one reactor coolant loop.<br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the Reactor Protection System (RPS) and the Auxiliary Feedwater System (AF).
311 | 3112018001 | 2018-05-07 | QR6 | Manual Reactor Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | At 0325 on May 7, 2018 Salem Unit 2 experienced a manual reactor trip from approximately 90% power when 21 Reactor Coolant Pump (RCP) motor winding temperature reached the abnormal operating procedural limit of > 302 Degrees Fahrenheit requiring the RCP to be promptly removed from service. <br /><br /> As expected, the Auxiliary Feedwater (AFW) pumps started following the unit trip. Unit 2 was stabilized in Mode 3 at normal operating pressure and temperature with the 22, 23, and 24 RCPs in-service.<br /><br /> The cause of the adverse temperature trends of 21 RCP motor winding temperature was a high resistance termination contact, due to a loose connection, at the motor stator winding Resistance Temperature Detector (RTD) terminal point where field wires connect to the control room recorder.<br /><br /> This report is being made in accordance with 10CFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the Reactor Protection System (RPS) and the Auxiliary Feedwater System (AF).
311 | 3112018002 | 2018-09-14 | QP5 | Excessive Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 90 | On September 14, 2018 Salem Unit 2 tripped from 90 percent power when 23 steam generator water level reached the HI-HI setpoint. This caused a trip of the main turbine generator, both steam generator feedwater pumps and closure of feedwater isolation and control valves. The trip of the main turbine generator caused an automatic reactor trip. All systems functioned as expected and Unit 2 was stabilized in MODE 3 at normal operating pressure and temperature. <br /><br /> The cause of the high water level was failure of 23BF19 (steam generator water level control valve). 23BF19 fully opened when a positioner feedback arm failed due to cyclic fatigue due to vibration. The positioner feedback arm was replaced and the station returned to operation at a reduced power level that did not induce the vibration. The feedwater control valve or the feedwater control system will be modified to adjust system parameters to reduce vibration.<br /><br /> This event is reported per 10CFR50.73{a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," for this event actuation of the reactor protection system and the auxiliary feedwater system. Notification of this event was provided via ENS report 53606.
311 | 3112019001 | 2019-01-31 | QR6 | Manual Reactor Trip | [45 empty] | Salem 2 | P | WE | PO | 100 | On January 31, 2019 at 0301, Salem Unit 2 Reactor was manually tripped when four of six circulators were manually tripped on high traveling water screen differential pressures (DP) due to the accumulation of Frazil Ice on the traveling water screens. All systems functioned as expected and Unit 2 was stabilized in MODE 3 at normal operating pressure and temperature.<br /><br /> This event was reportable in accordance with 10CFR50.73(a)(2)(iv)(A). Notification of this event was provided via ENS report 53852.
311 | 3112019002 | 2019-08-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Salem 2 | P | WE | PO | 83 | At 0814 on 8/11/19, with Unit 2 at 83 percent power during a planned load reduction, the reactor was manually tripped due to degraded feedwater flow control to the 23 Steam Generator caused by a malfunction of the associated Feedwater Regulating Valve, 2313F19 All systems responded normally post-trip An actuation of the Auxiliary Feedwater system occurred following the manual reactor trip as expected due to low level in the steam generators. The unit was stabilized in Mode 3 <br /><br /> The failed equipment was repaired. <br /><br /> This event is reportable in accordance with 10 CFR 50 73(a)(2)(iv)(A).
312 | 3121988008 | 1988-05-04 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Rancho Seco | P | BW | PO | 28 | On May 4, 1988, at 09:25:35 hours during the performance of Special Test Procedure STP.660 "Integrated Control System Tuning At Power," the Control Room operators initiated a manual turbine trip from 28% power. Twenty-two seconds later, the reactor tripped automatically on high pressure. At 09:26:49 hours the Main Generator Output Circuit Breakers (OCBs) opened. The delay for the OCB trip was approximately 29 seconds beyond the normal 45-second duration. <br /><br />At 0928 hours the Control Room operators received initial indications of a leak within the containment. By 0934 hours Control Room operators determined that the "A" Letdown Cooler relief valve (PSV-22021) had lifted and not reseated. By 0940 hours Control Room operators had isolated "A" Letdown Cooler and terminated the leak. Based on an evaluation of the RCS leakage rate, the Shift Supervisor declared and terminated an Unusual Event at 0947 hours. The Shift Supervisor closed out the Unusual Event based on the earlier termination of the leak. <br /><br />An automatic actuation of the Reactor Protection System resulted in the unplanned reactor trip and is reportable under the requirements of 10 CFR Part 50.73(a)(2)(iv).
312 | 3121988015 | 1988-10-14 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Rancho Seco | P | BW | PO | 92 | At 0614 hours on October 14, 1988, while the plant was at 92% power, a transmission line phase to phase voltage imbalance fault caused the loss of two reactor coolant pumps. This caused the automatic actuation of the Reactor Protection System on power level to number of pumps running logic, tripping the reactor. This constitutes an automatic actuation of an Engineered Safety Feature. <br /><br />Concurrent with the reactor trip, the other two reactor coolant pumps tripped on phase imbalance and the Emergency Feedwater Initiation and Control System initiated auxiliary feedwater flow. This constitutes an automatic actuation of an Engineered Safety Feature. Natural circulation cooling was established and maintained until "D" reactor coolant pump was started at 0742 hours. By 0830 hours, all reactor coolant pumps were running and the plant was in the normal post trip window. <br /><br />At 0344 hours on October 15, 1988, almost simultaneous ground faults on incoming transmission lines caused a momentary degradation of electrical power at Rancho Seco. This caused two Safety Features Valves to close. This constitutes an automatic actuation of an Engineered Safety Feature. <br /><br />The actuations of the Engineered Safety Features are reportable pursuant to 10 CFR 50.73(a)(2)(iv). To prevent a reoccurrence of the October 14 trip, the phase to phase fault protection was extended past Stagg substation.
312 | 3121988018 | 1988-12-09 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Rancho Seco | P | BW | PO | 60 | On December 9, 1988, at 1826 hours, Rancho Seco tripped from 60% power due to high Reactor Coolant System (RCS) pressure. <br /><br />The specific condition to which the beginning of the event can be traced began at approximately 0940 hours when a Control Room Operator (CRO) placed the Integrated Control System (ICS) Diamond Control Panel into manual to allow for the calibration of Nuclear Instrumentation. <br /><br />After the calibration had been completed at 1820 hours, the CRO returned the ICS Diamond Panel to automatic. The CRO then observed an increase in feedwater demand and feedwater flow rate, and placed both feedwater loop master controls "in-hand" to manually decrease feedwater flow rate. The reduction in feedwater resulted in a high RCS pressure condition which automatically tripped the reactor. The CRO then took actions in accordance with Emergency Operating Procedure E.01 "Immediate Actions." <br /><br /> The direct cause of the reactor trip was a high RCS pressure condition caused by a main feedwater oscillation after the Diamond Station was transferred from manual to automatic. <br /><br />The root cause of the reactor trip was the failure of an ICS megawatt calibrating integral module due to a failed Field Effect Transistor. <br /><br />No adverse safety consequences resulted from this event.
312 | 3121988019 | 1988-12-12 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Rancho Seco | P | BW | PO | 12 | At approximately 1433 hours on December 12, 1988, Control Room operators manually tripped the reactor from 12% power. Operations personnel were manually controlling auxiliary steam header pressure because two pressure control valves had failed 4 hours earlier. During manual control, a loss of steam pressure to the 'B' main feedwater pump caused the loss of feedwater flow and subsequently caused the Once-Through Steam Generator (OTSG) level to drop to the Emergency Feedwater Initiation and Control (EFIC) low level initiation setpoint for 'B' auxiliary feedwater (AFW). Having observed the initiation of EFIC, Control Room operators followed Casualty Procedure C.10 "Loss of Steam Generator Feed" and tripped the plant. Operators observed the reactor cooldown outside the post-trip window and isolated the AFW supply to the 'B' OTSG in accordance with emergency procedures. This resulted in the 'B' OTSG boiling dry, terminating the reactor cooldown. <br /><br />At approximately 1500 hours, the operators restored AFW flow to the OTSG at a rate of 50 gpm. By 1530 hours, the 'B' OTSG pressure had returned to normal. <br /><br />There was no damage to plant equipment as a result of the valve failures involved and subsequent plant trip. There was no impact to the health or safety of the public due to this event.
312 | 3121989004 | 1989-03-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Rancho Seco | P | BW | PO | 93 | On March 28, 1989, at 1516 hours, while operating at 93% power, the plant's Main Feedwater Pumps (MFPs) experienced speed control problems. This resulted in a rapid loss of feedwater flow to the steam generators. The corresponding increase in Reactor Coolant System (RCS) pressure caused the plant to automatically shut down. <br /><br /> Because of the MFP controller problems, the Integrated Control System (ICS) response to the pre-trip underfeed caused the post-trip feedwater refeed to the RCS to be greater than expected. This resulted in a pressurizer level drop to the elevation of the level indicator tap. <br /><br /> The plant did not exit the post-trip window, and normal post-trip levels were established 14 minutes after the trip.
313 | 3131987004 | 1987-08-15 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Arkansas 1 | P | BW | PO | 12 | On 8/15/87 during power ascension operations at approximately 12 percent power, 'B' main feedwater (MFW) pump control was shifted from manual to automatic. Feedwater oscillations ensued resulting in the MFW pump turbine controls shifting to a 'track and hold' mode. 'B' MFW pump turbine speed unexpectedly decreased to a speed lower than that required to supply feedwater to the steam generators. Emergency feedwater (EFW) subsequently actuated on low steam generator water level. A reactor trip occurred due to high reactor coolant system pressure. After the trip, control of the 'B' MFW pump was regained and EFW was secured. Post trip plant response was satisfactory. The plant startup procedure was modified to provide guidance to plant operators to keep MFW pumps in manual control until at least 20 percent power before switching to automatic control. This provides for more stable operating conditions for transfer from manual to automatic. Troubleshooting revealed that the integrated control system (ICS) was supplying a negative voltage to the MFW pump turbine Lovejoy control system. This is believed to have caused the abnormal pump operation. A damaged chip in the 'track and hold' circuit was replaced and modifications to the ICS were made to prevent the input of a negative voltage to the MFW pump turbine control system.
313 | 3131987005 | 1987-08-25 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Arkansas 1 | P | BW | PO | 70 | With the unit operating at 70 percent power, one of two parallel generator output breakers was removed from service for maintenance. When the breaker was tripped during post maintenance testing, one of three phases failed to open. A phase discordant signal was produced due to the perceived fault resulting in a breaker failure lockout. A breaker failure module in the breaker circuitry should have been pulled prior to testing as the breaker was isolated from the switchyard. The module was not pulled due to personnel error. This caused other switchyard breakers to open, one of which was the other generator output breaker resulting in a load rejection. The breaker failure lockout also caused a turbine trip and reactor trip on loss of turbine anticipatory trip. Only one of the station 6900 volt busses accomplished a fast transfer to offsite power. The other busses performed a slow transfer. The slow transfer of the busses resulted in loss of both main feedwater pumps and subsequent actuation of emergency feedwater on low steam generator water level. Momentary engineered safeguard (ES) busses undervoltage due to the slow transfer caused the emergency diesel generators to start but not to tie on to the busses. The plant was stabilized at Hot Shutdown. Improved controls for switchyard maintenance activities and modifications to the breaker failure circuitry are being considered.
313 | 3131988003 | 1988-02-17 | QR3 | Reactivity Control Imbalance | [45 empty] | Arkansas 1 | P | BW | PO | 23 | During reactor protection system (RPS) monthly surveillance testing, Group 7 control rods dropped into the core. An automatic RPS reactor trip subsequently occurred on low reactor coolant system pressure. Following the trip, 'A' main feedwater (MFW) block valve CV-2625 failed to close and both MFW pumps minimum speed was observed to be slightly higher than expected. These conditions resulted in an overfeed of the 'A' once through steam generator (OTSG). When 'A' OTSG water level reached 100% on the operating range level instrumentation, the overfeed was terminated by manually actuating emergency feedwater (EFW) and tripping the MFW pumps. Primary and secondary system responses post-trip were near normal with the exception of 'A' OTSG water level. An unidentified malfunction of the power sequencing programmer for Group 7 coupled with the conditions existing during RPS testing caused the Group 7 drop. CV-2625 failed to close because of a failure in the valve operator drive clutch. Steam sources which are available in the post-trip mode versus the mode existing when the MFW pump minimum speeds were originally set caused the higher than expected MFW pump speed. The programmer for Group 7 was replaced. A temporary modification was installed and a drive clutch adjustment made to CV-2625. Further inspection and repair of the drive clutch assembly for CV-2625 will be performed at the next outage of sufficient duration. An evaluation will be performed to determine improvements which could be made in setting MFW pump minimum speeds for acceptable post-trip response.
313 | 3131989002 | 1989-01-20 | QR5 | Turbine Trip | [45 empty] | Arkansas 1 | P | BW | PO | 100 | On 1/20/89 a reactor trip occurred due to a failure in the main generator exciter. Following the trip, two reactor coolant pumps (RCPs) tripped on undervoltage when bus H1 failed to fast transfer to offsite power; the Main Feedwater (MFW) startup valves and low load control valves for both 'A' and 'B' MFW trains failed to close due to miswiring in the Integrated Control System; the 'B' MFW block valve failed to close due to an incorrect torque switch setting; MFW pump P1B failed to run back to the designed post-trip minimum speed due to an undetermined cause; and MFW pump P1A post-trip minimum speed was higher than designed minimum speed due to availability of steam from a Moisture Separator Reheater. The MFW system component failures caused an overfill of the 'B' once-through steam generator (SG). During the transient, operators initiated High Pressure Injection (HPI) to compensate for Reactor Coolant System (RCS) shrinkage caused by overcooling due to overfeeding the SGs. After securing HPI the combination of a partially failed open check valve and the RCP operating configuration allowed backleakage of reactor coolant into HPI system piping outside containment. During recovery from the transient, the Emergency Feedwater System automatically actuated on 'B' SG low level. A reactor building inspection following the trip revealed a small unisolatable leak in an RCS drain line and the unit was placed in cold shutdown. The component failures were corrected. Extensive reviews of the HPI system are being conducted to determine necessary corrective actions.
313 | 3131989018 | 1989-05-01 | QR5 | Turbine Trip | [45 empty] | Arkansas 1 | P | BW | PO | 50 | On May 1, 1989, the reactor tripped on a turbine trip caused by maintenance personnel inadvertently jarring a turbine control panel containing Mercoid switches for turbine trip functions. Maintenance personnel had gone inside the main turbine housing to replace an electro-hydraulic fluid filter for a turbine throttle valve. As personnel exited the work area by climbing down from a catwalk to the top of a ladder approximately five feet below, the control panel was being used as an intermediate stepping place without incident. However, at 1556 hours, the unit tripped when switches for the turbine solenoid trip function changed state as the panel was stepped on. Following the trip, Main Feedwater Pump P1B failed to run back to minimum speed due to control air pressure buildup in an isolated sensing line in the control system. Also, a Main Steam Safety Valve (MSSV) failed to completely reseat after lifting due to a missing cotter pin. The missing pin allowed a nut to vibrate down the valve stem while the valve was relieving steam, preventing the valve from fully closing. The turbine control panel has been labeled with a caution that it is a unit trip hazard. The isolated sensing line has been unisolated. The MSSV missing cotter pin was replaced and cotter pins were verified installed on the other MSSV.
313 | 3131989037 | 1989-11-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Arkansas 1 | P | BW | PO | 74 | On November 10, 1989 at approximately 2255, a reactor trip occurred as a result of the inadvertent grounding of a Reactor Protection System (RPS) power supply during surveillance testing. The grounding resulted in the loss of the RPS power supply and deenergized the reactor power auctioneering circuit for the Integrated Control System (ICS) which resulted in a reactor power/feedwater flow mismatch. The ICS automatic response to this mismatch was to reduce feedwater flow to the steam generators and to withdraw control rods. These actions resulted in a rise in Reactor Coolant System (RCS) temperature and pressure and a reactor trip at 2355 psig. The initial plant response following the trip was as expected, with all post trip parameters being normal. However, due to various steam leakage paths in the secondary system, the steam generator pressures gradually decayed to approximately 860 psig and RCS temperature decreased to 535 degrees. The cause of this event was an inadequate procedure which required connecting a test lead to a soldered connection in the back of the RPS cabinet. This connection was within one eighth inch of the connection which was inadvertently grounded. The RPS calibration procedure was revised to specify taking the required reading from a more suitable location. In addition, an evaluation was performed to identify and recommend appropriate corrective actions for long standing secondary system deficiencies.
313 | 3131989038 | 1989-11-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Arkansas 1 | P | BW | PO | 74 | On November 14, 1989 at approximately 2323, a reactor trip occurred as a result of the inadvertent closure of a main feedwater isolation valve. While attempting to close the suction isolation valve from the condensate storage tank to the steam driven emergency feed pump during MOVATS testing, a licensed plant operator inadvertently closed the main feedwater isolation valve for the "B" steam generator. This action caused the "B" main feedwater pump to trip on high discharge pressure and resulted in a reactor trip due to a high Reactor coolant System (RCS) pressure of 2355 psig. The initial plant response following the trip was normal. However, due to various steam leakage paths in the secondary system, steam generator pressures gradually decayed to 935 psig and 891 psig for the "A" and "B" generators respectively. RCS temperature decreased to 540.2 degrees. These values are slightly below those normally anticipated during post trip conditions. The root cause of this event was personnel error in that the operator failed to ensure that he was manipulating the correct valve. Disciplinary action was taken against the operator responsible for manipulating the wrong valve. In addition, a Secondary Systems Evaluation Team was formed to identify and recommend corrective actions for secondary system deficiencies. Significant deficiencies were corrected during mid cycle outage 1M89, which is presently in progress.
313 | 3131989048 | 1989-12-28 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Arkansas 1 | P | BW | PO | 42 | POWER LEVEL - 042%. ON 12/28/89, AT APPROXIMATELY 1529, AN AUTOMATIC REACTOR TRIP AND ACTUATION OF THE EMERGENCY FEEDWATER SYSTEM (EFW) OCCURRED AS A RESULT OF THE LOSS OF ALL MAIN FEEDWATER FLOW WHICH RESULTED FROM THE INADVERTENT TRIPPING OF A MAIN FEEDWATER PUMP (MFP). EARLIER IN THE DAY, THE 'A' MFP HAD TRIPPED ON OVERSPEED DUE TO A MALFUNCTION IN THE PUMP CONTROL CIRCUITRY. ANOTHER MALFUNCTION IN THE TRIP OIL SYSTEM HAD CAUSED AN 11 SECOND DELAY IN THE SENSING OF THE TRIP BY THE INTEGRATED CONTROL SYSTEM (ICS). AT THE TIME OF THE EVENT, TROUBLESHOOTING WAS IN PROGRESS TO DETERMINE THE CAUSE OF THE DELAY. OPERATIONS PERSONNEL HAD LATCHED, AND THEN TRIPPED THE 'A' MFP WITH NO OBSERVED DELAY IN TRIP INDICATION BY THE ICS. DURING THE PERFORMANCE OF A SECOND TEST, AN OPERATOR MISTAKENLY TRIPPED THE OPERATING MFP ('B'). THIS ACTION RESULTED IN A TOTAL LOSS OF FEEDWATER FLOW WHICH INITIATED AN AUTOMATIC REACTOR TRIP AND ACTUATION OF THE EFW SYSTEM. THE ENGINEERED SAFETY FEATURES ACTUATED, AS DESIGNED, AND PRIMARY AND SECONDARY PARAMETERS WERE MAINTAINED WITHIN ACCEPTABLE LIMITS. THE ROOT CAUSE OF THIS EVENT WAS DETERMINED TO BE PERSONNEL ERROR. DISCIPLINARY ACTION WAS TAKEN AGAINST THE OPERATOR WHO TRIPPED THE WRONG MFP. ADDITIONAL ACTIONS ARE ALSO BEING TAKEN TO MINIMIZE THE OCCURRENCE OF PERSONNEL ERRORS.
313 | 3131991001 | 1991-01-10 | QR5 | Turbine Trip | [45 empty] | Arkansas 1 | P | BW | PO | 100 | On January 10, 1991, at approximately 2326, with the plant at 100 percent of rated power, a reactor trip occurred as a result of the main turbine tripping due to loss of field excitation to the main generator. An anticipatory Reactor Protection System (RPS) trip was initiated, as designed, when the main turbine tripped while reactor power was greater than 43 percent. Plant response to the trip was as expected. Reactor Coolant System (RCS) pressure decreased to 1828 psig and was quickly recovered into the post trip window. Minimum post trip RCS temperature was 553 degrees. A temporary exciter was installed while the plant remained in the hot shutdown condition and the reactor was returned to power on January 17, 1991. The temporary exciter was replaced with a permanent exciter during mid cycle outage 1M91, which began on April 7, 1991. The cause of the exciter failure was inadequate cleanliness/material accountability controls. Strengthened controls were implemented during the permanent exciter installation.
313 | 3131991005 | 1991-05-21 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Arkansas 1 | P | BW | PO | 100 | On May 21, 1991, at approximately 0951, with the plant at 100 percent of rated power, an automatic anticipatory reactor trip on loss of main feedwater occurred when the circuit breaker supplying two cross-tied non-vital 480 volt load centers tripped on overload and de-energized the control oil pumps for both main feedwater pumps. Plant response to the trip was as expected. Water level was maintained in both steam generators by the emergency feedwater system. The load centers had been cross-tied to perform maintenance on one of the load center feeder breakers. The loading from both load centers exceeded the trip rating of one feeder breaker because the evolution was performed at power without first having shed the excess loads. The root cause of the event was inadequate procedural guidance contained in the electrical system normal operating procedure being used for the cross-tie evolution. The procedure has been revised to prevent recurrence. A contributing cause was insufficient review associated with the planning, scheduling, authorizing and performing of an infrequent and unusual evolution. Those personnel involved with this event have been counseled concerning their responsibilities.
313 | 3131993001 | 1993-03-05 | QR5 | Turbine Trip | [45 empty] | Arkansas 1 | P | BW | PO | 100 | On March 5, 1993, at approximately 1414, ANO-1 experienced a reactor trip which was initiated by the Anticipatory Reactor Trip System (ARTS) as a result of a main turbine trip. The plant post trip response was normal and no major equipment malfunctions were experienced. The reactor was returned to criticality at approximately 0726 on March 7, 1993 and the main turbine generator was tied to the grid at 0345 on March 8. The trip was determined to have been caused by the simultaneous occurrence of two grounds on the 125 VDC bus D-01. One of the grounds was on the Main Feedwater Pump control circuitry and the other was on the turbine trip circuitry. The two grounds created a short and resulted in actuation of the turbine trip circuitry, causing a turbine trip which initiated a reactor trip. The turbine trip circuitry ground was caused by vibration induced fretting where the wiring entered the cabinet. No grommet was installed in the cabinet. The cause of the MFP circuit ground is unknown. The grounds were repaired and grommets installed. Turbine trip circuit wiring subject to vibration in the HP turbine area was inspected for similar conditions.
313 | 3131994002 | 1994-04-11 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Arkansas 1 | P | BW | PO | 100 | On April 11, 1994, at approximately 2040, lightning struck in the vicinity of the ANO-1 Reactor Building causing a partial loss of power within channels 'B' and 'D' of t Emergency Feedwater Initiation and Control (EFIC) system. The power loss caused spurious trip of 'A' train of EFIC which initiated actuation of the Emergency Feedwater (EFW) system and automatic closure of Main Steam Isolation Valves (MSIVs). The Reactor Protection System initiated a reactor trip due to high Reactor Coolant System pressure s a consequence of the closure of the MSIVs at power. During the post-trip response, a slight overcooling condition occurred. This resulted from the power loss to channel 'B' EFIC which supplies the automatic control signal to train 'A' EFW flow control valves a 'B' steam generator atmospheric dump control valve. This caused the 'A' EFW flow control valves to remain fully open after the reactor trip, and the 'B' ADV control valve to fully upon loss of power, as designed. The operators terminated the overcooling event and returned the plant to normal post-trip parameters within eight minutes of the event. EFIC system power supplies were reset, other affected equipment was repaired, and various systems were demonstrated operable by surveillance. ANO-1 was returned to criticality at 0223 on April 15, 1994, and escalation to 100 percent power commenced.
313 | 3131995004 | 1995-04-03 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Arkansas 1 | P | BW | PO | 40 | On April 3, 1995, Arkansas Nuclear One Unit 1 was operating at 40 percent power while conducting testing following a refueling outage. Operations personnel in the control room noticed a rapid reduction in speed indication for the operating Main Feedwater pump (MFP) and a corresponding reduction in feedwater flow rate. Since the other MFP was out of service, the reactor was manually tripped at 1733 hours. Nine seconds after the trip, an automatic actuation of the Emergency Feedwater (EFW) system occurred due to low water level in the Once Through Steam Generators (OTSGs). Plant response to the transient was normal. EFW pumps maintained OTSG water levels until the plant was stabilized at Hot Shutdown conditions. The root cause of the MFP speed reduction was determined to be a human error by vendor personnel who incorrectly programmed a microcomputer as part of an upgrade to the MFP controls. The upgrade had been installed during the refueling outage. The programming errors were corrected and the MFPs performed without a recurrence of the problem during the subsequent power escalation testing.
313 | 3131995005 | 1995-04-20 | QR5 | Turbine Trip | [45 empty] | Arkansas 1 | P | BW | PO | 100 | On April 20, 1995, at approximately 0313, an automatic reactor trip was initiated by the Reactor Protection System as a result of a main turbine trip. The turbine trip was initiated by a generator lockout which was caused by a negative sequence relay (NSR) actuation. All control rods inserted into the core, as designed, and immediate operator actions were accomplished with no complications. The plant was safely taken to Hot Shutdown although some minor abnormalities occurred post-trip. Investigation into the cause of the trip identified a ground in the NSR circuitry which caused a current imbalance to the NSR which resulted in actuation of the relay. The most probable cause of the ground was vibration induced wear of wiring insulation inside an electrical junction box. The grounded wire was repaired and a rubber insulation mat was installed in the junction box to prevent vibration induced insulation wear. other similar junction boxes were examined and no additional discrepancies were identified
313 | 3131995009 | 1995-07-15 | QR5 | Turbine Trip | [45 empty] | Arkansas 1 | P | BW | PO | 100 | On July 15, 1995, at approximately 0818, an automatic reactor trip was initiated by the Reactor Protection System on high Reactor Coolant System pressure which resulted from the automatic closure of the main turbine governor and intercept valves by the turbine Electro Hydraulic Control (EHC) system. All control rods inserted into the core, as designed, and the post trip plant response was normal. Immediate operator actions were completed with no significant complications. The reactor trip occurred when one of the two main generator output circuit breakers was opened for maintenance. The EHC system sensed that both of the output circuit breakers were open due to a failed contact in the closed output circuit breaker which provides breaker position status to the system. The EHC system then shifted from the load control mode to the speed control mode and initiated closure of the governor and intercept valves (as designed). The ensuing transient resulted in the reactor trip. The root cause of the contact failure is indeterminate. A failure analysis will be conducted after the contact switch is repaired during the next refueling outage. Spare contacts were wired in parallel with all of the main generator output circuit breaker status contacts in the EHC logic circuit to prevent a single contact failure from giving a false breaker position indication. The reactor was returned to power and the unit was tied to the grid at 2112 on July 16, 1995.
313 | 3131996005 | 1996-05-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Arkansas 1 | P | BW | PO | 100 | ANO-1 experienced a reactor trip on high Reactor Coolant System (RCS) pressure. The pressure increase was caused by reduced Main Feed Water (MFW) flow originating from a component failure affecting controls of one of the operating MFW pumps. After the reactor trip, the other MFW pump tripped on high discharge pressure. Emergency Feed Water (EFW) automatically actuated. As expected, several Main Steam Safety Valves (MSSVs) opened following the reactor trip. One MSSV failed to re-seat. This led to the manual start of one High Pressure Injection pump because of reduced pressurizer level and manual actuation of Main Steam Line Isolation of the affected Once Through Steam Generator (OTSG). The MSSV failed to re-seat because inadequate engagement between the valve release nut and a cotter pin used to lock it in place allowed the nut to rotate and engage the manual lift top lever. Secondary water inventory of the affected OTSG was depleted via the open MSSV. Isolation of the OTSG, which provides the primary source of main turbine gland sealing steam, caused degradation of main condenser vacuum. RCS temperature control was maintained by the Atmospheric Dump System on the other OTSG. The open MSSV was gagged shut. Water inventory was restored by EFW. The first MFW pump control anomaly was caused by a drop in power supply voltage due to a shorted speed sensor. The failed speed sensor was replaced. Modifications were made to fuse the speed sensors and correct the cause of the second MFW pump trip. A modification was made to the MSSVs (other than the one gagged) to minimize the possibility of future inadequate pin engagement.
313 | 3131996007 | 1996-09-12 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Arkansas 1 | P | BW | PO | 100 | An automatic reactor trip was initiated when a non-vital 6.9 kV electrical bus providing power to two Reactor Coolant Pump (RCP) motors sensed an under voltage condition. A circuit breaker being racked down created vibration when its springs discharged causing the bus protection circuitry to open the RCP motor breakers. The root cause was a mechanical failure of a fuse in the bus protection circuitry. A defective solder joint between the element and end cap resulted in interruption of continuity. Following the trip, both trains of the Emergency Feedwater System actuated when water level in one Once Through Steam Generator reached the initiation setpoint. Level decrease was due to the associated main feedwater block valve not closing automatically because of a failed capacitor in the electrical clutch mechanism circuit. Because of the proximity to a scheduled refueling outage, the unit was not returned to power. A failure analysis of the defective fuse was performed by the fuse vendor. The defective fuse and the other one in the same fuse block were replaced. Repairs were completed for the main feedwater block valve and the redundant valve by replacing capacitors in the clutch control circuits.
313 | 3131998005 | 1998-12-25 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Arkansas 1 | P | BW | PO | 100 | On December 25 and 28, 1998, the reactor was manually tripped due to reduced Circulating Water (CW) System flow caused by unusually large build-up of fish, mostly threadfin shad, on the traveling screens. The cause of both events was the traveling screen system being unable to remove the existing volume of shad while maintaining acceptable screen differential pressure and CW flow. Following the first event, corrective actions were taken to increase fish removal capability and reduce CW flow rate during shad runs; however, another large shad run during the startup resulted in the second reactor trip. Additional actions to increase screen capacity and reliability were taken and the plant was successfully restored to full power. During both events, Reactor Coolant System parameter responses were normal and rod drop times were within limits. Emergency Feedwater was manually actuated during the first event as a contingency for potential loss of condenser vacuum. The condition of the traveling screens did not cause the safety-related Service Water System to be inoperable during either event. The necessity for additional long-term corrective actions is being evaluated.
313 | 3131998005 | 1998-12-28 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Arkansas 1 | P | BW | PO | 100 | On December 25 and 28, 1998, the reactor was manually tripped due to reduced Circulating Water (CW) System flow caused by unusually large build-up of fish, mostly threadfin shad, on the traveling screens. The cause of both events was the traveling screen system being unable to remove the existing volume of shad while maintaining acceptable screen differential pressure and CW flow. Following the first event, corrective actions were taken to increase fish removal capability and reduce CW flow rate during shad runs; however, another large shad run during the startup resulted in the second reactor trip. Additional actions to increase screen capacity and reliability were taken and the plant was successfully restored to full power. During both events, Reactor Coolant System parameter responses were normal and rod drop times were within limits. Emergency Feedwater was manually actuated during the first event as a contingency for potential loss of condenser vacuum. The condition of the traveling screens did not cause the safety-related Service Water System to be inoperable during either event. The necessity for additional long-term corrective actions is being evaluated.
313 | 3132000004 | 2000-03-14 | QR6 | Manual Reactor Trip | [45 empty] | Arkansas 1 | P | BW | PO | 82 | On March 14, 2000, at approximately 0005, the reactor was manually tripped following a component failure in the main turbine electro-hydraulic control system. During plant startup, the main turbine steam supply valve position limits were set at 100 percent to allow full travel of the valves. When reactor power reached 82 percent during power escalation, the turbine operator identified an alarm on the plant computer alarm display indicating that the valve position limit was slightly greater than 100 percent. The operator attempted to clear the alarm by depressing the "lower" pushbutton on the panel. The third time the pushbutton was depressed, the valve position limit decreased and continued to rapidly decrease after the button was released. The decreasing valve position limit caused the main turbine steam supply valves to rapidly close and the main steam safety valves began lifting. The reactor was manually tripped and all control rods inserted into the core well within their expected drop times. The cause of this event was determined to be a stuck contact on the valve position limit pushbutton. The switch was replaced prior to plant startup.
313 | 3132001001 | 2001-01-05 | QR6 | Manual Reactor Trip | [45 empty] | Arkansas 1 | P | BW | PO | 72 | On January 5, 2001, at approximately 0848, the reactor was manually tripped due to excessive hydrogen leakage from the main generator. A small hydrogen leak was detected at approximately 0445 on January 4, 2001, and a small increase in the leak rate was noted that night. A significant change in leakage occurred at approximately 0830 on January 5, 2001, and a rapid plant shutdown in accordance with pre-planned contingency plans was initiated. During the power reduction operators near the generator reported that significant leakage and loss of hydrogen was occurring. The reactor was then manually tripped to allow a rapid depressurization of the generator via the vent pathway to the turbine building roof. All control rods inserted into the core well within the expected drop time. The post trip plant response was normal and the plant was placed in a stable hot shutdown condition. The cause of the leak was a failed pipe support in the main generator hydrogen cooling system that allowed excessive vibration and ultimate failure of a vent pipe. Following completion of corrective actions the reactor was restarted and tied to the grid at 1853 on January 7, 2001.
313 | 3132001004 | 2001-07-24 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Arkansas 1 | P | BW | PO | 100 | An automatic reactor trip occurred on high Reactor Coolant System pressure due to rapid closure of the Turbine Generator governor valves. All control rods fully inserted and no Engineered Safety Features actuations occurred. The root cause was determined to be failure of a chip in the reference up-down counter card in the Electro-Hydraulic Control (EHC) System. Another card in the EHC System was also found to have failed. A common failure mode could not be identified. The unit returned to power operation after the cards were replaced. An EHC reliability study is being conducted to determine the need for system upgrades and improved maintenance strategies. This event had minimal safety significance. There have been no previous similar events reported by Arkansas Nuclear One as Licensee Event Reports.
313 | 3132002002 | 2002-10-04 | QR5 | Turbine Trip | [45 empty] | Arkansas 1 | P | BW | PO | 42 | While performing the Main Turbine Overspeed Trip Test with reactor power approximately 42 percent, an automatic actuation of the Reactor Protection System (RPS) occurred. Upon completion of the Overspeed Trip Test, the trip/latch lever failed to fully reset and latch, thereby preventing restoration of the Auto Stop Oil System pressure. When the test lever was released, the turbine tripped resulting in a reactor trip. Plant response to the trip was normal and uncomplicated. The plant was stabilized in hot standby conditions. The direct cause for the Auto Stop Oil System pressure failing to be restored was determined to be binding of the mechanical trip spool valve in a partially tripped condition due to the buildup of corrosion particles and oil-based residue on the spool valve surfaces. The Auto Stop Oil System and the mechanical trip spool valve and associated components were inspected and cleaned or repaired as necessary. Preventive maintenance tasks will be developed requiring routine inspections and flushing of the Auto Stop Oil System. The event was determined to have had minimal safety significance.
313 | 3132003001 | 2003-08-29 | QR5 | Turbine Trip | [45 empty] | Arkansas 1 | P | BW | PO | 100 | At 1428 CDT on August 29, 2003, ANO-1 experienced an automatic actuation of the Reactor Protection System due to high Reactor Coolant System (RCS) pressure. The RCS high pressure condition was caused by the inadvertent closure of the main turbine governor valves due to a lightning-induced Electro Hydraulic Control (EHC) System malfunction. Following the trip, the main generator output breakers failed to open automatically due to the failure of both the primary and secondary reverse power relays to trip. The output breakers were manually opened approximately 1.5 minutes after the reactor trip. Main Feedwater Block Valve CV-2675 to the ''B" Once-Through Steam Generator failed to fully close resulting in erratic control of feedwater flow to the steam generator. The Emergency Feedwater Initiation and Control System actuated as expected and initiated emergency feedwater flow to the affected steam generator. Failure of CV-2675 to close was due to a failed rectifier that supplies DC voltage to the valve's clutches. The damaged and failed components were replaced and the main feedwater block valve and main generator output breakers were tested to verify operability. The EHC System and its power supplies were tested and found to be satisfactory. Improvements to the EHC System to provide isolation for the interlock circuit for the main generator output breakers are being developed.
313 | 3132005003 | 2005-12-26 | QR5 | Turbine Trip | [45 empty] | Arkansas 1 | P | BW | PO | 95 | At 1047 CST, on December 26, 2005, Arkansas Nuclear One, Unit 1 (ANO-1), experienced an automatic actuation of the Reactor Protection System due to a Main Turbine trip caused by low turbine bearing lube oil pressure. The Reactor Protection System performed as designed resulting in a reactor trip from 95 percent power. Analysis of the event has determined that the reduction in turbine bearing lube oil pressure was caused by a failure of the lube oil ejector discharge check valve, LO-79. Subsequent analysis established that a weld failure within the valve internals had caused the disc to separate from the hinge resulting in blockage of lube oil flow. Examination of the failed welds indicated that they were undersized for the applied load. To correct this condition, a replacement valve assembly, meeting original equipment manufacturer design requirements, was installed. Following the reactor trip, a spurious actuation of Emergency Feedwater (EFW) occurred which was caused by an invalid low steam generator level signal generated by the Emergency Feedwater Initiation and Control system. To reduce the likelihood of recurrence of an invalid EFW actuation, a Technical Specification amendment was prepared and implemented upon NRC approval, allowing a reduction of the EFW low steam generator level initiation setpoint and an increase in the low level actuation time delay.
313 | 3132008001 | 2008-12-12 | QR6 | Manual Reactor Trip | [45 empty] | Arkansas 1 | P | BW | PO | 32 | At 0855 CST, on December 12, 2008, and again at 1212 CST, on December 20, 2008, Arkansas Nuclear One, Unit-1, initiated a manual plant trip from power in accordance with plant procedures in response to receipt of asymmetric rod alarms and recognition of abnormal control rod group 7 movements. The Control Rod Drive Control System (CRDCS) was in automatic at the time of each occurrence. Post trip responses were normal with all plant systems functioning as expected and with no safety system actuations. Testing and analysis determined that the probable root cause was degradation of two of the Automatic Bus Transfer (ABT) relays as the result of inadequate preventive maintenance. The two subject ABT relays were replaced as well as the programmer for the Group 7 Control Rods which was identified as single point failure vulnerable. In addition to the immediate actions to replace the above components, actions have been initiated to evaluate and upgrade the preventive maintenance associated with the CRDCS. Additional online monitoring requirements were implemented to obtain diagnostic information and enhanced inspection requirements were implemented for the CRD programmers. Both occurrences were reported to the NRC Operations center pursuant to 10CFR50.72 reporting requirements.
313 | 3132008001 | 2008-12-20 | QR6 | Manual Reactor Trip | [45 empty] | Arkansas 1 | P | BW | PO | 100 | At 0855 CST, on December 12, 2008, and again at 1212 CST, on December 20, 2008, Arkansas Nuclear One, Unit-1, initiated a manual plant trip from power in accordance with plant procedures in response to receipt of asymmetric rod alarms and recognition of abnormal control rod group 7 movements. The Control Rod Drive Control System (CRDCS) was in automatic at the time of each occurrence. Post trip responses were normal with all plant systems functioning as expected and with no safety system actuations. Testing and analysis determined that the probable root cause was degradation of two of the Automatic Bus Transfer (ABT) relays as the result of inadequate preventive maintenance. The two subject ABT relays were replaced as well as the programmer for the Group 7 Control Rods which was identified as single point failure vulnerable. In addition to the immediate actions to replace the above components, actions have been initiated to evaluate and upgrade the preventive maintenance associated with the CRDCS. Additional online monitoring requirements were implemented to obtain diagnostic information and enhanced inspection requirements were implemented for the CRD programmers. Both occurrences were reported to the NRC Operations center pursuant to 10CFR50.72 reporting requirements.
313 | 3132009001 | 2009-02-05 | QR6 | Manual Reactor Trip | [45 empty] | Arkansas 1 | P | BW | PO | 61 | On Thursday, February 5, 2009, at approximately 1524 CST, Arkansas Nuclear One, Unit 1 was manually tripped from 61 percent power due to increasing temperatures of the Control Rod Drive (CRD) Motors resulting from a loss of CRD cooling water flow. The CRD Motors share cooling water flow from the Non-Nuclear Intermediate Cooling Water (ICW) system with Service Air Compressors and other non-nuclear loads. A failed head gasket on the C-3A Service Air Compressor resulted in the introduction of large quantities of air into the ICW system which resulted in cavitation of P-33A ICW pump and both P-79A and P-79B CRD Motor cooling pumps. This loss of CRD cooling flow caused CRD temperatures to approach 180F which is the reactor trip criteria for OP-1203.003, CRD Malfunction Actions procedure. Post trip responses were normal with all plant systems functioning as expected and with no safety system actuations. The ICW supply and return lines to the Service Air Compressors were isolated restoring ICW and CRD Motor cooling flow. An alternate source of Service Air was provided, and the unit was returned to power on February 6, 2009, at 2219 CST. The root causes of this event were inadequate original design and inadequate maintenance instruction. Corrective actions include providing an alternate source of Service Air, evaluating the equipment for upgrade, and evaluating similar equipment for the same failure scenario.
313 | 3132009002 | 2009-02-07 | QR6 | Manual Reactor Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Arkansas 1 | P | BW | PO | 90 | On February 7, 2009, at approximately 1046 CST, the reactor was manually tripped from 90 percent power in response to a report of a fire at the main generator hydrogen addition station. Prior to the occurrence of the fire, Operations personnel were preparing to add hydrogen to the main generator. The Inside Auxiliary Operator (IAO) who was to perform the task conducted a pre job brief with the Shift Technical Advisor, who was also a qualified Shift Manager. The IAO then proceeded to the hydrogen addition station to perform the task. The procedure requires that the hydrogen station to generator inlet isolation valve, which is a normally open valve, be verified open. The IAO first attempted to open the valve with no success, then unsuccessfully attempted to close the valve. Assuming the valve was stuck on its closed seat; the operator obtained a pipe wrench and proceeded to rotate the valve handle in the open direction. Suddenly, the bonnet, hand wheel, and valve internals assembly ejected from the valve body, releasing hydrogen under pressure to the atmosphere. The operator immediately exited the area and the hydrogen quickly ignited. Operations personnel expeditiously initiated action to isolate the hydrogen leak. As a conservative action, the reactor was manually tripped at 1046 CST. The cause of this event was personnel error. The involved individual will receive remedial training and go through a requalification process.
313 | 3132010003 | 2010-04-18 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | Arkansas 1 | P | BW | PO | 11 | On April 18, 2010, Arkansas Nuclear One-Unit 1 (ANO-1) was operating at approximately 11 percent Reactor power, nearing the completion of the twenty-second refueling outage, and preparing to connect the Main Generator to the Electrical Grid (Grid). The ANO-1 Operating Staff entered the Reactor Coolant Pump Abnormal Operating Procedure at 1346 Central Daylight Time (CDT) due to indications of a degraded third stage seal on a Reactor Coolant Pump (P-32C). The cause of the P-32C seal failure was later determined to be an inadequate tolerance between the pump coupling slinger ring and stand pipe splash shield. At 1356 CDT, an Operator stationed at the Main Turbine reported smoke and small flames at Main Turbine Governor Valve 3 (GV3). An electro-hydraulic control (EHC) fluid leak that had previously been repaired during the outage resulted in EHC fluid entrainment in the calcium silicate piping insulation at GV3, promoting an exothermic reaction between the EHC fluid and the insulation when exposed to operating temperatures. The Operating Staff manually tripped the Main Turbine and conservatively performed a manual Reactor scram at 1357 CDT. A local CO2 fire extinguisher was used to extinguish the small flames at GV3 immediately following detection by the Operator stationed at the valve. MODE 5 conditions were established, and after repairs to the Main Turbine insulation and P-32C seal replacement, ANO-1 was connected to the Grid at 1918 CDT on April 25, 2010.
313 | 3132010004 | 2010-04-25 | QR8 | Spurious Reactor Trip | [45 empty] | Arkansas 1 | P | BW | PO | 19 | On April 25, 2010, at approximately 2126 Central Daylight Time (CDT), with the plant operating at ~19.5% heat balance power following a refueling outage (1R22), a Reactor Protection System (RPS) actuation during Nuclear Instrument (NI) calibration resulted in a reactor trip at Arkansas Nuclear One, Unit 1. During performance of the NI calibration, a large neutron error signal developed resulting in a mismatch between selected power and indicated power which resulted in Group 7 control rods withdrawing for 38 seconds. The rod withdrawal initiated an RPS trip on 2 of the 4 channels, resulting in an automatic reactor trip. The failure to appropriately use and adhere to procedures was determined to be the major factor in this event. Procedure steps were not performed as written and not read verbatim to the operator as required by procedure guidance. As a result, immediate stand-downs with involved departments were conducted and additional control room oversight was established.
313 | 3132013001 | 2013-03-31 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [7 empty] | X | [25 empty] | X | [11 empty] | Arkansas 1 | P | BW | PO | 100 | On March 31, 2013, at approximately 0750 CDT, during lifting and removal of the Arkansas Nuclear One Unit 1 (ANO-1) original Main Generator Stator (Stator), the temporary lift assembly collapsed due to failure of one of the structural columns, resulting in the Stator falling onto the turbine deck (386' elevation) and rolling down into the ANO-1 train bay (354' elevation) adjacent to Arkansas Nuclear One Unit 2 (ANO-2). The event resulted in one fatality, multiple injuries, structural damage to the ANO-1 and ANO-2 turbine buildings, and damage to non-vital systems and electrical equipment. At the time of the event, ANO-1 was in MODE 6 and ANO-2 was in MODE 1 at approximately 100 percent power. The event resulted in a loss of offsite power for ANO-1, with both Emergency Diesel Generators (EDGs) starting to supply safety loads. ANO-1 decay heat removal was lost for approximately four minutes. ANO-2 automatically tripped off-line after the vibration from the dropped Stator resulted in the actuation of relays in the ANO-2 switchgear located adjacent to the train bay, subsequently tripping a reactor coolant pump motor breaker. After the reactor trip, emergency feedwater was manually initiated by ANO-2 Control Room Operators. As debris fell into the train bay, an 8-inch firewater pipe was ruptured and the Alternate AC Diesel Generator electrical tie to ANO-1 was severed. At 0923 CDT that same day, water intrusion from the ruptured firewater piping into a 4160 volt breaker resulted in an ANO-2 Startup Transformer lockout, de-energizing a safety bus. An EDG automatically started as designed and supplied the affected safety bus. An ANO-2 Notification of Unusual Event was declared at 1033 CDT due to fire or explosion from an electrical fault in the 4160 volt switchgear with indications of bus damage. After damage assessment and repairs, ANO-2 returned to power operation on April 28, 2013. ANO-1 returned to power operation on August 7, 2013.
313 | 3132015001 | 2015-12-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Arkansas 1 | P | BW | PO | 100 | On December 15, 2015, at approximately 0544, Arkansas Nuclear One, Unit 1 (ANO-1), manually scrammed during a scheduled automatic down power to 35% power for planned maintenance. The Integrated Control System (ICS) (JB) was being utilized for the down power. During the down power, oscillations occurred in the Main Feedwater (MFW) (SJ) system. The ICS was placed in manual and efforts were made to dampen the MFW oscillations. The Operators manually tripped the reactor from approximately 43% power when it became evident that an automatic reactor trip was imminent, based on the observed Reactor Coolant System (RCS) (AB) pressure rise caused by the significant reduction in MFW flow.<br /><br /> The direct cause of the manual plant trip is currently considered a result of placing the "B" startup valve in HAND (manual) when the valve was -36% open, which resulted in a significant underfeed condition of the "B" Once-Through Steam Generator (OTSG). There are currently two root causes considered for this condition: (1) inadequate maintenance practices applied to the ICS modules, and (2) inadequate procedural guidance to address ICS malfunctions.
313 | 3132017001 | 2017-04-26 | C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) |  |  | X | [13 empty] | X | [28 empty] | Arkansas 1 | P | BW | PO | 100 | On April 26, 2017, Arkansas Nuclear One, Unit 1 (ANO-1), was operating normally at 100% rated thermal power. The 500kV transmission line to the substation at Pleasant Hill, Arkansas was out of service for planned maintenance. The area around the plant was experiencing severe weather from thunderstorms and tornado warnings had been issued from the National Weather Service for the four county area. <br /><br /> At approximately 1002 CST switchyard breakers for 500kV lines opened on fault current. High winds had damaged the transmission towers approximately 16 miles away from ANO and caused phase to ground faults. This resulted in a loss of all offsite power lines to the 500kV bus. The autotransformer also locked out as designed when the 500kV transmission lines faulted. <br /><br /> The Reactor Operator initiated a manual reactor trip about 8 seconds after the 500kV lines tripped and prior to the reactor protection system initiating an automatic trip. During this time both emergency diesel generators (EDGs) [EK] started as expected. EDG #2 re-energized one Engineered Safeguards bus. EDG #1 ran unloaded until shutdown. <br /><br /> The plant was stabilized in Mode 3 with Emergency Feedwater (EFW) pumps supplying the steam generators, maintaining the water level at the natural circulation setpoint.
313 | 3132018001 | 2018-05-16 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Arkansas 1 | P | BW | PO | 10 | During the Arkansas Nuclear One, Unit 1 (ANO-1) startup from refueling outage 1R27 at ~1750 CDT on May 16, 2018, the reactor experienced an automatic reactor trip from approximately 10 percent power due to a Reactor Protection System (RPS) trip from a loss of main feedwater as a result of a trip of the “B” Main Feedwater Pump (MFP) due to operator error. The “A” MFP was not in operation at the time. The ANO-1 Control Room was in the process of raising reactor power to a band of 12 – 15% when the MFP tripped on high discharge pressure. <br /><br /> The MFP trip resulted in a RPS actuation (reactor trip) followed by an Emergency Feedwater actuation. All control rods inserted into the core and the reactor was verified shutdown.
313 | 3132018003 | 2018-06-16 | QR6 | Manual Reactor Trip | [45 empty] | Arkansas 1 | P | BW | SU | 2 | On June 16, 2018, Arkansas Nuclear One, Unit 1 (ANO-1), performed a manual reactor trip due to a Turbine Bypass Valve (TBV) failing open during reactor startup. The copper instrument tubing, which connects the positioner output to the top of the TBV cylinder booster, was found broken at the tubing ferrule. The instrument tubing failure was determined to be due to high cycle fatigue and vibration. The root cause of this event was determined to be the instrument air copper tubing had less than adequate robustness for the TBV system high vibration application. Corrective actions include replacement of the tubing and fittings with stainless steel and flex-lines for the four ANO-1 TBVs during the next scheduling refueling outage. <br /><br /> This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission on June 16, 2018 via Event Notification 53459.
313 | 3132018004 | 2018-12-18 | C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) |  |  | X | [13 empty] | X | [28 empty] | Arkansas 1 | P | BW | PO | 100 | On December 18, 2018, Baker testing of the Arkansas Nuclear One, Unit 1, Main Chiller motor was being performed. Unit 1 was operating at 100%. Baker motor testing is completed to gather performance monitoring data on various motors. The testing is intended for use in detection of motor health, input power, and other dynamic electrical problems with electric motors.<br /><br /> At approximately 1120 on December 18, 2018, during restoration from the subject testing, an electrical arc was observed. The arc was observed upon the removal of the third voltage test clip from a non-vital 4160 volt (V) bus. The arc caused the two fuses in one of the electrical phases to open in order to protect the bus Control Power Transformer. The loss of the control power circuit resulted in the 4160V feed from the unit Auxiliary Transformer opening, causing the 4160V bus to de-energize. The Startup Transformer feeder breaker to the 4160V bus did not automatically close upon loss of 4160V bus voltage because its closing logic was not satisfied. The loss of the 4160V bus resulted in load shedding of the respective buses, automatic start and connection of the associated Emergency Diesel Generator to the respective vital 4160 bus, and a subsequent plant transient. The direct cause of the event was determined to be an electrical arc event when removing the test leads due to the close proximity of the test lead to ground. <br /><br /> The plant transient lead to a reactor trip on high Reactor Coolant System pressure following the loss of one of the two operating Main Feedwater pumps. After the reactor trip, the unit was stabilized in Mode 3 with feedwater being supplied to the Steam Generators by the unit Auxiliary Feedwater pump.
313 | 3132021001 | 2021-03-14 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Arkansas 1 | P | BW | PO | 100 | On March 14, 2021 at 1315 Central Daylight Time (CDT), Arkansas Nuclear One, Unit 1 (ANO-1) was manually tripped due to an indicated degraded voltage and momentary loss of the non-vital 4160VAC bus A-2. Degraded voltage of the non-vital 4160VAC bus A-2 resulted in de-energizing the vital 4160VAC bus A-4. All systems responded as designed and the plant was stabilized in MODE 3 (Hot Standby). <br /><br /> The cause of this event was a bent primary moveable contact in the 4160VAC Non-Vital bus A-2 Potential Transformer (PT) drawer. The damage to the primary moveable contact was corrected and repaired. <br /><br /> The most likely cause was the ANO-1 Stator Drop accident in 2013 and subsequent repair of the 4160VAC Non-Vital bus A-2. <br /><br /> There were no consequences to the general safety of the public, nuclear safety, industrial safety or radiological safety. No radiological releases occurred due to this event.
313 | 3132021002 | 2021-11-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Arkansas 1 | P | BW | PO | 100 | On November 29, 2021, at 1458 Central Standard Time (CST), while operating in Mode 1 at 100% power, Arkansas Nuclear One, Unit 1, (ANO-1) automatically tripped due to high Reactor Coolant System pressure following a Main Feedwater System transient. All control rods fully inserted and all systems responded as designed. The plant was stabilized in Mode 3 (Hot Standby). <br /><br /> The cause of the Main Feedwater System transient was the failure of the ‘A’ MFP High Pressure (HP) governor to respond to lowering ‘A’ MFP speed. The initiating event was a failure of the ‘A’ MFP LP governor servo drive and actuator. When the LP governor servo drive failed, the HP governor did not respond to restore ‘A’ MFP speed. Proper program values had not been input in the HP governor controller during previous maintenance in 2015. The HP governor failure to respond resulted in underfeeding the ‘A’ Steam Generator and an automatic reactor trip due to high Reactor Coolant System pressure.
315 | 3151987008 | 1987-06-04 | QP5 | Excessive Feedwater Flow | [45 empty] | Cook 1 | P | WE | PO | 90 | On June 4, 1987, at 1034 hours, an ESF actuation (turbine/reactor trip) occurred due to an extreme high level in Steam Generator number 12. The level transient occurred during the performance of a test procedure. During the execution of the test, an operator was directed to place the automatic/manual level controller in the manual position, then transfer the steam flow and feedwater flow selector switches from the Channel I position to the Channel II position. Once transferred, the level controller can be placed in the automatic position and testing can commence on Channel I. <br /><br />The cause of the event was the mispositioning of both the level controller (due to malfunction) and the feedwater flow selector switch (due to misleading switch position labeling). This resulted in an increase in feedwater pump speed, the automatic opening of the Steam Generator number 12 feedwater flow control valve and subsequent extreme high Steam Generator level. <br /><br />The level controller was removed, inspected, refurbished and determined to be operable. The escutcheon plate on the feedwater flow selector switch has been relabeled to identify the correct position. In addition, a memo was issued to all operators describing lessons learned from this event.
315 | 3151987021 | 1987-10-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 1 | P | WE | PO | 69 | On October 13, 1987, at 0818 hours, an Engineered Safety Features actuation (Reactor Trip) occurred due to a feedwater flow/steam flow mismatch coincident with low level on steam generator number 11. <br /><br /> At approximately 0817 hours, a licensed operator removed the east main feedwater pump alternating current auxiliary oil pump from service as directed by procedure. The shaft driven oil pump failed to maintain control oil pressure as expected. This resulted in a main feedwater system transient which culminated in the reactor trip. <br /><br />Post-event evaluation identified no component failure, other than the shaft-driven oil pump, which significantly affected the event. The east main feedwater pump shaft driven oil pump was found to be damaged. It was repaired and the feedwater pump was returned to service.
315 | 3151988001 | 1988-01-13 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Cook 1 | P | WE | PO | 90 | On January 13, 1988, at 0821 hours, Unit One experienced an Engineered Safety Features Actuation (Reactor Trip) as a result of the inadvertant opening of the Train B Reactor Trip Breaker. At the time of this event the Unit was operating in Mode 1 (Power Operation) at 90 percent rated thermal power. <br /><br />This event was the result of cognitive personnel error on the part of the licensed operator involved, who attempted to manipulate the Train B Reactor Trip Breaker instead of Reactor Trip Bypass Breaker B during the monthly Solid State Protection System (SSPS) surveillance. <br /><br />Following the reactor trip all actions and verifications required by the facility emergency operating procedures were complied with and the Unit was stabilized in Mode 3 (Hot Standby). <br /><br />Administrative controls have been established to ensure proper equipment configurations and adequate job briefings during surveillance testing. Procedural enhancements will be made to improve communications and component status verifications, and are tentatively scheduled for completion by April 7, 1988. Lastly, appropriate administrative action and counseling has been effected with the personnel involved in this occurrence.
315 | 3151988011 | 1988-10-19 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Cook 1 | P | WE | PO | 90 | POWER LEVEL - 000%. ON 10/19/88 AT 1522 HOURS, UNIT ONE EXPERIENCED AN ENGINEERED SAFETY FEATURES ACTUATION (REACTOR TRIP) FROM THE LOSS OF REACTOR FLOW LOGIC CIRCUIT OF THE PLANT PROTECTION SYSTEM, ALTHOUGH NO ACTUAL LOSS OF REDUCTION OF REACTOR COOLANT FLOW EXISTED. THE REACTOR TRIP SIGNAL WAS THE ULTIMATE RESULT OF THE FAILURE OF AN INDICATING LIGHT ASSEMBLY CONNECTED DIRECTLY TO ONE OF THE CLASS 1-E INSTRUMENT AND UNINTERRUPTABLE POWER SOURCES WHICH FEED THE SOLID STATE PROTECTION SYSTEM (SSPS). THE FAILURE CREATED A SHORT CIRCUIT, RESULTING IN EXCESSIVE CURRENT DEMAND ON THE POWER SOURCE. THE INLINE PROTECTIVE FUSE OPENED AS REQUIRED, RESULTING IN LOSS OF POWER IN ONE SSPS INPUT BAY. THE RELAYS WITHIN THE AFFECTED INPUT BAY THEN DE-ENERGIZED TO THE FAIL-SAFE POSITION. ONE OF THESE RELAYS IS ASSOCIATED WITH THE REACTOR COOLANT PUMP (RCP) BREAKER POSITION LOGIC CIRCUIT. BECAUSE THIS CIRCUIT HAS A ONE OUT OF FOUR COINCIDENCE WHEN REACTOR POWER IS ABOVE 50%, A REACTOR TRIP RESULTED. THE FAULTED LAMP AND SOCKET ASSEMBLY WAS REPLACED AND UNIT STARTUP WAS ACCOMPLISHED.
315 | 3151988013 | 1988-11-23 | QR8 | Spurious Reactor Trip | [45 empty] | Cook 1 | P | WE | PO | 90 | On November 23, 1988 at 2304 hours, Unit One experienced an Engineered Safety Features Actuation (Reactor Trip) from the Loss of Reactor Flow Logic Circuit of the Plant Protection System concurrent with all four Reactor Coolant Pump (RCP) breakers tripping open. <br /><br />The reactor trip signal was concluded to be a spurious indication of a Reactor Coolant Pump Busses underfrequency condition originating from the Solid State Protection System (SSPS) based on the following: 1) The only trip function that will trip all four reactor coolant pumps and the reactor is an underfrequency signal on at least two out of four RCP busses; 2) There were no relay operations or relay targets indicating an actual low frequency condition; and 3) There were no physical indications of loose connections or relay problems within the SSPS. <br /><br /> In an attempt to prevent recurrence of the trip two SSPS cards (in both Train A and Train B) of SSPS, in which an intermittent failure could cause the same conditions, were replaced.
315 | 3151989001 | 1989-01-16 | QL7 | Degraded condenser vacuum | [45 empty] | Cook 1 | P | WE | PO | 71 | On 01/16/89 the Plant Heating Boiler (PHB) was being operated for testing purposes after maintenance. The Unit Supervisor gave instructions to a Reactor Operator (RO) for placing auxiliary steam load on the PHB. These instructions included opening the steam supply to the start-up air ejectors if the normal steam loads were not enough. <br /><br /> After placing the normal steam loads on the PHB, the RO identified the control switch for the steam supply to the start-up air ejectors. A few minutes later the Control Room was notified that the PHB needed more load. The RO proceeded to open the steam supply to the start-up air ejectors, but he erroneously operated the control switch for the condenser air off-takes to the start-up air ejectors due to inadequate self checking. This caused a rapid decrease in condenser vacuum which resulted in a unit trip.<br /><br /> Preventive action will include operator training to emphasis the importance of self checking. The labeling of the involved control switches will be enhanced for human factor concerns. Appropriate administrative action was taken with the involved operator.
315 | 3151989003 | 1989-03-18 | QR8 | Spurious Reactor Trip | [45 empty] | Cook 1 | P | WE | PO | 10 | On March 18, 1989 at 0611 hours while Unit One was shutting down in preparation for refueling, an Engineered Safety Features (ESF) actuation (reactor trip sequence) occurred. The reactor trip was due to a standing high flux trip on the Intermediate Range (IR) Nuclear Instrumentation Channel I (N-35) which had not reset prior to power dropping below Permissive P-10 (approximately 9 percent) which automatically unblocks the IR high flux reactor trip.<br /><br /> The low value for the trip reset setpoint was due to the methodology used to determine the current equivalent values of the trip setpoint which resulted in a conservatively low setpoint for both the reactor trip and the trip reset. <br /><br /> To prevent recurrence, changes are being made in the method used to determine the current equivalent values for the trip and trip reset setpoints that will ensure the trip setpoint is conservative and will also ensure the reset setpoint will be above P-10. These changes will be in effect prior to Unit One going above P-10.
315 | 3151991004 | 1991-05-12 | QR7 | Other Reactor Trip (Valid RPS Trip) |  | X | [11 empty] | X |  | X | [28 empty] | X | Cook 1 | P | WE | PO | 100 | On May 12, 1991 at 0826 hours while performing a main generator "maximum reactive capability" test, a Reactor Protection System actuation (reactor trip sequence) occurred.<br /><br /> The reactor trip was due to an undervoltage condition sensed on the reactor coolant pump (4KV) busses. An investigation concluded that the bus undervoltage condition was due to a decrease in main generator output voltage. This decrease resulted from a transfer from automatic to manual control of the main generator voltage, which was initiated by the malfunction of a protective "exciter field current limiter" device. <br /><br /> The main generator voltage regulation system "exciter field current limiter panel" has been determined to be defective. This component will be replaced. Changes have been made to appropriate operating procedures requiring the matching of manual and automatic main generator voltage regulator setpoints. This will avoid large deviations between setpoints and will enhance electrical distribution system stability during any future transfers of main generator voltage regulation from automatic to manual control.
315 | 3151992012 | 1992-10-28 | QR5 | Turbine Trip | [45 empty] | Cook 1 | P | WE | PO | 16 | On October 28, 1992, at 0253 hours, with Unit One at 16 percent Reactor Thermal Power, a Turbine Trip/Reactor Trip occurred. The trip occurred during a power increase to 30 percent to perform a routine calometric test and was the result of a signal from an erroneously set main turbine thrust bearing wear device. <br /><br /> The erroneous signal was the result of the thrust bearing wear detector setpoint not being set, after maintenance, such that a turbine shaft displacement of approximately six mils would result in a Turbine Trip Signal. <br /><br /> Following the Reactor Trip, all automatic protection responses, including reactor trip and its associated actuations were verified to have functioned properly as a result of the reactor trip. The Unit was stabilized in Hot Standby (Mode 3) at 0310 hrs on October 28, 1992. <br /><br /> Prior to restarting Unit One, the main turbine thrust bearing wear detector was adjusted to the proper setpoint. To prevent recurrence, administrative guidelines are being developed to provide positive control on work order activities related to major turbine inspections.
315 | 3151995003 | 1995-07-14 | QL6 | Condenser Leakage | [45 empty] | Cook 1 | P | WE | PO | 100 | At O426 hours on July 14,1995, while at 100 percent Rated Thermal power, Unit 1 received a reactor trip signal as a result of a turbine top due to low condenser vacuum. The cause of the loss of condenser vacuum was a broken weld on the 1 inch drain trap bypass for steam dump valve 1-URV- 110 into the 'A' condenser. The break was at the socket to pipe weld joint and completely separated the pipe from the fitting, allowing air to be admitted into the 'A' condenser and vacuum to decrease beyond the trip setpoint.<br /><br /> All safety systems operated normally in response to the top signal. With the exception of the failure of bleed steam to feedwater heaters 5B and 6B to automatically isolate due to a defective relay, all post reactor trip responses were normal. The unit was stabilized in Mode 3, Hot Standby, and repairs were performed. This event was determined to have no actual or potential adverse effect on the health and safety of the public.
315 | 3151995012 | 1995-12-07 | QR6 | Manual Reactor Trip | [45 empty] | Cook 1 | P | WE | PO | 32 | On December 7, 1995 at 2235 hours with Unit 1 in Mode 1 at approximately 32 percent Rated Thermal Power, while reducing power from 71 percent to 7 percent to remove the Turbine-Generator from service for repairs to the Main Transformer and Electro-Hydraulic Control System, the Unit 1 reactor was manually tripped due to increasing vibrations on the Main Turbine. The reactor trip was ordered as a conservative measure by the Unit Supervisor to prevent possible damage to the turbine. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(iv), as an event that resulted in manual actuation of the reactor protection system. The appropriate prompt notification was made under 10CFR50.72. <br /><br /> The increased sensitivity of the Main Turbine to steam temperature changes after installation of the new Monoblock rotor was not fully understood. The increased sensitivity of the machine resulted in the elevated vibration levels. To prevent a recurrence, the appropriate procedures have been revised to minimize thermal transients. <br /><br /> All safety systems operated normally in response to the trip signal. The event had no actual or potential adverse impact on the health and safety of the public.
315 | 3151996002 | 1996-03-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 1 | P | WE | PO | 100 | At 1527 hours on March 17, 1996, with Unit 1 at 100% Rated Thermal Power, a reactor trip signal was received. This signal was generated as a result of low feedwater flow coincident with low Steam Generator level in the number 4 Steam Generator. The low level resulted from the failure of the Main Feedpump (MFP) differential pressure controller, which automatically controls the differential pressure between feedflow pressure into the SG, and main steam pressure exiting the Steam Generator. The Operators took manual control of the feedpumps to regain level in the Steam Generator, however, the reactor trip logic conditions were met before level could be restored and the trip signal was generated. <br /><br /> All safety systems operated normally in response to the trip signal and the unit was stabilized in Mode 3. The event was determined to have been caused by a failure in an integrated circuit logic chip in the main feedpump differential pressure controller. The failed controller was replaced and subsequently returned to the manufacturer for further analysis. The event was determined to have no actual or potentially adverse effect on the health and safety of the public.
315 | 3151996004 | 1996-09-22 | QR5 | Turbine Trip | [45 empty] | Cook 1 | P | WE | PO | 88 | On September 22, 1996, at 0049 hours with Unit 1 in Mode 1 at 88 percent power, a Unit 1 Main Transformer Sudden Pressure Trip (SPT) signal was received. This signal caused a Main Generator trip, which in turn, caused a reactor trip. This event is being reported in accordance with 10CFR50.73(a)(2)(iv), as any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS). <br /><br /> The Main Transformer Sudden Pressure trip signal is attributed to a confirmed lighting strike which occurred approximately 200 milliseconds prior to the receipt of the SPT signal. The lightning strike was a through fault and seen by the Main Generator, but was not considered a large magnitude transient when compared with previous strikes at the site. <br /><br /> The SPT relay was tested and replaced due to inconsistent performance. The balance of the SPT relay circuitry was tested and found to be satisfactory. Transformer oil sample analysis was performed and verified that the SPT signal was spurious. <br /><br /> After the reactor trip, all safety systems operated normally in response to the trip signal and all post reactor trip responses were normal. The reactor was stabilized in Mode 3, Hot Standby. This event was evaluated and determined to have no actual or potential adverse effect on the health and safety of the public.
315 | 3152001001 | 2001-02-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 1 | P | WE | PO | 100 | On February 15, 2001 at 1417 hours, while at approximately 100 percent power, a low vacuum trip on the Unit 1 east main feedwater pump turbine occurred. The operator manually tripped the reactor in accordance with plant procedures. The post trip investigation indicated that all safety related systems performed as designed. Prior to the event, the main feedpump water box differential pressure and backpressure was being monitored on an increased frequency due to a rising trend on both parameters. The previous shift had attempted to improve this condition by flushing the circulating water side of the main condenser waterboxes. A downpower had been previously scheduled to allow cleaning of the main feedwater condenser. However, the fouling occurred more rapidly than anticipated. In accordance with 10 CFR 50.72 (b)(3)(iv)(B)(1), a four-hour ENS notification was made to the NRC at 1545 hours on February 15, 2001, as an event or condition that resulted in an actuation of the reactor protection system when the reactor is critical. The cause of the feedwater pump trip was loss of condenser vacuum as the result of corrosion scales obstructing flow at the condenser's inlet-side tubesheet. This condition lead to an elevated condenser backpressure and a subsequent low vacuum trip of the east main feedwater pump. The feedwater pump turbines are non-safety related, non-safety interface, balance of plant equipment. The function of providing feedwater flow to support power operation is not a safety related or accident mitigating function. Therefore, with respect to the main feedwater system, this condition has no safety significance. Following the reactor trip, both the east and west main feed pump condensers were opened and cleaned. Between March 30 and April 1, 2001, Units 1 and 2 respectively were reduced to approximately 60 percent power to clean and inspect the feed pump condensers. No new scale formation was observed.
315 | 3152002005 | 2002-06-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 1 | P | WE | PO | 88 | At 1443 hrs on June 14, 2002, Unit 1 was manually tripped following the trip of the East main feedwater (FW) pump (MFP). The East MFP tripped due to a loss of main feed pump turbine condenser vacuum caused by an influx of debris following the start of the #13 circulating water (CW) pump. On June 14, 2002, at 1751 hours, in accordance with 10 CFR 50.72 (b)(2)(iv)(B), a four-hour ENS notification (Event No. 38993) was made to the NRC for a condition that resulted in an actuation of the reactor protection system when the reactor is critical. The cause of this event was the transport of debris (primarily zebra mussel shells and sand) into the East MFP turbine condenser upon the start of the #13 CW pump. A contributing factor was the closure of 12-WMO-30 (the center lake water intake valve) a few days prior to the start of the #13 CW pump. The safety significance of this event was minimal since plant procedures and operator training provided sufficient direction for control room personnel to shutdown the plant and maintain it in a safe shutdown condition. In addition, this event had no impact on the ability of the main FW system to perform its feedwater isolation accident mitigation function. The Unit 1 East and West MFP turbine condenser tubes and waterboxes were cleaned on June 14, 2002. CNP will take actions to mitigate the effects of debris on CW pump startups with the unit on line. Specifically, precautions will be added to the CW system operating procedure to identify the potential vulnerability for debris intrusion associated with starting CW pumps with the unit on-line. The procedures will also include guidance for use of MFP turbine condenser waterbox lancing when starting a CW pump with a unit on-line.
315 | 3152003001 | 2003-01-15 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Cook 1 | P | WE | PO | 100 | On January 15, 2003, at approximately 2010 hours, a fault occurred in the Unit 1 main transformer. The fault caused the current differential relays to actuate resulting in an automatic trip of the main transformer. A sudden internal fault within the main transformer ruptured the transformer oil tank resulting in a loss of oil and a fire. The loss of the main transformer precipitated an automatic trip of the main generator and an immediate turbine and reactor trip. The main transformer fire was extinguished within 35 minutes of the event with one minor ref lash, which was promptly controlled and extinguished by onsite fire brigade members. One minor personnel injury occurred requiring off site medical attention. An Unusual Event was declared based on a fire of more than 15 minutes in duration within the protected area. All safety-related components functioned properly and no significant discrepancies in equipment time responses were noted. In accordance with 10CFR 50.72(b)(2)(iv)(B), 10CFR 50.72(b)(2)(xi), and 10CFR 50.72(b)(3)(iv)(A), all, applicable event (EN #39513) and emergency plan required notifications were completed in a timely manner. As such, this LER is being submitted in accordance with the requirements of 10CFR 50.73(a)(2)(iv)(A) for a condition resulting in an automatic actuation of the reactor protection system. A one-hour report was completed at 2105 hours and the remaining three reports were completed by a single notification at 2339 hours. The apparent cause of the event was a sudden internal fault within the main transformer. Corrective actions included replacement of the main transformer. Other non-safety related components damaged by the resultant fire were either repaired or replaced.
315 | 3152003003 | 2003-04-24 | QL4 | Loss of Non-safety-Related Cooling Water |  |  |  |  | X | [5 empty] | X | [10 empty] | X |  | X | [16 empty] | X |  |  |  |  | Cook 1 | P | WE | PO | 100 | On April 24, 2003, between 0255 and 0305 hours, a large school of alewives began impinging on the traveling water screens (TWS) located upstream of the common forebay of the circulating water (CW) and the essential service water (ESW) systems. As the volume of fish impinging on the TWS increased, the TWS system was overwhelmed. Differential pressure across the screens increased rapidly, resulting in most of the screens stopping due to either shear pin failure or tripping of breaker thermal overloads, and the eventual failure of multiple screen panels within the TWS system. As a result of the screen panel failures, the fish subsequently entered the suction of the CW and ESW pumps. Components serviced by the CW and ESW pumps began fouling. At approximately 0327 hours, Unit 1 was manually tripped due to fouling of the main feed pump condensers and at approximately 0330 hours Unit 2 was tripped due to degraded forebay conditions. Donald C. Cook Nuclear Plant (CNP) verified the availability of offsite power as specified by Action e of Technical Specification 3.8.1.1. However, the verification was not completed within one hour as required by the technical specifications. The root cause of the event included the lack of a fully-developed operational response to debris intrusion, the failure to maintain the TWS system, and the failure of CNP to address long-standing or repetitive equipment problems. Corrective actions include flushing and inspection of affected components, repair of the damaged TWS components, improvements in CNP's debris intrusion mitigation strategy, enhanced maintenance program for the TWS, and the development of action plans to address the top equipment reliability concerns. This condition is reportable in accordance with the reporting criteria established in 10 CFR 50.73(a)(2)(iii) and 10 CFR 50.73 (a) (2)(iv)(A) for the manual trip of both Unit 1 and Unit 2 reactors.
315 | 3152005001 | 2005-04-26 | QR8 | Spurious Reactor Trip | [45 empty] | Cook 1 | P | WE | PO | 8 | At 0002 hours on April 26, 2005, the Donald C. Cook Nuclear Plant Unit 1 reactor automatically tripped while at 8% reactor power. Preparations were being made to synchronize the main generator with the offsite electrical power grid. The post-trip investigation determined that the trip was caused by an intermediate range high flux reactor trip signal. The intermediate range high flux reactor trip occurred below the reactor protection system actuation normally set at 22% reactor power. This reactor trip has a one-of-two channel trip logic. The trip is interlocked to be active below 10% reactor power. It was determined the cause was a spurious lowering of the trip setpoint due to age-related degradation of the level adjust potentiometer in the circuitry of 1-NRI-35, Nuclear Instrumentation Channel 1 Intermediate Range Neutron Flux Detector. The affected bistable and relay driver assembly, 1-NRI-35-NC35F, for the intermediate range channel 1-NRI-35, was replaced. Additionally, preventive maintenance tasks for periodic replacement of nuclear instrument bistable relay drivers will be developed. All plant systems functioned normally following the reactor trip. The auxiliary feedwater system actuated and performed as expected during this event. This event was reported under event notification system number 41639 per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), as a valid reactor trip and actuation of the auxiliary feedwater system, respectively. This LER is being reported per requirements of 10 CFR 50.73(a)(2)(iv)(A).
315 | 3152007001 | 2007-08-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 1 | P | WE | PO | 100 | On August 28, 2007, at 1354 hours, Donald C. Cook Nuclear Plant (CNP) Unit 1 received a reactor trip and main turbine trip signal as a result of low Steam Generator #11 water level coincident with a steam flow - feedwater flow mismatch. All control rods fully inserted and the Auxiliary Feedwater System (AFW) started and performed as designed. The reactor trip was uncomplicated and all major plant components functioned as designed. The reactor trip was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and the AFW actuation was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). The reactor trip and AFW actuation are reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A). The trip was the result of an over voltage condition on one of the Digital Control System (DCS) power supplies. The over voltage condition caused the controller for the East Main Feed Pump control valve to automatically trip, causing an inadequate feedwater flow condition to the steam generators. Corrective actions included replacement of the DCS power supply.
315 | 3152008001 | 2008-02-02 | QR6 | Manual Reactor Trip | [45 empty] | Cook 1 | P | WE | PO | 93 | On February 2, 2008, at 0530 hours, Donald C. Cook Nuclear Plant Unit 1 operators initiated a manual reactor trip from 93% power when main turbine bearing vibration reached the manual trip setpoint. All control rods fully inserted and the Auxiliary Feedwater System (AFW) started and performed as designed. The reactor trip was uncomplicated and all major plant components functioned as designed. The reactor trip and AFW actuations were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) respectively, and are reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A). An unintentional cooldown of Main Turbine Lube Oil (MTLO) induced an oil whip condition that exacerbated main turbine bearing vibrations. After raising MTLO temperature, operators were performing a power reduction in an attempt to lower main turbine vibration. During the power reduction, vibration levels reached the manual trip setpoint and operators manually tripped the reactor in accordance with plant procedures. Corrective actions included installation of main turbine balance weights to return vibration to normal levels as well as actions to address the MTLO cooldown.
315 | 3152008006 | 2008-09-20 | QR6 | Manual Reactor Trip | [7 empty] | X |  |  | X | [22 empty] | X | [5 empty] | X | [5 empty] | Cook 1 | P | WE | PO | 100 | On September 20, 2008, at 2005 hours, Donald C. Cook Nuclear Plant Unit 1 control room operators initiated a manual reactor trip from 100% power following high-high vibration alarms on all main turbine supervisory instrumentation vibration points. In addition, numerous alarms on components in the condensate and feedwater flowpaths along with severe vibration and rumbling were noted by control room operators. Upon the reactor trip, all control rods fully inserted, the Auxiliary Feedwater System (AFW) and other major plant components functioned as designed. The main generator was reported to be on fire, and the Shift Manager declared an Unusual Event (UE) when the fire was not extinguished within 15 minutes. The f ire was declared extinguished at 2028 hours. At 2044 hours, the operators tripped closed the Main Steam Isolation Valves (MSIV) in accordance with procedure. Closure - was based on an observed cooldown of the Reactor Coolant System (RCS) . RCS temperature recovered following closure of the MSIVs . The reactor trip, UE, AFW actuation, and MSIV closure were reported in accordance with 10 CFR 50.72(b) (2) (iv) (B) , 10 CFR 50.72(a) (1) (i) , and 10 CFR 50 . 72 (b) (3) (iv) (A) . The reactor trip, AFW actuation and MSIV closure are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73 (a) (2) (iv) . (A) . The cause of the reactor trip was high-high vibration of the main turbine. Corrective actions have commenced and include repair of the main turbine and generator.
315 | 3152011001 | 2011-09-07 | QR5 | Turbine Trip | [45 empty] | Cook 1 | P | WE | PO | 100 | On September 07, 2011, at 0854 hours, Donald C. Cook Nuclear Plant (CNP) Unit 1 Reactor tripped automatically due to a trip of the main turbine. All control rods fully inserted and the auxiliary feedwater system (AFW) started and performed as designed. The reactor trip was uncomplicated and all major plant components functioned as designed; as such, there were no safety system functional failures. The reactor trip was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and the AFW actuation was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). The reactor trip and AFW actuation are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A). The main turbine tripped due to an automatic turbine trip signal generated by the main turbine thrust bearing wear detection system. The initial investigation has concluded that there was no actual thrust bearing wear condition. The cause of the inadvertent trip signal has been determined to be a result of inadequate installation of sensing equipment. This inadequate installation resulted in a spurious trip signal common to both channels. Corrective actions have been taken to correct the installation.
315 | 3152014003 | 2014-11-01 | QL7 | Degraded condenser vacuum | [45 empty] | Cook 1 | P | WE | PO | 100 | On November 1, 2014, at approximately 0249, Donald C. Cook Plant Unit 1 (U1) and Unit 2 (U2) reactors were manually tripped from 100 percent and 55 percent power, respectively, when high winds and high waves on Lake Michigan resulted in a heavy influx of dune grass and debris into the forebay which resulted in degraded forebay conditions, lowering forebay level, and damaged trash racks. Following the U1 trip, the U1 Turbine Driven Auxiliary Feed Pump (TDAFP) tripped unexpectedly three minutes following the automatic start. Following the U2 trip, the U2 Main Generator trip was performed manually when the automatic trip failed.<br /><br /> Corrective actions taken include cleaning and repair of damaged forebay trash racks and travelling water screens. Corrective maintenance also corrected the causes of the U1 TDAFP trip and the U2 Main Generator trip function. Planned corrective actions include revising plant procedures to provide a comprehensive approach to adverse lake conditions.<br /><br /> The manual Reactor Protection System actuation and the automatic Auxiliary Feedwater System actuation were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) (Event Notification 50587). The valid actuations are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A). The storm and lake conditions necessitating the reactor trips is reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iii).
316 | 3161987004 | 1987-06-01 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Cook 2 | P | WE | PO | 90 | On June 1, 1987, at 2340 hours, a turbine trip/reactor trip occurred due to a loss of main condenser vacuum. The loss of vacuum was the result of a degraded isolation valve (LPD-169) utilized while removing a blank flange installed at LPD-170 (miscellaneous drain tank header isolation to Unit 1 and the turbine room sump). <br /><br />The cause of this event has been determined to be the failure of a manual isolation valve. Following the trip, inspection of LPD-169 (a soft seat butterfly valve) revealed that severe degradation of the valve seat had occurred. This degradation allowed excessive air in-leakage to occur from the open drain tank discharge header. This air in-leakage in turn resulted in the reduction of condenser vacuum and the subsequent turbine trip/reactor trip. <br /><br />Immediate corrective actions involved Operations personnel implementing plant procedures to verify proper response of the automatic protection system and to assess plant conditions for initiating appropriate recovery actions. The subject valve was replaced - (no additional preventive action has been deemed necessary).
316 | 3161987005 | 1987-06-02 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Cook 2 | P | WE | SU | 5 | On June 2, 1987, at 1949 hours, an Engineered Safety Features actuation (Reactor Trip) occurred due to low-low Steam Generator level in number 23 Steam Generator. Prior to the trip, the reactor had been stable in Mode 2 (Reactor Startup) at 4.5 percent Reactor Thermal Power. Steam Generator levels were being maintained in manual utilizing low flow feedwater preheating. <br /><br />Due to the operator assigned the responsibility to maintain Steam Generator levels becoming involved with other related Control Room activities, Steam Generator number 23 dropped substantially in level. In an attempt to avoid a trip actuation, the operator increased steam flow via the steam dump system while simultaneously increasing feedwater flow. Steam Generator level increased momentarily, however, shortly thereafter level dropped and at 1949 hours the low-low level setpoint was reached actuating the reactor trip sequence. <br /><br />The cause of this event was determined to be personnel error. Appropriate administrative action was taken concerning the individual involved. In addition, a memo was issued to all operators describing lessons learned from this event.
316 | 3161987007 | 1987-07-14 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Cook 2 | P | WE | PO | 80 | On July 14, 1987, at 0707 hours, an Engineered Safety Features Actuation (Reactor Trip) occurred due to undervoltage of the reactor coolant pump busses. The undervoltage condition was the result of the failure of the main generator voltage control system. <br /><br />The Unit was stabilized in Mode 3 (Hot Standby) at approximately 0755 hours, July 14, 1987. No abnormal reactor trip sequence responses were noted. The NRC was notified of the event via the ENS at 0815 hours, July 14, 1987. <br /><br />Post-event testing of the voltage control system components revealed two failed power supplies (automatic and manual), and six failed SCR Modules. All failed/suspected components were replaced. Investigation regarding industry experience with Brown Boveri voltage control systems indicates that the failures which occurred are consistent with those experienced at other plants and is not a result of operator error or lack of maintenance. Evaluation as to the necessity for the redesign of the voltage control system, via the Plant Modification program, continues - however, no specific preventive measures have been identified to date.
316 | 3161987008 | 1987-07-22 | QP5 | Excessive Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 19 | On July 22, 1987, at 2232 hours, an engineered safety features (ESF) actuation (reactor trip sequence) occurred due to an extreme high level in the No. 24 Steam Generator. Prior to the trip, a unit power ascension was in progress, Steam Generator levels were being maintained in manual utilizing low flow feedwater preheating. The main feedwater delta pressure (Delta P) controller was in automatic and responding as designed with no apparent difficulties. <br /><br />At approximately 2210 hours, an occurrence involving the erratic response (intermittent failure) of the feedwater pump delta P controller meter resulted in a severe transient in the Steam Generators. The resultant feedwater transient increased the level within the No. 24 Steam Generator to the extreme high trip setpoint actuating the reactor trip sequence. <br /><br />The main feedwater delta P controller was inspected/tested immediately following the event. No faulty components were identified and the response/failure experienced could not be reproduced - however, as a preventive measure, the delta P controller meter was replaced. In addition, a memo was issued to all Operators describing the lessons learned from this event.
316 | 3161987013 | 1987-10-10 | QR8 | Spurious Reactor Trip | [45 empty] | Cook 2 | P | WE | PO | 8 | On October 10, 1987 at 1213 hours the Unit Two Reactor tripped from a turbine trip. The turbine was being rolled in preparation for the overspeed testing and power was being maintained below the Permissive P-13 interlock setpoint in order to avoid a reactor trip when the turbine was tripped on overspeed. <br /><br />At approximately 8 percent power the turbine tripped and a reactor trip occurred because the P-13 bistable setpoint was too conservative, caused by a setpoint calculation error. The Technical Specification requirement is for P-13 to be active at greater than or equal to 51 psig turbine impulse pressure. The bistable setpoint was to be at 45 psig for conservatism, however, an error was made in calculating the setpoint and as a result, the setpoint was actually equivalent to 31.132 psig. No abnormal reactor trip sequence responses were noted. The NRC was notified via the ENS at 1300 hours on October 10, 1987. <br /><br />Upon discovery of the error, the setpoint was recalculated and the bistable was calibrated to the correct value.
316 | 3161989014 | 1989-08-14 | QR8 | Spurious Reactor Trip | [45 empty] | Cook 2 | P | WE | PO | 100 | On August 14, 1989 at 1601 hours, a Reactor Protection System (RPS) actuation (reactor trip) occurred when operators transferred the Control Room Instrumentation Distribution (CRID) IV (vital bus) inverter to its normal Class 1E power supply and the inverter failed. When the CRID IV inverter failed, a reactor trip signal was initiated due to the Reactor Coolant Pump (RCP) circuit breaker position indication open (fed from CRID IV). <br /><br /> Prior to the trip (at approximately 1540 hours), the CRID inverter had transferred to its alternate non-class 1E power supply at the same time that a control power fuse had blown on Power Range Nuclear Instrumentation System (NIS) Channel IV (N-44). Subsequent investigation determined that the CRID inverter failure was due to a failed silicon controlled rectifier (SCR) in the static transfer switch. This also resulted in the failure of fuses and power supplies in various components fed from the CRID. <br /><br /> The faulted SCR's were replaced and the CRID inverter declared operable. All components fed from the CRID were inspected and, where necessary, fuses and/or power supplies were replaced.
316 | 3161990004 | 1990-06-11 | QR3 | Reactivity Control Imbalance | [45 empty] | Cook 2 | P | WE | PO | 86 | On June 11, 1990 at 1417 hours, the Unit 2 reactor tripped from a power range, neutron flux, high negative rate signal. This signal requires a 2 out of 4 (2/4) logic to initiate a trip. Although the cause of the trip is not conclusively known, it is believed that a drop of more than one (1) control rod caused the reactor to trip. At the time of the reactor trip, a technician was walking on top of the rod control system power cabinets. It could not be determined whether the presence of the technician contributed to the postulated rod control system failure. No hardware failure that would have resulted in the dropping of control rods was identified. Prior to Unit restart, all control rods were successfully exercised. <br /><br /> Following the reactor trip, no malfunctions of safety-related systems or components occurred. In addition, all safety equipment responded as designed. The NRC was notified via the Emergency Notification System (ENS) at approximately 1537 hours on June 11, 1990.
316 | 3161990012 | 1990-12-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 100 | On December 12, 1990 at 0318 hours, the Unit 2 reactor tripped as a result of steam-to-feedwater flow mismatch (difference between steam and feed flows on one of two measured channels of each parameter for a steam generator (SG)) in coincidence with low SG level (one of two SG narrow range channels for a SG) conditions in the number 4 SG. These conditions arose following a trip of one of the two Turbine Driven Main Feedwater Pumps (TD-MFWP) due to an erroneous actuation of the turbine thrust bearing wear/shaft position detection alarm and trip device. No malfunctions of safety-related systems or components occurred. <br /><br /> The turbine thrust bearing wear/shaft position detection device was removed from the MFWP turbine driver and inspected. This device, and the similar device on the other turbine driver, were bench calibrated and properly set-up on the MFWP turbines at turning gear and no-load operating speeds.
316 | 3161990013 | 1990-12-15 | QR5 | Turbine Trip | [45 empty] | Cook 2 | P | WE | PO | 100 | On December 15, 1990, at 0840 hours during a Technical Specification (TS) Surveillance, the 2-AB plant battery was declared inoperable when a single cell's voltage decreased below a test limit. Efforts taken to restore the cell voltage were unsuccessful and a reactor shutdown was initiated. During the shutdown at approximately 35 percent rated thermal power, a reactor protection system actuation occurred due to a turbine trip from an unnecessary actuation of the Anticipated Transient Without Scram Mitigation System Actuation Circuitry (AMSAC). All equipment performed as expected and there were no component failures following the trip. <br /><br /> The reactor entered Mode 5 at 0600 hours on 12-16-90 to exit the battery TS Action Statement and the battery cell of concern was removed from service via a jumper. A proposed TS Amendment is being prepared to request changing the surveillance to align with industry standards and conform to Standard TS. <br /><br /> The AMSAC actuation occurred due to an improper setpoint. All AMSAC input setpoints were verified and corrected as needed.
316 | 3161991004 | 1991-03-13 | QR5 | Turbine Trip | [45 empty] | Cook 2 | P | WE | PO | 100 | On March 13, 1991 at 0651 hours, the Unit 2 reactor tripped as a result of a turbine trip generated by a moisture separator-reheater (MSR) high water level trip. The turbine-generator trip and reactor trip were a result of off-site electrical transmission system disturbances. Ice and snow damaged 765 KV transmission lines which caused a significant load rejection on the main turbine. The closing of the main turbine control valves in response to the load rejection created a MSR pressure transient which actuated the MSR high water level trip and tripped the main turbine and reactor. The plant was stabilized in Mode 3. <br /><br /> Abnormalities noted during the event included the electronic overspeed trip of the turbine driven auxiliary feedwater pump, closure of one of the four main steam isolation valves, and apparent slow closure of the #4 combined intercept valve. All equipment malfunctions were reviewed with no unreviewed safety questions and the reactor bus returned critical on March 15, 1991 at 1113 hours.
316 | 3161991006 | 1991-08-01 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Cook 2 | P | WE | PO | 97 | On August 1, 1991, at 1931 hours, the Unit 2 reactor tripped as a result of a turbine trip generated by the generator differential protective relays operating caused by a fault/explosion of the phase three current transformer (CT) of the main generator output breaker. The CT was disassembled and inspected. The inspection revealed that the CT had an internal failure, possibly arising from past stresses on the CT. The American Electrical Power Nuclear Organization will be taking responsibility for future scheduling of the predictive and preventive maintenance activities related to switchyard CT internal deterioration detection, an activity which had not been prudently applied to this particular CT prior to the event. <br /><br /> Abnormalities noted during the event included the electronic overspeed trip of the turbine-driven auxiliary feed pump as the operator was removing it from service, and closure of one of the four main steam isolation valves, which should have stayed open. The turbine-driven auxiliary feedwater pump was immediately reset and placed in standby, and the closed main steam isolation valve was promptly reopened.
316 | 3161991010 | 1991-11-15 | QR5 | Turbine Trip | [45 empty] | Cook 2 | P | WE | PO | 100 | On November 15, 1991 at 1113 hours, the Unit 2 reactor tripped as a result of a low-low Steam Generator (SG) water level in SG #21. Prior to the reactor trip, instrumentation was being installed on the main turbine control fluid circuit. The purpose of this instrument was to investigate oscillations of control valve A which was scheduled to be tested later that evening. A pressure indicator which measures the output of the turbine operating device was to be isolated and another transmitter was to be installed in parallel to it. However, unknown to personnel involved, worn threads on the stem of the manual isolation valve prevented the pressure indicator from being completely isolated. As a drain plug was removed to vent pressure from the instrument isolation valve, pressure on the output of the operating device was also decreased. This effectively lowered the setpoint supplied to the speed governor, which compares actual turbine speed to the operating device setpoint, and fully closed the high pressure and low pressure turbine control valves. With the steam supply isolated, SG pressure rapidly increased and caused SG level to decrease below the reactor trip setpoint. <br /><br /> The root valve's bonnet was replaced and damaged stem threads were repaired. During the outage, repairs were also completed to reduce the turbine load swings experienced during valve testing. A review of the work control process will be performed to identify any enhancements that can be added to reduce the probability of an unplanned actuation occurring from similar activities in the future. Any change indicated by the review will be implemented by March 30, 1992.
316 | 3161992007 | 1992-07-02 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Cook 2 | P | WE | PO | 8 | On July 2, 1992 at 1120 hours, the Unit 2 reactor tripped from a turbine trip coincident with turbine power greater than 10%. Unit 2 was in Mode 1 at 8% thermal power with the main turbine operating at synchronous speed (1800 rpm) and unloaded. Main condenser vacuum was being adjusted using a startup air ejector to investigate a turbine vibration problem. During this evolution, main condenser vacuum decreased at a greater than anticipated rate which resulted in the main turbine control valves opening automatically to maintain 1800 rpm. This caused turbine first stage pressure to increase which enabled the reactor trip from turbine trip logic. When main condenser vacuum decreased to 24.8 in. Hg., the operators manually tripped the turbine in accordance with the loss of condenser vacuum abnormal procedure. An automatic reactor trip from turbine trip immediately followed. <br /><br /> All automatic protection responses, including reactor trip and its associated actuations were verified to have functioned properly as a result of the reactor trip signal. Unit 2 was stabilized in Hot Standby (Mode 3) at 1128 hours on July 2, 1992. Procedure enhancements have been made and Operator training will be conducted as a result of this event.
316 | 3161993007 | 1993-08-02 | QR5 | Turbine Trip | [45 empty] | Cook 2 | P | WE | PO | 70 | On August 2, 1993, at 1226 hours, the Unit 2 reactor tripped as a result of a main turbine trip, caused by a spurious actuation of the Exhaust Hood High Temperature Trip Switches. Investigation revealed that eight of nine Exhaust Hood High Temperature Trip Switch setpoints were found to be significantly below the normal trip setpoint. Investigation of the event determined that the method used to calibrate the switches may have caused the setpoint to be misadjusted, and that vibration can cause a downward shift in the setpoint. These factors, combined with a slight increase in hood temperatures and vibration levels which resulted from the removal of a main condenser half from service, are believed to have caused the spurious trip. <br /><br /> To prevent recurrence, the Main Turbine Exhaust Hood high temperature turbine trip was disabled. Written instructions for a manual turbine trip on receipt of a verified Main Turbine Exhaust Hood Extreme High Temperature Alarm have replaced the defeated automatic trip. .
316 | 3161993008 | 1993-08-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 90 | On August 27, 1993, at 0502 hours with Unit 2 in Mode 1 (Power Operation) at 90 percent Rated Thermal Power, a Reactor Trip occurred from a Steam Flow/Feed Flow Mismatch coincident with a low level in the No. 4 Steam Generator. These conditions were the result of an uncontrollable speed decrease on the East Main Feed Pump (MFP) Turbine. An investigation revealed that the loss of speed control was the result of a malfunctioning Current-to-Current Repeater (I/I). I/Is were installed in both the East and West MFP Turbine speed control circuits on August 13, 1993 via a Temporary Modification (TM). This action was taken following diagnosis of a ground condition which was interfering with the transfer of the turbine speed control circuit from manual to the automatic control mode. Post modification testing and power operation following installation of the TM demonstrated that the TM had isolated the grounding problem from the speed controller and had restored proper functioning of the control circuit. Following the trip, troubleshooting of the East MFP speed control circuit found that the I/I was malfunctioning. <br /><br /> The defective I/I was replaced on August 30, 1993. Following replacement of the I/I, circuit checks revealed inconsistencies which ultimately led to a decision to remove the TM. The East and West MFP speed control circuits were returned to their original design on September 12, 1993. The control mode transfer problems caused by the ground condition are being controlled administratively. Trouble shooting of the ground and subsequent repairs are scheduled for completion during the next Unit 2 Outage of sufficient duration .
316 | 3161994001 | 1994-02-21 | QL5 | Partial Closure of MSIVs | [45 empty] | Cook 2 | P | WE | PO | 60 | On February 21, 1994 at 1413 hours with Unit 2 in Mode 1 at 60 percent Rated Thermal Power, Unit 2 received a reactor trip signal from a Steam Generator No. 24 low-low level condition. At the time of the trip, the Control Room crew was restoring Main Steam Stop Valve 2-MRV-240 to operable status. The valve had been declared inoperable earlier in the day (1043 hours) to repair Beat leakage on 2-MRV-241, one of the two associated dump valves. The repair work required voluntary entry into Technical Specification 3.7.1.5, which allowed continued power operation provided the inoperable valve was restored to operable status within four hours. When the dump valve was placed in service following repairs, it failed to remain closed. This caused the stop valve to begin to quickly close, which in turn, lead to a reactor trip on low-low steam generator level. <br /><br /> The root cause of this event is attributed to the valve actuator recoupling procedure. The procedure for inspection and adjustment of pneumatic/spring actuators, associated positioners, and limit switches was revised to improve the direction for coupling actuators to valves to better ensure the correct stroke length and set pressures are accurately obtained when coupling the valve to the actuator.<br /><br /> All safety systems operated normally in response to the trip signal. The event had no actual or potential adverse impact on the health and safety of the public.
316 | 3161994005 | 1994-08-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 60 | On August 15, 1994 at 2350 hours with Unit 2 in Mode 1 at 60 percent Rated Thermal Power, Unit 2 received a reactor trip signal from a Steam Generator Number 23 Low Feedwater Flow Coincident with Low SG Level. At the time of the trip, the Control Room crew was in the process of removing the Number 21 Circulating Water (CW) Pump from service to troubleshoot a spurious low voltage alarm on the 4 KV bus. The closing of a CW pump discharge valve and stopping of the pump caused debris in the CW system to be stirred up and entrained in the cooling flow. The entrained debris then entered the Main feedpump turbine (FPT) condenser waterbox supply lines. The flow restriction in the FPT condenser waterboxes caused a rapid loss of vacuum and the West Main feedpump tripped on low vacuum. The reactor subsequently tripped on low feed flow coincident with low level on Loop 3. <br /><br /> The root cause of this event is attributed to zebra mussels within the Circulating Water system which temporarily blocked cooling flow through the main feedpump condenser water box tubes and caused a main feedpump trip on low vacuum. <br /><br /> After the reactor trip all safety systems operated normally and the reactor stabilized in Mode 3. The main feedpump condenser water boxes were cleaned and inspected and the reactor was returned to critical on August 16, 1994 at 2233 hours.
316 | 3161994008 | 1994-12-11 | QR5 | Turbine Trip | [45 empty] | Cook 2 | P | WE | PO | 19 | On December 11, 1994, at 1705 hours with Unit 2 in Mode 1 at 19 percent Rated Thermal Power, Unit 2 received a turbine trip/reactor trip signal from a Main Turbine Moisture Separator High Level. At the time, of the trip, the Control Room crew was attempting to transfer the Right Moisture Separator Reheater (MSR) drain from the Main Condenser to the 4B Feedwater Heater via the Right Moisture Separator Drain Tank (MSDT). Level alarms which normally precede the MSR high level trip signal did not actuate. The turbine trip signal caused the reactor trip. <br /><br /> Despite the efforts of a troubleshooting team assigned to determine the root cause of this event, the cause of the MSR high level trip signal could not be conclusively determined. Other than the failure of the Right MSDT level alarms to actuate, no system, control or procedural abnormalities were noted. An extreme high level was observed prior to the trip in the 4B heater, but is not unusual during startup and could not be established as the cause of the event. <br /><br /> After the reactor trip, all safety systems operated normally and the reactor stabilized in Mode 3. The Right MSDT high water level alarms were inspected, repaired, and tested. The reactor was returned to critical on December 12, 1994 at 2033 hours.
316 | 3161995002 | 1995-02-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 100 | On February 23, 1995, at 1645 hours with Unit 2 in Mode 1 (Power Operation) at 100 percent Rated Thermal Power, a Reactor Trip occurred from a steam flow/steam feed flow mismatch coincident with a low level in the No. 4 Steam Generator. These conditions were the result of an apparent transistor failure and blown fuse on a digital board in the feed flow signal controller for the Loop 4 Feedwater Regulating Valve (FRV). The failed signal controller caused the FRV to close, creating a steam flow/feed flow mismatch. The Control Room Operator attempted to take manual control of the FRV. A Reactor Trip occurred when a low level condition was created in No. 4 Steam Generator. Following the Reactor Trip all systems functioned as required, with the exception of the generator trip circuitry. The Main Generator failed to trip when a limit switch, associated with Turbine Control/Stop Valve-D did not make-up mechanically when the valve closed. The generator remained connected to the grid for 128 seconds, until the generator was manually tripped. The defective FRV signal controller was replaced. The misaligned limit switch on Turbine Control/Stop Valve-D was repositioned for proper mechanical alignment. This event had no actual or potential impact on public health and safety.
316 | 3161995004 | 1995-08-26 | QR5 | Turbine Trip | [45 empty] | Cook 2 | P | WE | PO | 100 | At 0149 hours on August 26, 1995 while at 100 percent Rated Thermal Power, Unit 2 received a turbine trip/reactor trip signal from a Main Turbine Moisture Separator High Level. was in progress with no abnormal alarms standing. Level alarms which normally precede the MSR High Level trip signal did not actuate. The turbine trip signal caused the reactor trip. <br /><br /> After the reactor trip, all safety systems operated normally in response to the trip signal. With the exception of the failure of the Nuclear Instrumentation Channel I Source Range to indicate the correct counts per second due to abnormally low indication, all post reactor trip responses were normal. The reactor was stabilized in Mode 3, Hot Standby, and repairs were performed. This event was determined to have no actual or potential adverse effect on the health and safety of the public.
316 | 3161995005 | 1995-08-29 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Cook 2 | P | WE | PO | 100 | On August 29, 1995 at 0924 with Unit in Mode 1 at 100 percent Rated Thermal Power, the South Control Rod Drive Motor Generator (CRD-MG) output breaker tripped via its directional overcurrent relay. This was followed by the automatic tripping of the North CRD-MG output breaker due to its overvoltage relay logic. Control Rod Drive Mechanisms (CRDM's) which allowed all control rods to insert into the core. The Reactor Protection System (RPS) detected the resulting rapid drop in Reactor power and initiated a Reactor trip signal based on the high negative rate logic. <br /><br /> After the Reactor trip, all Safety systems operated normally with the exception of two motor operated valves (MOVs) associated with the West Motor Driven Auxiliary Feedwater Pump (W MDAFP). These valves were in their normally open position at the time of the Reactor trip, and did not respond to a close signal following the trip. This resulted in higher than desired feed water flow to the #21 & #24 steam generators, causing an RCS cooldown to 535 degrees, 12 degrees below the normal RCS post-trip (no load) temperature of 547 degrees. <br /><br /> This event was determined to have no actual or potential adverse effect on the health and safety of the public.
316 | 3161995006 | 1995-09-08 | QR8 | Spurious Reactor Trip | [45 empty] | Cook 2 | P | WE | PO | 100 | On September 8, 1995 at 2125 hours, while Unit 2 Was at 100 percent Reactor Thermal Power, a reactor trip occurred on a manual reactor trip signal. The reactor trip signal resulted from a cognitive error by Operations personnel while supporting a surveillance test-on the Solid State Protection System (SSPS). The Reactor Operator improperly placed a reactor trip breaker control switch in the trip position while intending to close the breaker.<br /><br /> Operations personnel implemented plant procedures to verify proper response of the automatic protection systems and to assess plant conditions for initiating recovery actions. All safety systems operated normally in response to the trip signal, and the unit was stabilized in Mode 3, Hot Standby. <br /><br /> Administrative actions have been taken to lessen the possibility of a recurrence, and the Operations Department has developed an action plan to minimize the number of events caused by personnel errors. <br /><br /> It was determined that the health and safety of the public were not jeopardized by this event.
316 | 3161996005 | 1996-05-08 | QR5 | Turbine Trip | [45 empty] | Cook 2 | P | WE | SU | 7 | At 1144 hours on May 8, 1996, during performance of the Main Turbine overspeed trip test and with the reactor at 7 percent power, a Reactor Protection System actuation was received. The actuation was the result of an anticipated Main Turbine overspeed trip signal coincident with an unanticipated indication on one out of two channels of turbine impulse pressure equivalent to turbine power of greater than 10 percent of full power. This report is being submitted in accordance with 10CFR50.73(a)(2)(iv), as an event that resulted in actuation of an Engineered Safety Feature, including the Reactor Protection System. <br /><br /> This event was caused by a lack of detailed guidance in the overspeed trip test procedure. The lack of detail led to the improper operation of the operating device which resulted in a rapid increase in turbine impulse pressure and enabled the reactor trip from a main turbine trip circuit. When the turbine overspeed trip occurred, a reactor trip resulted. <br /><br /> All safety systems functioned as designed with the exception of three motor operated valves in lines from the East and West Motor Driven Auxiliary Feedwater pumps to Steam Generators 1, 3, and 4. These valves closed to their preset throttled position in response to spurious flow retention signals. These spurious signals were attributed to the rapid rise in system pressure when the two Motor Driven Auxiliary Feedwater pumps automatically started. <br /><br /> This event was evaluated and determined to have no adverse impact on the health and safety of the public.
316 | 3161997001 | 1997-03-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 100 | On March 11, 1997 at 1056 hours with Unit 2 at 100 percent Rated Thermal Power, an automatic reactor trip signal was initiated by the Reactor Protection System (RPS). The trip signal resulted from a #21 Steam Generator (SG) low level coincident with a Steam Flow/Feed Flow mismatch. An unplanned ESF actuation consisting of a second automatic start of the Turbine Driven Auxiliary Feedwater Pump (TDAFP) also occurred. This event is reportable in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in the automatic actuation of Engineered Safety Features (ESF), including the Reactor Protection System (RPS). <br /><br /> This event was caused by the failure of the controller for 2-FRV-210, due to static discharge. The controller for 2-FRV-210, a Taylor MOD 30, was replaced with a newly configured controller. Corrective Actions were completed for all Unit 2 Taylor controllers prior to restart. <br /><br /> No safety systems were out of service prior to the trip. After the reactor trip, all safety systems operated as designed. Normal off-site power was available and an automatic transfer to this source occurred after the Main Generator trip. This event was determined to have no safety significance, and to have no potential or actual effect on the health and safety of the public.
316 | 3162001004 | 2001-10-27 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Cook 2 | P | WE | PO | 8 | On October 7, 2001, a reactor trip occurred at 8 percent reactor power. The trip was the result of a loss of rod control system voltage. The cause of the loss of rod control system voltage was an open resistor at the input to the north control rod drive motor generator (CRD-MG) voltage regulator. The open resistor caused a low voltage transient when the north CRD-MG field collapsed. A protective auxiliary relay removed power from the south CRD-MG voltage regulator resulting in a loss of rod control system voltage. The loss of voltage caused all control rods to rapidly insert, thereby, initiating a Power Range, Neutron Flux, High Negative Rate trip from the reactor protection system (RPS). The RPS actuation was initiated by actual plant conditions that satisfied the requirements for the initiation of the trip, and was, therefore, a valid RPS actuation. The failed resistor was determined to be the result of a random component failure. The resistor was original equipment and inspection revealed no evidence of overheating or manufacturing defect. The defective resistor was replaced and, as a precaution, the remaining series resistor in the north CRD-MG along with the identical resistors in the south CRD-MG were replaced. This event was reported in accordance with 10 CFR 50.72(b)(1)(iv)(B).
316 | 3162002005 | 2002-05-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 100 | At 2301 hrs on May 12, 2002, Unit 2 tripped due to an instrument rack power supply failure. Specifically, the second of two redundant 24-volt direct current (VDC) power supplies to reactor control instrumentation control group cabinet 2-PS-CGC-16 failed. The failure of both power supplies caused steam generator (SG) feedwater regulating valve 2-FRV-210 to close. Unit 2 subsequently tripped on low water level in SG-21 coincident with low feedwater flow. In accordance with 10 CFR 50.72 (b)(2)(iv)(B), a four-hour ENS notification (Event #38915) was made to the NRC on May 13, 2002, at 0255 hours for an event or condition that resulted in an actuation of the reactor protection system (RPS) when the reactor is critical. As such, this LER is being submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(iv)(A) for a condition or event that resulted in an automatic actuation of the RPS system. The preliminary cause of this event was age-related failure of components within the power supplies. A contributing factor was that no provisions existed for periodic monitoring of the power supplies. This event had minimal safety significance since plant procedures and operator training provided sufficient direction for control room personnel to shutdown the plant and maintain it in a safe shutdown condition. The failed 24-VDC power supplies were replaced. The remaining 24-VDC control group power supplies in Unit 2 were inspected and one power supply was replaced. Routine tasks have been established to verify the availability of the 24-VDC power supplies for both Unit 1 and Unit 2.
316 | 3162002006 | 2002-07-22 | QL7 | Degraded condenser vacuum | [45 empty] | Cook 2 | P | WE | PO | 100 | At 0045 hours on July 22, 2002, Unit 2 tripped due to low condenser vacuum. At the time of the trip, operators were performing a flush of the main condensers in preparation for the upcoming biocide treatment of the circulating water system. In accordance with 10 CFR 50.72 (b)(2)(iv)(B), a four-hour ENS notification (Event # 39081) was made to the NRC on July 22, 2002, at 0233 hours for an event or condition that resulted in an actuation of the reactor protection system (RPS) when the reactor is critical. As such, this LER is being submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(iv)(A) for a condition or event that resulted in an automatic actuation of the RPS system. The apparent cause of the event is a previously unrecognized steam side heat transfer anomaly in "C" main condenser that has resulted in "C" North water box removing significantly more heat than in "C" South water box. Corrective actions to prevent recurrence of this event will be determined by an equipment root cause investigation to be performed after the steam side of the "C" main condenser has been inspected during the next Unit 2 outage of sufficient duration. Additional corrective actions, including preventive actions, may be developed based on the results of the investigation. If significant changes are identified as a result of completion of the root cause investigation, an update to this LER will be submitted. As a compensatory action, the main condenser water box flushing and isolation procedure has been revised to provide improved guidance for performing these activities to minimize the possibility of a unit trip. The safety significance of this event was minimal. Plant systems responded per design with no significant anomalies noted. Plant procedures and operator training provided sufficient direction for control room personnel to shutdown the plant and maintain it in a safe shutdown condition. There was no impact on the health and safety of the public as a result of this event.
316 | 3162003002 | 2003-02-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 100 | On February 5, 2003, at 2058 hours, Donald C. Cook Nuclear Plant (CNP) Unit 2 tripped due to the failure of both redundant 24 volt direct current (VDC) control group cabinet #3 power supplies. This caused the feedwater regulating valve for steam generator #23 to fail closed and the reactor to trip on a feed-flow/steam-flow mismatch coincident with low level in the #23 steam generator. All control rods inserted, the turbine tripped, and the auxiliary feedwater pumps started as expected. Following the reactor trip, the operators closed the main steam isolation valves to limit cooldown. This LER supplement is being submitted in accordance with 10 CFR 50.73(a) (2) (iv) (A) and NUREG-1022, Section 5.1.5. This LER reports the root cause, corrective actions to prevent recurrence, and safety significance of the event. The root cause of the event was age degradation of the Control Group III power supplies. Corrective actions included replacement of the control group power supplies and implementation of an optimized preventive maintenance program to address timely replacement of critical power supplies.
316 | 3152003003 | 2003-04-24 | QL4 | Loss of Non-safety-Related Cooling Water |  |  |  |  | X | [5 empty] | X | [10 empty] | X |  | X | [16 empty] | X |  |  |  |  | Cook 2 | P | WE | PO | 100 | On April 24, 2003, between 0255 and 0305 hours, a large school of alewives began impinging on the traveling water screens (TWS) located upstream of the common forebay of the circulating water (CW) and the essential service water (ESW) systems. As the volume of fish impinging on the TWS increased, the TWS system was overwhelmed. Differential pressure across the screens increased rapidly, resulting in most of the screens stopping due to either shear pin failure or tripping of breaker thermal overloads, and the eventual failure of multiple screen panels within the TWS system. As a result of the screen panel failures, the fish subsequently entered the suction of the CW and ESW pumps. Components serviced by the CW and ESW pumps began fouling. At approximately 0327 hours, Unit 1 was manually tripped due to fouling of the main feed pump condensers and at approximately 0330 hours Unit 2 was tripped due to degraded forebay conditions. Donald C. Cook Nuclear Plant (CNP) verified the availability of offsite power as specified by Action e of Technical Specification 3.8.1.1. However, the verification was not completed within one hour as required by the technical specifications. The root cause of the event included the lack of a fully-developed operational response to debris intrusion, the failure to maintain the TWS system, and the failure of CNP to address long-standing or repetitive equipment problems. Corrective actions include flushing and inspection of affected components, repair of the damaged TWS components, improvements in CNP's debris intrusion mitigation strategy, enhanced maintenance program for the TWS, and the development of action plans to address the top equipment reliability concerns. This condition is reportable in accordance with the reporting criteria established in 10 CFR 50.73(a)(2)(iii) and 10 CFR 50.73 (a) (2)(iv)(A) for the manual trip of both Unit 1 and Unit 2 reactors.
316 | 3162003005 | 2003-12-30 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 100 | On December 30, 2003, at approximately 1328 Eastern Standard Time, the Unit 2 reactor automatically tripped on low steam generator water level coincident with feed flow less than steam flow for Steam Generator #22. Just prior to the trip, the Control Room Instrument Distribution (CRID) IV inverter transferred to the alternate power supply. A Feedwater Isolation Relay (K666)(2), powered from CRID IV, opened. The opening of the relay initiated a seal-in closure signal to Steam Generator #22 and #23 Feedwater Isolation Valves (2-FMO-202 and 2-FMO-203), resulting in a loss of feedwater flow to Steam Generators #22 and #23 and produced a low steam generator water level trip coincident with feed flow less than steam flow. Following the reactor trip, the Unit Output Breakers failed to automatically open because a Main Turbine Stop Valve position indicator failed to provide a closed indication. The Unit Output Breakers were manually opened in accordance with the reactor trip response procedure. All safety components started and performed as expected. The initiator of the reactor trip was determined to be a momentary ground on the GRID IV bus, which occurred during the conduct of instrument calibration. The ground caused the automatic transfer of CRID IV to the alternate power source. The voltage drop on the CRID IV bus caused the Feedwater Isolation Relay to open. The root cause of the event has been determined to be inattention on the part of the Instrument and Control Technician who was performing the calibration. Corrective actions include the establishment of enhanced controls for the disconnecting and connecting of electrical leads.
316 | 3162004001 | 2004-03-29 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Cook 2 | P | WE | PO | 100 | On March 29, 2004, at 1404 hours, Unit 2 received an automatic actuation of the Reactor Protection System (RPS). The RPS actuation occurred while an operator was attempting to rack out the train A Reactor Trip Bypass Breaker (RTBB) during restoration from Solid State Protection System (SSPS ) testing. The direct cause of the event was human error. The operator who performed the breaker manipulation incorrectly inserted the breaker racking bar, causing a momentary ground of one phase of the rod control motor-generator set 260 VAC output. This de-energized the stationary gripper coils for multiple control rods, causing them to drop into the core, resulting in a Power Range Nuclear Instrument Hi-Negative rate RPS actuation. The Auxiliary Feedwater (AFW) System automatically started and functioned as designed. The reactor shutdown and automatic start of the AFW System was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) respectively (EN #40622). Corrective actions included inspection and repair of the RTBB and associated indicator circuits, and verification of operator proficiency with breaker operation prior to manipulation of an RTBB in the plant.
316 | 3162004002 | 2004-04-08 | QP5 | Excessive Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 48 | On April 8, 2004 at approximately 2215 Eastern Standard Time, Unit 2 reactor experienced an unplanned automatic reactor protection system (RPS) actuation, resulting in a plant trip from 48 percent power. Prior to the trip, Unit 2 was in the process of lowering power from 82 percent to 8 percent power level. The operating main feedwater pump was being controlled manually via the differential pressure (DP) controller. Failure to manually control DP within the prescribed values, caused all four feedwater regulating valves (FRVs) to begin modulating excessively. All four FRVs were placed in manual control to mitigate the feedwater flow oscillations. However, rising water level in number 24 Steam Generator reached the high level trip setpoint causing an automatic turbine trip which caused the automatic RPS actuation. Plant equipment responded as expected, including the start of the auxiliary feedwater system, except the main generator output breakers failing to open and a condensate leak developing in the main turbine condenser hotwell area. The main generator output breakers were manually opened in accordance with the reactor trip response procedure and the condensate leak was stopped by securing pumps in accordance with plant procedures. The root causes of the event were determined to be inadequate manual main feedwater DP control and inadequate communications between the control room operators and other shift personnel. Corrective actions include redefining and reinforcing standards for the conduct of operations and personnel action taken in accordance with appropriate performance management policies for the control room personnel involved. This event was reported in accordance with 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.72 (b)(3)(iv)(A).
316 | 3162005001 | 2005-11-08 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Cook 2 | P | WE | PO | 100 | At 0358 hours on November 8, 2005, Donald C. Cook Nuclear Plant Unit 2 experienced an automatic reactor trip due to reactor coolant pump bus undervoltage (UV). The trip resulted from problems with the main generator exciter slip ring brushes which caused a UV condition and tripped the reactor and main turbine. The B train Emergency Diesel Generator (EDG) automatically started and loaded B train emergency bus T21A (one of two B train emergency buses). However, the trip was complicated in that the other B train emergency bus, T21B, failed to energize automatically on the start of the B train EDG. The A train emergency buses transferred to reserve feed as expected. The A train EDG was out of service for scheduled maintenance. An additional anomaly occurred at 0510 hours when the EDG output breaker supplying the T21A bus opened and re-closed after 23 seconds without manual action. The cause of the event was poor brush contact on the exciter rotor. This resulted in a loss of main generator excitation, which caused a UV condition. The root cause was identified as inadequate exciter brush preventive maintenance. Corrective actions taken included repairs to the exciter, and investigation and repair of the B train EDG output breaker failures. This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A), "any event or condition that results in manual or automatic actuation of any systems listed ...," specifically reactor trip, auxiliary feedwater, and emergency AC electrical power system actuations. This report is also required per 10 CFR 50.73(a)(2)(i)(B), "any operation or condition which was prohibited by the plant's technical specifications." This is due to a latent defect in the EDG output breaker control circuit, revealed during this event, which rendered the EDG inoperable. It is also reported under 10 CFR 50.73(a)(2)(v)(A), as a condition which could have prevented the fulfillment of a safety function, for periods of time (approximately 16 hours in total) when both Unit 2 EDGs were inoperable simultaneously.
316 | 3162009001 | 2009-07-26 | QR6 | Manual Reactor Trip | [45 empty] | Cook 2 | P | WE | PO | 100 | On July 26, 2009, at 1506 hours, Donald C. Cook Nuclear Plant (CNP) Unit 2 Control Room Operators performed a manual reactor trip in response to a malfunctioning reactor coolant pump (RCP) seal. All control rods fully inserted and the auxiliary feedwater system (AFW) started and performed as designed. The reactor trip was uncomplicated and all major plant components functioned as designed; as such, there were no safety system functional failures. The reactor trip was reported in accordance with 10 CFR 50.72 (b) (2) (iv) (B) and the AFW actuation was reported in accordance with 10 CFR 50.72(b) (3) (iv) (A). The reactor trip and AFW actuation are reportable as a Licensee Event Report in accordance with 10 CFR 50.73 (a) (2) (iv) (A). As Control Room Operators were responding to indications of a malfunctioning RCP seal, they were procedurally directed to perform a manual reactor trip and then remove the RCP from service. The immediate cause of the trip was manual actuation due to a malfunctioning RCP seal. The root cause was a failure by the station to recognize that a buildup of corrosion products had the potential to enter the seal, causing failure. The seal assemblies in RCP 21 and RCP 22 were replaced. A plan has been developed and will be implemented for flushing the RCP seal components.
316 | 3162012002 | 2012-04-30 | QR5 | Turbine Trip | [45 empty] | Cook 2 | P | WE | PO | 91 | On April 30, 2012, at 2328 hours, during power ascension following a recent refueling outage, Donald C. Cook Nuclear Plant (CNP) Unit 2 Reactor tripped automatically from a trip of the main turbine. All control rods fully inserted and the auxiliary feedwater system (AFW) started and performed as designed. On May 1, 2012, at 0013 hours, the Main Steam Isolation Valves (MSIV) were closed and the Reactor Coolant System (RCS) temperature was controlled by the steam generator atmospheric relief valves (PORV). Closure of the MSIVs was based on cooldown of the RCS and recovered after closing the MSIVs. All major plant components functioned as designed with no safety system functional failures. The reactor trip was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and the AFW actuation was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). The reactor trip and the AFW system actuation are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A). The turbine trip was caused by the actuation of the main generator unit differential and overall differential lockout relays. The overall differential function of a multifunctional digital relay actuated and operated the lockout relays. The relay was installed during a recent refueling outage. The actuation was caused by an incorrect current transformer winding compensation setting within the relay. Action taken included correcting the relay setting.
316 | 3162013001 | 2013-07-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Cook 2 | P | WE | PO | 100 | On July 28, 2013, the Donald C. Cook Nuclear Plant Unit 2 reactor was operating at 100 percent power. At 1018, reactor operators manually tripped the reactor when reaching a low steam generator level threshold during a secondary plant transient event.<br /><br /> The secondary plant transient occurred when a steam supply valve closed to the Right Moisture Separator Reheater which resulted in feedwater heater level oscillations followed by Heater Drain Pumps tripping on heater low levels. This caused feedwater pump suction pressure to lower and automatically tripped the West Main Feedwater Pump. As a result, steam generator level lowered to 23 percent on the #4 Steam Generator. The reactor operators manually tripped the reactor based on a manual trip threshold for Steam Generator levels that was established by the Unit Supervisor.<br /><br /> The initiating cause of the steam supply valve closure and subsequent secondary plant transient was a loss of control air to the air operated valve resulting from fretting of the control air line.<br /><br /> The Reactor Protection System and the specified Auxiliary Feedwater System actuation was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). The valid actuation is reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A).
316 | 3152014003 | 2014-11-01 | QL7 | Degraded condenser vacuum | [45 empty] | Cook 2 | P | WE | PO | 100 | On November 1, 2014, at approximately 0249, Donald C. Cook Plant Unit 1 (U1) and Unit 2 (U2) reactors were manually tripped from 100 percent and 55 percent power, respectively, when high winds and high waves on Lake Michigan resulted in a heavy influx of dune grass and debris into the forebay which resulted in degraded forebay conditions, lowering forebay level, and damaged trash racks. Following the U1 trip, the U1 Turbine Driven Auxiliary Feed Pump (TDAFP) tripped unexpectedly three minutes following the automatic start. Following the U2 trip, the U2 Main Generator trip was performed manually when the automatic trip failed.<br /><br /> Corrective actions taken include cleaning and repair of damaged forebay trash racks and travelling water screens. Corrective maintenance also corrected the causes of the U1 TDAFP trip and the U2 Main Generator trip function. Planned corrective actions include revising plant procedures to provide a comprehensive approach to adverse lake conditions.<br /><br /> The manual Reactor Protection System actuation and the automatic Auxiliary Feedwater System actuation were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) (Event Notification 50587). The valid actuations are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A). The storm and lake conditions necessitating the reactor trips is reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iii).
316 | 3162015001 | 2015-04-23 | QR6 | Manual Reactor Trip | [45 empty] | Cook 2 | P | WE | SU | 2 | On April 23, 2015, at 0210, Donald C. Cook Nuclear Plant Unit 2 Reactor was manually tripped from approximately 2 percent of rated thermal power during plant restart following a refueling outage. Unit 2 Reactor was manually tripped due to the inability to maintain Average Reactor Coolant System Temperature above the Technical Specification (TS) required minimum Temperature for Criticality when two newly installed Steam Dump Valves failed open while being manually valved into service. The valves were subjected to, but not designed for, two phase flow. <br /><br /> The Root Cause has been determined to be that the modification process failed to identify and document all system operational vulnerabilities. The corrective action to preclude repetition is an enhancement of the Engineering Modifications procedure to require development and inclusion of a narrative to describe system operation, including key interfacing system operation. <br /><br /> The manual Reactor Protection System (RPS) actuation was reported via Event Notification 51004 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), and 10 CFR 50.72(b)(2)(i). The valid RPS actuation and the completion of the plant shutdown required by TS are reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(2)(i)(A) respectively.
316 | 3162016001 | 2016-07-06 | QK4 | Steam or Feed Leakage | [45 empty] | Cook 2 | P | WE | PO | 100 | On July 6, 2016, with the Donald C. Cook Nuclear Plant Unit 2 Reactor operating in Mode 1 at 100 percent power, the control room received a report of a steam leak on the Unit 2 B Right Moisture Separator Reheater (MSR) crossover piping and damage to the turbine building structure. This information resulted in a decision by the crew to manually trip the Unit 2 Reactor at 0038. The cause of the steam leak was the sudden failure of the balance bellows on the Unit 2 B Right MSR crossover expansion joint, which also resulted in damage to the west wall of the turbine building. <br /><br /> The Root Cause was determined to be an organizational failure to recognize the risk significance of, and to adequately correct or mitigate, previously identified vibration issues with the Unit 2 B Right MSR crossover expansion joint tie rod and bellows in a timely fashion. <br /><br /> This event is being reported in accordance with 10CFR 50.73(a)(2)(iv)(A) as a manual actuation of the Reactor Protection System and an automatic actuation of the Auxiliary Feedwater system.
316 | 3162018003 | 2018-05-07 | QR6 | Manual Reactor Trip | [45 empty] | Cook 2 | P | WE | PO | 30 | On May 7, 2018, Unit 2 was operating at approximately thirty percent power following completion of a refueling outage. The control room staff received a high-high level alarm in a moisture separator drain tank (MSDT) and manually tripped the reactor in accordance with plant procedures. Plant systems responded as expected. The plant was stabilized in hot standby conditions. <br /><br /> An investigation discovered condensate heater level column isolation valves were inadvertently left closed and not restored following system testing activities. This condition resulted in a loss of level control in the corresponding heater. Excess condensate could not drain from the heater and eventually backfilled through a steam supply line into the MSDT. This caused the drain flow capacity of the MSDT to be exceeded which resulted in corresponding high and high-high level alarms. The level column isolation valves were later returned to the open position which restored the condensate drain flow paths and cleared the alarms.<br /><br /> The manual reactor trip caused actuation of the Reactor Protection System and an automatic actuation of the Auxiliary Feedwater System. Therefore, the event is reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
316 | 3162019001 | 2019-07-21 | QR6 | Manual Reactor Trip | [45 empty] | Cook 2 | P | WE | PO | 17 | On July 19, 2019, Donald C. Cook Nuclear Plant (CNP) Unit 2 started experiencing degraded performance on the Unit 2 Non-Essential Service Water System (NESW), which affected one (1) NESW pump. On July 21, 2019, a second NESW pump on Unit 2 was affected. On July 21, 2019, a rapid downpower over approximately 40 minutes was conducted on Unit 2, and a manual reactor trip was initiated from 17 percent power to allow for investigation and repair of the degraded NESW System, before any thresholds were exceeded. The manual reactor trip was completed at 0826 EDT on July 21, 2019. <br /><br /> The manual Reactor Protection System (RPS) actuation was reported via Event Notification 54176 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). This manual RPS actuation is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as, "Any event or condition that resulted in manual or automatic actuation of the RPS." <br /><br /> The direct cause of the degraded NESW system performance was a high differential pressure on both Unit 2 NESW strainers, due to excessive loading of small mussels and plugged backwash lines. Both strainers were cleaned, backwashed lines flushed, and returned to service.
316 | 3162020003 | 2020-09-04 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | Cook 2 | P | WE | PO | 92 | On September 4, 2020, at 22:04, Unit 2 control room operators completed a planned power reduction from 100 percent to 92 percent reactor power in preparation to perform Main Turbine Stop and Control Valve testing. As Reactor Coolant System (RCS) pressure reached 2235 psig, one of two Pressurizer Spray Valves began to close as expected and the other valve traveled unexpectedly to the fully open position. The operators were unable to close the failed open valve and manually tripped the reactor at 22:42 due to lowering RCS pressure. RCS pressure continued to lower below the safety injection (SI) actuation setpoint and an automatic SI occurred. All safety systems responded as expected and RCS pressure recovered to normal. <br /><br /> The cause of the failed open valve was due to foreign material from the control air supply lodged in the positioner spool valve. The valve positioner and electro-pneumatic transmitter were replaced which returned the valve back into service. Planned corrective actions include installing point of use filtration upstream of susceptible valve positioners or replace associated regulating valves to include a filter. <br /><br /> This event was reported via Event Notification 54885 in accordance with 10 CFR 50.72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv)(B), and 10 CFR 50.72(b)(3)(iv)(A). This event is reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(ivXA).
316 | 3162020004 | 2020-10-12 | QL7 | Degraded condenser vacuum | [45 empty] | Cook 2 | P | WE | PO | 100 | On October 12, 2020, at 0026, Donald C. Cook Nuclear Plant Unit 2 Reactor automatically tripped from 100% power due to a Low-Low Steam Generator (SG) Water Level in #24 SG. <br /><br /> The initiating event for this trip was a Human Performance Error that resulted in a degraded Main Condenser Vacuum. Auxiliary Operators were in the process of realigning blowdown, when a procedure use error resulted in a reduction of Vacuum. Unit 2 Control Room Operators recognized the degrading condenser vacuum, and took action to raise Main Feedwater demand while directing field operators to close a valve to restore vacuum. Vacuum subsequently recovered; however, Main Feedwater Pump performance had degraded to the point that sufficient Feedwater flow could not be supplied to the SGs to avoid tripping on Low-Low SG Water Level in #24 SG. <br /><br /> The cause of this error was a procedure use error and the immediate corrective action was restoration of the SG Blowdown System to a normal operational alignment. This event was reported via Event Notification 54944 in accordance with 10 CFR 50.72(b)(2)(iv)(B), and 10 CFR 50.72(b)(3)(iv)(A). This event is also reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A).
316 | 3162021002 | 2021-06-22 | QR6 | Manual Reactor Trip | [45 empty] | Cook 2 | P | WE | PO | 100 | On June 22, 2021, Donald C. Cook Unit 2, was operating at 100 percent power. At approximately 2305 hours, equipment operators reported a steam leak in a crossover pipe at the Right Moisture Separator Reheater (MSR) joint that was unisolable. Operators manually tripped the reactor at 2331 hours. All safety systems and Engineered Safety Features equipment operated as expected. <br /><br /> Prior to the reactor trip, operators closed the Low Pressure Turbine (LPT) 'B' Left Reheat Steam Intercept Valve at 1040 hours, due to an electro-hydraulic control (EHC) fluid leak from the valve's hydraulic actuator. Following closure of the intercept valve, the EHC fluid leak from the hydraulic actuator was manually isolated. No abnormal system conditions were noted following closure of the valve. This valve closure is an abnormal system alignment. <br /><br /> A failure investigation determined that the steam leak occurred at a right MSR crossover piping expansion joint. The expansion joint protective liner was displaced downstream due to a failed weld that exposed the bellows to direct steam flow. <br /><br /> The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), System Actuation, due to the valid actuation of the Reactor Protection System (RPS) and the Auxiliary Feedwater System, as a result of the manual reactor trip.
317 | 3171987003 | 1987-01-27 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [6 empty] | X | [8 empty] | X | [21 empty] | X |  |  |  | Calvert Cliffs 1 | P | CE | PO | 100 | At 1809 on January 27, 1987 the unit was manually tripped due to decreasing Steam Generator levels, which resulted from a loss of Instrument Air. At 1816 the Reactor Coolant Pumps were stopped, because cooling water was isolated upon the loss of air pressure. Reactor Coolant system temperature was maintained by the use of Auxiliary Feedwater and manual control of the Atmospheric Dump Valves. At 1825 Instrument Air Pressure was restored, and two Reactor Coolant Pumps were started. At 1840 the remaining two Reactor Coolant Pumps were started and the unit was maintained in MODE 3 (Hot Standby). <br /><br />To prevent recurrence of this type of event an engineering analysis is being performed to identify modifications that can increase the reliability of the Instrument Air System, and the General Supervisor-Operations is reviewing this event with all operators.
317 | 3171987004 | 1987-02-01 | QR6 | Manual Reactor Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 50 | At 0035 on February 1, 1987, while operating at 50% power, the unit was manually tripped because of high pressurizer pressure. The high pressure resulted from a turbine runback, actuated by a low Main Generator Stator Coolant pressure. The Stator Coolant pressure, which is automatically maintained 3 psi below generator hydrogen pressure, was low because hydrogen pressure was lowered during an evolution to increase hydrogen purity (bleed and feed). <br /><br /> This event was caused by improper procedural guidance for operators, when reducing Main Generator hydrogen pressure. <br /><br />To prevent recurrence of this type of event the following corrective actions are being taken: <br /><br />1. Required reading has been issued to make all operators aware of this event. <br /><br />2. Changes have been made to plant operating procedures, to prevent reducing hydrogen pressure below the turbine runback setpoint. <br /><br />3. Procedural changes are being made to ensure setpoint changes are thoroughly reviewed for effects on plant operation.
317 | 3171987011 | 1987-07-14 | QP5 | Excessive Feedwater Flow | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | Unit 1 tripped automatically at 1345 on July 14, 1987 on high steam generator water level. The cause of the transient which resulted in the high steam generator water level was an excess feedwater cooling event combined with an overboration event. Prior to the transient, the unit was operating at 100% power. There are no similar events reported in an LER. <br /><br />Maintenance was performed on the 16A high pressure feedwater heater flow controller. After the maintenance was completed the level control valve failed to open, and the feedwater heater filled with water. This caused a power increase. In response to the power increase, the reactor operator borated the RCS. <br /><br />Because of an operator error, boration was not terminated after the initial injection. Due to the continuing boration a rapid drop in reactor power occurred. Recovery from the power drop was not possible and the unit was tripped. The reactor protective systems operated properly and the plant was brought to a safe shutdown condition. <br /><br />The following corrective actions will be implemented: 1) a review of the CVCS design will be performed and the results presented to POSRC. The design and operation of the mode selector switch will be part of this review; 2) a training module will be developed for the simulator to train the operators how to respond to a loss of the high pressure feedwater heaters; 3) Plant Operators will review this LER during a future training cycle.
317 | 3171987012 | 1987-07-23 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | At 1525 on July 23, 1987 a fault developed on one (Transmission Line 5052) of the two 500KV transmission lines connecting Calvert Cliffs Nuclear Power Plant to the company's bulk power distribution grid at Waugh Chapel Station. The circuit breakers for line 5052 at Waugh Chapel and Calvert Cliffs tripped to isolate the fault. In addition, circuit breakers at Calvert Cliffs for the other transmission line (line 5051) incorrectly tripped open. This resulted in isolating the generating plant from the power grid resulting in both reactors tripping on loss of load of all off site nonemergency AC power. All three Emergency Diesel Generators started automatically to power the vital 4KV buses. Emergency Operating Procedures 0 and 2 were initiated to place both reactors in a stable condition. At 1530 an Emergency Response "Alert" condition was declared. The event was downgraded to an "Unusual Event" at 1700 upon completion of a checkout of the 500KV switchyard. At 1723 off site electrical power was provided to a vital 4KV bus from the alternate off site power line. Normal off site power was restored at 1910 via transmission line 5051. The fault on transmission line 5052 was caused by a tree that came in contact with the transmission line. All trees in the area have been cut down to prevent recurrence. The cause of transmission line 5051 circuit breakers tripping incorrectly was determined to be the fault of a defective logic circuit card in the primary static relay panel. This circuit card allowed the relays to trip the circuit breaker despite the absence of a "Permissive Signal" from the corresponding relays at Waugh Chapel. This tripping function was disenabled (tripping function protection provided by backup relays) upon restoring transmission line 5051 to service. The tripping function was subsequently restored after swapping the repaired logic assembly with one from another location in the power grid.
317 | 3171987013 | 1987-09-11 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | At 0515 on September 11, 1987, while operating in MODE 1 at 100% power, the Unit 1 reactor automatically tripped on a low reactor coolant flow signal initiated by Reactor Coolant Pump 12A breaker tripping open. The RCP breaker trip was due to a failed surge capacitor. The surge capacitor was replaced and the pump returned to service on September 13, 1987. During the automatic shutdown of the unit, #12 Charging Pump failed to start on an automatic signal. The pump was manually started. The cause of the failure was a loose connection in the breaker which controls the pump starts. <br /><br /> The corrective action is to replace the RCP surge capacitors with inductors located at the RCP breaker switchgear. This is scheduled for the next refueling outage for each unit. The loose connection on the #12 charging pump breaker has been fixed and a program is under way to check all similar breakers for loose connections.
317 | 3171987015 | 1987-11-11 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | At 1626 on November 11, 1987 Unit 1 tripped from 100% power due to the failure of the east secondary bushing (H-3, C phase) of Transformer U-25000-12. The bushing apparently shorted due to weather related problems. The turbine generator tripped on transformer high-side leads differential. The reactor tripped on loss of turbine load. The plant was brought to a safe shutdown condition. Several unrelated problems were encountered during implementation of the safe shutdown procedures. <br /><br /> 1. The Turbine Bypass Valve controller did not operate properly. <br /><br /> 2. The plant computer was out of service during the event. However, strip chart recorders were functioning and provided the data necessary to properly analyze the event. <br /><br />3. No. 11 Atmospheric Dump Valve (ADV) stuck open as it was being manually cycled after the trip. <br /><br />4. AFAS actuated but did not lock in. However, the motor driven auxiliary feedwater pump (No. 13) did start and was secured following verification of main feedwater flow <br /><br />. Corrective actions are as follows: <br /><br /> - The ADV is being scheduled for a maintenance overhaul. <br /><br /> - A Facilities Change Request (FCR 84-149) has been generated to install a time delay on the motor driven auxiliary feedwater pump to prevent unnecessary starts. <br /><br />- An investigation to determine and correct root cause of the vibration of the turbine bypass valves has been planned.
317 | 3171988006 | 1988-07-15 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 89 | At 0305, July 15, 1988, Calvert Cliffs Unit 1 (89% power) tripped on Loss of Load when its turbine tripped. The turbine tripped when maintenance personnel improperly isolated level switches on #12C Feedwater Heater. The maintenance procedure used was unclear and, therefore, misinterpreted by the technicians. <br /><br /> During the trip recovery, operators discovered #12 Atmospheric Dump Valve (ADV) stuck open. It was manually isolated. The valve internals were inspected and repaired. The failure was caused by improper adjustment of valve stroke. All installed ADVs have been properly adjusted. <br /><br /> CORRECTIVE ACTIONS <br /><br />1. Maintenance Planners will be trained in formulating clear maintenance instructions. <br /><br />2. Specific instructions will be written for isolating instrumentation that could directly cause a reactor trip. <br /><br />3. At the discretion of the shift supervisor, a briefing will be held prior to performing directly trip-sensitive maintenance. <br /><br />4. Directly trip-sensitive maintenance will be performed under the direction of a maintenance supervisor or senior maintenance individual. <br /><br />5. Upper isolation valves for feedwater heater level switches capable of initiating a main turbine trip (feedwater heaters 11, 12, 21, 22) will be locked open.
317 | 3171988009 | 1988-08-24 | QP5 | Excessive Feedwater Flow | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | At 2332, August 24, 1988, Calvert Cliffs Unit 1 (100% power) tripped on Loss of Load when its Main Turbine tripped on high Steam Generator level. The Main Turbine tripped when the air line on #12 Main Feed Regulating Valve failed and the valve failed to the full open position causing a high level in #12 steam generator. The air line to the feed regulating valve failed due to vibration and stress. <br /><br /> Corrective Actions <br /><br /> 1. Pressure switch 1-PS-1121 was relocated and mounted on a secure structure to minimize feed header vibration on the airline. <br /><br />2. A walkdown was performed on selected components to identify and correct the location of component instrument air lines subject to excessive stress. <br /><br />3. The tubing installation standard will be improved to provide detailed guidance on tubing configuration, support, bending, and connecting. <br /><br />4. Upon development of adequate standards, an evaluation will be done of other air supply installations, the failure of which could lead to a trip.
317 | 3171988012 | 1988-11-14 | QR6 | Manual Reactor Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 70 | At 0327 on November 14, 1988, while operating at 70% power, a turbine runback was actuated by low stator coolant pressure. At 0329, the Shift Supervisor ordered the reactor tripped because of increasing pressurizer pressure. The low stator coolant pressure that caused the runback resulted from a reduction in the generator hydrogen pressure during a hydrogen feed and bleed procedure. During the previous maintenance cycle (June 1988), the low stator coolant pressure alarm had been set at 56 PSIG, 12 PSIG above the correct setpoint. <br /><br />CORRECTIVE ACTIONS <br /><br /> 1. The setpoint file has been revised to correct the design setpoint for the low stator cooling pressure. <br /><br />2. Other safety related and turbine trip setpoints have been reviewed to determine whether offsets have been correctly applied. <br /><br /> 3. The format of the setpoint file will be modified to provide clear, consistent information. <br /><br />4. The Setpoint Control Procedure will be amended to incorporate the lessons learned from this event. <br /><br /> No Technical Specification limits were exceeded and there is minimal safety significance associated with this event.
317 | 3171991003 | 1991-10-01 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 93 | On October 1, 1991 Calvert Cliffs Unit 1 tripped from 93 percent power due to low Steam Generator (SG) water levels. The low SG water levels resulted from a loose fuse in the power supply to 12 Feedwater Regulating Valve (FRV) differential pressure (dp) controller and 12 Steam Generator Feed Pump (SGFP) turbine speed controller. A bent fuse clip caused an electrical discontinuity. The fuse holder has been replaced and personnel whose duties involve fuse manipulation will be trained on proper fuse installation and removal.
317 | 3171992008 | 1992-11-24 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On November 24, 1992, at 2:18 p.m., Calvert Cliffs Unit 1 automatically tripped from 100 percent power due to a ground overcurrent fault in the isolated phase (isophase) bus duct system. The fault occurred when an upper isophase bus duct inspection window came loose and fell into the duct. Ground protection circuitry tripped the main generator and the main turbine. The reactor protective system tripped the reactor on loss of turbine load. This event did not result in any significant safety consequences. Operations personnel implemented established emergency operating procedures and placed the plant in a safe shutdown condition. The apparent cause of this event is that someone stepped on and loosened the window during a recent maintenance activity in the area. Normal duct vibration probably freed the glass. Immediate actions were taken to quarantine the area, initiate an event investigation, and conduct necessary repairs. Actions to prevent recurrence and inform plant personnel of the potential personal safety consequences of this event are in progress.
317 | 3171993003 | 1993-06-10 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On Thursday, June 10, 1993 at 8:28:13 a.m., a flashover relay in the Calvert Cliffs switchyard actuated, causing the loss of the 500 kv "Red" bus feeding Unit 2. Unit 2 immediately tripped on low coolant flow. Unit 1 was manually tripped 25 seconds later by operators anticipating a total loss of offsite power. <br /><br /> The most probable cause of the Unit 2 trip is induced vibration of the flashover relay. The decision to trip Unit 1 resulted from the Control Room Supervisor's having concluded that a loss of offsite power was underway. <br /><br /> We will train appropriate personnel on avoiding inadvertent relay actuation. We will minimize the protective features left operative when breakers are opened for extended periods. We will evaluate improvements to operator training.
317 | 3171993004 | 1993-06-11 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 16 | On June 11, 1993, Unit 1 tripped due to an automatic actuation of the Reactor Protection System (RPS). An RPS loss of load signal was generated when the turbine tripped due to a low pressure feedwater heater (FWH) high level turbine trip signal. The signal was generated because the FWH high level dump (HLD) valve handswitch was left closed during startup. The unit was at 16 percent power.<br /><br /> A cause of the event was that opening the FWH HLD valves for plant startup was not adequately proceduralized. One contributing factor was that one operating crew questioned the valves position but did not effectively follow-up on the question or pass it along to the next crew who did not detect the improper handswitch positions. Procedure changes were made to open the appropriate FWH HLD valves during plant startup. The design of the FWH high and high-high level alarm circuits was reviewed. Reactor trip and normal shutdown procedures and valve lineups will be reviewed for similar valve position problems. Troubleshooting of the FWH water level alarm circuits will be performed.
317 | 3171994001 | 1994-01-24 | QR8 | Spurious Reactor Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On January 24, 1994, at 0926, Calvert Cliffs Unit 1 experienced a reactor trip and partial actuation of system ZB of the Engineered Safety Features Actuation System (ESFAS). The reactor trip and ESFAS actuation occurred due to fluctuations in the output voltage from 12 120 VAC Vital Bus Inverter. The inverter output voltage fluctuated due to a defective voltage regulator board within the inverter. At the time of the event, Unit 1 was at 100 percent power with normal operating temperature and pressure. <br /><br /> Troubleshooting after the event identified the defective regulator board. The board appeared to be defective either due to a loose fuse in the voltage feedback circuit or due to a screw found wedged between the boards of the card. Additional inspections identified a loose capacitor and defective oscillator board. <br /><br /> Corrective actions include the inspection of the other inverters on Unit 1 and 2, replacement of the inverter with upgraded models, and an evaluation to determine if debris intrusion controls for the inverters are adequate.
317 | 3171994006 | 1994-06-16 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On June 16, 1994, Calvert Cliffs Unit 1 tripped from 100 percent power due to an automatic actuation of the Reactor Protection System (RPS). The RPS signal was the result of low steam generator water levels due to feedwater shrink after all four main turbine stop valves (MTSVs) unexpectedly closed during performance of a weekly MTSV test. After the trip, steam generator levels trended downward with Steam Generator 12 level decreasing more rapidly than Steam Generator 11 level. About eight minutes after the trip, the auxiliary feedwater system actuated, restoring positive level trends in both steam generators. <br /><br /> Troubleshooting efforts did not positively identify the specific hardware cause of the MTSVs closing. Subsequent to this event, another trip of the Unit occurred on July 19, 1994, due to MTSV closure with no testing in progress. The root cause analysis of these two events have been combined. The results will be provided in the supplement to LER 317-94-007 concerning the July 19 event.
317 | 3171994007 | 1994-07-19 | QR5 | Turbine Trip | [6 empty] | X | [19 empty] | X | [18 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On July 19, 1994 at 1824 Calvert Cliffs Unit 1 tripped from 100 percent power due to a Reactor Protection System (RPS) actuation. The RPS actuation was the result of low steam generator water levels due to level shrink after all four main turbine stop valves (MTSV) unexpectedly closed. During the resulting transient both Reactor Coolant System (RCS) power-operated relief valves opened and one code safety relief valve (RV) opened, closed, and then began leaking by its seat at approximately 25 gpm.<br /><br /> The event did not result in any significant potential or actual nuclear or personnel safety consequences.<br /><br /> Short-term corrective actions to support a safe Unit restart were completed. The RV manufacturer has initiated process improvements to prevent recurrence of inadequate staking of a disc holder to bellows assembly inside the RV. The root cause of the MTSV closure has been incorporated into an ongoing turbine EHC Systems improvement effort.
317 | 3171995002 | 1995-06-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On Friday, June 16, 1995 at 1917 hours, Calvert Cliffs Unit 1 was manually tripped following the loss of the 12 Steam Generator Feed Pump (SGFP). Following the reactor trip, 11 SGFP tripped on high discharge pressure and the Auxiliary Feedwater Actuation System automatically actuated. <br /><br /> The root cause of this event was degradation of the 12 SGFP overspeed trip mechanism due to wear over many years. <br /><br /> The overspeed trip mechanism was repaired and Unit I restarted. The preventive maintenance procedure for overhauling the SGFP was revised to require examination of the trip mechanism. A review will be conducted to identify similar configurations and verify appropriate preventive maintenance. The circumstances of this event will be factored into an ongoing effort to improve the preventive maintenance program.
317 | 3171995005 | 1995-11-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On November 9, 1995 at 1457 hours, an alarm notified Operators of a high Steam Generator (SG) 11 level (+15 inches). Operators verified that SG 11 level was increasing and attempted to place its feedwater regulating valve controller in the manual mode without success. Steam Generator 11 level increased to approximately +35 inches and the reactor was manually tripped.<br /><br /> The cause of the trip was a failure of digital feedwater control module FIC-1111. Testing determined the most probable cause was electromagnetic interference. A comparison of the as-installed input/output/power cabling found it was not shielded in accordance with the vendor technical manual. Electromagnetic interference can induce a fault causing the FIC-1111 output signal to ramp up, slowly opening the SG 11 feedwater regulating valve.
317 | 3171995006 | 1995-11-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On Thursday, November 16, 1995, at approximately 2252 hours, Calvert Cliffs Unit 1 was manually tripped following the loss of the 12 Steam Generator Feed Pump (SGFP). Unit 1 was operating at 100 percent power at the time of the trip. <br /><br /> At approximately the same time 12 SGFP tripped, the pump's standby lube oil pump started due to a pressure decrease in the oil system. A troubleshooting team determined oil losses from the SGFP trip mechanism and turbine thrust allowed oil pressure to drop and to trip the pump before the standby pump could restore pressure. The cause for the initial oil pressure decreases has not been determined. <br /><br /> The trip mechanism and thrust for the pump were cleaned and adjusted. A check valve was also installed in the control oil portion of the system to further increase the trip margin. Unit 1 was restarted on November 20, 1995, using 11 SGFP; 12 SGFP was returned to service on December 3, 1995
317 | 3171997009 | 1997-10-24 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Calvert Cliffs 1 | P | CE | PO | 100 | On October 24, 1997 at 0917 a.m., Calvert Cliffs Unit 1 automatically tripped on low condenser vacuum when the condenser vacuum breaker unexpectedly opened. The plant was brought to a safe shutdown condition. This event resulted in no significant consequences to the health and safety of the public. At the time of the event, Unit 1 was operating at 100 percent power. <br /><br /> The cause of this event was a failure to properly terminate an electrical lead on the condenser vacuum breaker handswitch during prior handswitch maintenance. The Plant General Manager formed a Significant Incident Finding Team to investigate. Over 200 similar connections were inspected for a similar deficiency. Additional corrective actions will be taken once the results of the Significant Incident Finding Team investigation are finalized.
317 | 3171999004 | 1999-07-24 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | At 1438 on July 24, 1999, Unit 1 tripped from 100 percent power due to electrical arcing (flashover) across the No. 12 Main Transformer (U-25000-12) A-phase 500 kV bushing. The main generator output breaker opened, and the Unit 1 Reactor tripped on loss of turbine load. A thunderstorm was in progress at the time of the Unit trip with high winds and heavy rain. Witnesses observed a lightning strike near the affected transformer. Lightning apparently struck the A-phase 500 kV transmission line near the transformer, increasing the electrical potential beyond the insulating capabilities of the bushing, creating an electrical arc around the bushing. The arcing across the A-phase bushing affected the A-phase current flow. Protective relays sensed the abnormal condition, and opened two Switchyard Breakers (552-22 and 552-23), the Generator Field Breaker, and the Exciter breaker. Operators responded appropriately and plant systems functioned as designed. The plant was brought to a safe shutdown condition.
317 | 3171999006 | 1999-09-22 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Calvert Cliffs 1 | P | CE | PO | 100 | On September 22 1999, at 9:08 a.m., Calvert Cliffs Unit 1 was manually tripped from 100 percent power in response to loss of main feedwater, which occurred when a circuit breaker supplying two cross-tied non-vital 480 volt motor control centers (MCCs) tripped on overload and de-energized the lube oil pumps for both main feedwater pumps. Water level was maintained in both steam generators by the auxiliary feedwater system. The MCCs had been cross-tied to perform maintenance on one of the MCCs feeder breakers. The electrical loading from both MCCs exceeded the trip rating of one feeder breaker because the evolution was performed at power without first having shed the excess loads. Operators responded appropriately to the loss of feedwater and plant systems functioned as designed after the trip. The root causes of this event include less than adequate trip risk assessment and weaknesses in the electrical maintenance training program. Corrective actions include evaluating the trip risk assessment process for enhancements and assessing the training needs of electricians to improve knowledge levels in the area of electrical theory application.
317 | 3172000001 | 2000-01-14 | QR8 | Spurious Reactor Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | At 0950 on January 14, 2000, Calvert Cliffs Unit 1 tripped from 100 percent power due to a failure of the No. 11 Motor Generator (MG) Local Voltage Adjust Handswitch. Contacts closed on the handswitch causing No. 11 MG Voltage Regulator to raise the output voltage, increasing the voltage on the reactor trip bus. The output voltage increased to the setpoints of both the Nos. 11 and 12 MG sets' Overvoltage Relays, opening the output contactors of both MG sets. With both MG output contactors open, the reactor trip bus had zero voltage, causing control element assemblies to insert into the core. Operators responded appropriately and primary plant systems functioned as designed. The plant was brought to a safe shutdown condition. Number 11 MG's Local Voltage Adjust Handswitch and Voltage Regulator card was replaced. Both MG sets were meggered, bridged, and load tested. The three remaining voltage control handswitches on Unit 1 were inspected and no wear similar to that of the failed handswitch was found. The unit was restarted January 15, 2000.
317 | 3172000005 | 2000-09-10 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | At 2123 on September 10, 2000, Calvert Cliffs Unit 1 tripped from 100 percent power due to a spurious signal from Channel A of the Engineered Safety Features Actuation System Steam Generator Isolation Signal. A logic module in the Steam Generator Isolation Signal produced a spurious signal that closed the Main Steam Isolation Valves. The closed Main Steam Isolation Valves created shrink in both steam generators and the Unit 1 reactor tripped on low steam generator water level. Operators responded appropriately and primary plant systems functioned as designed. The plant was brought to a safe shutdown condition. The suspect Channel A Steam Generator Isolation Signal logic module was replaced and the new module was post-maintenance tested satisfactorily. The suspect logic module was sent to the vendor for testing and destructive analysis. The unit was restarted September 12, 2000. A detailed root cause analysis is in progress to determine causal factors, generic implications, and establish additional corrective actions, as required.
317 | 3172002003 | 2002-07-24 | QR6 | Manual Reactor Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On July 24, 2002, at approximately 1338 hours, Unit 1 received a low level alarm on 11A Reactor Coolant Pump (RCP) motor upper bearing oil reservoir. At approximately 1620 hours, Unit 1 Control Room Supervisor ordered a rapid downpower of Unit 1 in response to indications of increasing RCP motor thrust bearing temperatures. At 1628 hours, the Unit 1 Control Room Supervisor ordered a manual trip of Unit 1 when 11A RCP motor thrust bearing temperature reached 195 degrees Fahrenheit, in accordance with plant operating instructions. Unit 1 was manually tripped and all systems responded satisfactorily, with the exception of a turbine bypass valve, which closed slowly, causing Unit 1 Steam Generator pressures to approach the point of operator action to shut the main steam isolation valves. This event was caused by the failure of a butt weld on an RCP motor oil cooler line. The weld failure resulted in a through-wall crack that allowed lubricating oil to drain from the reservoir. This loss of oil resulted in oil starvation of the thrust bearing and subsequent overheating of the RCP motor thrust bearing.
317 | 3172004001 | 2004-03-20 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [27 empty] | X |  |  | X | Calvert Cliffs 1 | P | CE | PO | 100 | At 13:40 on March 20, 2004, Calvert Cliffs Unit 1 tripped from 100 percent power after Bus 1Y09 was grounded during scheduled maintenance. While replacing a chart recorder in a Control Room cabinet, a power lead feeding the recorder became pinched between the recorder and its case. The insulation on one of the power leads was cut, exposing the live power lead, and a short to case was experienced. This resulted in a loss of 11 Digital Feedwater Automatic Bus Transfer bus which in turn resulted in the deenergization of the 11 Main and 12 Backup Central Processing Units for the digital feedwater system. Mechanical binding of the 11 Feedwater Regulating Valve positioner selector solenoid valve resulted in a loss of signal to the 11 Feedwater Regulating Valve, which immediately began closing. The 11 Steam Generator water level lowered quickly, resulting in an automatic plant trip. The root cause of the trip lies in Human Performance in the area of work practices and design control. Corrective actions include procedure changes to improve risk management of maintenance, on-line testing of components, and monitoring plans for trip sensitive components. Unit I was restarted and paralleled to the grid on March 22, 2004 at 01:03.
317 | 3172005002 | 2005-03-01 | QR6 | Manual Reactor Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 15 | On March 1, 2005 during a planned Unit 1 power reduction to Mode 2 for performance of maintenance on 11 Moisture Separator Reheater drain tank vent line piping, a manual reactor scram was initiated from 15 percent power. An automatic turbine trip followed the manual reactor scram as designed. The reactor was manually scrammed per Abnormal Operating Procedure-7E "Main Turbine Malfunction," when bearing number 5 exceeded 12 mils vibration. The excessive vibration was due to rotor bowing caused by friction heat developed during rotor rubbing. The rubbing most likely developed because the packing to rotor clearances were tight and the steam path was subjected to temperature transients causing shell thermal distortions. Corrective actions include review of previous turbine roll ups/shutdowns for rub levels and rub locations, and incorporating lessons learned from this event into the appropriate operating instruction. The turbine was placed on turning gear during the maintenance outage and was returned to service without problems. The Unit 1 reactor was restarted and paralleled to the grid on March 2, 2005 at 10:30 am.
317 | 3172006004 | 2006-12-12 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On December 12, 2006 at 0907 a.m., Unit 1 was manually tripped due to a pressure transient on the primary system during performance of a turbine control system maintenance activity. Subsequent trouble-shooting identified a wire was broken at the wire-to-connector interface in the electrical cabinet to Turbine Control Valve 3. The broken wire resulted in inaccurate position feedback and initiated control valve closure, which caused the pressure transient. The wire was repaired and additional inspections were performed to verify there were no other broken wires. The turbine control system was tested to verify correct response and returned to service. Unit 1 was returned to service December 16, 2006.
317 | 3172010001 | 2010-02-18 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 93 | On February 18, 2010, at 8:24 a.m., Unit 1 experienced an automatic reactor trip from 92.8 percent power. The 12B Reactor Coolant Pump (RCP) tripped and the Reactor Protective System actuated on Reactor Coolant System low flow. The 12B RCP tripped due to a phase to ground short near one of the current transformers for the 12B RCP bus 14P differential/ground current protection. The ground fault was not isolated close to the source due to a failed ground protection relay in breaker 252-2202 the feeder breaker from Service Transformer P-13000-2 to the Unit 1 RCP buses. This resulted in Service Transformer P-13000-2 being deenergized. The loss of P-13000-2 resulted in a loss of the normal power supply to 14 4 kV bus. This caused the 1B Emergency Diesel Generator to start and supply power to 14 4 kV bus. The cause of the fault was a phase to ground short near one of the current transformers for the 12B RCP bus differential/ground current protection due to water intrusion. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation and automatic start of the 1B Emergency Diesel Generator. Corrective actions include revision to a relay test procedure and improved management of roof issues.
317 | 3172010003 | 2010-05-12 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On May 12, 2010 at 13:51, Unit 1 experienced an automatic reactor trip from 100 percent power, when the Reactor Protective System actuated on high pressurizer pressure due to a complete load rejection. At the time of the event, maintenance was being performed in the switchyard requiring two 500 kV breakers to be open with a third 500 kV breaker (552-22) closed, thus allowing Unit 1 main turbine generator output to the grid. However, due to a loose connection in the 125 VDC distribution panel board for the breaker disconnect switches, breaker 552-22 tripped open upon receiving a trip signal from its trip circuitry, resulting in the complete load rejection condition. The root cause of the event was a loose electrical connection in the 125 VDC distribution panel board. After the trip, one of the pressurizer safety valves leaked. The Unit was taken to Mode 5 to repair the leaking pressurizer safety valve. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to a valid actuation of the Reactor Protective System. Corrective actions include checking the electrical connections in the 125 VDC distribution panel for tightness, increasing the time delay to the re-trip feature of the subject type relays, replacing the disconnect bucket and revising the risk management procedure.
317 | 3172011001 | 2011-08-27 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On August 27, 2011, at 2248 eastern daylight time, Unit 1 experienced an automatic reactor trip from 100 percent power. The Reactor Protective System actuated on loss of load. The loss of load occurred due to a phase-to-phase short circuit on the main transformer when main transformer lines were struck by dislodged Turbine Building siding caused by winds associated with Hurricane Irene. Immediately following the short circuit, 14 Containment Air Cooler stopped operating. Shortly after the plant trip occurred, 1A Emergency Diesel Generator was declared inoperable due to a shorted speed switch. The root cause analysis performed to address this event concluded that the Turbine Building Northwest corner siding was not installed per design during original construction. This resulted in a weaker siding connection to the Turbine Building structure, allowing the siding to come off in wind speeds less than design. At Calvert Cliffs, there have been no recent similar events involving a reactor trip associated with severe weather. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation. Corrective actions include testing and inspection of the main transformer, replacement of B and C phase high line drops to the main transformer and inspection and repair of electrical connectors on the 1A Emergency Diesel Generator.
317 | 3172014001 | 2014-01-21 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On January 21, 2014, at 9:25 p.m., Unit 1 experienced an automatic reactor trip from 100 percent power. The reactor trip occurred when 13 kV Service Bus 21 deenergized due to a ground fault on feeder breaker 252-2104. The loss of the service bus caused a loss of power to safety-related 4 kV Bus 14, which caused an automatic start of the 1B Emergency Diesel Generator to power 4 kV Bus 14. When the 1B Emergency Diesel Generator repowered 4 kV Bus 14, the resultant voltage spike caused the main turbine controls to reboot. This deenergized the electrical trip device solenoids, depressurized the emergency trip supply header, and initiated turbine control valve closure. During this time, the turbine controls could not communicate a trip signal to the Reactor Protective System and the Unit 1 reactor subsequently tripped on high reactor coolant system pressure.<br /><br /> The root cause was determined to be an electrical design vulnerability not anticipated in the original design, where a voltage spike can result in turbine controls rebooting. No actions were required to return systems to pre-event normal status. There have been no recent similar events.
317 | 3172014006 | 2014-05-01 | QR8 | Spurious Reactor Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On May 1, 2014 at 1016, Unit 1 experienced an automatic reactor trip from 100 percent power. Surveillance Test Procedure M-212E-1, Reactor Protective System Matrix Functional Test was being performed during the time of the trip. Two reactor trip circuit breakers opened as expected for the in-progress testing and approximately four minutes later, the remaining six reactor trip circuit breakers opened, resulting in a reactor trip. Operator actions were appropriate and in accordance with procedures. Plant response to the trip was uncomplicated. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation. The root cause was determined to be that the contacts on the matrix relay trip test pushbuttons had silver sulfide contamination causing erratic contact resistance. Corrective actions will replace the remaining matrix relay trip test pushbuttons, assign locations codes, and develop a maintenance strategy to these components. No similar licensee event reports were identified.
317 | 3172015002 | 2015-04-07 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On April 7, 2015 at 1239 Calvert Cliffs experienced a dual unit trip due to an off-site grid disturbance resulting in an undervoltage condition that caused all four Engineered Safety Features (ESF) Buses to trip. Due to this condition, all of the emergency diesel generators (EDGs) started and loaded with the exception of 2B EDG which started but tripped due to a failed electronic speed switch in the startup circuitry. The associated 4 kV ESF bus was repowered from the normal power source. Additionally, while 2A EDG energized its respective 4 kV ESF bus, the associated shutdown sequencer failed to start 21 Saltwater pump which was subsequently manually started. Unit 1 tripped on loss of all power to generator excitation and all required safety systems responded as designed. Unit 2 tripped due to generator loss of load and is classified as an unplanned scram with complications as 24 4 kV ESF bus was de-energized for greater than 10 minutes. The failed 2B EDG speed switch and 2A EDG shutdown sequencer were replaced and tested satisfactorily. Future corrective actions include to design and implement a speed switch modification to eliminate the single-point failure risk, and to procure and install a newly manufactured sequencer in each channel.
317 | 3172016001 | 2016-01-25 | QL6 | Condenser Leakage | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 10 | At 0313 on January 25, 2016, Operators initiated a manual reactor trip on Unit 1 due to high levels of sodium in the Feedwater and Condensate systems that exceeded the threshold levels in Abnormal Operating Procedure 10, Abnormal Secondary Chemistry Conditions. Subsequent investigation determined the high sodium levels were due to a condenser tube leak located in 13A Condenser. The failed condenser tube and several adjacent tubes were plugged and Unit 1 was returned to power operation at 2220 on January 25, 2016. During the 2016 Unit 1 refueling outage eddy current testing confirmed a circumferential crack on the failed condenser tube. The apparent cause is that the condenser tube failure was vibration induced. Radial stakes were installed to help limit future vibration. A causal analysis will be completed following the Unit 1 refueling outage.
317 | 3172016003 | 2016-05-31 | QR8 | Spurious Reactor Trip | [45 empty] | Calvert Cliffs 1 | P | CE | PO | 100 | On May 31, 2016 at 1626, Calvert Cliffs Unit 1 experienced an automatic reactor trip. The cause of the trip was a spurious high level steam generator signal due to a failed Steam Generator 11 Channel B High Level Turbine Trip Under Voltage Logic Module, 12/4BL-XA27. The spurious high level trip signal resulted in a turbine trip followed by an automatic reactor protection system trip on loss of load. The failed under voltage logic module was sent off-site to the vendor to conduct a failure analysis. The analysis identified two most probable causes for the failure. The first most probable cause was due to an intermittent failure of an integrated circuit of the under voltage logic module. The second most probable cause was due to an inadvertent solder bridge between a pin on the integrated circuit chip and the board. A refurbished logic module was installed and subsequently tested prior to the unit returning to power. The corrective action planned to prevent recurrence is to replace the current Engineered Safety Features Actuation System (which includes the non-safety high level turbine trip) with a system that will eliminate single point vulnerabilities within this system.
318 | 3181987002 | 1987-02-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 94 | On February 28, 1987, at 2356, the steam generator downcomer level lead/lag unit of the #21 Feedwater Regulating Valve (FRV) control system failed to an output of +9.5 inches steam generator level. The output should have been +.5 inches. The level dominant Three Element Feedwater Control System automatically responded, in a proper manner, by closing #21 FRV. The closed FRV caused #21 Steam Generator level to decrease at a rate of approximately 0.8 inches per second. The closing of #21 FRV also caused a high differential pressure across the valve. The rapid increase in FRV differential pressure caused #22 Steam Generator Feed Pump (SGFP) to automatically reduce speed (#21 SGFP was in manual control). Control room operators were alerted when #22 SGFP Turbine Speed Hold or System Trouble Alarm sounded. Operators took action to feed the steam generator but, approximately 15 seconds after the alarm, the reactor tripped on low steam generator water level. All reactor safety systems functioned as expected. Both steam generator feed pumps tripped shortly after the reactor trip on High Discharge Pressure. Auxiliary Feedwater Actuation occurred. Emergency Operating Procedures were carried out and the plant was returned to a stable condition. <br /><br /> The failed lead/lag unit was replaced. It was sent to the vendor, where the root cause was found to be a failed electrolytic capacitor. Redundant analog trains or a digital control system are being considered to prevent recurrence.
318 | 3181987005 | 1987-07-03 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 7 | Prior to startup, Calvert Cliffs Unit 2 main turbine generator controller was calibrated using a new Westinghouse simulator. Results required setting the Initial Valve Position Percent micrometer at .162. This setting should cause the turbine generator to initially pick up 5 percent of rated load. <br /><br /> On July 3, 1987, with reactor power at 7 percent, the main breaker was shut. The generator picked up approximately 100 megawatts, or 12 percent of rated load, and caused a sudden increase in steam demand resulting in quickly lowering steam generator pressure. <br /><br /> The Operators took action to reduce steam demand. Turbine Bypass Valves were shut and turbine load was manually lowered, but the reactor tripped on Low Steam Generator Pressure. <br /><br /> Following discussion, the Initial Valve Position Percent micrometer was changed to the previous outage result, .050. The turbine generator picked up approximately 2 megawatts and more load had to be picked up manually. The turbine generator was later taken off line for turbine balancing. Considering the results of the previous two startups, the micrometer was then adjusted to .100 and the turbine generator picked up approximately 5.5 percent of rated load <br /><br />. In retrospect the .162 setting was too high. Comparisons of results with the plant set-point log settings that may require further supervisory review of questionable results will be made. The calibration procedure is being simplified and improved. The simulator and controller were recalibrated. The subsequent startup was normal.
318 | 3171987012 | 1987-07-23 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | At 1525 on July 23, 1987 a fault developed on one (Transmission Line 5052) of the two 500KV transmission lines connecting Calvert Cliffs Nuclear Power Plant to the company's bulk power distribution grid at Waugh Chapel Station. The circuit breakers for line 5052 at Waugh Chapel and Calvert Cliffs tripped to isolate the fault. In addition, circuit breakers at Calvert Cliffs for the other transmission line (line 5051) incorrectly tripped open. This resulted in isolating the generating plant from the power grid resulting in both reactors tripping on loss of load of all off site nonemergency AC power. All three Emergency Diesel Generators started automatically to power the vital 4KV buses. Emergency Operating Procedures 0 and 2 were initiated to place both reactors in a stable condition. At 1530 an Emergency Response "Alert" condition was declared. The event was downgraded to an "Unusual Event" at 1700 upon completion of a checkout of the 500KV switchyard. At 1723 off site electrical power was provided to a vital 4KV bus from the alternate off site power line. Normal off site power was restored at 1910 via transmission line 5051. The fault on transmission line 5052 was caused by a tree that came in contact with the transmission line. All trees in the area have been cut down to prevent recurrence. The cause of transmission line 5051 circuit breakers tripping incorrectly was determined to be the fault of a defective logic circuit card in the primary static relay panel. This circuit card allowed the relays to trip the circuit breaker despite the absence of a "Permissive Signal" from the corresponding relays at Waugh Chapel. This tripping function was disenabled (tripping function protection provided by backup relays) upon restoring transmission line 5051 to service. The tripping function was subsequently restored after swapping the repaired logic assembly with one from another location in the power grid.
318 | 3181987006 | 1987-09-07 | QR6 | Manual Reactor Trip | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | At 1513 on September 7, 1987 Unit Two's Reactor was manually tripped in response to a rupture in the main turbine's Electro-Hydraulic Control (EHC) system hydraulic fluid tubing. At the time of the incident the unit was operating at 100% power. The unit was manually tripped after operators received low pressure and low level alarms in the EHC system and when the closure of the turbine main steam valves (and subsequent reactor trip) was imminent. The unit's safety systems performed as expected and the plant was returned to a stable condition without incident. <br /><br />Subsequent investigation pinpointed the location of the fluid rupture to be in a 1/2" stainless steel tubing leading to a pressure transmitter off of #21 EHC Pump Discharge Line. Corrective action consisted of replacing the ruptured tubing and of installing additional tubing clamps to better support this tubing. Fracture mechanic analysis done on the affected section of tubing revealed the cause of failure to be from vibration induced metal fatigue. Unit two was restarted and paralleled to the electric distribution grid at 0222 on September 8, 1987.
318 | 3181987008 | 1987-11-22 | QR3 | Reactivity Control Imbalance | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 80 | During performance of the CEA Partial Movement Test (STP-0-29-2), Control Element Assembly 29 (CEA-29), dropped fully into the reactor core and would not raise. During the replacement of the malfunctioning Upper Gripper Power Switch Module for CEA-29, the same module for CEA-28 was removed inadvertently due to personnel error. This removal caused CEA-28 also to drop fully into the reactor core. The reactor was immediately manually tripped due to two dropped CAEs. <br /><br />Corrective actions are as follows: <br /><br />1. The electricians involved were counselled regarding this error. The details of this event have been reviewed with all maintenance electricians. <br /><br />2. A step-by-step CEA troubleshooting procedure will be written. <br /><br />3. A mechanical interlock will be added to CEA test compartment door. <br /><br />4. The CEA number will be added to module description labeling. <br /><br /> 5. The malfunctioning gripper module was replaced for CEA-29. The failed module was returned to the manufacturer to determine the root cause of the failure.
318 | 3181987009 | 1987-12-21 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | Unit 2 tripped on December 21, 1987 from 100% power due to a loss of load signal. The loss of load was caused by a failure of the Unit 2 main generator permanent magnet generator due to the stator frame being misaligned. During the post-trip cooldown, an atmospheric dump valve malfunctioned (failed to fully shut) causing a more rapid cooldown than normal. The operators secured the steam loads to minimize cooldown and supplied the steam generators from the auxiliary feedwater system. The cooldown was terminated when the atmospheric dump valve was manually isolated. <br /><br /> The following corrective actions were taken. <br /><br />1. Turbine-Generator Maintenance Procedures were significantly upgraded. <br /><br /> 2. The atmospheric dump valve was repaired and returned to service. The failed roll pin was tested by the materials laboratory. The pin was verified to be made of the proper material. Subsequent maintenance of other atmospheric dump valves has not revealed similar problems. Atmospheric dump valve maintenance procedures have been upgraded.
318 | 3181988002 | 1988-01-22 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | During troubleshooting of the three phase Unit 2 computer inverter, power was lost to the non-vital 208/120V A.C. Instrument Bus 22 (2Y10). The de-energization of 2Y10 resulted in reduced feedwater flow and caused the reactor to be tripped near the low steam generator level setpoint. <br /><br /> The loss of Instrument Buss 22 (2Y10) was caused by personnel error when a plant electrician's misinterpretation of electrical prints and unclear communications with the inverter vendor led to the placement of temporary jumpers in the inverter, causing a direct short circuit that was reflected back to the main power feed circuit breaker causing it to trip thus de-energizing Instrument Bux 22 (2Y10). <br /><br />CORRECTIVE ACTIONS <br /><br />1. A study of the proper size fusing and fuse to circuit breaker coordination is in progress. <br /><br />2. Clarify the inverter manufacturers electrical prints to show the actual placement, in the circuit, of the power factor correction capacitors. <br /><br />3. Investigate the use of "special" procedures in troubleshooting complex equipment. <br /><br />4. All Maintenance Electricians will be trained on the details of this event as part of our continuing training program.
318 | 3181988004 | 1988-04-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | At 0848, April 27, 1988, Calvert Cliffs Unit 2 tripped on Low Steam Generator Water Level after #21 Steam Generator Feed Pump tripped for no apparent reason. Subsequent testing and investigation has yielded no prior symptoms or root cause for the pump trip. <br /><br />In addition to the permanent monitoring equipment, temporary monitoring equipment has been installed on the trip circuitry associated with various Steam Generator Feed Pump Turbine trips. The #21 Atmospheric Dump Valve was automatically controlling Reactor Coolant System temperature improperly. A control signal of incorrect magnitude from the Reactor Regulating System was found. The control signal was readjusted. <br /><br /> Corrective Action <br /><br />1. The temporary additional monitoring of the trip circuit for #21 Steam Generator Feed Pump will be continued in an effort to determine the root cause of this event. Specific corrective actions to prevent recurrence can not be delineated until the root cause is determined. <br /><br /> 2. An evaluation of replacements for the currently installed Turbine Thrust Bearing Wear Monitor is in progress.
318 | 3181991005 | 1991-05-02 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Calvert Cliffs 2 | P | CE | PO | 8 | At 1050 on May 2, 1991, a Low Steam Generator (SG) Level Reactor Protective System Trip occurred at Calvert Cliffs Unit 2 while attempting to control SG level oscillations at low power level. At the time of the trip, Unit 2 was operating in MODE 1 (Power Operation) at 8 percent power. The low SG level was caused by a loss of feedwater event when the operating SG Feed Pump (SGFP) was lost due to a speed controller failure. <br /><br /> The initiating loss of feed event was caused by a failed circuit board edge connector which prevented the operator from resetting the SGFP speed controller and restoring feed.<br /><br /> Immediate corrective actions included replacing the circuit board and connector, and inspecting like SGFP speed controllers for similar problems. A SGFP speed controller alignment procedure including functional test will be written, and this event will be included in the next cycle of Instrument Maintenance continuing training.
318 | 3181992001 | 1992-01-02 | QK4 | Steam or Feed Leakage | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 92 | On January 2, 1992 at 2219 hours, Calvert Cliffs Unit 2 was manually tripped from 92 percent power following a feedwater leak from a lifted 3/4 inch feedwater heater relief valve. A manual trip was initiated after leaking feedwater caused electrical grounds in the secondary system and a charging pump tripped without apparent cause. The failed relief valve has been replaced and an engineering evaluation will recommend corrective actions to prevent future failures of similar valves.
318 | 3181992003 | 1992-06-24 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Calvert Cliffs 2 | P | CE | PO | 100 | On June 24, 1992, at 3:09 a.m., Calvert Cliffs Unit 2 was manually tripped due to a rapid loss of Main Condenser vacuum. The low vacuum condition was caused by the failure of the 21 Main Condenser Expansion Joint. Unit 2 was at 100 percent power at the time of the event. <br /><br /> This event did not result in any significant safety consequences. The immediate cause of the event was air in-leakage through the torn expansion joint belt of 21 Main Condenser. <br /><br /> Unit 2 was placed in COLD SHUTDOWN (MODE 5) on June 25, 1992. An improved design belt was installed in 21 Main Condenser Expansion Joint. A new inspection procedure for the expansion joints has been implemented. <br /><br /> A preventive maintenance procedure to periodically replace the expansion joints will be implemented.
318 | 3181992005 | 1992-08-01 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Calvert Cliffs 2 | P | CE | PO | 100 | At 2009, August 1, 1992, a loss of condensate and feed system pumps occurred at Calvert Cliffs Unit 2 while at 100 percent power. A non-licensed plant operator caused a circuit breaker relay to operate, tripping the feeder breaker and causing the trip. At 2010, Plant operators manually tripped the reactor and stabilized the plant by 2021. An Auxiliary Feed Actuation System actuation was experienced during the post-trip transient. <br /><br /> Incomplete corrective actions from a 1985 event appear to have contributed to this trip. Additionally, the conditions of the breaker cubicle door and its affected relay contributed significantly to the event. <br /><br /> As corrective action, temporary signs were hung on similar feeder breakers and appropriate personnel were informed. Planned actions include procedure changes to address the primary and contributory causes, training, door functional checks, and permanent cubicle-door caution signs.
318 | 3181992006 | 1992-08-17 | QL5 | Partial Closure of MSIVs | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On August 17, 1992, the Unit 2 reactor tripped due to an automatic actuation of the Reactor Protection System (RPS). An RPS Asymmetric Steam Generator Trip signal was generated when Main Steam Isolation Valve (MSIV) 22 inadvertently travelled shut to less than 90 percent open during performance of Surveillance Test Procedure O-47B-02, Partial Stroke Test of MSIVs. At the time, Unit 2 was at 100 percent power (MODE 1). <br /><br /> The most likely cause of the event was an MSIV hydraulic problem or mechanical binding. There were no significant safety consequences as a result of this event. Corrective actions already taken include appropriate actions for the plant trip, changing out the MSIV hydraulic fluid and replacing the hydraulic fluid sample valve. Corrective actions which will be taken include replacing MSIV 21 and 22 dump valve solenoids, performing an evaluation of higher grade hydraulic fluid, instituting a situational preventive maintenance procedure for changing out the hydraulic fluid, and a review and revision if necessary of the procedures for preventive maintenance deferrals.
318 | 3181992007 | 1992-09-29 | QR6 | Manual Reactor Trip | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 77 | On September 29, 1992, at 1141, Calvert Cliffs Unit 2 was manually tripped due to high temperature on the Main Turbine Rear Thrust Bearing Faces. The bearing temperatures rose as a direct result of a pressure imbalance caused by the lifting and failure to reseat of the 23 Moisture Separator/Reheater (MSR) shell-side relief valve while at power. At the time of the trip Unit 2 was at 77 percent power. The relief valve lifted at normal system pressure apparently due to the combined effects of pilot disc leakage and setpoint drift. The valve in question has been repaired, the frequency of inspection for MSR relief valve pilots has been doubled, and a vendor modification to aid in closing the main disc will be scheduled for the next refueling outage.
318 | 3181993003 | 1993-06-25 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Calvert Cliffs 2 | P | CE | SU | 3 | On Thursday, June 25, 1993 at 8:05 p.m., Calvert Cliffs Unit 2 automatically tripped on low level in the 21 Steam Generator (SG). Operators had noted divergent SG level oscillations with the Full Range Digital Feedwater Control System (FCS) in automatic. They took manual control with SG level at +25 inches but did not provide sufficient feedwater. The reactor tripped on low SG level. <br /><br /> The causes of this event include inadequate communication of pertinent information regarding the response of the FCS at low power, inadequate communication during shift turnover regarding a just-completed power increase, the lack of Project Team involvement at the time of the incident, and the work practices of the operations personnel involved in this incident. <br /><br /> Operations management will reemphasize expectations for the improvement of communications between operating crews. An FCS Project Team representative will be available to the Control Room for future startups and planned shutdowns until FCS performance meets expectations. We will provide classroom training to all operating crews on the details of this event.
318 | 3181994001 | 1994-01-12 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On January 12, 1994 at 0552, Calvert Cliffs Unit 2 tripped when an electrical protective relay actuated in the 13.8 kv voltage regulator (2H2103) for Unit Service Transformer (UST) U-4000-22. This actuation caused the loss of 4 kv Busses 22, 23, and Safety Bus 24. Both control element drive mechanism motor generator sets lost power, causing a reactor trip from loss of power to the control element drive assemblies and a main turbine trip. <br /><br /> The cause of the 13.8 kv feeder breakers opening was the actuation of the sudden pressure trip circuit for the 13.8 kv voltage regulators due to intermittent grounds on their associated 125 VDC bus.<br /><br /> A Significant Incident Finding Team was appointed by the Plant General Manager to investigate the event. The results of this investigation and associated corrective actions are included in this supplemental report.
318 | 3181994004 | 1994-08-10 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On August 10, 1994 at 2154, Calvert Cliffs Unit 2 experienced a reactor trip due to a main generator trip. The generator tripped when the exciter field breaker and generator output breakers tripped opened due to a loss of field. At the time of the event, Unit 2 was operating at 100 percent power with normal operating temperature and pressure. <br /><br /> The cause of the event was a drop in main generator excitation leading to the actuation of the loss of field relay. Excitation was low after the operators transferred the voltage regulator from the ON to OFF position. <br /><br /> Corrective actions included testing of the excitation system prior to restart; replacement of failed components; refresher training for operators; and monitoring of the system.
318 | 3181994005 | 1994-09-24 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 16 | On September 24, 1994, at 2016, Calvert Cliffs Unit 2 experienced a reactor trip at 16 percent power due to low Steam Generator (SG) pressure. The low pressure was sensed after a rapid increase in steam demand was experienced due to an unexpected opening of No. 21 main turbine governor valve. <br /><br /> Troubleshooting after this event identified a loose wire on No. 21 governor valve's Linear Voltage Differential Transformer (LVDT). This loose wire essentially removed the LVDT feedback from the valve's positioning circuit. Thus, No. 21 governor valve started to open and continued to open due to the lack of feedback from the LVDT. The sudden increase in steam flow that occurred after No. 21 governor valve ramped open caused SG pressure to drop low enough to cause the reactor trip. <br /><br /> In response to this event the wire on No. 21 governor valve LVDT was tightened and the wiring on all of the other Unit 2 main turbine throttle and governor valves was checked as well. Additional system monitoring and evaluation is being performed as well.
318 | 3181994006 | 1994-10-27 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On Thursday, October 27, 1994 at about 2353 hours, Calvert Cliffs Unit 2 tripped on receipt of a Reactor Protective System Loss of Load signal. Investigators found that a ground had been caused by the 'A' phase Main Generator transition links, which were damaged by overheating after having been installed incorrectly.<br /><br /> The root cause of this event was failure to adequately address the potential risks of work newly assumed by the Electrical Maintenance group. <br /><br /> New links were correctly installed and the Unit was brought back on line. Since the time the links were installed, improvements have been made to our Maintenance processes. These existing practices will be reviewed in light of the circumstances of this event to verify their adequacy.
318 | 3181995002 | 1995-01-13 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On January 13, 1995, at approximately 1047, Calvert Cliffs Unit 2 tripped from 100 percent power due to low levels in the Steam Generators (SGs). The Reactor Protective System low level trip occurred after an Engineered Safety Feature Actuation System Steam Generator Isolation Signal (SGIS) was generated.<br /><br /> At around 1020 on Friday, January 13, 1995, Instrument Maintenance (IM) technicians tripped SGIS Channel ZG as part of surveillance testing. At around the same time an IM safety tagger, walking down a tagging request, twisted an instrumentation cable for SG pressure transmitter 2PT1013A to read the cable scheme number. A wire in the cable was broken and SGIS Channel ZD tripped, resulting in the SGIS actuation. <br /><br /> Corrective actions include placing restrictions on electrical walkdowns; retermination of the transmitter wires, and changes to surveillance procedures.
318 | 3181995003 | 1995-01-15 | QP5 | Excessive Feedwater Flow | [45 empty] | Calvert Cliffs 2 | P | CE | SU | 4 | On January 15, 1995, at approximately 0246, Calvert Cliffs Unit 2 tripped due to a Reactor Protective System loss of load signal. The loss of load signal was generated after power increased from 4 percent to 13 percent and the turbine was not on-line. The power excursion occurred after problems were experienced in controlling 22 Steam Generator Feed Pump (SGFP) and a rapid increase in steam generator levels resulted in a cooldown of the Reactor Coolant System. <br /><br /> The causes of the event are related to human performance. Areas determined to be less than adequate included operator experience and knowledge related to SGFP control; decision making with respect to operating 22 SGFP; work practices including pre-evolution briefings and communication; procedural adherence; and reactivity management. <br /><br /> Short-term corrective actions were completed prior to startup and additional long-term corrective actions have been implemented.
318 | 3181995005 | 1995-05-24 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On May 24, 1995, at 12:49 p.m., Calvert Cliffs Unit 2 was manually tripped from 100 percent power due to the lose of five out of six circulating water pumps (CWP) that resulted from a ground fault inside a non-safety-related motor control center (MCC). <br /><br /> The root causes of this event were: (1) plant equipment improperly restored to service; and (2) the assessment of the potential risk to plant personnel and equipment safety was less than adequate. This event did not result in any significant nuclear or personnel safety consequences. <br /><br /> Corrective Actions include repair and restoration of the affected MCC, inspection of similar MCCs, strengthened expectations and work practices to increase personnel safety, reduce equipment hazards, and trip potentials.
318 | 3181996001 | 1996-02-27 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On Tuesday, February 27, 1996, at 5:08 p.m., 500 kV Breakers 552-41, 552-21, and 552-61 tripped open in the Calvert Cliffs switchyard, causing the loss of the 500 kV Red Bus. Unit 2 automatically tripped on a low reactor coolant flow signal when power was lost to its' reactor coolant pumps. The 500 kV Black Bus feeding Unit 1 was unaffected. At the time of the event, Unit 1 and Unit 2 were at 100 percent power. <br /><br /> The most probable cause of the Unit 2 trip was the failure of an auxiliary relay card in Breaker 552-41 in conjunction with less than adequate switchyard control. Previous corrective actions for a similar event did not prevent recurrence. <br /><br /> The failed relay card was replaced, the circuit tested satisfactory and the Red Bus was restored to service. Interim controls for work in the switchyard are in place. Long-term expectations and procedural controls will be developed to prevent recurrence.
318 | 3181996005 | 1996-11-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On November 17, 1996, at 1059 a.m., Calvert Cliffs Unit 2 automatically tripped on low water level in No. 21 Steam Generator when No. 21 Feedwater Regulating Valve (FRV) went shut. condition. This event resulted in no significant consequences to public health and safety. At the time of the event, Unit 2 was at 100 percent power. <br /><br /> The cause of the event was failure of the spring retainer in No. 21 FRV positioner. The spring retainers for Nos. 21 and 22 FRV positioners were replaced. We will inspect the similar Unit 1 FRV positioner spring retainers at the next shutdown of sufficient duration. Other corrective actions include an evaluation of applicable maintenance procedures and training on this event to appropriate site personnel.
318 | 3181998004 | 1998-07-23 | K1 | Steam Line Break Outside Containment | [9 empty] | X | [26 empty] | X | [8 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On July 23, 1998, at approximately 1820, with Unit 2 in Mode 1 (100 percent power), a 2-inch diameter vent line from No. 21 Moisture Separator Reheater 2nd stage to No. 25A Feedwater Heater ruptured emitting a large volume of steam to the Unit 2 Turbine Building. Because of the volume of steam being emitted into the Turbine Building and resultant difficulty in isolating the leak, Control Room Operators manually tripped the unit. This event resulted in no significant consequences to the health and safety of the public. There were no personnel injuries or associated equipment damage as a result of the steam leak. The cause of the pipe rupture was flow accelerated corrosion. The ruptured pipe was replaced and an inspection of a representative sample of other small bore high-energy piping in the Turbine Building was completed. An assessment of the Flow Accelerated Corrosion Program is underway.
318 | 3182003003 | 2003-05-28 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | At 11:34 AM on May 28, 2003, Calvert Cliffs Unit 2 experienced an automatic reactor trip from 100 percent power. The automatic reactor trip was initiated by the Reactor Protective System due to the high pressurizer pressure condition that resulted from the rapid loss of load. The rapid loss of load occurred when the Main Turbine Governor Valves shut unexpectedly during planned troubleshooting on the Main Turbine controls in Turbine Auxiliaries Electro-Hydraulic Control Cabinet 2T11. A short circuit created during the troubleshooting induced a loss-of-voltage to the valve position limiter causing the governor valves to shut unexpectedly. The short circuit was caused by incorrect use of test equipment during planned troubleshooting; therefore, the root cause of the trip lies in Human Performance in the area of Work Practices. Also, contributing causes in the area of Verbal Communications and Procedural Clarity were identified. Corrective actions include awareness training on the event, its causes and recommendations, procedure changes, and also initial and continuing training on appropriate work practices when using test equipment. The unit was restarted and paralleled to the grid on May 29, 2003 at 7:03 PM.
318 | 3182004001 | 2004-01-23 | QP2 | Partial Loss of Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | At 15:26 on January 23, 2004, Calvert Cliffs Unit 2 tripped from 100 percent power, initiated by the Reactor Protective System due to low steam generator water level caused by an erroneous over speed trip signal on the steam generator feed pump. The erroneous trip signal occurred because of a degraded digital speed monitor supply voltage caused by corrosion of an inline fuse and the fuse holder. The turbine bypass valves and atmospheric dump valves opened as designed, but the quick-open signal did not clear due to the failure of a relay in the reactor regulating circuit. The open valves resulted in over-cooling of the Reactor Coolant System, a Steam Generator Isolation Signal, and a Safety Injection Actuation Signal causing a loss of normal heat removal. During the recovery, a large insurge of subcooled water cooled the pressurizer, lowering reactor coolant pressure to produce a second Safety Injection Actuation Signal. The corroded fuse, fuse holder, and failed relay were replaced. Operations staff was briefed on the effect of a large insurge of water on reactor coolant pressure, and Unit 2 was restarted and paralleled to the grid on January 25, 2004 at 21:53.
318 | 3182006001 | 2006-11-16 | QR0 | RCS High Pressure (RPS Trip) | [6 empty] | X | [21 empty] | X | [16 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On November 16, 2006, the Unit 2 Reactor automatically tripped due to a pressurizer pressure high signal from the Reactor Protective System, during the performance of a clearance order to support scheduled maintenance. The clearance order required opening an electrical disconnect for personnel safety. However, the personnel involved with developing and reviewing the clearance order were unaware that opening this disconnect would result in a reactor trip. As a result of the trip, Reactor Coolant System pressure increased causing the two power-operated relief valves (PORVs) to open as designed. One PORV remained open longer than expected resulting in a valid safety injection actuation signal. The PORV was replaced prior to returning Unit 2 to power. The root causes for this event were in the area of human performance. Corrective actions require clearance orders to be completed and second-reviewed at least three weeks prior to performance of scheduled maintenance and, loss of power/power restoration effects must be clearly understood when electrical isolation devices support clearance orders. Unit 2 was returned to 100 percent power on November 21, 2006. Unit 1 was not affected by this event.
318 | 3182010001 | 2010-02-18 | C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) |  |  | X | [13 empty] | X | [28 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On February 18, 2010, at 8:24 a.m., Unit 2 experienced an automatic reactor trip from 99.5 percent power. The Unit 2 Reactor Coolant Pumps (RCPs) lost power and the Reactor Protective System actuated on Reactor Coolant System low flow. The RCPs lost power due to a loss of Service Transformer P-13000-2 and the 500 kV Switchyard Red Bus being deenergized, deenergizing the 22 13 kV RCP Bus. The loss of P-13000-2 resulted in a loss of the normal power supply to 24 4 kV bus. This caused the 2B Emergency Diesel Generator (EDG) to start. Shortly after receiving a start signal, the 2B EDG tripped due to a low lube oil pressure trip. The event was initiated when the Unit 1 12B RCP tripped due to an electrical fault in relay protective circuitry. The ground fault was not isolated close to the source due to a failed ground protection relay in breaker 252-2202, the feeder breaker from Service Transformer P-13000-2 to the Unit 1 RCP buses. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation and automatic start of the 2B EDG, 10 CFR 50.73(a)(2)(i)(B) due to the inoperable condition of the 2B EDG and 10 CFR 50.73(a)(2)(v)(D) for those periods when two EDGs were out-of-service.
318 | 3182013003 | 2013-05-08 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On May 8, 2013, at 2147 eastern daylight time, Unit 2 experienced an automatic reactor trip from 99.5 percent power. The Reactor Protective System actuated on high pressurizer pressure. The high pressurizer pressure condition occurred due to a loss of load event caused when main turbine steam admission valves closed. The most probable cause of the event was an intermittent failure of a component or signal path in main turbine control cabinet 2T11 that resulted in a control signal to the steam admission valves to close. At Calvert Cliffs, there have been no recent similar events involving a reactor trip caused by the failure of the turbine control system. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation. Corrective actions include replacement of circuit cards in the main turbine overspeed protection circuitry, monitoring selected control system signals which could indicate the source of the signal should the event recur, and implementation of a project plan for selected turbine control circuit card replacement during a future refueling outage.
318 | 3182013004 | 2013-05-21 | QP5 | Excessive Feedwater Flow | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On May 21, 2013 at 0533, Calvert Cliffs Nuclear Power Plant Unit 2 initiated a manual reactor trip from 99.5 percent power in response to a trip of 22 Steam Generator Feed Pump (SGFP). All post-trip actions were completed and the event terminated without complications. The cause of the initiating event was the failure of the 22 SGFP coupling that connects the pump to its steam turbine driver, such that the pump and steam turbine were effectively disconnected. Inspection of the pump end of the coupling assembly revealed mechanical damage and separation along a weld seam. Forensic analysis identified areas of incomplete weld fusion on the turbine end of the failed coupling dating to the original component manufacture, combined with stresses induced by high cycle stress as being the root cause of 22 SGFP coupling failure. Immediate corrective actions taken included the examination, inspection, and replacement of the 22 SGFP coupling.
318 | 3182014001 | 2014-01-21 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On January 21, 2014, at 9:25 p.m., Unit 2 experienced an automatic reactor trip from 99.5 percent power. The reactor trip occurred when 13 kV Service Bus 21 deenergized due to a ground fault on feeder breaker 252-2104. The loss of the service bus caused a loss of power to non-safety-related 4 kV buses, which caused a loss of circulating water pumps and main condenser vacuum, requiring the use of auxiliary feedwater and atmospheric dump valves to maintain Reactor Coolant System temperature. Power was also lost to safety-related 4 kV Bus 24, which caused an automatic start of the 2B Emergency Diesel Generator to power 4 kV Bus 24.<br /><br /> The loss of power to non-safety-related 13 kV Service Bus 21 was caused by water intrusion when an air filter assembly located at the back of breaker 252-2104 cubicle became dislodged during a snow storm, allowing snow to enter the cubicle, melt, and cause a ground fault. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation and the automatic start of the 2B Emergency Diesel Generator. Corrective actions include repairs to 13 kV Service Bus 21 and installation of a new filter housing. Previous events related to safety-related structures have been documented in Licensee Event Reports 317/2010-001 and 317/2011-003.
318 | 3172015002 | 2015-04-07 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On April 7, 2015 at 1239 Calvert Cliffs experienced a dual unit trip due to an off-site grid disturbance resulting in an undervoltage condition that caused all four Engineered Safety Features (ESF) Buses to trip. Due to this condition, all of the emergency diesel generators (EDGs) started and loaded with the exception of 2B EDG which started but tripped due to a failed electronic speed switch in the startup circuitry. The associated 4 kV ESF bus was repowered from the normal power source. Additionally, while 2A EDG energized its respective 4 kV ESF bus, the associated shutdown sequencer failed to start 21 Saltwater pump which was subsequently manually started. Unit 1 tripped on loss of all power to generator excitation and all required safety systems responded as designed. Unit 2 tripped due to generator loss of load and is classified as an unplanned scram with complications as 24 4 kV ESF bus was de-energized for greater than 10 minutes. The failed 2B EDG speed switch and 2A EDG shutdown sequencer were replaced and tested satisfactorily. Future corrective actions include to design and implement a speed switch modification to eliminate the single-point failure risk, and to procure and install a newly manufactured sequencer in each channel.
318 | 3182015001 | 2015-12-01 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On December 1, 2015 at 1820, Unit 2 turbine driven 22 Steam Generator Feed Pump (SGFP) tripped. Operations attempted to reset 22 SGFP unsuccessfully. Facing lowering steam generator water level, Operations manually initiated a reactor trip. It was determined that 22 SGFP tripped due to a failed coupling. This occurred because excessive misalignment developed between the pump and turbine due to insufficient tensioning of the pump's casing to pedestal studs thus causing 22 SGFP coupling to fail. Investigation determined that the vender supplied stud tensioning values used in tensioning the hold down studs on both Unit 2 SGFPs during the 2015 refueling outage were incorrect and resulted in insufficient clamping force being applied to all the studs. The root cause of the failure was that Engineering personnel failed to address the full scope and critical parameters associated with use of a different tool for installation of studs in lieu of capscrews for 22 SGFP. The coupling for 22 SGFP was replaced and 22 SGFP was realigned. Corrected tensioning values were then applied to all the hold down studs on 21 and 22 SGFPs. Corrective actions include briefings to applicable groups on adherence to procedure requirements for owner's acceptance review of external technical products. Unit 2 was returned to Mode 1 operations at 1326 on December 6, 2015.
318 | 3182016001 | 2016-12-03 | QR5 | Turbine Trip | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 100 | On December 3, 2016, Operations was conducting a Performance Evaluation of the auto start feature of Unit 2 Main Turbine Electro-Hydraulic Control (EHC) Pumps. At 2223, the standby EHC pump started per the procedure and a normal rise in pressure was noted. At 2224, Unit 2 Main Turbine tripped automatically which was followed by an automatic reactor protection system trip. The Main Turbine tripped on a Main Generator Directional Power Relay trip following the closure of all Unit 2 Main Turbine Governor Valves and Intercept Valves. This was due to an EHC leak on 21 Main Turbine Governor Valve Actuator Emergency Trip Fluid Check Valve which caused a rapid decrease in EHC header pressure. The trip was an uncomplicated reactor trip as all safety functions performed as expected. The failed emergency trip fluid check valve was sent off site to a lab for forensic investigation. This analysis determined the check valve failed due to Inter Granular Stress Corrosion Cracking (IGSCC). The most likely cause of the IGSCC on this check valve was exposure to ammonia during some previous maintenance activity. Corrective actions include replacement of all similar Unit 2 EHC valves during the 2017 refueling outage and establishment of a preventive maintenance strategy to periodically replace similar EHC valves. Unit 2 was returned to full power at 1647 on December 5, 2016.
318 | 3182021002 | 2021-03-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Calvert Cliffs 2 | P | CE | PO | 38 | On March 21, 2021 at 2219 while returning Unit 2 to full power following a refueling outage, a manual reactor trip was initiated due to lowering water levels in 21 Steam Generator. This event was caused by 21 Steam Generator Feedwater Regulating Valve, 2CV1111, failing shut. <br /><br /> Troubleshooting determined that 21 Steam Generator Feedwater Regulating Valve Positioner B, 2ZC1111B, had malfunctioned due to the presence of foreign material in the positioner. Since the redundant positioner, 21 Steam Generator Feedwater Regulating Valve Positioner A, 2ZC1111A, was already out of service, no automatic transfer to the redundant positioner occurred and 2CV1111 failed in the shut position. This resulted in 21 Steam Generator water levels lowering to near the automatic trip setpoint level at which point a manual reactor trip was initiated. Water levels were restored to 21 Steam Generator by a manual start of an Auxiliary Feedwater Pump. <br /><br /> Following troubleshooting, Maintenance replaced both positioners and subsequently completed post maintenance testing to demonstrate the satisfactory operation of the positioners and 2CV1111. Operations then commenced actions to return Unit 2 to power operation.
318 | 3182021004 | 2021-11-21 | QC5 | Loss of Non-safety-Related Bus | [13 empty] | X | [30 empty] | X | Calvert Cliffs 2 | P | CE | PO | 100 | On November 21, 2021 when energizing 12 Spent Fuel Pool Cooling Pump, an arc-flash event occurred on 12 Spent Fuel Pool Cooling Pump Breaker, 2BKR52-2411. As a result, upstream 24A 480V Bus Feeder Breaker, 2BKR52-2412, tripped open. This caused downstream loss of power effects including the loss of the non-vital 120VAC Instrument Bus, 2BUS2Y10. Loss of 2BUS2Y10 led to repositioning of Unit 2 mini flow and high-level dump valves that created a secondary transient which resulted in Steam Generator Feedwater Pumps 21 and 22 tripping off. This loss of 2BUS2Y10 additionally caused a loss of Control Element Drive System power and created an inability to manually move control rods (automatic function was not impacted). At 1046, Unit 2 was manually tripped from 100% power due to receipt of steam generator low level pre-trips and steam generator water levels not recovering. <br /><br /> Troubleshooting determined that the arc-flash event was caused due to technicians failing to remove plastic protective stab covers, that were installed as electrical safety measures during conduct of maintenance on 2BKR52-2411 before racking in the breaker. <br /><br /> Corrective actions to address the human performance gaps causing this event have been put in place. Actions are being evaluated that might enable the unit to minimize the operational impact from a loss of 2BUS2Y10.
321 | 3211987001 | 1987-01-01 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 1/1/87 at approximately 1350 CST, Unit 1 was in the run mode at an approximate power of 2430 MWt (100 percent of rated thermal power). At that time, the main turbine tripped (closure of the main turbine stop valves). The closure of these valves is a scram input to the Reactor Protection System (RPS). A full reactor scram occurred without any complications. <br /><br />The event is believed to have been caused by a spurious ground fault signal or spurious electrical noise from welding operations which induced a voltage transient in the turbine electrohydraulic control system. This resulted in the trip of the main turbine backup electrical overspeed device which tripped the main turbine and resulted in the reactor scram. <br /><br />Corrective actions for this event included performing an engineering evaluation of the event and testing the main turbine backup overspeed circuitry.
321 | 3211987002 | 1987-01-15 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 99 | On 1/15/87 at approximately 1800 CST, Unit 1 was in the run mode at an approximate power of 2423 MWt (99 percent of rated thermal power). At that time, the main generator (TB) tripped and the main turbine (TA) tripped on closure of the main turbine stop valves. The closure of these valves is a scram input to the Reactor Protection System (RPS) (JC). A full reactor scram occurred without any complications. As a result of a low reactor water level condition caused by the scram, a Primary Containment Isolation System (PCIS) (JM) valve group 2 isolation also occurred. <br /><br />The event was caused by the trip of the main generator ground fault detector. The trip of this device occurred due to the combination of a loose wire and a conductive film on the outside of the wire's insulation. <br /><br />Corrective actions for this event included: 1) performing an engineering analysis of the event, 2) testing the main turbine trip circuitry, 3) cleaning and tightening of generator components, 4) meggering of the main generator field, and 5) formulating recommendations for additional preventative maintenance.
321 | 3211987011 | 1987-07-23 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 7/23/87 at approxiMately 2114 CDT, Unit 1 was in the run mode at an approximate power level of 2436 MWt (approximately 100 percent of rated thermal power). At that time, Vital AC (EIIS Code EE) power was lost. This resulted in a decrease in the reactor feedwater pumps flow and a decrease in reactor water level. The reactor water level decreased to the Reactor Protection System (RPS EIIS Code JC) actuation setpoint and a reactor scram occurred. <br /><br />The root cause of this event is attributed to equipment failure due to inadequate ventilation design to ensure the Vital AC equipment is properly cooled. The electronic equipment failure in the inverters is attributed to the high room temperatures. <br /><br />Corrective actions for this event include: 1) refurbishing the inverter, 2) adding temporary cooling to the inverter rooms, 3) installing a new HVAC system for cooling inverter rooms, 4) developing a preventive maintenance procedure for the Unit 1 and 2 inverters, 5) performing an engineering evaluation for inverter replacement, 6) installing new Vital AC inverters for both Units I and 2, 7) replacing the failed RCIC EGM module, and 8) performing a follow up inspection of the HPCI EGM module.
321 | 3211987013 | 1987-08-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 8/3/87 at approximately 2007 CDT, Unit 1 was in the run mode at an approximate power level of 2433 MWt (approximately 100 percent of rated thermal power). At that time, the master feedwater controller circuitry (EIIS Code JK) failed. This failure caused a decrease in the Reactor Feedpumps (RFPs EIIS Code SJ) flow and a decrease in reactor water level. The reactor water level decreased to the Reactor Protection System (RPS EIIS Code JC) actuation setpoint and a reactor scram occurred. <br /><br />The root cause of this event is equipment failure. Specifically, two capacitors in the master feedwater controller amplifier short circuited. When these two capacitors shorted, the voltage' output signal to the individual feedpump controllers was lost. This caused the feedpumps to ramp down to their low speed stops. <br /><br />Corrective actions for this event included: 1) replacing the capacitors and returning the circuit board to service, and 2) investigating similar problems on Unit 2 and replacing components.
321 | 3211988003 | 1988-02-26 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 2/26/88 at approximately 0839 CST, Unit 1 was in the run mode at an approximate power level of 2436 MWt (approximately 100 percent of rated thermal power). At that time, a main generator field ground detection relay (EIIS Code EL) tripped. This resulted in a turbine trip which caused a scram signal to be inserted into the Reactor Protection System (RPS EIIS Code JC) logic. This was an unanticipated actuation of the RPS. <br /><br />The root cause of this event (actuation of the ground fault detection relay) could not be conclusively determined. Plant personnel performed a detailed investigation. However, all equipment that was checked, functioned correctly. It is concluded the ground relay spuriously actuated. <br /><br />Corrective actions for this event included: 1) cleaning, testing and inspecting electrical equipment, 2) inspecting and testing the field ground relay, 3) investigating and replacing pressure transmitters, 4) reviewing other utilities' operating experiences, and 5) scheduling evaluation of future actions to prevent the possibility of recurrence.
321 | 3211988005 | 1988-04-19 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 4/19/88 at approximately 0802 CDT, Unit 1 was in the run mode at an approximate power level of 2433 MWt (approximately 100 percent of rated thermal power). At that time, plant operations personnel were exchanging the main Turbine Lubrication Oil Coolers (TLOCs EIIS Code TD). Shortly after the exchange of the TLOCs, a reactor scram occurred. <br /><br />The root cause of this event is personnel error. Specifically, plant operations supervisory personnel assigned an infrequently performed task without issuing sufficient guidance relative to the performance of the task. Additionally, operations personnel failed to notify operations supervision that they were unfamiliar with the task. <br /><br />The corrective actions for this event included: 1) counseling of involved operations personnel, and 2) revising plant procedures to provide guidance relative to removing and returning the TLOCs to service. It is anticipated the procedure revisions will be completed by approximately 6/1/88.
321 | 3211988009 | 1988-05-20 | QL5 | Partial Closure of MSIVs | [45 empty] | Hatch 1 | B | GE | PO | 20 | On 5/20/88 at approximately 0216 CDT, Unit 1 was in the run mode at an approximate power of 488 MWt (approximately 20 percent of rated thermal power). At that time, a reactor scram occurred when three of the four Main Steam Isolation Valves (MSIVs EIIS Code SB) were less than 90 percent open. This was an unanticipated actuation of the Reactor Protection System (RPS EIIS Code JC). <br /><br /> The root cause of this event is procedure deficiency. A start up procedure did not provide sufficient guidance relative to exchanging instrument air and nitrogen systems. Both systems supply motive power to the MSIVs. <br /><br />Corrective actions for this event included: 1) restoring nitrogen to the MSIVs, 2) temporarily revising plant procedures, and 3) scheduling permanent revisions to plant procedures.
321 | 3211988013 | 1988-09-04 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Hatch 1 | B | GE | PO | 100 | On 9/4/88, at 1456 CDT, Unit 1 was in the run Nod? at approximately 100 percent rate thermal power (2436 MWT). At that time, the 'A' Reactor Feed Pump controller malfunctioned, resulting in a decrease in reactor water level. By 1501 CDT, reactor water level had been restored to normal. Power level had been reduced to approximately 66 percent. <br /><br />At 1515 CDT, the 'B' Reactor Feed Pump (RFP) controller failed downscale causing the 'B' RFP to decrease in speed. This resulted in reactor water level decreasing rapidly and the Reactor Protection System actuating on low water level. The transient included Primary Containment Isolation System valve Groups 2 and 5 isolations, and the actuation of the High Pressure Coolant Injection, Reactor Core Isolation and Standby Gas Treatment Systems. The reactor water level was subsequently returned to the normal range and startup begun. <br /><br />The root causes of the event included: (1) a poorly soldered connection on the signal converter board within the 'A' RFP control loop (2) failure of the 'B' RFP controller caused by a non-responsive master feedwater controller amplifier. <br /><br /> The corrective actions for this event included resoldering a connection and replacing the controller amplifier.
321 | 3211988018 | 1988-12-17 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 85 | On 12/17/88, at approximately 0002 CST, Unit 1 was in the run mode at approximately 2080 CMWT (approximately 85 percent of rated thermal power). At that time, the main turbine (EIIS Code TA) tripped on loss of Electrohydraulic Control (EHC, EIIS Code TG) system pressure resulting in a reactor scram on turbine stop valve closure. Upon transfer of the nonessential loads to the startup auxiliary transformer (SAT, EIIS Code EA) 1D (as expected following a reactor scram), SAT 1D protective relaying actuated resulting in a loss of power to the Unit 1 nonessential loads. <br /><br />The cause of the scram was apparently personnel error in that a non-licensed operator implemented a system clearance on the EHC system of the wrong reactor unit. The cause of the SAT 1D failure was equipment failure. Specifically, malfunctioning transfer relaying resulted in a trip of the transformer supply breaker. <br /><br />Corrective actions include training of operations shift personnel and replacement and calibration of a transformer differential relay.
321 | 3211990012 | 1990-06-10 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Hatch 1 | B | GE | PO | 25 | On 6/10/90 at approximately 0826 CDT, Unit 1 was in the Run mode at an approximate power level of 609 CMWT. At that time, a procedurally controlled manual scram was directed by management to allow for termination of Offgas system flow to facilitate full investigation and resolution of offgas operational problems. The Group 2 Primary Containment Isolation System valves isolated and an automatic Reactor Protection System actuation was received on low level due to the expected void collapse as a result of the manual scram. Level was restored using the "B" Reactor Feedwater Pump. The Offgas system problems resulted in a reduction of hydrogen and oxygen recombination and an eventual hydrogen ignition in the carbon adsorber beds. At 1331 CDT, it was confirmed combustion was taking place and, at 1338 CDT, a Notification of Unusual Event (NUE) was declared for a fire lasting longer than 10 minutes (after discovery). The Offgas system was purged with nitrogen for several days. Exhaustive testing was completed at approximately 1315 CDT on 6/16/90 demonstrating the fire was extinguished and the NUE was terminated at 1325 EDT. <br /><br /> The cause of the fire in the Offgas system was component malfunction due to a combination of component failure, discrepancies in as-built equipment configuration, and less than adequate system operating procedures.<br /><br /> Corrective actions for this event include replacement of failed components, correcting equipment configuration, and revisions to procedures.
321 | 3211990013 | 1990-06-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hatch 1 | B | GE | PO | 25 | On 6/20/90 at approximately 0245 CDT, Unit 1 was in the Run mode at an approximate power level of 600 CMWT (approximately 24.6% rated thermal power). At that time, the reactor scrammed on low reactor vessel water level. Water level decreased to the scram setpoint when the 1B Reactor Feedwater Pump (RFP) failed to respond to an increasing demand signal from the Master Feedwater Control Unit or the 1B RFP Control Unit (the 1A RFP had been removed from service earlier). Group 2 and 5 Primary Containment Isolation System (PCIS) signals were received and all Group 2 and the inboard Group 5 Primary Containment Isolation Valves (PCIVs) closed. The High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems automatically initiated and injected per design. Unit 1 and Unit 2 Standby Gas Treatment (SBGT) systems received automatic initiation signals and the 1A train started (the 2A train was already running at the time of the event.) <br /><br /> The cause of this event is unknown. The 1B RFP responded as if high pressure steam to the 1B RFP turbine was unavailable. However, no evidence high pressure steam was not available could be found in the investigation following the event. <br /><br /> Corrective actions for this event included testing of the master and 1B RFP control loops, visual inspection and testing of the 1B RFP turbine controls, and testing of the 1B RFP during unit startup.
321 | 3211990020 | 1990-10-06 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 22 | On 10/6/90, at approximately 0337 CDT, Unit 1 was in the Run mode at approximately 536 CMWT (approximately 22 percent of rated thermal power) and decreasing as part of a scheduled shutdown to support maintenance on a Recirculation pump seal. At that time, a Main Turbine trip occurred on high vibration and a full Reactor Protection System actuation and Recirculation pump trip were initiated on Turbine Stop Valve (TSV) closure. <br /><br /> A second RPS actuation and a Primary Containment Isolation System Group 2 isolation occurred per design when reactor vessel water level decreased to Reactor Low Water Level 3. Reactor feedwater pumps restored and maintained reactor vessel water level and the Turbine Bypass Valves automatically controlled reactor pressure. <br /><br /> Causes of the event include a valve malfunction, a less than optimal design of TSV closure scram bypass pressure switches, and a failed Central Processing Unit (CPU) board. <br /><br /> Corrective actions include changing a valve motor operator torque switch setting, replacing a CPU board, and evaluating replacement of the pressure switches.
321 | 3211990021 | 1990-10-15 | QR6 | Manual Reactor Trip | [45 empty] | Hatch 1 | B | GE | PO | 70 | On 10/15/90 at approximately 1507 CDT, Unit 1 was in the Run mode at an approximate power of 1698 CMWT (approximately 70% rated thermal power). At that time, the unit was manually scrammed due to high vibration of the Main Turbine (EIIS Code TA). Following the manual scram, reactor vessel water level decreased as expected due to void collapse caused by the rapid power reduction. This resulted in a redundant Reactor Protection System (EIIS Code JC) actuation, a Group 2 Primary Containment Isolation System (PCIS, EIIS Code JM) isolation signal on low water level (Level 3), and closure of Group 2 Primary Containment Isolation Valves (PCIVs). The Reactor Feedwater Pumps (RFPs, EIIS Code SJ) and the Reactor Core Isolation Cooling (RCIC, EIIS Code BN) System were used to restore and maintain reactor vessel water level. Reactor pressure was controlled by the Turbine Bypass Valves (EIIS Code JI). <br /><br /> The cause of the Main Turbine high vibration has not been determined. A potential cause was the closure of Reheat Steam Source Valves (RSSVs, EIIS Code SB) 1N38-F101A and B to the second stage Moisture Separator Reheater (MSR, EIIS Code SB). Closure of the RSSVs would cause a rapid drop in the temperature of the low pressure turbine inlet steam and could result in movement of the low pressure turbine rotor in relation to the turbine shell as the two bodies of metal cooled at different rates. This could cause rubbing in the shaft seal area and an increase in main turbine vibration. The cause for RSSV closure has not been determined. All possible causes were investigated but no actual failure was revealed. Corrective actions include disabling a switch which can cause RSSV closure and correcting a drawing error.
321 | 3211991001 | 1991-01-18 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Hatch 1 | B | GE | PO | 100 | On 01/18/91, at approximately 1500 CST, Unit 1 was in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power). At that time, a remote power transmission line failed at its attachment point to the supporting electrical tower. In addition, a breaker in the Plant Hatch 230 kV switchyard failed to fully open in response to the sensed electrical fault conditions resulting in the trip of the Unit 1 main transformer auxiliary lockout relay. This resulted in main generator and main turbine trips, which, in turn, resulted in a reactor scram. This also resulted in a loss of power to the Unit 1 nonessential electrical busses and the prevention of the normal automatic transfer to the alternate supply due to the transfer logic. Power was manually restored to nonessential loads within approximately 2 to 3 minutes allowing for the initiation of operator actions to restore feedwater flow. In the interim, to recover reactor water level, the High Pressure Coolant Injection system (HPCI) automatically initiated. Although it exhibited erratic behavior in the automatic mode, it was successfully controlled manually and water level was restored and maintained with HPCI until feedwater flow was restored. Reactor pressure was controlled by the turbine bypass valves.<br /><br /> The root causes of the scram were the failure of the high tension power line and the failure of the main breaker to fully open. The root cause of the erratic HPCI operation was component failure in the HPCI speed controller. <br /><br /> Corrective actions included repairing the failed power line, repairing the failed breaker, and replacing the failed HPCI speed controller.
321 | 3211991004 | 1991-02-12 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 2/12/91 at approximately 0911 CST, Unit 1 was in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power). At that time, the unit scrammed on Turbine Stop Valve (TSV) closure. The main turbine tripped on a low Electrohydraulic Control (EHC) system hydraulic fluid pressure signal. Reactor water level decreased to approximately 3 inches above instrument zero and was restored to normal using the Reactor Feedwater Pumps (RFPs). Reactor vessel steam dome pressure briefly peaked at approximately 1111 psig and the Bypass Valves (BPVs) successfully controlled pressure. No Safety Relief Valves (SRVs) lifted. The pressure experienced in the main steam lines was transitory and apparently less than reactor vessel steam dome pressure. However, using steam dome pressure, the SRVs were possibly not in compliance with their 1% Technical Specifications tolerance requirement. The valves were removed and tested in accordance with code requirements. The actual drift experienced was within the bounds of a previous analysis demonstrating adequate overpressure protection. <br /><br /> The cause of this scram was vibration-induced component failure of Hydraulic Fluid Pressure Switch 1N32-N300. The cause of the SRV setpoint drift was corrosion-induced bonding of the surface between the pilot valve disc and seat. <br /><br /> Corrective actions for this event included replacing the pressure switch and moving it away from the source of vibration. The SRVs were tested and refurbished. Georgia Power Company (GPC) will continue to participate in the BWR Owners' Group action plan to resolve setpoint drift.
321 | 3211991007 | 1991-02-27 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Hatch 1 | B | GE | PO | 100 | On 2/27/91 at approximately 1247 CST, Unit 1 was in the Run mode at an approximate power level of 2436 CMWT (approximately 100% rated thermal power). At that time, both Recirculation Pumps tripped while plant Instrument and Controls (I&C) technicians were performing the quarterly surveillance on the turbine first stage pressure permissive input to the Reactor Protection System and the End-of-Cycle (EOC) Recirculation Pump trip logic. Loss of recirculation system flow caused a rapid increase in reactor water level and the Main Turbine and both Reactor Feedwater Pump Turbines tripped on high reactor water level. The Main Turbine trip resulted in a full scram per design. Reactor water level decreased such that the Group 2 Primary Containment Isolation System valves isolated. Reactor water level was recovered using the High Pressure Coolant Injection system and "A" Reactor Feedwater Pump. Reactor pressure was controlled with the Main Turbine Bypass Valves. <br /><br /> The cause of this event was personnel error. I&C technicians had inadvertently left in place a jumper following performance of a different surveillance on 2/22/91. This jumper, in conjunction with the surveillance on the turbine first stage pressure permissive instruments, was sufficient to actuate enough of the EOC Recirculation Pump trip logic to cause a trip of both pumps. <br /><br /> Corrective actions for this event include counseling the involved personnel, performing an inspection of both units' Main Control Room panels, and revising procedures.
321 | 3211991013 | 1991-08-09 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 8/9/91 at 1523 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, Generator Field Ground Detecting Relay 1N51-K751 actuated causing a Main Turbine trip and reactor scram on Turbine Stop Valve (TSV) closure per design. Reactor vessel water level decreased as expected due to void collapse resulting in a Group 2 Primary Containment Isolation System signal on low water level. All Group 2 Primary Containment Isolation Valves closed per design except Drywell Equipment Drain Sump Outboard Isolation Valve 1G11-F020. This valve took 114 seconds to close; however, it is required to close within 15 seconds of the receipt of an isolation signal. Valve 1G11-F019, the inboard isolation valve for the Primary Containment penetration, closed in 11 seconds, effectively isolating the penetration in the required time frame. Reactor vessel pressure increased to about 1120 psig following closure of the TSVs. All the Safety Relief Valves (SRVs) except 1B21-F013J opened to decrease pressure. A review of post-scram data indicated SRV 1B21-F013J behaved properly during the event. The Main Turbine Bypass Valves operated to control pressure after the SRVs closed. <br /><br /> The cause of this event is believed to have been a short duration ground. Post-scram testing of the generator revealed no existing ground fault. Calibration of relay 1N51-K751 indicated its trip setpoint had drifted, but spurious actuation of the relay could not be proven. The reason valve 1G11-F020 was slow to close is still under investigation. <br /><br /> Corrective actions include testing the generator, replacing relay 1N51-K751, and timing and scheduling an inspection of valve 1G11-F020.
321 | 3211991017 | 1991-09-11 | QR8 | Spurious Reactor Trip | [13 empty] | X | [30 empty] | X | Hatch 1 | B | GE | PO | 100 | On 9/11/91, at approximately 0925 CDT, unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent of rated thermal power). At that time, the Reactor Feedwater Pumps and the Main Turbine tripped on a false high reactor water level signal. Subsequently, the reactor scrammed and the Recirculation pumps tripped on Turbine Stop Valve (TSV) closure. Reactor pressure immediately increased to 1102 psig resulting in ten of the eleven Main Steam System Safety Relief Valves opening as designed. Reactor water level decreased to the Low Level 3 and 2 setpoints initiating actuation signals to the Primary Containment Isolation System (PCIS), the Units 1 and 2 Standby Gas Treatment Systems (SGTS), the Reactor Protection System (RPS), the High Pressure Coolant Injection (HPCI) system, and the Reactor Core Isolation Cooling (RCIC) system. Level was restored using the HPCI and RCIC systems. Immediately following the scram, RPS bus 'A' de-energized due to an undervoltage condition being sensed on the bus. This is a possible occurrence when RPS is on alternate supply and the 4160 V buses transfer as designed following a Main Turbine trip. The loss of the RPS bus resulted in initiation signals being transmitted to PCIS, SGTS, and the Main Control Room Environmental Control System pressurization mode logic. The bus was re-energized six minutes following the scram.<br /><br /> The cause of the event was cognitive personnel error on the part of a nonlicensed, contract Health Physics technician. The technician inappropriately leaned a hand-held radiation detector against a scram-sensitive panel. The instrument fell, contacting instrumentation valving and ultimately causing the false high level signal. The technician was counseled. A plant-wide directive will be issued addressing the event.
321 | 3211992009 | 1992-03-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 3/28/92 at 0432 CST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, reactor water level decreased as a result of operator actions in response to a feedwater flow transient caused by a momentary loss of power to the Reactor Feedwater Pump Turbine (RFPT) control system. When power was interrupted, flow from both Reactor Feedwater Pumps (RFPs) began to decrease causing water level to decrease. A licensed Operator took manual control of the RFPs, but was unable to prevent water level from decreasing to the scram and Group 2 PCIS isolation setpoint. The reactor scrammed and the Group 2 Primary Containment Isolation Valves closed per design. Water level reached a minimum of 12 inches below instrument zero (146 inches above the top of the active fuel). Operations personnel restored water level with the RFPs. No Emergency Core Cooling Systems initiated nor were any required to do so. Reactor pressure was controlled automatically with the Main Turbine Bypass Valves. No Safety Relief Valves were required to lift. <br /><br /> The causes of this event are personnel error and a less than adequate procedure. The Unit 1 Shift Supervisor mistakenly opened the supply breaker to 600V bus 1B thereby causing a loss of power to the RFPT control system. Procedure 34SO-R23-004-1S, "Hot Transfer of 600V AC System," did not require Danger tags to be hung on breaker control switches before breaker racking operations were performed. Corrective actions for this event include counseling involved personnel and revising appropriate procedures.
321 | 3211992014 | 1992-05-22 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 47 | On 5/22/92 at 2326 CDT, Unit 1 was in the Run mode at a power level of 1138 CMWT (47% rated thermal power). At that time, the four Turbine Stop Valves (TSVs) unexpectedly closed causing a full scram on TSV closure per design. As expected, water level decreased immediately following the scram due to void collapse from the rapid reduction in power. Level decreased to instrument zero (158 inches above the top of the active fuel) before being recovered to and maintained at its normal level (37 inches above instrument zero) with the "A" Reactor Feedwater Pump. As water level decreased to below 12.5 nches above instrument zero, a Group 2 Primary Containment Isolation System signal was received on low water level per design. All Group 2 Valves closed; however, valve 1G11-F019 did not close within the Technical Specifications required time limit of 15 seconds. It took approximately 16 seconds to close. <br /><br /> The cause of the event was an apparent manufacturer error. Filters supplied for use in the Unit 1 Electrohydraulic Control (EHC) system were made of material apparently incompatible with EHC fluid. As a result, they failed, allowing foreign particles to enter the system. This caused the fine mesh strainer on the servovalve of TSV #2 to clog resulting in closure of the TSVs. The cause of valve 1G11-F019 not closing within its required time was apparently excessive stem friction from the packing. Corrective actions for this event include replacing the Unit 1 and Unit 2 EHC system filters with the correct type, replacing the Unit 1 EHC servovalve inlet screens, replacing a solenoid valve, lubricating the stem on valve 1G11-F019, increasing the surveillance frequency on valve 1G11-F019, and repacking the valve during the next outage in which Cold Shutdown is achieved.
321 | 3211992021 | 1992-08-27 | QR7 | Other Reactor Trip (Valid RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Hatch 1 | B | GE | PO | 100 | On 8/27/92 at 0222 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the unit scrammed, the Group 1 Primary Containment Isolation System (PCIS) valves closed, and the pressurization mode of the Main Control Room Environmental Control System initiated per design on Main Steam Line (MSL) high radiation. Reactor water level decreased as expected due to void collapse from the rapid decrease in power. This resulted in isolation of Group 2 PCIS valves, isolation of Units 1 and 2 Secondary Containments, initiation of Units 1 and 2 Standby Gas Treatment systems, a trip of both Reactor Recirculation pumps, and initiation of the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems. Water level reached a minimum of 44 inches below instrument zero (114 inches above the top of the active fuel) before being recovered and controlled. Reactor pressure reached a peak of 1079 psig. Low Low Set was initiated manually and all four Low Low Set SRVs opened to decrease and control pressure per design. <br /><br /> The cause of this event was most probably an organic intrusion. It is believed that oil trapped on the resin and filter elements of the 'B' Condensate Filter/Demineralizer (F/D) entered the reactor feedwater when it was freed by flow and pressure changes resulting from the F/D being returned to service. The oil broke down in the reactor causing an increase in activation product carryover to the MSLs. This caused an increase in MSL radiation levels. Corrective actions for this event include increasing the time to return the F/Ds to service, replacing the filter elements in the 'B' Condensate F/D, and preparing a Technical Specifications change request.
321 | 3211992024 | 1992-09-30 | QR6 | Manual Reactor Trip | [45 empty] | Hatch 1 | B | GE | PO | 86 | On 9/30/92 at 0733 CDT, Unit 1 was in the Run mode at a power level of 2100 CMWT (86% rated thermal power). At that time, the unit was manually scrammed due to high turbine vibration. Reactor water level decreased as expected due to void collapse from the rapid decrease in power. This caused isolation of Groups 2 and 5 Primary Containment isolation valves, isolation of Unit 1 Secondary Containment, initiation of Units 1 and 2 Standby Gas Treatment systems, trip of both Reactor Recirculation pumps, and initiation of the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems. All systems functioned per design except that four Unit 2 Secondary Containment isolation dampers did not close. Water level reached a minimum of 38 inches below instrument zero (120 inches above the top of the active fuel) before being recovered. Reactor pressure was controlled by the Turbine Bypass Valves at its pre-scram value. <br /><br /> The cause of the high vibration was component failure. The bellows of pressure switch 1N38-N776 developed a leak which caused water to accumulate in its housing. The water shorted the switch terminal points causing the Reheat Steam Source Valves to the Moisture Separator Reheaters to close on a false low pressure signal. This caused a drop in the low pressure turbine steam inlet temperature and an increase in turbine vibration as different parts of the turbine cooled at different rates. The cause of the dampers not closing was a less than adequate design. The automatic isolation function of the dampers was defeated when their control switches were placed in the 'open' position. <br /><br /> Corrective actions include replacing the pressure switch, tagging the damper control switches in the 'auto' position, and implementing a design change.
321 | 3211993001 | 1993-03-16 | QL7 | Degraded condenser vacuum | [45 empty] | Hatch 1 | B | GE | PO | 36 | On 3/16/93 at 0812 CST, Unit 1 was in the Run mode at a power level of 877 CMWT (36% rated thermal power). At that time, Operations personnel manually scrammed the reactor in response to decreasing main condenser vacuum. Vacuum began decreasing approximately 45 minutes prior to the manual scram. Operations personnel noted the decrease and investigated possible causes. They also lowered reactor power from 1267 CMWT (52% rated thermal power) to 877 CMWT in an attempt to stop the decrease. However, vacuum continued to decrease and, with vacuum at 23.2 inches Hg, the reactor was manually scrammed to avoid an automatic scram and a trip of the Reactor Feedwater Pumps on low condenser vacuum. Reactor water level decreased to two inches above instrument zero (160 inches above the top of the active fuel) immediately following the scram due to void collapse from the rapid reduction in power before being recovered with the "A" Reactor Feedwater Pump. As water level decreased to below 12.5 inches above instrument zero, a Group 2 Primary Containment Isolation signal was received on low (Level 3) water level per design. All Group 2 isolation valves closed; however, valve 1G11-F019 did not close within the required time of 15 seconds. <br /><br /> The loss of vacuum was apparently caused by component failure. The steam trap in the condensate drain line for the Unit 1 steam packing exhauster apparently stuck in the open position. This created an air inleakage flow path to the main condenser. The inleakage flow rate exceeded the capacity of the main condenser steam jet air ejector; therefore, vacuum decreased. The cause of valve 1G11-F019 not closing within its required time was apparently excessive stem friction from its packing, Corrective actions for this event include rebuilding the steam trap, repacking valve 1G11-F019, and rebuilding its actuator.
321 | 3211993009 | 1993-05-14 | QR8 | Spurious Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Hatch 1 | B | GE | PO | 7 | On 5/14/93 at 0535 CDT, Unit 1 was in the Run mode at a power level of 170 CMWT (7% rated thermal power). At that time, the unit scrammed when licensed operations personnel moved the reactor mode switch to the Run position. At 0536 CDT, a Group 1 Primary Containment Isolation System (PCIS) isolation signal was received on low reactor pressure while in the Run mode. The Main Steam Isolation Valves (MSIVs) closed per design. Three seconds after receipt of the Group 1 PCIS isolation signal, operations personnel moved the mode switch out of the Run position as required by plant procedures. This bypassed the Group 1 PCIS isolation on low reactor pressure before two of the four reactor pressure switches could trip. Consequently, sufficient isolation logic was not initiated to close the remaining Group 1 PCIS valves. Reactor water level decreased to a minimum of 25 inches above instrument zero (183 inches above the top of the active fuel) due to void collapse from the rapid decrease in reactor power. Water level was restored automatically with the "A" Reactor Feedwater Pump. <br /><br /> The cause of the scram was less than adequate maintenance procedures, less than adequate post-maintenance testing, and personnel error. Because the MSIV limit switch maintenance procedures were less than adequate, it appears the replacement of the limit switches resulted in blown fuses in the Reactor Protection System (RPS). Less than adequate testing and personnel error resulted in a failure to detect the blown fuses. As a result, a scram on MSIVs less than 90% open resulted when the mode switch was moved to the Run position, arming that portion of the RPS logic tripped by the blown fuses. Corrective actions include revising procedures and disciplining personnel.
321 | 3211993012 | 1993-06-15 | QR8 | Spurious Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Hatch 1 | B | GE | PO | 100 | On 6/15/93, at 1453 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent of rated thermal power). At that time, an automatic reactor scram and isolation of the inboard Group 2 Primary Containment Isolation System (PCIS) valves occurred due to a false low reactor water level signal. Control rods fully inserted as designed. As expected, actual water level decreased immediately following the scram, reaching a minimum level of 34 inches below instrument zero (124.5 inches above the top of the active fuel). At approximately 10 inches above instrument zero, an actuation of the outboard PCIS occurred on an actual low water level condition. The Reactor Feedwater Pumps (RFPs) responded to the actual low level condition and restored water level. No Emergency Core Cooling Systems actuated as a result of the low water level condition, nor were they required to actuate. Reactor pressure decreased as a result of the scram and was then controlled by the Turbine Bypass Valves at approximately 920 psig. Due to misleading level indications, level increased above the bottom of the Main Steam Lines, resulting in water intrusion into the lines. <br /><br /> The cause of the event was a loose packing nut on an instrument isolation valve becoming disengaged during an instrument calibration. This ultimately resulted in depressurization of the sensing line and a false low reactor water level signal. Corrective actions include repairing the valve, checking other similar installations on both units, performing a walkdown of system piping, and analyzing the effect of water in the Main Steam Lines.
321 | 3211993013 | 1993-10-22 | QP3 | Loss of Condensate Flow | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 10/22/93 at 1744 CDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the condensate pumps tripped. This caused a decrease in feedwater flow to the reactor vessel and a corresponding decrease in reactor water level. At 1744 CDT, with water level at approximately 18 inches above instrument zero and decreasing, personnel inserted a manual reactor scram. Water level decreased to a minimum of 52.4 inches below instrument zero (106 inches above the top of active fuel) due to the loss of feedwater flow and void collapse from the decrease in reactor power. A Group 2 Primary Containment Isolation System signal was received at about 12.3 inches above instrument zero. All Group 2 Primary Containment Isolation Valves (PCIVs) closed. Also, the recirculation system pumps tripped, the Unit 1 secondary containment isolated, the Unit 1 and Unit 2 Standby Gas Treatment systems initiated, and the Group 5 PCIVs closed. The High Pressure Coolant Injection and Reactor Core Isolation Cooling systems automatically started when water level decreased to 35 inches below instrument zero. They restored reactor water level to greater than 12 inches above instrument zero within four minutes of the scram. All systems functioned per design. Thermal stratification led to violations of pressure and temperature and heatup rate limits. The trip of the condensate pumps appears to have been most likely caused by vibration in a condenser hotwell level instrument. This level instrument provides a trip signal to all the condensate pumps. The exact problem has not been determined. Corrective actions included trouble shooting the instrument and logic circuit and implementing a temporary modification to disable the pump trip on low hotwell level.
321 | 3211993016 | 1993-12-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 12/7/93 at 0602 EST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the unit automatically shut down on low reactor vessel water level caused by an automatic shutdown of the "A" Reactor Feedwater Pump (RFP) and a failure of the Reactor Recirculation pumps to run back to 44% speed per design. A Group 2 Primary Containment Isolation System (PCIS) signal on low reactor water level was also received, and the Group 2 Primary Containment Isolation Valves (PCIVs) closed as required. As water level decreased due to void collapse from the rapid reduction in power, the Group 5 PCIVs closed, the Unit 1 secondary containment isolated, the Unit 1 and Unit 2 Standby Gas Treatment systems initiated, the Recirculation pumps automatically shut down, and the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems initiated on low low reactor water level per design. The High Pressure Coolant Injection system did not inject to the vessel because its initiation signal cleared before the injection valve received all of its permissive signals to open. Water level decreased to a minimum of 50 inches below instrument zero (108 inches above the top of active fuel) before being recovered by the "B" RFP and the Reactor Core Isolation Cooling system. Water level was maintained greater than 24 inches above instrument zero with the "B" RFP. <br /><br /> The "A" RFP shut down due to a low RFP lube oil system pressure resulting from a loss of power to the "B" lube oil system pump. The supply breaker to the lube oil system pump inadvertently opened and de-energized the pump motor. The standby lube oil pump did not prevent the RFP trip due to pressure fluctuations in the oil header. The Recirculation system pumps did not run back due to a clogged sensing line which delayed a low RFP flow signal to the runback logic.<br /><br /> Corrective actions included testing the breaker, clearing the sensing line, reviewing the lube oil system response to a pump trip, replacing a pressure switch, and adding an automatic start signal to the lube oil pumps.
321 | 3211994003 | 1994-03-29 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 3/29/94 at 0101 EST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time a full Reactor Protection System (RPS) actuation and an automatic reactor shutdown occurred due to a trip of the Main Turbine. When the Main Turbine tripped, reactor pressure increased as expected to a maximum of 1085 psig and was relieved by the automatic opening of the Main Turbine Bypass Valves and seven safety relief valves (SRVs) per design. The SRVs closed as required and reactor pressure was then controlled by the Main Turbine Bypass Valves. Reactor water level decreased to a minimum of 14 inches above instrument zero (172 inches above the top of active fuel), resulting in closure of the inboard Group 2 Primary Containment Isolation System valves. Normal reactor water level was restored with the Feedwater System. The cause of this event was a loss of Main Generator field excitation leading to a trip of the Main Turbine and an automatic reactor shutdown. Field excitation was lost when arcing occurred between the Main Generator Exciter (MGE) brush rigging and one of the collector rings on the MGE rotor. Engineering personnel believe the primary factor in the arcing was sticking of a brush in the brush rigging. <br /><br /> Corrective actions for this event included replacing the damaged MGE rotor with a rotor from the Unit 2 MGE, sending the Unit 1 MGE rotor off site for repair, and increasing the frequency of MGE brush inspections to daily.
321 | 3211994014 | 1994-11-19 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 59 | On 11/19/94 at 0005 EST, Unit 1 was in the Run mode at a power level of 1437 CMWT (59 percent rated thermal power). Load had been reduced from about 99 percent rated thermal power 24 minutes earlier in response to a complete loss of feedwater heating. At 0005 EST, the reactor automatically shut down per design on Turbine Stop Valve closure. The Turbine Stop Valves closed when the turbine shut down on Moisture/ Separator Reheater (MSR) A/B high water level. Reactor vessel water level decreased from its normal value of 36 inches to a minimum of seven inches (151 inches above the top of the active fuel). The Group 2 Primary Containment Isolation System valves automatically closed on low reactor vessel water level per design. The Reactor Feedwater Pumps restored and maintained water level. No Emergency Core Cooling Systems were required to actuate. Reactor pressure was adequately controlled by the Turbine Bypass valves. <br /><br /> The cause of the loss of feedwater heating was a damaged wire in a drain pot level switch combined with out-of-adjustment heater controls. This switch was repaired on 11-19-94. A more restrictive thermal limit was temporarily imposed on the core to insure a similar loss of feedwater heating event will not result in exceeding fuel design limits.<br /><br /> Investigation did not reveal any equipment problems that would have led to a high water level condition in the MSR.
321 | 3211996001 | 1996-01-04 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Hatch 1 | B | GE | PO | 95 | On 1/4/96 at 0005 EST, Unit 1 was in the Run mode at a power level of 2315 CMWT (95 percent rated thermal power). At that time, personnel noted a Main Turbine Bypass Valve (BPV) opening and the No. 2 Main Turbine Control Valve (TCV) closing. The Shift Supervisor ordered power reduced in order to close the BPV. By 0010 EST, the BPV had closed and reactor power had been reduced to approximately 72 percent rated thermal power. However, at 0020 EST, all three BPVs opened, the No. 1 and No. 3 TCVs closed, and the reactor automatically shut down on high pressure. Water level decreased due to void collapse from the rapid reduction in power and resulted in a Group 2 Primary Containment Isolation System isolation signal and closure of the Group 2 valves per design. Level reached a minimum of approximately instrument zero (158 inches above the top of the active fuel) before being restored automatically by the Feedwater Pumps. No Emergency Core Cooling Systems actuated nor were any required to actuate. Pressure reached its maximum value of 1046 psig at the time of the automatic shutdown and was controlled automatically thereafter by the BPVs. No Safety/Relief Valves lifted nor were any required to lift. <br /><br /> This event was caused by clogging of the TCV servovalve strainers by a foreign substance. With the strainers clogged, the electrohydraulic control system could not maintain sufficient pressure in the servovalves. The source of the substance has not yet been identified positively.
321 | 3211996004 | 1996-03-23 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Hatch 1 | B | GE | PO | 17 | On 3/23/96 at 0135 EST, Unit 1 was in the Run mode at a power level of 424 CMWT (17.4% rated thermal power). At that time, personnel manually shut down the turbine. When the turbine was shut down as part of a planned activity for the purpose of beginning a refueling outage, reactor pressure increased to approximately 1045 psig and the reactor automatically shut down on high pressure. Water level decreased due to void collapse from the rapid reduction in power. However, the transient did not result in level decreasing to the automatic reactor shutdown and Primary Containment Isolation System setpoint; therefore, no additional automatic actions occurred. Level decreased to 12 inches above instrument zero (170 inches above the top of the active fuel) before being restored by the reactor feedwater pump. No Emergency Core Cooling Systems actuated nor were any required to actuate. Pressure reached its maximum value of 1045 psig at the time of the automatic shutdown and was reduced and controlled by steam loads and the turbine bypass valves. No safety/relief valves lifted nor were any required to lift.<br /><br /> This event was caused by an inadequate procedure. When the turbine is manually shut down, an immediate pressure increase occurs. Procedure 34SO-N30-001-1S, 'Main Turbine Operation,' did not require pressure to be decreased in order to provide sufficient margin to the high pressure automatic shutdown setpoint prior to manual shutdown of the turbine. Procedures 34SO-N30-001-1S and 34SO-N30-001-2S, 'Main Turbine Operation,' have been revised.
321 | 3211996008 | 1996-04-30 | L3 | Turbine Bypass Unavailable | [10 empty] | X | [30 empty] | X |  |  |  | Hatch 1 | B | GE | SU | 11 | On 4/30/96 at 0841 EST, Unit 1 was in the Run mode at a power level of 280 CMWT (11% rated thermal power). At that time, the main turbine bypass valves closed unexpectedly causing reactor pressure to increase. The reactor shut down automatically on high pressure. Reactor water level decreased to 20.5 inches above instrument zero (179 inches above the top of the active fuel) before being restored by the reactor feedwater system. Reactor water level remained above the automatic reactor shutdown and Primary Containment Isolation System setpoint; therefore, no additional automatic actions occurred. Pressure reached its maximum value of 1081 psig two seconds after the automatic shutdown and was reduced by steam loads. No safety/relief valves lifted nor were any required to lift. <br /><br /> This event was caused by an inadequate procedure. Procedure 34SO-N32-001-1S, 'EHC Hydraulic System,' contained instructions intended to isolate a portion of the Electrohydraulic Control (EHC) system while maintaining bypass valve capability. However, as was discovered after the event, the configuration of the EHC system piping does not allow a portion of the system to be isolated while maintaining bypass valve capability. When this subsection of the procedure was performed to repair EHC system leaks on the main turbine stop and control valves, EHC system fluid was partially isolated to the bypass valves and they failed closed per design. The procedure has been revised to eliminate the use of the incorrect instructions.
321 | 3211996009 | 1996-05-26 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Hatch 1 | B | GE | PO | 18 | At 0517 EDT on 5/26/96, Unit 1 was in the Run mode at a power level of 460 CMWT (18 percent rated thermal power). The main turbine had previously been removed from service to allow repair of a leaking hydraulic control line. At that time, Control Room operators received annunciators indicating that both reactor feed pumps had automatically tripped. Reactor water level began decreasing and licensed operators attempted unsuccessfully to restart one of the tripped feed pumps. When it became apparent that the water level decrease could not be reversed, operators inserted a manual reactor shutdown signal in anticipation of receiving an automatic reactor shutdown signal on low reactor water level. Prior to water level reaching the setpoint for automatic initiation of the High Pressure Coolant Injection (HPCI) system, operators manually started the Reactor Core Isolation Cooling (RCIC) system to restore water level. Water level began increasing after reaching a minimum of 30 inches below instrument zero (128.4 inches above the top of the active fuel). Pressure was controlled by the bypass valves and water level was controlled by the RCIC and Control Rod Drive systems. The cause of this event was a component failure. A failed electronic circuit board in the reactor feed pump turbine monitoring system resulted in automatic shutdown of both reactor feed pump turbines. An inadequate logic system design was a contributing factor to the event. Corrective actions for this event include: 1) replacement of the failed component; and 2) modification of the system design during upcoming refueling outages currently scheduled for Fall 1997 (Unit 1) and Spring 1997 (Unit 2).
321 | 3211999003 | 1999-05-07 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 53 | On 05/07/1999 at 0822 EDT, Unit 1 was in the Run mode at a power level of 1465 CMWT (53 percent rated thermal power). At that time, the Unit 1 reactor automatically shut down when the Main Turbine control valves closed, resulting in a high reactor pressure condition. Reactor water level decreased due to void collapse from the rapid power reduction, resulting in receipt of a Group 2 Primary Containment Isolation System signal and closure of Group 2 valves as designed. Level reached a minimum of approximately 32 inches below instrument zero (126 inches above top of active fuel) before being restored automatically by the Feedwater Level Control system. No emergency cooling systems actuated nor were any required to actuate to restore or maintain reactor water level. Pressure reached its maximum value of approximately 1083 psig at the time of the shutdown, decreasing thereafter until the main turbine bypass valves automatically controlled pressure. The peak pressure was below the Main Steam Safety/Relief Valve actuation setpoints; thus, no Safety/Relief Valve operation was required or occurred. This event was caused by the manual closure of a valve common to the pump discharge of both loops of the Main Turbine ElectroHydraulic control system, which in turn caused a loss of system pressure to the Main Turbine Control Valves, resulting in their automatic closure. A plant equipment operator performed the manual valve closure in error as part of an equipment clearance evolution preceding routine changeout of an EHC discharge filter. Corrective actions included personnel discipline and procedure improvement.
321 | 3212000002 | 2000-01-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 01/26/2000 at 0653 EST, Unit I was in the Run mode at a power level of 2763 CMWT (100% of rated thermal power) when the reactor shut down automatically, and the Group 2 Primary Containment Isolation Valves (PCIVs) closed on low water level. Water level decreased when feedwater flow was reduced following the unexpected closure of an inlet valve to a feedwater heater. Following shutdown, water level continued to decrease due to a void collapse from the rapid reduction in power, resulting in closure of the Group 5 PCIVs and automatic initiation of the Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) systems. The secondary containment dampers automatically isolated, and all trains of the Unit I and Unit 2 Standby Gas Treatment systems automatically started on low water level. Water level reached a minimum of 54 in. below instrument zero. The Reactor Feedwater Pumps, RCIC, HPCI, and Control Rod Drive systems restored level to > 40 in. above instrument zero within 40 sec of the shutdown. Pressure decreased from its normal value of 1030 psig to a minimum of 746 psig approximately 2 min following shutdown. At that time, the main steam line isolation valves (MSIVs) were closed because water level was approaching the main steam line nozzles. MSIV closure caused pressure to increase to a maximum of 1085 psig approximately 17 min following shutdown. Pressure was reduced and controlled using manual and automatic safety/relief valve actuation. The feedwater heater inlet valve closed upon receipt of an apparent spurious signal from its control switch. The inlet valve closure was most likely the result of a slight jarring of either the control switch or its panel. Switches of this type have been known to actuate with very little movement of the control mechanism. The delay of the HPCI system to trip automatically at its high level setpoint resulted in water level reaching the main steam line nozzles. Testing of the level transmitters, trip units, relays, and logic system revealed no reason for the delay in tripping. Corrective actions include replacing control switches, reviewing the type and frequency of logic system testing, and additional operator training.
321 | 3212000004 | 2000-07-10 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 99 | On 07/10/2000 at 1050 EDT, Unit 1 was in the Run mode at a power level of 2754 CMWT (99.7 percent rated thermal power). At that time, the reactor scrammed and the reactor recirculation pumps tripped automatically on turbine stop valve fast closure caused by a turbine trip. The turbine tripped when the vibration instrument on the #10 bearing failed causing a false high vibration trip signal to be generated. Following the reactor scram, water level decreased due to void collapse from the rapid reduction in power. However, the reactor feedwater pumps maintained water level higher than seventeen inches above instrument zero. Consequently, no safety system actuations on low level were received nor were any required. Pressure reached a maximum value of 1128 psig; nine of eleven safety/relief valves lifted to reduce reactor pressure. Pressure did not reach the nominal actuation setpoints for the remaining two safety/relief valves. The temperature in the vessel bottom head region decreased by more than the Technical Specification allowed 100 in one hour before a recirculation pump could be re-started. This event was caused by component failure. The vibration instrument on the #10 bearing failed, generating a false high vibration signal. The high vibration signal caused the main turbine to trip, producing a reactor scram on turbine stop valve fast closure per design. The failed vibration instrument was replaced. The vibration instruments on the remaining bearings were checked resulting in the replacement of the shaft rider probe on the #6 bearing. No other instrument problems were found.
321 | 3212000011 | 2000-09-29 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Hatch 1 | B | GE | PO | 55 | On 09/29/2000 at 1357 EDT, Unit 1 was in the Run mode at a power level of approximately 1520 CMWT (55 percent rated thermal power). At that time, the reactor was scrammed manually following a trip of the operating Reactor Feedwater Pump (RFP) and a decrease in water level. Personnel inserted the scram in anticipation of an automatic scram on low water level. Following the scram, level continued to decrease due to void collapse from the rapid reduction in power and the trip of the RFP resulting in closure of the Group 2 and Group 5 Primary Containment Isolation Valves as designed. Level reached a minimum of approximately 40 inches below instrument zero causing automatic initiation of the Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) systems. Secondary containment automatically isolated and all four trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low level. The RCIC and HPCI systems recovered level; an RFP was placed into service to maintain level. Pressure decreased immediately following the manual scram; no Safety/Relief Valves lifted nor were any required to lift. Pressure was controlled automatically by the Main Turbine Bypass Valves. This event was caused by component failure. During the implementation of a clearance to isolate a condensate pump, air was introduced into the condensate pump suction header through a leaking pump suction isolation valve. The presence of air led to the trip of the operating RFP on low suction pressure. The valve will be repaired or replaced as necessary during the refueling outage that began on 09/29/2000.
321 | 3212001002 | 2001-03-28 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 100 | On 03/28/2001 at 1853 EST, Unit 1 was in the Run mode at a power level of 2763 CMWT (100 percent rated thermal power). At that time, the reactor scrammed on turbine control valve fast closure caused by a turbine trip. The turbine tripped when actuation of phase 2 and 3 differential relays for unit auxiliary transformer lB resulted in actuation of a lockout relay, generating a direct turbine trip signal. Following the scram, water level decreased due to void collapse from the rapid reduction in power resulting in closure of Group 2 and the outboard Group 5 primary containment isolation valves and automatic initiation of the Reactor Core Isolation Cooling and High Pressure Coolant Injection systems. The low level initiation signal cleared before either system could inject water to the vessel. The outboard secondary containment dampers automatically isolated, and all trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low water level. Level reached a minimum of 37 inches below instrument zero. The Reactor Feedwater Pumps restored level to its pre-event value of approximately 35 inches above instrument zero within 30 seconds of the scram. Pressure reached a maximum value of 1127 psig; five of eleven safety/relief valves lifted to reduce pressure. Pressure did not reach the nominal actuation setpoints for the remaining safety/relief valves. This event was caused by an internal fault in unit auxiliary transformer 113. The fault occurred on the high side winding of transformer phase 3. The transformer was removed from service; its loads will continue to be supplied from their alternate supply until a new transformer can be procured and installed.
321 | 3212002001 | 2002-02-08 | QL7 | Degraded condenser vacuum | [45 empty] | Hatch 1 | B | GE | PO | 27 | On 02/08/2002, at 2252 EST, Unit 1 was in the Run mode at 27% rated thermal power (746 CMWt). At that time, the Reactor Protection System (RPS) was manually actuated to facilitate placing the Main Condenser mechanical vacuum pump in service. Prior to the reactor shutdown, on 02/08/2002, at approximately 2100 EST, degraded operation of the Main Condenser Off Gas Recombiner System had resulted in high hydrogen in the Off Gas. Procedure 34AB-N62-001-1S (FAILURE OF RECOMBINER AND CONTROL OF SUSTAINED COMBUSTION IN THE OFF GAS SYSTEM) was entered at about 2100 EST and licensed personnel proceeded to reduce reactor power from 100 percent rated thermal power beginning at about 2105 EST. Per the procedure, the in-service Steam Jet Air Ejector was removed from service at about 2200 EST due to Off Gas Hydrogen concentration reaching approximately 4%. Unit 1 was scrammed to facilitate placing the mechanical vacuum pump in service for maintaining the Main Condenser as the heat sink. The lowest Reactor Water Level during the scram was approximately 165 inches above the top of the active fuel (7 inches above instrument zero) this was above any ESF actuation settings. Therefore, no automatic ESF actuations were received and none were required. There was no Reactor Pressure increases during the scram. Reactor pressure following the reactor shutdown did not exceed the pre-event level of 1035 psig. The cause of the event was component failures that resulted in blocked drain lines in the off gas system. The blocked drain lines caused the recombining action to degrade resulting in high hydrogen in the off gas system. Corrective actions included restoring the off gas system drain lines.
321 | 3212002002 | 2002-04-19 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Hatch 1 | B | GE | PO | 18 | On 4/19/02 at 1650 EST, Unit 1 was in the Run mode at a power level of approximately 525 CMWT (19 percent rated thermal power). Power was reduced in order to identify and repair the source(s) of leakage into the drywell floor drain sump. Limiting Condition for Operation (LCO) 3.4.4 establishes limits for both the increase in rate within a 24-hour period and the overall rate of unidentified leakage in the drywell. The leakage exceeded the allowable limits of Technical Specifications LCO 3.4.4. Therefore, at approximately 2100 EST a manual scram was inserted using the normal shutdown procedure, shutting down the unit as required by LCO 3.4.4, Required Action C. 1. A drywell entry was made, and on 4/20/02 at approximately 0036 EST it was determined that the source of drywell leakage originated from a leaking Safety Relief Valve (SRV) 1B21F013J. The tailpipe vacuum breaker (1B21F037J) associated with this SRV had failed in the stuck open position allowing steam to vent directly into the drywell. By 0146 EST, the drywell unidentified leakage rate was within the Technical Specification limits. The cause of SRV 1B21FO13J leaking was component failure. The valve's main disc was stuck in the partially open position. The actuator piston had become cocked on the main disc's stem causing it to bind in the valve body. The cause of the vacuum breaker (1B21F037J) failing was determined to be the result of leakage past the main seat of SRV 1B21FO13J. This leakage caused the vacuum breaker to rapidly cycle open and closed which caused the bolts holding the disc to the swing arm to break. The safety relief valve and the vacuum breaker were replaced and functionally tested.
321 | 3212005002 | 2005-10-29 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Hatch 1 | B | GE | PO | 100 | On 10/29/2005 at 1330 EST, Unit 1 was in the Run mode at an approximate power level of 2804 CMWT (100 percent rated thermal power). At that time, the reactor tripped on turbine control and stop valve fast closures. The turbine and generator tripped when the main power transformer experienced a fault which resulted in a main generator neutral ground overcurrent lock-out. Following the reactor scram, water level decreased due to void collapse from the rapid reactor pressure increase, reaching a minimum of approximately sixteen inches below instrument zero (about 142 inches above the top of the active fuel). The decrease in water level resulted in closure of the Group 2 primary containment isolation valves per design. The operating reactor feedwater pump restored level to its design set point. Reactor pressure peaked at approximately 1145 psig, resulting in all eleven main steam safety relief valves opening as designed to reduce pressure. The event was caused by an internal fault in the main power transformer. Heat from the fault resulted in an explosive rupture of the transformer shell at its top edge, and a subsequent fire within the transformer. A Notice of Unusual Event was declared, and the installed fire suppression system along with the on-site fire brigade extinguished the fire. The transformer was replaced, and all systems and components affected by the fire or the transformer fault were inspected and repaired.
321 | 3212008003 | 2008-07-04 | QR5 | Turbine Trip | [45 empty] | Hatch 1 | B | GE | PO | 99 | On July 4, 2008 at 08:39 EDT, Unit 1 was in the Run mode at a power level of approximately 2797 CMWT, 99.7 percent rated thermal power. At that time testing of the 'Electro-hydraulic Control (EHC) pump auto start was in progress. During the testing, a Low EHC Pressure was sensed which resulted in a turbine trip. The reactor tripped on turbine control valve fast closure. Following the reactor scram, reactor pressure peaked at approximately 1120 psig, resulting in four of the eleven safety relief valves (SRV’s) opening as designed to reduce pressure. Water level decreased due to void collapse resulting in the closure of the Group 2 primary containment isolation valves, and a Reactor Feed Pump Turbine speed increase, both per design. The feedwater level control system controlled reactor water level with a minimum water level of approximately 2.5 inches above instrument zero (about 160 inches above the top of active fuel). All control rods fully inserted. Pressure did not reach the nominal actuation set points for the remaining seven SRV’s. This event was caused by a sensed low pressure in the EHC system tripping the main turbine which results in an automatic reactor scram. Performance of the weekly EHC pump auto start procedure has been suspended pending additional corrective actions. Installation of a time delay circuit, relocation of the pressure sensor tap to its previous location, along with additional corrective actions will be considered and tracked in the corrective action program.
321 | 3212008004 | 2008-11-22 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Hatch 1 | B | GE | PO | 99 | On November 22, 2008 at approximately 1019 EST, Unit 1 was in the Run mode at a power level of approximately 2800 CMWT, 99.8 percent rated thermal power. A manual scram was inserted due to Reactor Water Level (RWL) decreasing to 10 inches above instrument zero and continuing to decrease. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) automatically started on low RWL, Level 2. RWL decreased to approximately negative 68 inches (about 90 inches above the top of active fuel) prior to it being recovered by HPCI and RCIC operation. Due to the RWL reaching the Anticipated Transient Without Scram - Recirculation Pump Trip (ATWS-RPT) low level, the recirculation pumps tripped as designed. As RWL was recovering, HPCI was manually secured and RCIC flow was decreased. The 1A Reactor Feed Pump (RFP) was subsequently restarted and RWL control was then transitioned to the 1A RFP. Investigation determined that the direct cause of the event was failure of DC power supply 1N21-K088 which provides power to the differential pressure (DP) controller for the (Steam Jet Air Ejector) SJAE Intercondenser Cooling water control valve 1N21-F211. The DC power supply 1N21-K088 was replaced and a repetitive task has been created to replace the component at a prescribed interval.
321 | 3212009004 | 2009-05-10 | QR8 | Spurious Reactor Trip | [45 empty] | Hatch 1 | B | GE | PO | 8 | On May 10 at 1041 EDT, Unit 1 was in run at 224 CMWT, 8 percent power. At this time a reactor startup from a planned maintenance outage was in progress. Upon placing the reactor mode switch to the run mode as part of normal startup activities, a full reactor scram was initiated. Intermediate Range Neutron Monitoring (IRM) upscale trips were received in each of the two Reactor Protection System (RPS) scram channels. Investigation revealed that the ‘1A’ IRM (Bus A) and the ‘1 H’ IRM (Bus B) had spiked upscale when the mode switch was taken to run. The cause of the scram was an electrical noise spike transmitted into the IRM’s. The noise signal was sufficient to cause IRM “A” and “H” to trip on "high-high" neutron flux level. Replacing degraded cables, and connections, as well as improving grounding of the neutron monitoring system improved noise levels in the system. In addition ferrite beads were installed on each cable entering and/or exiting the preamplifier NEMA enclosures on each of the eight IRM channels.
321 | 3212013001 | 2013-02-10 | QL6 | Condenser Leakage | [45 empty] | Hatch 1 | B | GE | PO | 100 | On February 10, 2013 at 0536 Eastern Standard Time (EST), while operating at 99.8 percent rated thermal power (RTP), a system operator reported that the "System Inlet High Conductivity" alarm had been received at the local Condensate Polishing System panel. This annunciator is set to alarm when conductivity reaches 0.239 micro mhos per cm. Control room instruments immediately began to indicate that conductivity levels were slowly increasing for the condenser and the reactor vessel coolant. The crew entered the abnormal operating procedure for Condenser Tube Leaks/Chemical Intrusion and began decreasing power to 88 percent at 0555 EST. The crew continued to reduce power to 47 percent RTP. Inlet conductivity reached 5 micro mhos per cm and the shift supervisor directed the crew to enter the abnormal operating procedure for a manual SCRAM at 0700 EST. The unplanned manual RPS actuation was initiated as a protective action for the reactor vessel, as the increasing water chemistry conductivity indicated a possibly serious condition in which circulating water tube(s) were damaged within the condenser and were leaking into the hot well. After shutdown, significant damage to condenser internals was discovered, including fractures in the false bottom and divider wall. A section of a tube bundle was damaged by impact from fractured steel sections. The direct cause of this damage was operating the condenser with high hotwell water levels while thermodynamically driven pressure surges were taking place under the false bottom. Repairs were made and better methods of monitoring and controlling hotwell levels were instituted. Measures were put in place to better control theromdynamic inputs into the hotwell.
321 | 3212017005 | 2017-04-20 | QR8 | Spurious Reactor Trip | [45 empty] | Hatch 1 | B | GE | SU | 1 | On April 20, 2017 at 0302 EDT with Unit 1 at approximately 1 percent rated thermal power due to a reactor startup from a planned maintenance outage, an automatic reactor scram was received due to the "A" and "B" Intermediate Range Monitors (IRMs) spiking upscale simultaneously. The instrument's set points for high-high neutron flux were reached, giving false trip signals to both channels of the reactor protection system (RPS) trip logic. Upon the automatic reactor scram signal, all control rods fully inserted appropriately. No primary containment isolation system (PCIS) actuations occurred and none were expected to occur based upon plant conditions following the reactor scram. <br /><br /> The cause of the event is due to the integrity of the IRMs signal cable connectors being in a degraded condition. Degradation was found on "A" IRM at the detector connector, while the "B" IRM had connection issues between the penetration and the jumper connector. These IRM cable integrity issues allowed a signal path to exist between the cables' shielding and center conductors, causing the IRMs to spike upscale. The "A" and "B" IRM jumper cables and the associated connections were replaced and all Unit 1 IRM cables and associated trip logics were tested satisfactorily.
321 | 3212021001 | 2021-08-03 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Hatch 1 | B | GE | PO | 100 | On 08/03/2021 at 1026 EDT, Unit 1 experienced an automatic reactor SCRAM and containment isolation due to low reactor water level. A spurious trip of a Turbine Building 600V breaker caused a loss of control power and immediate trip of both 1A and 1B reactor feed pumps. Due to loss of reactor feedwater, the reactor water level lowered to the setpoints for the following automatic actuations: reactor SCRAM, High Pressure Coolant Injection (HPCI) start, Reactor Core Isolation Cooling (RCIC) start, and both primary and secondary containment isolation. All safety-related actuations occurred as designed. Reactor operators responded to stabilize the plant and control reactor water level. Unit 2 was not affected. The initial notification to the NRC was documented in Event Notification 55394. <br /><br /> Corrective action was completed to replace the failed breaker with a more reliable breaker. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuations of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
321 | 3212022001 | 2021-12-29 | QR6 | Manual Reactor Trip | [45 empty] | Hatch 1 | B | GE | PO | 90 | On 12/29/2021 at 1552 EST, with Unit 1 in Mode 1 at 90% power, the reactor was manually tripped due to reactor pressure perturbations. The cause of the reactor pressure perturbations was the failure of a main steam throttle pressure transmitter, Additionally, closure of containment isolation valves (CIVs) in multiple systems occurred during the trip as a result of reaching the actuation setpoint on reactor water level. The trip was not complex, with all systems responding normally post-trip. <br /><br /> Corrective action was completed to replace the failed transmitter. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuations of systems listed in 10 CFR 50,73(a)(2)(iv)(B).
323 | 3231987001 | 1987-03-05 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Diablo Canyon 2 | P | WE | SU | 4 | At 1727 PST, March 5, 1987, with the unit in Mode 2 (Startup), an automatic reactor trip occurred due to a low-low steam generator (SG) 2-4 water level. The appropriate procedures were followed and the unit was stabilized in Mode 3 (Hot Standby) at 1737 PST, March 5, 1987. The significant event notification required by 10 CFR 50.72 was completed by 1820 PST, March 5, 1987. <br /><br />Operations personnel were in the process of rolling the main turbine after a short forced outage. The auxiliary feedwater (AFW) pumps were supplying feedwater as the main turbine speed was being increased. The increased steam demand required to accelerate (ramp) the turbine generator was greater than the AFW pumps capacity to supply feedwater causing SG water levels to decrease. Attempts were made to restore SG levels by slowing the ramp and then placing the ramp on hold; however, the actions were taken too late to prevent the low-low SG water level trip. <br /><br /> The root cause is attributed to personnel error in that the operators failed to control the steam demand from the steam generators within the capacity of the AFW system and that miscommunication occurred between the shift foreman and the control operator about when to commence the plant startup. This event was reviewed by all control room personnel.
323 | 3231987003 | 1987-03-21 | QL5 | Partial Closure of MSIVs | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On March 21, 1987, at 0743 PST, with Unit 2 in Mode 1 (Power Operation) operating at 100 percent power, Main Steam Isolation Valve FCV-41 shut with the ensuing transient resulting in a high steam flow coincident with low steam line pressure safety injection and subsequent reactor trip. An Unusual Event was declared and the unit was stabilized in Mode 3 (Hot Shutdown) in accordance with approved plant procedures. The one hour NRC notification required by 10 CFR 50.72 was completed at 0805 PST. <br /><br /> This was the eighth emergency core cooling system actuation cycle that resulted in a discharge of water into the reactor coolant system. <br /><br /> This event was determined to have been caused by the failure of the valve closure position switch POS-821 following a rainstorm. The failure was caused by water entering into the switch housing which shorted a switched contact and produced the necessary logic to vent the valve actuator and close FCV-41. <br /><br /> To prevent recurrence, the failed switch was replaced with a newer design switch with improved housing seals. The remaining switches of the same model and service as the one that failed will be replaced during the current refueling outage for Unit 2 and during the next refueling outage for Unit 1.
323 | 3231987004 | 1987-04-03 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 12 | On April 3, 1987, at 2352 PST, with the unit in Mode 1 (Power Operation), a turbine generator trip and subsequent reactor trip occurred while licensed operators were shutting down the unit in preparation for a refueling outage. Approximately 23 seconds after the reactor trip, a safety injection occurred on a high steam flow signal coincident with low-low Tavg. The four-hour report required by 10 CFR 50.72 was made at 0020 PST, April 4, 1987. <br /><br /> The turbine generator tripped due to antimotoring relay actuation while the main generator was producing approximately 50 MW of electrical power. A reactor trip was automatically initiated following the turbine trip because reactor power was greater than 10 percent. The safety injection occurred due to rapid fluctuations in signals from the main steam flow transmitters, in conjunction with a low-low Tavg signal from the unit cooldown following the reactor trip. <br /><br />This was the ninth emergency core cooling system actuation cycle that resulted in a discharge of water into the reactor coolant system. <br /><br />A design change to the antimotoring relay circuitry will be evaluated. PGandE is investigating modifications to reduce sensitivity of the steam flow measurement devices to fluctuations following transients such as a reactor trip.
323 | 3231987016 | 1987-07-14 | QR7 | Other Reactor Trip (Valid RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Diablo Canyon 2 | P | WE | PO | 12 | At 0759 PDT, July 14, 1987, with the unit in Mode 1 (Power Operation) during generator startup, a high steam generator level turbine trip and subsequent reactor trip occurred. A safety injection followed due to high steam flow coincident with low steam generator pressure caused by a high rate of change of steam line pressure. The event occurred following turbine-generator synchronization when a control room operator manually loaded the turbine generator, creating a high steam flow condition which caused steam pressure to decrease and steam generator level to swell. <br /><br />This was the tenth emergency core cooling system (ECCS) actuation cycle that resulted in a discharge of water into the reactor. <br /><br />An unusual event was declared at 0800 PDT on July 14, 1987, and terminated at 0827 PDT on July 14, 1987. The unit was stabilized in Mode 3 (Hot Standby) at 0827 PDT on July 14, 1987. As required by 10 CFR 50.72 (b)(1)(iv), a 1-hour report was made at 0830 PDT, July 14, 1987. <br /><br /> The cause of the event was personnel error, in that the operator relied on a single meter, for indication of generator load, which was later determined to be improperly wired. A contributing cause to this event was the lack of: (1) providing the proper level of detail for postmaintenance testing; and (2) documentation of wire removal and installation. <br /><br /> To prevent recurrence, PGandE will revise procedures regarding generator synchronization, post maintenance testing, and wire removal and installation. This event will also be reviewed with all operations personnel.
323 | 3231987024 | 1987-11-07 | QR6 | Manual Reactor Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 98 | At 1315 PST, November 7, 1987, with the unit in Mode 1 (Power Operation) at 98 percent power, a manual reactor trip was initiated when arcing was discovered in non safety related isophase bus phase C motor operated disconnect (MOD) switch. The unit was stabilized in Mode 3 (Hot Shutdown) at 1430 PST. The four hour nonemergency report required by 10 CFR 50.72 was made at 1330 PST. On Monday, November 9, 1987 a replacement MOD was obtained. The replacement switch and the switches from the unaffected phases were inspected, cleaned, lubricated, and aligned. The unit was returned to power on November 14, 1987. <br /><br /> The MOD failure was caused by a combination of high ambient temperature and high resistance at the contacts. The high resistance was caused by dust and hardened lubricant on the contacts and a slight misalignment of some contacts. A comprehensive preventive maintenance procedure, MP E-61.9A "Isolated Phase Bus, And Motor Operated Disconnect Preventive Maintenance" was developed and implemented for the isophase bus MODs.
323 | 3231988002 | 1988-03-03 | QR8 | Spurious Reactor Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On March 3, 1988, at 1343 PST, with the unit in Node I (Power Operation), a reactor trip and subsequent turbine trip occurred during performance of Surveillance Test . Procedure (STP) I-72B, "Calibration of the Seismic Trip Channels." During performance of this STP, a simulated seismic test signal was input to the X axis of seismic sensor package number 1. This simulated test signal together with a previously undetected open coil failure of seismic trip relay K4 (sensor package number 2), in the Train B trip logic development circuit, satisfied the two-out-of-three (in one axis) logic requirements resulting in a reactor trip. <br /><br />All systems functioned as designed and the unit was stabilized in Mode 3, at approximately 1424 PST. Diesel generators 2-2 and 1-3 started during the event but, by design, did not load. <br /><br />The 4-hour nonemergency report required by 10 CFR 50.72 was made at 1411 PST, March 3, 1988. <br /><br /> The root cause for this event was attributed to the failure of the K4 seismic trip relay coil due to deterioration of the coil insulation, and the lack of seismic trip system annunciation to identify the individual protection channel component failures.
323 | 3231988008 | 1988-07-17 | H1 | Fire |  | X | [5 empty] | X | [7 empty] | X | [17 empty] | X | X | [10 empty] | Diablo Canyon 2 | P | WE | PO | 50 | On July 17, 1988, at 0717 PDT, with Unit 2 in mode 1 (Power Operation), a manual reactor trip and a manual reactor coolant pump (RCP) 2-2 trip were initiated due to electrical faults indicated in RCP 2-2. The other three RCPs were tripped due to continued feeder ground alarms placing the unit on natural circulation at 0746 PDT. At 0746 PDT, start up transformer breaker OCB 212 opened, making startup power unavailable to either unit. Diesel Generators (DG) 1-3, 2-1, and 2-2 started and loaded onto their respective Unit 2 4 kV vital buses. In addition, the loss of startup power caused the autostart of Unit 1 DGs 1-1 and 1-2. At 0757, secondary system transients resulted in a steamline differential of pressure safety injection (SI). An Unusual Event (UE) was immediately declared in accordance with plant emergency procedures. At 0759 a pressurizer power operated relief valve lifted. At 0814 PDT, the UE was reported to the NRC in accordance with 10 CFR 50.72(a)(1)(i). <br /><br />Galled aluminum threads resulted in an electrical connection which, with thermal and electrical cycling, deteriorated over 4 years and eventually produced enough heat to cause a ground fault. The connection was replaced, the 12 kV system inspected, and RCP 2-2 returned to service. <br /><br />This was the eleventh emergency core cooling system actuation cycle that resulted in a discharge of water into the reactor.
323 | 3231988010 | 1988-09-01 | QR8 | Spurious Reactor Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On September 1, 1988, at 1129 PDT, with the unit in Mode I (Power Operation), a reactor trip and subsequent turbine trip occurred during performance of Surveillance Test Procedure (STP) I-72A, "Functional Test of the Seismic Trip Channels". During performance of this STP, a simulated seismic test signal was input to the X axis of seismic sensor package number 2. This simulated test signal together with a previously undetected relay contact failure of seismic trip relay K7 (sensor package number 3), in Train A trip logic development circuit. satisfied the two-out-of-three (in one axis) logic requirements resulting in a reactor trip. <br /><br />All systems functioned as designed and the unit was stabilized in Mode 3 (Hot Standby), at approximately 1155 PDT. Diesel generator 2-2 started during the event but, by design, did not load. <br /><br />The seismic trip logic relay contact failure went undetected due to the trip. channel and logic status not being available to technicians or control room operators. <br /><br />The seismic trip system will be upgraded to provide trip channel and logic indication during testing.
323 | 3231989005 | 1989-04-16 | QR5 | Turbine Trip | [10 empty] | X | [30 empty] | X |  |  |  | Diablo Canyon 2 | P | WE | PO | 52 | On April 16, 1989, at 2004 PDT, a reactor trip due to low low steam generator (SG) water level occurred following a main generator trip and transfer of all electrical buses. At 2056 PDT, a 4-hour non-emergency report was made to the NRC in accordance with 10 CFR 50.72. <br /><br /> An Event Investigation Team (EIT) was established to investigate the event. Based on inspections, tests performed and a review of available information, the EIT determined that actuation of the generator backup protective relay caused the main generator trip. Coincident with the generator breakers opening, all vital buses transferred to standby power. A circulating water pump failed to restart on this transfer preventing the actuation of the condenser steam dumps. SG pressure increased causing SG level to shrink to the low low SG water level reactor trip setpoint. <br /><br /> Additional instrumentation was installed for the unit restart. No abnormalities were observed during the restart of the unit. The generator backup relay actuation was caused by a temporary voltage transient. The circulating water pump failure to restart was caused by a failure to adequately control equipment removed from service. Applicable procedures are being revised and Operations issued an incident summary to all applicable personnel.
323 | 3231989007 | 1989-07-16 | QR6 | Manual Reactor Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 27 | On July 16, 1989 at 0258 PDT, Diablo Canyon Power Plant (DCPP) Unit 2 was manually tripped in accordance with DCPP Abnormal Operating Procedure AP-20, "Condenser Tube Leak." A 4 hour non-emergency report was made to the NRC at 0358 PDT on July 16, 1989 in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> DCPP Unit 2 was in a planned maintenance curtailment at about 50 percent power for cleaning main condenser tube sheets. On July 16, 1989 a short time after restarting circulating water pump 2-1, a condensate pump discharge high cation conductivity alarm annunciated in the Control Room. The Shift Foreman directed the Control Room operators to enter procedure AP-20, which requires power to be reduced. At 27 percent power, feedwater conductivity increased and the reactor was manually tripped per procedure. <br /><br /> The cause of this event was failure of a condenser tube sheet plug. The plug was not recoverable for examination, and therefore the reason for failure could not be determined. The most likely root cause for the failure was either improper plug installation or use of a material susceptible to corrosion. Other tube sheet plugs were inspected and found to be installed correctly and of the proper material. A new plug was installed in the tube sheet.
323 | 3231989008 | 1989-08-28 | QR6 | Manual Reactor Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On August 28, 1989, at 2057 PDT, with Unit 2 in Mode 1 at 100 percent power, operators initiated a manual reactor trip after observing electrical ground alarms for Reactor Coolant Pump (RCP) 2-1, Circulating Water Pumps (CWPs) 2-1 and 2-2, and the Auxiliary Transformer, and elevated, fluctuating motor current for RCP 2-1. Operators tripped the reactor and then tripped RCP 2-1. Feeder ground alarms for RCP 2-1 and both CWPs cleared. At 2115 PDT, the Unit was stabilized in Mode 3 with an RCS temperature of approximately 525 F. In accordance with 10 CFR 50.72(b)(2)(ii) a 4-hour Non-Emergency Report was completed at 2205 PDT on August 28, 1989. <br /><br /> The event was caused by an inadequate electrical connection on RCP 2-1. <br /><br /> All 12kv electrical connectors, including the failed connector, were replaced on RCP 2-1. All other 12kv connectors for Unit 2 RCPs were examined to the extent practicable with no abnormalities found.
323 | 3231989010 | 1989-10-27 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On October 27, 1989, at 0655 PDT, the Unit 2 turbine and reactor were manually tripped and the fire alarm sounded following confirmed reports of smoke and arcing in the main electrical generator exciter housing. <br /><br /> As a precaution, operators requested backup firefighting assistance from the California Department of Forestry. Plant operators also vented the hydrogen from the generator and evacuated the turbine building of all nonessential personnel. PG&E declared an Unusual Event at 0703 PDT, October 27, 1989. <br /><br /> The PG&E fire brigade responded, entered the exciter housing and ventilated the enclosure of smoke. No further action was required. At 0828 PDT, October 27, 1989, with Unit 2 in Mode 3 (Hot Standby) the Unusual Event was terminated. <br /><br /> The smoke was caused by an exciter bearing failure that resulted in damage to the permanent magnet generator.<br /><br /> To prevent recurrence. the annunciator response manual was changed to require an immediate unit trip upon any generator radio frequency monitor alarm coincident with a change in bearing temperature or bearing vibration. Also, the exciter bearing temperature indicator was removed. All control operators will receive training regarding this event and the new annunciator response requirements.
323 | 3231993001 | 1993-01-30 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On January 30, 1993, at 2147 PST, with Unit 2 at 100 percent power, a turbine trip and reactor trip occurred during a routine surveillance test. Plant operators stabilized the plant in Mode 3 (Hot Standby) in accordance with emergency operating procedures. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on January 31, 1993, at 0009 PST. <br /><br /> The immediate cause of the main turbine trip was an inadvertent simulated low condenser vacuum signal that satisfied turbine protection logic. <br /><br /> Investigations have eliminated all but two possible root causes: personnel error or contaminated turbine lube oil. An operator holding a test lever may have inadvertently permitted the lever to move from the full-travel position, unblocking a turbine trip signal. Contaminates in the turbine lube oil may have blocked flow in an orifice, thus enabling the turbine trip. There is no firm evidence to verify or refute either possible cause. <br /><br /> Corrective actions include issuance of a Night Order Log entry for Operations personnel review, an Operations Department Incident Summary describing the event, implementation of a design change to improve performance of the surveillance test initiating in this event, and procedure revisions to clarify maintenance and testing requirements. These corrective actions resolve both possible root causes.
323 | 2751994020 | 1994-12-14 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On December 14, 1994, at 0026 PST, with Unit 1 and Unit 2 in Mode 1 (Power Operation) at 100 percent power, both units experienced reactor trips. Both units were stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A four-hour, non-emergency report was made at 0131 PST in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The reactor trips were due to an undervoltage on the auxiliary power bus that provides power to the reactor coolant pumps. The undervoltage condition was due to a system disturbance external to the PG&E system. <br /><br /> Due to the circumstances of the event, no corrective actions were deemed necessary. However, the Western System Coordinating Council, a utility coordination group composed of the eleven western states and British Columbia that are interconnected through the 500 kV Pacific Intertie, will study the transient and a formal report should be available in several months. If PG&E determines that any corrective actions are necessary as a result of this final report, a supplement to this LER will be issued.
323 | 3231994012 | 1994-12-19 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Diablo Canyon 2 | P | WE | PO | 35 | On December 19, 1994, at 1014 PST, with Unit 2 in Mode 1 (Power Operation) at approximately 35 percent power, a manual Unit 2 trip was initiated due to circulating water pump cavitation due to intake screen fouling. The unit was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. On December 19, 1994, at 1202 PST, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The event was due to the fouling of the intake circulating water screens during a period of high ocean swells that dislodged ocean plant life from the bottom. <br /><br /> An audible alarm was installed at the intake that activates if a traveling screen drive fails. Possible design and maintenance practice enhancements will be investigated. An annunciator will be installed in the control room to alarm on high condenser differential pressure. Operation Procedure AP-7, 'Partial Loss of Condenser Vacuum and Condenser Fouling,' was revised to include guidance on condenser fouling. The operator rounds sheets were revised to provide guidance on monitoring performance of the intake screen wash system. A computer program was installed that enables control room operators to monitor and trend condenser differential pressures.
323 | 3231995002 | 1995-09-23 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Diablo Canyon 2 | P | WE | PO | 40 | On September 23, 1995, at 0911 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 40 percent power, plant operators initiated a manual Unit 2 reactor trip when the traveling screens stopped running due to excessive debris loading. The unit was stabilized in Mode 3 (Hot Standby) in accordance with emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1207 PDT in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The root cause of the event was excessive debris loading on the circulating water system traveling screens during a period of high seas that dislodged plant life from the ocean bottom. <br /><br /> Abnormal Operating Procedure AP-7, 'Degraded Condenser,' was revised to include further guidance on minimizing screen damage and the requirement to reduce reactor power during periods of heavy screen loading. Additional screen rakes will be added to the screens to improve the efficiency of debris removal. Simulator training will be provided to operators dealing with the loss of circulating water system screen functions.
323 | 2751996012 | 1996-08-10 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On August 10, 1996, at 1549 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, a major disturbance on the western transmission grid resulted in reactor trips on both units. Both units were stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1842 PDT in accordance with 10 CFR 50.72 (b)(2)(ii). <br /><br /> Undervoltage and underfrequency conditions were experienced on both the auxiliary and startup systems due to a disturbance on the 500 kV system external to the PG&E system. Unit 1 experienced a reactor trip due to a 12 kV auxiliary power system reactor coolant pump (RCP) feeder bus undervoltage and Unit 2 experienced a reactor trip due to two of four RCP breakers open. <br /><br /> The Unit 1 RCPs and the circulating water pumps remained running throughout the event. Since the Unit 2 RCPs were not running, control room operators closed the Unit 2 main steam isolation valves to prevent excessive cooldown. One RCP was restarted 69 minutes after the pumps tripped off the line; thus Unit 2 was on natural circulation for 69 minutes. <br /><br /> The Western System Coordinating Council study of the transient did not provide any recommendations applicable to Diablo Canyon Power Plant. PG&E determined that no additional corrective actions were necessary.
323 | 3231997002 | 1997-03-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On March 29, 1997, at 1057 PDT, with Unit 2 in Mode 1 (Power Operation) at 1 00 percent power, the Unit 2 reactor tripped on steam generator (SG) water level low-low in SG 2-2. The Unit was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1209 PDT in accordance with 10 CFR 50.72 (b)(2)(ii). <br /><br /> The low-low SG water level was caused by the failure of Main Feedwater Pump (MFWP) 2-1. The feedwater pump failed when a solenoid-operated shuttle valve in the control oil supply to the MFWP turbine governor valve jammed which resulted in the governor valve drifting shut. The valve failure was determined to be caused by iron oxide (rust) particulate contamination buildup in the valve spool. The iron oxide particulate generation occurred in the feedwater pump oil system as a result of water contamination. Steam/moisture entered the oil system from a potentially degraded inboard turbine seal via the adjacent bearing oil seal. <br /><br /> The MFWP 2-1 lube oil system was flushed. The associated filters were replaced. Water contamination was minimized by throttling MFWP 2-1 turbine gland seal supply steam. The planned maintenance and predictive maintenance systems are being improved to ensure proper operation of the MFWP control oil system. The MFWP inboard turbine gland seal will be repaired or replaced in the next refueling outage.
323 | 3231997003 | 1997-07-02 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Diablo Canyon 2 | P | WE | PO | 100 | On July 2, 1997, at 0456 PDT, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, a manual reactor trip was initiated due to a trip of both main feedwater pumps (MFWPs). A 4-hour, non-emergency report was made to the NRC, in accordance with 10 CFR 50.72(b)(2)(ii) at 0853 PDT. <br /><br /> On July 2, 1997, at 0452 PDT, a condensate/feedwater system transient initiated an automatic start of the standby condensate and booster pump set. Approximately 4 minutes later, low condensate flow and increasing MFWP demand resulted in condensate flashing and an overspeed trip of both MFWP steam driven turbines. The overspeed trip of both MFWP turbines resulted in a loss of normal feedwater. Plant operators manually tripped the reactor. <br /><br /> An event response plan (ERP) was initiated to investigate the cause of the event and implement immediate corrective actions to return Unit 2 to Mode 1. ERP actions included verification of proper operation of condensate system components and additional system monitoring during the Unit startup. <br /><br /> Due to the unknown root cause of this event, no corrective action to prevent recurrence could be identified. PG&E believes that a failure of a condensate system control valve coincident with an unknown rapid reduction in condenser vacuum resulted in the loss of main feedwater. <br /><br /> This revision is submitted to identify the contributory causes and add a conclusion regarding the cause of this event in Section III.
323 | 3231997005 | 1997-10-24 | QL5 | Partial Closure of MSIVs | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On October 24, 1997, at 0815 PDT, with Unit 2 in Model (Power Operation) at 100 percent reactor power, a reactor trip (RT) and safety injection (SI) occurred due to inadvertent closure of a main steam isolation valve. One power operated relief valve lifted to relieve reactor coolant system (RCS) pressure seven times during recovery from the RT and SI. The SI actuation signal was reset at 0829 PDT. An unusual event (UE) was declared for this event at 0832 PDT. The San Luis Obispo County Sheriff s Office Watch Commander was notified at 0837 PDT. A 1-hour emergency report was made to the NRC, in accordance with 10 CFR 50.72(a)(1)(i) at 0900 PDT. On October 24, 1997, at 0938 PDT, following stabilization of Unit 2 in Mode 3 (Hot Standby), the UE was terminated. This was the twelfth Unit 2 emergency core cooling system actuation cycle that resulted in a discharge of water into the RCS. The cause of the event was inadvertent actuation of the closed position switch for FCV-44 by a contract laborer removing scaffolding adjacent to the valve. Corrective actions to prevent recurrence include: (1) revision of the scaffolding program procedure and risk assessment procedure and (2) issuance of a maintenance policy to require a risk assessment and management approval for nonroutine work near critical components.
323 | 3231998005 | 1998-12-01 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On December 1, 1998, at 0347 PST, with Units 1 and 2 in Mode 1 (Power Operation) at approximately 100 percent power, plant operators initiated a Unit 2 manual reactor trip due to sudden heavy debris loading of the main circulating water systems during a Pacific Ocean storm. Unit 1 power was reduced to 50 percent to control debris loading. Unit 2 was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A 4-hour, non-emergency report was made to the NRC at 0529 PST in accordance with 10 CFR 50.72(b)(2)(ii). The cause of the event was sudden heavy debris loading on the circulating water system traveling screens during a period of high seas that dislodged plant life from the ocean bottom. PG&E cannot prevent the potential need to expedite manual reactor trips when high seas and dislodged plant life result in sudden heavy debris loading on the traveling screens. However, enhancements will be made to operating orders for storm conditions, improvements to circulating water system indication reliability in the control room, enhancement to shift turnover guidance, and additional operator training to include the lessons learned from this event.
323 | 2751999009 | 1999-10-28 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Diablo Canyon 2 | P | WE | PO | 30 | On October 28, 1999, at 1359 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 30 percent power, and at 1400 PDT, with Unit 1 in Mode 1 at 50 percent power, plant operators initiated manual reactor trips as required by Operating Procedure AP-7, "Degraded Condenser." The trips were required when differential pressure across the intake water traveling screens exceeded limits due to sudden heavy debris loading from a major Pacific Ocean storm. The units were stabilized in Mode 3 (Hot Standby) in accordance with emergency procedures. A 4-hour, non-emergency report was made to the NRC, in accordance with 10 CFR 50.72(b)(2)(ii), at 1520 PDT. PG&E previously added screen rakes and debris grinders to the seawater cooling system to improve debris removal. Operator training was enhanced regarding loss of circulating water system screen functions. PG&E cannot entirely eliminate the potential need to expedite manual reactor trips when high seas and dislodged plant life from the ocean bottom result in heavy debris loading on the traveling screens. PG&E will designate an operations management team to focus on lessons learned and streamline the coping strategy decision making process during storm warning conditions.
323 | 3232002002 | 2002-02-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On February 9, 2002, at 0337 PST with Unit 2 in Mode 1 (Power Operation) at 100 percent power, plant operators initiated a manual reactor trip due to failure of main feedwater regulating valve (MFRV) FW-2-FCV-540 that isolated feedwater to steam generator 2-4. A 4-hour, non-emergency report was made to the NRC on February 9, 2002, at 0709 PST in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A).Safety systems responded as required, except for an expected automatic reactor trip based on steam generator low level, which is evaluated in LER 1-2002-001, dated April 15, 2002, as referenced in sections II.B. and IV of this LER. The immediate cause of the failure was excess current in the coil of Asco solenoid valve (SV) SV-540B, which caused failure of a power fuse and forced the FCV-540 to close. The excess current in the SV was caused by failure of the insulation due to thermal aging degradation. Immediate corrective actions included replacing a failed fuse and the SV. Corrective actions to prevent recurrence include: 1) revising the environmental qualification (EQ)calculation and re-evaluating the replacement period for Asco SVs; 2) replacing Asco SVs or their coils for the MFRVs and bypass valves during the next refueling outage for each unit; 3) reviewing the adequacy of other EQ calculations prepared by the same individuals; and 4) reevaluating preventive maintenance frequencies for all continuously energized EQ solenoid valves. An additional prudent action was completed to prep area case study to communicate lessons learned from the inadequate EQ calculation.
323 | 3232006004 | 2006-12-12 | QC5 | Loss of Non-safety-Related Bus | [7 empty] | X | [25 empty] | X | [11 empty] | Diablo Canyon 2 | P | WE | PO | 25 | On December 12, 2006, at 1322 PST, with Unit 2 at approximately 25 percent power, an electrical failure occurred in the circulating water pump (CWP) motor enclosure for CWP 2-1. An Emergency Notification System (ENS) Notice of Unusual Event (NUE), Number 23, Confirmed Explosion Onsite, was reported in accordance with 10 CFR 50.72 (a)(1)(i) at 1359 PST. The NUE was terminated at 1430 PST following confirmation that the initial report was due to a CWP 2-1 electrical discharge and fire, that was extinguished. On December 12, 2006, at 1541 PST, ENS Event Number 43047 was updated to include a 4-hour report in accordance with 10 CFR 50.72 (b)(2)(iv)(B) due to a Reactor Protection System actuation while critical, and an 8-hour notification in accordance with 10 CFR 50.72 (b)(3)(iv)(A) due to the actuation of the accelerated system. All equipment responded as designed. The CWP 2-1 surge capacitor was replaced and the associated electrical system was repaired. The cause of the failure was a single random failure of the surge capacitor. Corrective actions will include replacing the 12kV three phase surge capacitors with more reliable single phase surge capacitors and enhancing the preventive maintenance program.
323 | 3232008001 | 2008-08-16 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On August 16, 2008, at 23:57 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 100 percent power, a main generator Unit Trip signal initiated a Reactor Trip due to the failure of the main electrical transformer "C" phase. On August 17, 2008, at 00:12 PDT, plant operators declared an Unusual Event (UE) due to an observed fire at the "C" phase transformer. Plant operators made an Emergency Event Notification (EN 44419) in accordance with 10 CFR 50.72(a)(1)(i) at 00:37 PDT. Plant operators stabilized Unit 2 in Mode 3 (Hot Standby) and updated the UE that the fire was out at 02:02 PDT. At 07:38 PDT, EN 44419 was updated to specify 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(3)(iv)(B). This event was due to a catastrophic failure of the main electrical transformer "C" phase high voltage bushing. The event investigation will continue, however, this event is considered a random component failure based upon onsite inspections and vendor reviews performed. Corrective actions include the "C" phase transformer replacement, electrical tests of transformers and bushings, oil analysis of transformers and bushings, installation of a bushing monitoring system, evaluation and replacement of equipment damaged as a result of the electrical failure, and review of industry and station operating experience regarding main transformer issues.
323 | 3232008002 | 2008-10-21 | QR6 | Manual Reactor Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On October 21, 2008, at 20:49 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 55 percent power, a manual Reactor Trip was initiated due to the failure of the Pacific Ocean Circulating Water System (CWS) debris removal system to maintain adequate flow for power operation. Plant operators stabilized Unit 2 in Mode 3 (Hot Standby) and made an emergency event notification (EN#44588) in accordance with 10 CFR 50.72(a)(1)(i) at 22:44 PDT. This event was due to a sudden large influx of Moon Jellyfish in the Pacific Ocean CWS that exceeded the ability of the debris removal system to effectively remove. PG&E has developed extensive models to help predict the impact of Pacific Ocean storms associated with CWS debris removal, and to give adequate time to prepare for such events. PG&E could not have anticipated this event and the potential adverse affects from the sudden large influx of jellyfish.
323 | 3232011001 | 2011-03-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Diablo Canyon 2 | P | WE | PO | 98 | On March 26, 2011 at 1449 PDT operators at Diablo Canyon Power Plant (DCPP) Unit 2 manually initiated a reactor trip in response to loss of main feedwater pump 2-1. The main feedwater pump 2-1 tripped after non-radioactive water sprayed on its control console. The water spray was caused by leakage from the flange of the relief valve on the feedwater heater 2-1A condenser dump valve line. All rods fully inserted on the reactor trip. The reactor was cooled by the auxiliary feedwater system with the condenser in service. All systems performed as designed with no unexpected pressure or level transients. Automatic main feedwater isolation, auxiliary feedwater actuation, and steam generator blowdown isolation occurred as expected. ENS notification 46701 provided the 4-hour non-emergency event report for the manual reactor trip of DCPP Unit 2 in accordance with 10 CFR 50.72(b)(2)(iv)(B), RPS Actuation (scram). Additionally, this notification provided the 8-hour non-emergency event report of the automatic actuation of the auxiliary feedwater system as a result of the reactor trip in accordance with 10 CFR 50.72(b)(3)(iv)(A), Specified System Actuation. The cause of the event was determined to be a failed gasket for the relief valve due to bolt torquing practices. Corrective actions include revising DCPP's bolt torquing procedure to provide bolt torquing specifications for bolted connections.
323 | 3232012002 | 2012-10-11 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On October 11, 2012, at 12:08 PDT, the Diablo Canyon Power Plant (DCPP) Unit 2 500kV line differential relay actuated, resulting in a unit trip. The 500kV coupling capacitor voltage transformer (CCVT) bushing experienced a flashover to ground, resulting in a unit trip and turbine trip. With the turbine tripped and Unit 2 operating above the 50 percent power permissive, the reactor protection system initiated a reactor trip as designed. All plant equipment, including the auto-start of the auxiliary feedwater (AFW) system, responded as designed.<br><br> DCPP determined that the bushing failed because the insulator minimum creepage distance was not consistent with industry codes and standards for its operating environment. When the bushing was replaced in 2011, DCPP staff made unvalidated assumptions, and over-relied on industry experts. DCPP will move CCVT metering to an area with lower contamination levels, and reinforce expectations to review current industry codes and standards.<br><br> Additionally, an unintended AFW pump restart occurred following this event as a result of a human performance error that resulted in a procedure not being revised following a plant modification. DCPP will revise procedure supporting documents and train procedure writing staff on use of the supporting documents to identify all changes required by a plant modification.
323 | 3232013005 | 2013-07-10 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On July 10, 2013, at 09:50 PDT, while performing the periodic hot-washing of the 500 kV insulators, a flashover of the Phase A 500 kV to ground across the Phase A lightning arrestor occurred and actuated the 500 kV differential relay. The actuation of the 500 kV differential relay opened the Unit 2 generator output breakers to isolate the generator, which then actuated a turbine trip. Since Unit 2 was operating above the 50 percent power permissive, the reactor protection system initiated a Unit 2 reactor trip. All plant equipment responded as designed.<br /><br /> Diablo Canyon Power Plant (DCPP) staff determined the root cause of this event to be the hot-washing of the Phase A transmission line string insulators (500 kV dead-end insulators) with inadequate controls for oversight of supplemental PG&E transmission line personnel and on-line maintenance risk analysis that resulted in a conductive overspray, which induced an external arc around the lightning arrester insulation resulting in flashover. The corrective action to prevent reoccurrence involves the development and implementation of a maintenance strategy for 500 kV dead-end insulators to ensure they remain adequately contamination free, structurally sound, and minimize risk to DCPP.<br /><br /> There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not have an adverse effect on the health and safety of the public.
323 | 3232014001 | 2014-02-02 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On February 2, 2014, at 1129 PST, a failure of the Diablo Canyon Power Plant, Unit 2, Phase B, 500 kV lightning arrester resulted in a direct short to ground and actuated the 500 kV tie-line current differential relay. The actuation of the 500 kV tie-line current differential relay opened the Unit 2 generator output breakers to isolate the generator, which then actuated a turbine trip. Since Unit 2 was operating above the 50 percent power permissive, the reactor protection system initiated a Unit 2 reactor trip. Plant equipment responded as designed.<br /><br /> The cause was indeterminate due to the component damage. The corrective actions, including installing lightning arresters with increased capability to withstand, periodic cleaning of the arresters, and enhanced condition monitoring, address all probably causes.<br /><br /> There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not have an adverse effect on the health and safety of the public.
323 | 3232018001 | 2018-12-01 | QR5 | Turbine Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On December 1, 2018, at 1006 PST, with Unit 2 at 100 percent power, the reactor automatically tripped following a load rejection from the 500 kV off site electrical system. The trip was not complex; all safety systems responded as designed. Due to the Unit 2 reactor trip and the expected actuation of the Auxiliary Feedwater System, this event is being reported per 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> This event was a result of an automatic operation of the Diablo Canyon Special Protection Scheme (DC-SPS) that occurred when DC-SPS sensed two out of three 500 kV lines out of service when all three lines were in service. The DC-SPS Remote Outage Detection (ROD) logic used local current, independent of breaker position, for detecting a remote-end outage to determine if 500k kV lines were in service. <br /><br /> The ROD logic portion of the DC-SPS circuitry has been disabled and mitigation measures have been implemented, including improved communications with the Grid Control Center. <br /><br /> There was no impact on the health and safety of the public or plant personnel.
323 | 3232020002 | 2020-07-17 | QR6 | Manual Reactor Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 100 | On July 17, 2020, at 13:46 Pacific Daylight Time, with Diablo Canyon Power Plant Unit 2 operating at 100 percent power, the reactor was manually tripped in accordance with plant procedures due to increasing hydrogen usage in the Unit 2 Main Generator. <br /><br /> The reactor trip was uncomplicated, and the auxiliary feedwater system started as expected. <br /><br /> This event is being reported per 10 CFR 50.73(a)(2)(iv)(A) due to a manual reactor trip and the associated automatic actuation of a specified safety system. <br /><br /> The cause of the increased hydrogen usage was due to a leak in a weld segment located on the Unit 2 Main Generator exciter end stator coil cooling water manifold. <br /><br /> There was no impact to the health and safety of the public or plant personnel.
323 | 3232021002 | 2021-10-15 | QR6 | Manual Reactor Trip | [45 empty] | Diablo Canyon 2 | P | WE | PO | 90 | On October 15, 2021, at 17:49 Pacific Daylight Time, with Diablo Canyon Power Plant Unit 2 operating at 90 percent power, the reactor was manually tripped in accordance with plant procedures due to increasing water level in Feedwater Heater (FWH) 2-5B. <br /><br /> This event included actuation of the auxiliary feedwater system as expected following manual reactor trip. <br /><br /> This event is being reported per 10 CFR 50.73(a)(2)(iv)(A) due to a manual reactor trip and the associated automatic actuation of a specified safety system. <br /><br /> The cause of the increased feedwater level was due to failure of multiple tubes in the FWH. <br /><br /> There was no impact to the health and safety of the public or plant personnel.
324 | 3241987001 | 1987-01-05 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Brunswick 2 | B | GE | PO | 100 | While increasing Unit 2 main generator output voltage, an automatic reactor scram from 100% power occurred at 1612 hours on 1/5/87. Primary Containment Isolation System (PCIS) Groups 1, 2, 3, 6, and 8 isolations occurred in addition to autostarting of the High Pressure Coolant Injection (HPCI) System, Reactor Core Isolation (RCIC) System, and the Units 1 and 2 common emergency diesel generators. During the scram recovery, the HPCI injection isolation valve, E41-F006, failed in the closed position at 1642 hours. While controlling reactor level with the RCIC System, a reactor low level occurred at 2026 hours causing a reactor scram signal and PCIS Groups 2, 6, and 8 isolations. The event at 1612 hours occurred due to loss of main generator field voltage following main generator output voltage oscillations resulting from corrosion and/or oxide film on the voltage regulator automatic and manual potentiometers. The HPCI F006 failure is attributed to possible heat-related breakdown of the valve motor internals. The event at 2026 hours resulted from inability of the RCIC System to provide sufficient inventory makeup due to failure of the RCIC full flow test isolation valve E51-F022 to close. <br /><br />The F006 valve motor was replaced. The F022 valve stem antirotation device was repaired. <br /><br />Subsequent Unit 2 criticality was achieved at 1358 hours on 1/12/87 and grid synchronization at 1237 hours on 1/13/87.
324 | 3241987004 | 1987-03-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Brunswick 2 | B | GE | PO | 100 | At 0307 on 3/11/87, a Unit 2 reactor scram occurred due to a low level in the reactor vessel. The low vessel level was caused by loss of the uninterruptible power supply (UPS) which caused the signal to the Feed Pump Control System to ramp back to minimum speed of approximately 2800 rpm. At this speed, the pumps were not able to maintain an adequate flow rate into the vessel, thus creating the low level condition. Following the scram recovery, during a subsequent HPCI System lineup verification, it was also noted that the High Pressure Coolant Injection (HPCI) System was inoperable. The HPCI System did perform as required during the scram. At the time of this event, Unit 2 was at 100% power. <br /><br />The loss of the UPS System stemmed from failure to follow procedures while attempting to transfer input power to UPS from the reserve but to the standby inverter. The HPCI System inoperability was due to a failed motor on the HPCI (E41) pump discharge valve E41-F007 with the valve in the closed position. The motor was replaced prior to startup and the HPCI System returned to operable status.
324 | 3241988001 | 1988-01-02 | QL7 | Degraded condenser vacuum | [45 empty] | Brunswick 2 | B | GE | PO | 55 | While performing a routine reactor shutdown in preparation for the Unit 2 1988 refueling/maintenance outage, a manual reactor protection system trip (scram) was initiated at 0017 hours on 1/2/88, due to a decreasing condenser vacuum. Reactor power was approximately 55% and vacuum had decreased to approximately -22 inches mercury. During the expected vessel level shrink following the scram, vessel level decreased to approximately 153 inches, thus initiating primary containment isolation valve groups 2, 6, and 8 at low level 1 (> 162.5"). Operator verification of these valve closures determined that the group 2 valves 2-G16-F003, -F004, -F019, and -F020 failed to close. These are the inboard and outboard isolation valves for the drywell floor drain sump (F003, F004) and the drywell equipment drain sump (F019, F020). The remaining safety systems operated as designed during this event. <br /><br />Investigation of the decreasing vacuum condition determined it resulted from numerous leaks on the main turbine and main steam reheat interconnecting piping to the main turbine, which were repaired during the unit outage. The failure of the group 2 PCIVs to close was caused by the failure of the associated solenoid valves to open due to adherence between the lower brass disc and EPDM elastomer seat.
324 | 3241988018 | 1988-11-16 | QP5 | Excessive Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Brunswick 2 | B | GE | PO | 100 | At 1026 hours on November 16, 1988, the Unit 2 reactor scrammed due to turbine control valve fast closure on a high level turbine trip. The unit was operating at 100% power. The Emergency Core Cooling Systems were operable and in standby readiness. During the event, Groups 1, 2, 3, 6, and 8 isolations were received. The D outboard main steam line isolation valve (MSIV) exhibited dual position indication. HPCI and RCIC received initiation signals and the RCIC system injected; however, the HPCI System received a trip signal and the injection valve immediately closed upon reaching full open. The operator manually opened the HPCI injection valve and restored level. Reactor pressure was controlled by auto and manual safety relief valve actuation. By 1052 hours the operator had reset the Group 1 and 3 isolations, and reestablished the condenser as a heat sink. <br /><br />The high reactor level was due to a feedwater logic control Topaz inverter tripping on high input voltage. The MSIV dual indication was due to a limit switch problem. HPCI is believed to have tripped on low suction pressure (LSP). <br /><br />The inverter has been recalibrated, the MSIV limit switch has been readjusted and the HPCI LSP trip has been disabled. This event had minimal safety,
324 | 3241989009 | 1989-06-17 | B1 | Loss of Offsite Power (LOOP) |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Brunswick 2 | B | GE | PO | 76 | At 2047 hours on June 17, 1989, a manual reactor scram was initiated on Unit 2, in accordance with I&E Bulletin 88-07, due to a loss of both reactor recirculation pumps. Both pumps were deenergized when troubleshooting on Unit 2 startup auxiliary transformer (SAT), which supplies power to the pumps, caused the SAT to trip on a high resistance ground fault. A planned power decrease was in progress prior to the loss of the SAT and the power level at the time of the scram was 76%. <br /><br /> As a result of the reactor scram and the loss of the SAT, Unit 2 experienced a loss of off-site power. The diesel generators automatically started and powered the Unit 2 emergency (E) buses per design. Due to the momentary loss of power on the E-buses and/or vessel low level (as applicable), containment isolation Groups 1, 2, 3, and 6 automatically isolated. Reactor pressure was controlled by the safety relief valves, high pressure coolant injection system, and the reactor core isolation cooling system. <br /><br /> The investigation determined that the cause was personnel error by the technician performing troubleshooting on the SAT. The technician placed a jumper across the SAT neutral grounding transformer primary thinking it was a current transformer; however, it is a potential transformer and the resulting high current caused the SAT to trip. Corrective actions include personnel counseling and procedure enhancements.
324 | 3241990004 | 1990-03-13 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Brunswick 2 | B | GE | PO | 7 | At 0536 on March 13, 1990, a manual scram was initiated due to the failure of safety/relief valve (SRV) B21-F013G to close during startup testing. Reactor power was approximately 7% and reactor pressure was approximately 250 psig. The 11 unit SRV's were being cycled in accordance with plant procedures to verify operability per Technical Specification 3.5.2. Ten of the eleven SRV's had been successfully tested prior to this failure. A normal scram recovery was conducted per plant procedures and no automatic safety actuations or isolations occurred. The investigation determined that the solenoid valve which allows remote manual operation of B21-F013G was inoperable. The solenoid would allow the SRV to be opened, but would not allow timely closure of the SRV. The solenoid valve was replaced, the unit returned to the required testing conditions and the SRV was successfully tested. The solenoid valve was sent to Wyle Laboratory and the root cause was determined to be failure of the solenoid disc to properly realign with its seat after de-energization. The report indicated that a potential cause was "dirt" embedded in the rubber pad located on the backseat. An investigation into the source of the material was conducted. A contamination source was not found and the investigation concluded that the instrument air system does not have a generic problem with contamination. The air monitoring program developed in response to GL 88-14, the recently installed pneumatic nitrogen systems on each unit, and the manufacturer's development of a more durable solenoid for future installation decreases the potential for a reoccurrence of this event. No further corrective actions are planned. This event had minimal safety significance as the Unit is analyzed for a stuck open SRV at 100% power.
324 | 3241990008 | 1990-08-16 | QP5 | Excessive Feedwater Flow | [45 empty] | Brunswick 2 | B | GE | PO | 100 | On August 16, 1990, Unit 2 reactor was at 100% power. The RPS, HPCI, RCIC, ADS, RHR/LPCI, CS, SBGT, SLC, DG and plant electrical system were operable in standby readiness. The reactor level control system was operating in automatic - three element control and at 185 inches. At 0942, the reactor automatically shutdown on a "TSV Fast Closure" RPS trip signal caused by a turbine trip on reactor high water level. During this event, the HPCI turbine stop valve cycled closed and then open, water intrusion into the HPCI oil was noted, the RCIC barometric condenser vacuum pump experienced an electrical fault, and a loss of the recirculation pumps resulted in temperature transients in the vessel. HPCI and RCIC operability were not affected; the recirculation pumps are now being powered from the start up auxiliary transformer to prevent their loss during future reactor trips. The cause of this event was failure of primary power fuse C32-F5, which supplied power to the steam flow inputs of the three element feedwater control logic. Loss of the steam flow inputs resulted in a maximum demand signal to the RFPs and a rapid increase in reactor level up to the high level turbine trip point which, in turn, caused a reactor scram on TSV position. Primary power fuse C32-F5 and its associated circuit were evaluated. The fuse has been replaced. The final Harris Energy and Environmental Center (HE&EC) report concluded that the fuse did not exhibit defects which could be interpreted as the cause for the fuse failure. The cause for the fuse failure is indeterminate. The HE&EC is continuing an analysis of the Gould Shawmut fuses. Past similar events include LERs 2-88-018, 1-88-023 and 2-90-008. The safety significance of this event is minimal. The plant responded as designed.
324 | 3241990009 | 1990-08-19 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Brunswick 2 | B | GE | PO | 100 | While testing the main condenser low vacuum instrumentation and isolation logic, an isolation signal was generated which closed the main steam isolation valves. Closure of the main steam isolation valves initiated a Unit 2 reactor scram at 2154 on 8/19/90. Reactor pressure peaked at approximately 1133 psig and the minimum water level reached was approximately 112 inches. No safety limits were exceeded in the plant response to the level and pressure transients. The operating crew was able to control the plant by using redundant equipment or alternate methods. The safety relief valve opening sequence and actuation pattern were questioned. The actuation pattern is not a concern. However, safety relief valve, B21-F013C (setpoint 1105 psig) did not open. The pilot valve assemblies were replaced on safety relief valves B21-F013A, B21-F013C, B21- F013G, B21-F013H, and B21-F013K. <br /><br /> Similar problems encountered during this scram have been reported in LERs 2-88-005, 2-88-019, 2-87-004, 1-87-011, 2-86-001, 2-86-013, 2-86-017, 2-85-003, 2-85- 011, and 1-85-033.
324 | 3241990012 | 1990-08-30 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Brunswick 2 | B | GE | SU | 8 | On August 30, 1990, Unit 2 reactor start-up was in progress. The reactor was at approximately 8% power and 300 psig. The Emergency Core Cooling Systems were operable in standby line up except for the High Pressure Coolant Injection System which was inoperable awaiting the performance of the HPCI System Operability Test. At 1656 the start-up level control valve (SULCV) failed closed resulting in a level transient. At 1657 the Reactor Protection System (RPS) low level #1 setpoint (165") was reached causing a reactor scram. Primary Containment Isolation System groups 2, 6 and 8 also received an isolation signal and actuated per design. Scram recovery was in accordance with the emergency flowcharts and procedures. Approximately 20 minutes after the scram, level was stabilized. The cause of the SULCV failure is believed to be worn o-ring seals. The seals have been replaced and the SULCv is operating properly. The worn seals are being analyzed to determine the cause of the failure. The safety significance of this event is minimal. Level was recovered without the need for safety system injection and the unit is designed for a level transient from full power.
324 | 3241990015 | 1990-09-27 | QR5 | Turbine Trip | [45 empty] | Brunswick 2 | B | GE | PO | 100 | On 9/27/90, while operating at 100% power, Unit 2 experienced generator voltage oscillations which resulted in a loss of the main generator due to loss of excitation. This resulted in a reactor scram due to control valve fast closure signal. The primary cause of the SCRAM was a voltage regulator that had become potentially unstable due to past improper adjustments. <br /><br /> Systems functioned as designed. Potential concerns were noted with a CRD that did not fully insert (02 position versus 00 position) and dual position indication on an MSIV. Cause of the SCRAM was inadequate configuration control on the voltage regulator adjustments and URAL circuit settings. Potentially contributing to the event was the grid system configuration on that date, the system voltage schedule, and procedural controls for maintaining generator excitation. Corrective actions include adjustments of the voltage regulator, updating the vendor technical manual to ensure proper future system performance, and evaluations of the grid stability requirements and design basis relative to system capacitance values.<br /><br /> The event safety significance is considered minimal. Transient parameters experienced were well within analyzed transient parameters for this type event.
324 | 3241990016 | 1990-10-12 | QP5 | Excessive Feedwater Flow | [45 empty] | Brunswick 2 | B | GE | PO | 100 | On October 12, 1990, the Unit 2 reactor was at 100% power and 1005 psi. The Emergency Core Cooling Systems were operable, in standby readiness. A functional check was in progress on a thermocouple mV/I module in the feedwater control cabinet, H12-P612, located in the control room back-panels. Fuse 2-C32-F3 is part of the circuitry which powers the referenced module. At 14:01:52, a high reactor level was detected. This resulted in a reactor scram turbine stop valve fast closure, per design. The control rods inserted and turbine bypass valves acted to control reactor pressure at 1005 psi. The scram was caused by a failure of the Gould Shawmut fuse 2-C32-F3 in the FWCS. The failure resulted in a false low level signal to the B turbine driven reactor feed pump (TDRFP) control circuitry which, in response, increased the B TDRFP output and resulted in a main turbine trip on reactor high water level. The reason the fuse blew in the FWCS has not been determined. The Gould Shawmut fuses have been sent to the CP&L Harris Energy & Environmental center for further testing and examination. In addition, an event recorder is currently monitoring the power supply circuitry to the 2-C32-F3 fuse. Past similar events include LERs 2-90-08 , 2-88-018 and 1-88-023. The safety significance of this event is minimal. Plant systems responded as designed and the event is bounded by the analysis in the Final Safety Analysis Report, Feedwater Control System failure.
324 | 3241991001 | 1991-01-25 | QP5 | Excessive Feedwater Flow | [45 empty] | Brunswick 2 | B | GE | PO | 100 | On January 25, 1991, Unit 2 reactor scrammed from 100% power. The scram was due to a turbine trip on high reactor water level which resulted from the Feedwater Level Control System responding to a sensed loss of feed flow during performance of a Process Computer point calibration on the Feedwater flow logic system. Instrumentation and Control (I&C) technicians performing the calibration failed to recognize a procedure prerequisite step which stated that the unit must be in cold shutdown or refuel to perform the procedure. <br /><br /> The event was due to the failure of the work control process to prevent this activity from being performed, caused by inadequate reviews in the scheduling and implementation phases of the process and the failure of the technicians to ensure the prerequisites were met. In addition, the procedure Summary Sheet incorrectly stated that no special plant conditions were required for the performance of the procedure. <br /><br /> Corrective actions included stoppage of the computer point calibrations, suspension of use of the procedure Summary Sheets, communication of the event with plant personnel, development of a Recovery Action Plan, and initiation of a working level Task Force to investigate this and similar recent personnel errors.<br /><br /> The safety systems functioned as designed. Equipment response concerns were identified, but none posed a significant safety concern.
324 | 3241991021 | 1991-12-17 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Brunswick 2 | B | GE | SU | 5 | At 09:42, on December 17, 1991, Unit 2 was at 5% Reactor power. A startup was in progress on completion of a refueling outage. The Emergency Core Cooling Systems were operable. The Reactor Scrammed when the High Pressure Coolant Injection (HPCI) system inadvertently started and injected relatively cold water into the reactor vessel. <br /><br /> Instrumentation and Controls (I&C) technicians were performing a routine surveillance (2MST-RHR23M) on the HPCI Reactor vessel Low Level 2 (118") initiation logic. Per the surveillance, an "A" channel level instrument was actuated and its relay contacts were verified closed by checking the voltage across the open "B" channel contacts. This voltage cheek was performed with a Fluke 860OA-01 digital voltmeter (DVM), which has since been verified to have an internal fault. The fault allowed sufficient current flow to actuate an initiation of the HPCI system. The relatively cold water injected by the HPCI system caused the Reactor power to exceed the 15% Average Power Range Monitor (APRM) Scram setpoints. Once the HPCI initiation was verified as invalid, the HPCI system was manually shut down. <br /><br /> After the cause of the Unit 2 Reactor Scram had been identified, startup was recommenced at 02:23 on 12/18/91. <br /><br /> This isolated event posed minimal safety significance in that plant systems responded as designed.
324 | 3241992001 | 1992-02-02 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Brunswick 2 | B | GE | PO | 79 | On January 29, 1992, Unit 2 was operating at approximately 100% steady state power. An annunciator for low electrohydraulic (EHC) fluid pressure was received. EHC pressure swings occurred. Reactor power was reduced to about 85% power to close #4 turbine control valve (TCV) which reduced the EHC pressure swings. On February 2, 1992, reactor power was reduced to approximately 79% and TCV testing began. During #2 TCV testing, the Control Operator (CO) did not have time to reset the scram logic for the 'B1' trip (received as expected) before the 'A1' trip signal was received causing a reactor scram. Following the reactor scram, RCIC automatically initiated and injected. HPCI initiated but level recovered prior to injection. The cause of this event was nitrogen trapped in the Turbine Control Valve Fast Closure (TCVFC) line creating a pressure perturbation on the TCVFC Pressure Switch #1 (2-EHC-PSL-1756) causing it to trip. The gas side of an EHC accumulator was found to be solid with EHC fluid. It is believed that a seal failure of the accumulators associated with this line allowed nitrogen to enter the EHC fluid. The accumulator seal failure is attributed to excessive cycling which began after installation of the partial arc conversion modification during the last Unit 2 refueling outage. General Electric and Carolina Power & Light are investigating the cause and developing a plan for corrective action. Until implementation of the corrective action, reactor power was reduced to decrease the EHC system oscillations. The EHC accumulators were rebuilt. During the scram recovery the CO was unable to reset the 'A' Reactor Feed Pump (RFP) turbine due to a failed reset relay coil in the RFP reset logic. The 'A' RFP also had a bound pump shaft assembly due to failure of wear ring cap screws. The safety significance of this event was minimal. Safety systems functioned as designed. Another similar event was reported in LER 1-90-017 (SCRAM during TCV/TSV testing due to procedural and switch problems). The cause classification for this event per the criteria of NUREG-1022 is Design, Manufacturing, Construction/Installation.
324 | 3241999002 | 1999-03-29 | QR5 | Turbine Trip | [45 empty] | Brunswick 2 | B | GE | PO | 97 | On March 29, 1999, at 0837 hours, an invalid high vibration signal from a failed main turbine bearing vibration detector caused a main turbine trip which resulted in a Unit No. 2 reactor trip and subsequent Primary Containment Isolation system Group 2, 6, and 8 valve isolations/signals being initiated. Safety Relief Valves (SRVs) "F" and "G" lifted and immediately closed. At the time of the event, Unit No. 2 was operating at 97 percent of rated power. The SRV lifts were evaluated and it was determined that the momentary lifts were to be expected based on the impact of the transient on the reactor/steam lines. The cause of the event is attributed to failed electrical connections on the vibration detector for the No. 9 main turbine bearing. The detector failure caused the invalid high vibration signal which initiated the event. Checks of bearing temperatures, the vibration behavior of adjacent bearings, and bearing oil samples were made to ensure that an actual vibration problem did not exist. The vibration detector was replaced and the other detectors for the turbine bearings were checked and replaced as applicable. Monitoring necessary to detect vibration instrumentation failure precursors is being established. A multi-disciplined team is being formed to develop and implement options to eliminate the single point turbine high vibration trip. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv), as a condition that resulted in the actuations of engineered safety features including the Reactor Protection system.
324 | 3241999006 | 1999-06-28 | QL7 | Degraded condenser vacuum | [45 empty] | Brunswick 2 | B | GE | PO | 100 | On June 28, 1999, with Unit 2 operating at rated power, an automatic main turbine trip occurred due to low condenser vacuum. Consequently, as designed, the turbine trip resulted in actuation of the Reactor Protection system (RPS) trip logic and subsequent reactor shutdown. Reactor vessel water level decreased below the low level 1 setpoint (i.e., 166 inches of water) resulting in Primary Containment Isolation system Group 2 (i.e., drywell floor and equipment drains), Group 6 (i.e., containment atmospheric control valves), and Group 8 (i.e., Residual Heat Removal system shutdown cooling valve) isolation signal actuations. The affected systems functioned as expected. The low condenser vacuum condition occurred due to successive trips of the circulating water intake pumps (CWIP's). Silt accumulation clogged the circulation water intake pump traveling screens, causing a high differential pressure condition across the screens, and subsequent pump trips. Corrective actions include review of operational guidance and development of an operational strategy to mitigate CWIP trips, evaluation of intake canal dredging and depth profile to determine adequacy, and review of the period of vulnerability for CWIP trips. This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(iv) in that the condition resulted in the automatic actuation of Engineered Safety Feature systems including the RPS.
324 | 3241999008 | 1999-09-20 | QR6 | Manual Reactor Trip | [45 empty] | Brunswick 2 | B | GE | SU | 4 | On September 20, 1999, at approximately 0009 hours, operational activities to drain the condenser pressure transmitter sensing lines resulted in a Group 1 Primary Containment Isolation system actuation. The subsequent activities to recover from the isolation and continue startup resulted in an unexpected reactor power increase and the insertion of a manual Reactor Protection system (RPS) actuation at 0105 hours. At the time of the event, Unit No. 2 was in Mode 2, operating at approximately four percent of rated power. The cause of the event is attributed to the inadequate implementation of corrective action to a previously identified condition (i.e., condensate buildup in the transmitter sensing lines). The inadequate implementation involved proceduralizing a work-around for the condition. Contributing factors to the event were inadequate procedural adherence and ineffective communication regarding crew interactions on the part of the Senior Reactor Operator (SRO) in charge of the startup. Corrective actions include a procedure revision to ensure adequate steps were included. An engineering review will be performed to better understand the work-around. An evaluation will also be performed to identify other "institutionalized" work-arounds, applying the lessons learned from this event. The SRO involved with this event has been coached regarding procedural adherence and the need for ensuring adequate communication skills regarding crew interactions.
324 | 3242000002 | 2000-09-22 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Brunswick 2 | B | GE | PO | 100 | On September 22, 2000, at 0340 hours, the Brunswick Steam Electric Plant (BSEP) Unit No. 2, was operating at 100 percent rated thermal power, when the Unit 2 B phase of the Main Power Transformer (U2 B MPT) experienced a fault resulting in a generator load reject and subsequent turbine trip and reactor scram. In addition, Primary Containment Isolation System Groups 2, 6, and 8 valve isolations/signals initiated as expected. The transformer fault was caused by a loss of cooling. The loss of cooling system is attributed to the tripping of an electrical breaker, which provided alternate power to the transformer cooling components (i.e., 480 V distribution panel 2-HB4 circuit breaker #7). The cause of the breaker tripping has not been conclusively determined. At the time of the event, the U2 B MPT auxiliaries were being powered from the alternate 480 V source due to maintenance that was being performed on the normal source. The causes of the event include the unexplained trip of the 2-HB4 circuit breaker #7 and the failure to establish adequate compensatory measures during the maintenance activity. Corrective actions include replacement of the U2 B MPT and 2-HB4 circuit breaker #7. In addition, enhancements to the work control process, procedure revisions, and event review with appropriate site personnel will be performed to preclude recurrence. The safety significance of this event is minimal since off-site power remained available throughout the event and all emergency diesel generators were operable.
324 | 3242001001 | 2001-02-23 | QR5 | Turbine Trip | [45 empty] | Brunswick 2 | B | GE | PO | 37 | On February 23, 2001, at 2220 hours, with a shutdown of Unit 2 for a refueling outage in progress, a false high turbine speed signal in the Electro-Hydraulic Control (EHC) system resulted in turbine control valves/combined intermediate valves closing and bypass valves opening followed by a generator/turbine trip from approximately 37 percent of rated thermal power. The four emergency diesel generators automatically started as designed when the generator tripped. Operators inserted a manual trip of the reactor protection system (RPS) to shut down the reactor, and the associated reactor vessel coolant low level transient resulted in the actuation of an automatic RPS signal as well as closure of containment isolation valves in groups 2 and 6. The plant responded as designed to the event. The cause of the event is attributed to an intermittent electrical connection that resulted in a false high turbine speed signal being detected by the frequency-to-voltage converter card in the EHC system. Maintenance personnel identified a wire termination with a loose crimped ring lug in a junction box located on the front standard of the turbine. Evaluation of the lug/wire termination determined that the wire had not been fully inserted into the barrel of the lug at the time the termination was crimped. The termination appeared to be from original construction of the plant. The lug was replaced and terminated in accordance with plant procedures. The other electrical terminations in the junction boxes on the turbine were checked for loose terminations and none were identified. The safety significance of this event is considered to be minimal. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A).
324 | 3242003003 | 2003-04-04 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Brunswick 2 | B | GE | PO | 22 | On April 4, 2003, at 1354 hours, during reactor startup following the Unit 2 refueling outage, a primary containment group one isolation occurred, which resulted in a reactor scram from 22 percent rated thermal power. All group one isolation valves closed as expected. The containment isolation signal was caused by low main steam line pressure after the main turbine bypass valves inadvertently opened. The main turbine bypass valves opened due to a malfunction in an Electro- Hydraulic Control (EHC) System pressure regulator. Following the scram, an expected reactor vessel coolant level shrink occurred, causing coolant level to decrease from approximately 187 (normal) to 150 inches above instrument zero. As a result of the low water level, primary containment groups 2, 6, and 8 isolation signals were received. All required isolations occurred as a result of the reactor low water level isolation signal. All control rods fully inserted on the scram and all systems responded as designed. Reactor Core Isolation Cooling was manually started to restore reactor water level to the normal band. The cause of the event was determined to be an intermittent error signal from an EHC card that was improperly engaged in its hardware slot in the EHC pressure control circuitry. Following the event, all cards in the EHC control circuits were verified to be properly engaged. The process for checking card engagement will be enhanced to prevent recurrence of this event. The safety significance of the event is considered to be minimal.
324 | 3242003004 | 2003-11-04 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Brunswick 2 | B | GE | PO | 96 | On November 4, 2003, at approximately 1732 hours, Unit 2 received a generator/turbine trip due to loss of generator excitation, which resulted in a Reactor Protection System (RPS) actuation. All control rods fully inserted into the core. Plant response to the transient also resulted in High Pressure Coolant Injection and Reactor Core Isolation Cooling System actuations on low reactor pressure vessel (RPV) coolant level with injection into the RPV Additionally, Primary Containment Isolation System (PCIS) actuation signals for Valve Groups 1, 2, 3, 6, and 8 were received and the valves closed as required. All four Emergency Diesel Generators automatically started but did not load because electrical power was not lost to the emergency buses. The initiator of the plant transient event and system actuations was the failure of the generator exciter inner collector ring and brush holders, which resulted in loss of excitation to the generator. The root cause of the failure is a fabrication deficiency due to poor workmanship at the time of original installation of the collector ring onto the exciter shaft. Weaknesses in brush maintenance, preventive maintenance, monitoring, and trending were also identified as the root cause of the event. The damaged components were replaced. Enhanced exciter brush monitoring has been implemented on both Units 1 and 2. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A). The safety significance of this occurrence is considered minimal.
324 | 3242005002 | 2005-04-09 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Brunswick 2 | B | GE | PO | 65 | On April 9, 2005, Unit 2 was operating at 65 percent of rated thermal power. At 0049 hours, a Condensate system transient tripped the Condensate Booster Pumps and the running 2B Reactor Feed Pump (RFP). Vessel water level lowered, resulting in an automatic reactor protection system actuation at 0050 hours. Vessel water level was restored with the 2A RFP, the Reactor Core Isolation Cooling system, and Control Rod Drive system flow. All appropriate system isolations and actuations occurred as designed. After the shutdown, Reactor Coolant system (RCS) heat up rates were exceeded; however this was not recognized at the time of occurrence and an engineering evaluation was not performed, per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.9 Required Action A.2, until after Unit 2 had changed operating modes to commence restart and power operation. This is prohibited by TS LCO 3.0.4. The cause of the shutdown was a failure to establish Condensate system flow limitations, which resulted in failure to maintain adequate pressure to the suction of the RFPs. The cause of the failure to evaluate RCS heatup rates prior to mode change was attributed to procedures that were deficient in addressing the operating configuration that occurred after the shutdown. Applicable operating procedures will be revised to provide appropriate guidance. The safety significance of this event is minimal because vessel water level was restored, all appropriate safety system actuations occurred, and the RCS was evaluated as acceptable for continued operation.
324 | 3242006001 | 2006-11-01 | B1 | Loss of Offsite Power (LOOP) |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Brunswick 2 | B | GE | PO | 100 | On November 1, 2006, at approximately 18:23 (EST) Unit 2 experienced a loss of the unit's Startup Auxiliary Transformer resulting in a loss of reactor forced circulation and initiation of a manual Reactor Protection System actuation. All control rods properly inserted when the manual reactor scram was performed. Due to the loss of the Startup Auxiliary Transformer offsite power to the unit's power buses was lost when the Unit 2 main generator tripped. The four Emergency Diesel Generators (EDGs) properly started and EDGs 3 and 4 supplied the Unit 2 emergency buses. Appropriate Primary Containment Isolation System (PCIS) isolations occurred upon the loss of power to the unit's power buses. An expected Reactor Pressure Vessel coolant shrink resulted in the coolant level decreasing below the Reactor Vessel Water Level - Low Level 1, with appropriate PCIS isolations. Additionally, coolant level subsequently reached Low Level 2, at which point an additional PCIS isolation and system actuations appropriately occurred. Loss of the SAT was caused by an ineffective mechanical connection between the SAT's x-winding non-segregated bus and the associated bus bar. The root cause of the event is the ineffective connection combined with the fact that the condition monitoring performed for this bus was not adequate to detect the latent problem. Corrective actions include implementation of enhanced predictive maintenance requirements that will include thermography inspections and trending of all Unit 1 and Unit 2 non-segregated buses.
324 | 3242006002 | 2006-11-11 | QL6 | Condenser Leakage | [45 empty] | Brunswick 2 | B | GE | SU | 1 | At 1243 EST on November 11, 2006, with the reactor critical and in Mode 2 for startup activities, high conductivity in the condenser resulted in initiation of a manual Reactor Protection System actuation. All control rods properly inserted when the manual reactor scram was performed. No emergency core cooling systems (ECCS) actuated. At the time of the conductivity excursion, the condensate/feedwater system was not feeding the vessel, thus the reactor water chemistry was not adversely affected. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The high conductivity in the condenser was determined to be the result of missing plugs on 165 condenser tubes, of which 17 of the tubes were found leaking (i.e., existing tube leaks reopened). The root cause is the failure to have procedural guidance to inspect the condenser water boxes for missing tube plugs following a Loss Of Offsite Power (LOOP) event. Corrective actions included reinstalling the missing plugs and checking all plugs for tightness.
324 | 3242006003 | 2006-12-25 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Brunswick 2 | B | GE | PO | 64 | On December 25, 2006, at 0539 an automatic reactor scram occurred on Unit 2 due to a Reactor Protection System (RPS) actuation. The unit was operating at 64% reactor power in single recirculation loop operation when the RPS actuated on Neutron Monitoring System Oscillation Power Range Monitors (OPRMs), channels 2 and 4. All control rods properly inserted. Reactor water level reached Low Level 1 (LL1) and Low Level 2 (LL2) as a result of the scram. The LL1 signal caused a Group 2, Group 6, and Group 8 isolation signal. All LL1 actuations occurred as designed. The LL2 signal causes a Reactor Core Isolation Cooling (RCIC) actuation, a High Pressure Coolant Injection (HPCI) actuation, a Group 3 isolation, a secondary Containment isolation, a Standby Gas Treatment initiation (SBGT), a Control Room Emergency Ventilation (CREV) initiation, a Reactor Recirculation Pump trip, and an Alternate Rod Insertion (ARI) actuation signal. The LL2 condition was reached momentarily, and did not affect all instruments. Further evaluation concluded that the appropriate LL2 isolations and actuations occurred as designed. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event or condition that resulted in manual or automatic actuation of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The root cause of this event was determined to be inadequate incorporation of Operating Experience into plant procedures and training.
324 | 3242008001 | 2008-08-30 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Brunswick 2 | B | GE | PO | 100 | On August 30, 2008, at 1503 hours Eastern Daylight Time (EDT), a Power/Load Unbalance (PLU) actuation caused the Turbine Control Valves (TCVs) and the Main Turbine Bypass Valves (BPVs) to cycle. The initial cycle resulted in BPV No. 1 partially opening while a second cycle resulted in four BPVs going full open. At that time, the order was given to insert a manual scram. An automatic scram signal occurred just as the operator was beginning to insert the manual scram. Reactor water level momentarily dropped below Low Level 1 (LL1) during the response, resulting in Primary Containment Isolation System (PCIS) Group 2 and Group 6 isolations. LL1 actuations occurred as designed. All control rods fully inserted and all systems responded as designed. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The select cause of this event was the lack of adequate work controls for transmission maintenance activities due to an inaccurate perception of risk. The corrective actions to prevent recurrence include the revision of site procedures to provide additional work controls and improve risk assessment.
324 | 3242008002 | 2008-11-09 | QG10 | Inadvertent Open/Close: 1 Safety/Relief Valve | [6 empty] | X | [19 empty] | X | [18 empty] | Brunswick 2 | B | GE | PO | 100 | On November 9, 2008, at 1108 hours Eastern Standard Time (EST), Safety Relief Valve (SRV) 2-B21-F013H (i.e., SRV H) spuriously opened with no Operator action or testing in progress. The SRV's control switch was cycled as required by Abnormal Operating Procedure with no success. At 1113 hours, the fuses were pulled for SRV H in an attempt to close the valve. At 1117 hours, a manual reactor scram was inserted based on the Suppression Pool temperature reaching 109.8 degrees Fahrenheit (F). Technical Specifications requires a manual reactor scram to be inserted when Suppression Pool average temperature exceeds 110 degrees F. All control rods fully inserted from the manual reactor scram signal. Reactor water level lowered to Low Level 2 resulting in Primary Containment Isolation System (PCIS) isolations of Groups 2, 3, 6, and 8. In addition, the Reactor Core Isolation Cooling (RCIC) system actuated and injected into the reactor. The High Pressure Coolant Injection (HPCI) system actuated but did not inject since reactor water level had recovered. An Alternate Rod Insertion signal was received, the Standby Gas Treatment (SBGT) system initiated, and the Reactor Recirculation pumps tripped as designed. All systems responded as designed. The root cause of this event was the failure to verify proper seating of the set pressure spring in the upper spring follower plate. The corrective action to prevent recurrence is to revise the corrective maintenance procedure to perform verification of proper set pressure spring seating prior to the reassembly of the pilot valve.
324 | 3242011002 | 2011-11-16 | QR6 | Manual Reactor Trip | [45 empty] | Brunswick 2 | B | GE | PO | 7 | On November 16, 2011, Unit 2 was in power ascension following a mid-cycle maintenance outage which required reactor vessel disassembly. At 0309 Eastern Standard Time (EST), with Unit 2 operating in Mode 2 at a maximum of 7 percent of rated thermal power, a manual reactor scram was inserted due to elevated drywell leakage. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the Reactor Protection System (RPS). On November 17, 2011, at 1345 EST, it was determined that an unanalyzed condition existed on Unit 2. With Unit 2 operating in Mode 4, leak investigation activities determined that the reactor pressure vessel (RPV) head was not fully tensioned. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B), as a condition that resulted in the plant being in an unanalyzed condition that significantly degraded plant safety. The root cause of this event is the failure to provide the proper training and procedure guidance to correctly interpret critical data used to validate that the RPV head nuts were properly tightened. Corrective actions include implementing refueling procedure and training program changes to ensure that adequate training and guidance is provided to refueling floor personnel.
324 | 3242019002 | 2019-03-30 | QR6 | Manual Reactor Trip | [45 empty] | Brunswick 2 | B | GE | PO | 23 | At 17:47 Eastern Daylight Time (EDT) on March 30, 2019, with Unit 2 in Mode 1 at approximately 23 percent power and main turbine startup in progress, high temperature was sensed at main turbine bearing 9. A manual main turbine trip and manual actuation of the Reactor Protection System (RPS) were initiated in response to the high bearing temperature. All control rods inserted as expected during the scram. When the scram was inserted, reactor water level dropped below the Low Level 1 (LL1) actuation setpoint. Per design, the LL1 signal resulted in automatic actuation of the Primary Containment Isolation System (PCIS) with closure of Group 2, 6, and 8 isolation valves. Operators manually closed the Main Steam Isolation Valves (MSIVs), in anticipation of low condenser vacuum, prior to the Group 1 PCIS signal being received. All systems responded as designed. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in valid actuations of RPS and PCIS. <br /><br /> The direct cause of this event was insufficient lubricating oil supply to the main turbine bearing 9 which caused the bearing to overheat; leading to the manual scram. The most probable cause for the insufficient oil flow was design differences which resulted in a misalignment between the lower half bearing flow channel and the oil supply port in the main turbine 9 bearing housing. Corrective actions include a procedure change to ensure that lubricating oil supply oil flow is not restricted as a result of bearing replacement.
325 | 3251987017 | 1987-06-12 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Brunswick 1 | B | GE | SU | 6 | During a Unit 1 reactor startup, while at six percent power, Primary Containment Isolation System (PCIS) Groups 1 and 3 isolations occurred at 0549 on 6/12/87 followed by an automatic reactor scram due to high vessel pressure. The Reactor Building Ventilation System auto-isolated, the Standby Gas Treatment System auto-started, and the reactor recirculation pumps tripped. This event occurred during reactor coolant pressure boundary leakage Periodic Test (PT) 80.2. A scram recovery was carried out per procedure. The Unit 1 Control Operator became aware of this event through Control Room indication and annunciation. <br /><br />While slowly valving in a test pressure gauge for PT-80.2, a momentary perturbation of the common reference sensing leg to reactor level instrumentation occurred causing the isolation instrumentation to erroneously sense a reactor low level condition thereby resulting in the event. An investigation determined procedure deficiency in PT-80.2 was the most significant cause in this event. <br /><br />PT-80.2 was revised to delete use of the involved test gauge. Unit 1 subsequent criticality was achieved at 0751 hours on 6/12/87, and the unit was synchronized to the main power grid at 2256 hours on 6/13/87.
325 | 3251987019 | 1987-07-01 | QR5 | Turbine Trip | [45 empty] | Brunswick 1 | B | GE | PO | 100 | At 1035 on July 1, 1987, a turbine power/load unbalanced relay tripped causing a main turbine trip and a reactor scram while at 100% power. During this event; 1) automatic actions included: diesel generators 1-4 started, Groups 1, 2, 3 (outboard valve only), 6, and 8 isolated, Standby Gas Treatment System started, Reactor Building ventilation isolated, A reactor recirculation pump tripped; 2) manual actions included: started High Pressure Coolant Injection System and Reactor Core Isolation Cooling System, opened safety relief valves (SRV) A, B, and E. SRV J failed to open when given an open signal. HPCI tripped on overspeed during the starting sequence but automatically reset and operated per design. <br /><br />This event occurred due to a failure of the manual voltage regulator while troubleshooting was in progress on the auto voltage regulator. SRV J failed due to a binding in the solenoid plunger. The auto and manual voltage regulators and the J SRV were repaired and the unit was returned to power operation at 1258 on July 5, 1987.
325 | 3251988023 | 1988-10-21 | QP5 | Excessive Feedwater Flow | [45 empty] | Brunswick 1 | B | GE | PO | 27 | AT 1243 HOURS ON 10/21/88, UNIT 1 AUTOMATICALLY SCRAMMED, WHILE AT APPROXIMATELY 27% POWER, DUE TO A MAIN TURBINE TRIP/TURBINE STOP VALVE CLOSURE CAUSED BY A HIGH REACTOR LEVEL OF
325 | 3251988024 | 1988-11-10 | QR5 | Turbine Trip | [45 empty] | Brunswick 1 | B | GE | PO | 72 | On November 10, 1988, at 2025 hours, the Unit 1 reactor scrammed due to a momentary Turbine Control Valve Fast Closure circuitry trip. The initiating signal is believed to have resulted from electrical noise in the turbine Electro-Hydraulic Control (EHC) system during the performance of a weekly Power/Load Unbalance (PLU) Test. The unit was brought to cold shutdown and a scheduled refueling outage was started a day early. Troubleshooting efforts determined that the Reactor Protection System received three out of four inputs from the Turbine Control Valve Fast Closure circuitry due to a suspected hydraulic pressure transient induced by the spurious closure of the Intercept Valves caused by electrical noise generated by the PLU test relays. Diodes have been installed on Unit 1 and will be installed on Unit 2 to 1 suppress the electrical noise. <br /><br />During this event the unit was operating at 71.6% power. The Reactor Core Isolation Cooling System, Automatic Depressurization System, A and B Residual Heat Removal/Low Pressure Coolant Injection Systems, and the A and B Core Spray Systems were operable and in standby readiness. <br /><br /> This event had minimal safety significance as the unit is analyzed for a turbine trip from full power without bypass and, in this instance, the control and stop valves remained open until the turbine tripped on reverse power at which time the bypass valves operated properly.
325 | 3251990017 | 1990-09-27 | L3 | Turbine Bypass Unavailable | [10 empty] | X | [30 empty] | X |  |  |  | Brunswick 1 | B | GE | PO | 22 | During a scheduled Unit 1 shut down for a refuel/maintenance outage on September 27, 1990, the reactor scrammed on high pressure at 0348, during the performance of periodic test (PT) 40.2.10, Turbine Control/Stop Valves (TCV/TSV) Leak Tightness Testing. Prior to the event, the reactor was at approximately 22% power and the Emergency Core Cooling Systems (ECCS) were operable in standby readiness. Event recovery was in accordance with site Emergency Operating Procedures, no ECCS or Engineered Safety Feature actuations or isolations other than scram signals occurred. The event was occurred by erroneous procedural guidance, incorporated into the PT from a vendor document, and defective switches on the TSVs which allowed the TCVs to open when the TSVs were closing. This resulted in the turbine bypass valves (BPV) open demand signal being limited by the Maximum Combine Flow circuitry of the turbine control system. The closure of the TBVs occurred reactor pressure to increase to the SCRAM setpoint. Maximum power attained during the SCRAM was 28%. This event had minimal safety significance as the reactor is analyzed for a high pressure SCRAM from full power. Past high pressure scram events were reviewed and found not to be related to this event. The procedure will be rewritten and the switches will be repaired.
325 | 3251991007 | 1991-03-05 | QR5 | Turbine Trip | [45 empty] | Brunswick 1 | B | GE | PO | 100 | On March 5, 1991, the Unit 1 Reactor was at 100% power and 1005 psig. The Emergency Core Cooling Systems (ECCS) were operable, in standby readiness. The Control Operator (CO) had reduced generator voltage to bring MegaVars to +100. At 0937 hours EST, Unit 1 scrammed. The SCRAM was caused by a turbine generator trip resulting from tripping of the 51V-B main generator overcurrent relay from a sensed overcurrent condition. The variation in the amperage seen as a result of the CO lowering the bus voltage triggered the relay to sense and overcurrent condition; however, no actual overcurrent condition existed during this event.<br /><br /> Immediately following the SCRAM, one of the main generator overcurrent relays (51V-B) was observed to have different settings than the two adjacent relays. This relay had been removed from the plant and taken to the Transmission Substation Maintenance (TSM) shop for calibration during the recently completed refueling outage. It was determined this event resulted from personnel error, the failure of the individual(s) performing the calibration and installation of the relay to return the relay settings to the correct operating configuration following calibration. A Human Performance Enhancement System (HPES) evaluation is being performed. The 51V-B relay settings were corrected and the relay returned to service. Relays worked by the involved TSM crew were visually inspected for proper settings on both units 1 and 2. The safety significance of this event is minimal. During the transient, no unusual safety system performance was noted. No ECCS system initiations were seen nor expected. Other SCRAMS in the past two years that have been attributed to personnel error are reported in LERs 2-89-009, 2-90-009, and 2-91-001.
325 | 3251991018 | 1991-07-18 | QR8 | Spurious Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Brunswick 1 | B | GE | PO | 100 | On July 18, 1991, Unit 1 reactor was at 100% power when it scrammed as the result of a Main Steam Line Isolation signal, inadvertently generated during surveillance 1MST-RSDP-21Q for reactor water level transmitter B21-LT-N026B, which was being returned to service. After extensive investigation it is suspected that an instrument isolation valve leaked-by, resulting in a pressure transient on the common instrument header which has instruments feeding both reactor protection divisions. The resulting erroneous level signals caused the following system actuations: Isolations - Group 1 (Main Steamlines), Group 3B (1/2 Reactor Water Cleanup System), and Initiations - Reactor Core Isolation Cooling (RCIC), High Pressure Coolant Injection (HPCI), Standby Gas Treatment (SBGT), Core Spray (CS), Emergency Diesel Generators (EDG). <br /><br /> The Emergency Core Cooling Systems (ECCS) were operable. <br /><br /> The safety significance of this event is minimal as plant safety systems responded as required.
325 | 3251992003 | 1992-01-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Brunswick 1 | B | GE | PO | 100 | At 0852 on January 17, 1992, Unit 1 reactor was operating at 100% steady state reactor power. Unit 2 was at 85% reactor power. Unit 1 and 2 Emergency Core Cooling Systems (ECCS) were operable. <br /><br /> Unit 1 Uninterruptable Power Supply (UPS) sustained momentary voltage losses due to failures in the Primary UPS static switch which prevented automatic and manually initiated electronic transfers of the UPS loads to the alternate source. The loss of Unit 1 UPS resulted in the common stack radiation monitor initiating a Primary Containment Isolation System (PCIS) Group 6 isolation (Containment Atmosphere Control), Reactor Building Ventilation Isolation, and Standby Gas Train (SBGT) initiations on both Units. On Unit 1, the reactor vessel water level decreased as a result of the reactor feed pump control system runbacks with a loss of UPS and with speed control lockouts occurring when the UPS voltage returned. Reactor vessel level passed the Low Level (LL) #1 (162.5") setpoint and momentarily the LL #2 (112.5") setpoint. These initiated a reactor scram and the following PCIS isolations signals: Group 2 (Drywell Floor and Equipment Drains), Group 3 (Reactor Water Cleanup), Group 6, and a Group 8 (Residual Heat Removal). At LL #2, High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) initiated and injected into the reactor vessel until they tripped on high reactor vessel level (210"). Over the next hour, the UPS system continued to experience isolated momentary periods of unstable operation, resulting in multiple Group 6 isolation signals from the stack radiation monitor. At 0922 and 1017 additional reactor vessel LL #1 signals were generated due to difficulties experienced with maintaining stable reactor vessel level control. <br /><br /> This isolated UPS failure is of minimal safety significance as UPS is classified as non-safety related and the plant responded as designed.
325 | 3251992005 | 1992-02-29 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Brunswick 1 | B | GE | PO | 80 | At 23:00 on February 29, 1992, Unit 1 reactor was at approximately 80% reactor power for Main Turbine Stop Valve (TSV) testing which was in progress, when a reactor scram occurred. During the testing on the "A1" Reactor Protection System (RPS) Logic Channel, a Turbine Stop Valve closure, "B1" (RPS) logic channel trip occurred. The simultaneous trip of these two logic channels resulted in a full scram signal to Unit 1. Analysis of the scram data indicated the full scram signal was caused by the closure of TSV's #1 and #3 in addition to the expected closure of TSV #2. The unexpected full scram is attributed to a circuit malfunction in the Master/Slave logic used for TSV #2. This circuit uses an "inhibit" to allow individual TSV testing. Such a malfunction during #2 TSV testing, would signal TSV's #1, #3, and #4 to begin closing, when TSV #2 is closed below 95% open. <br /><br /> Following the reactor scram, reactor vessel water level decreased below the low level 1 setpoint (162.5") and briefly approached the low level 2 setpoint (112"). This level decrease is normal during a high power reactor scram. As designed, the low level 1 signal resulted in Primary Containment Isolation System (PCIS) Groups 2 (Drywell Floor and Equipment Drains), 6 (Containment Atmosphere Control) isolations, and an isolation signal to the normally closed Group 8 (Residual Heat Removal Shutdown Cooling). As reactor vessel level approached the low level 2 setpoint, the Reactor Core Isolation Cooling System automatically initiated and injected, Standby Gas Trains initiated, and Secondary Containment and the PCIS Group 3 (Reactor Water Cleanup) isolated. As reactor vessel water level was only briefly at the low level 2 setpoint, High Pressure Coolant Injection (HPCI) initiated but did not inject. The safety significance of this isolated event is minimal as Safety Systems functioned as designed..
325 | 3251995011 | 1995-05-19 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Brunswick 1 | B | GE | PO | 27 | On May 19, 1995, during the startup of Unit 1 following refuel outage B110R1, a manual Reactor Protection System trip (scram) was initiated at 1806 hours due to decreasing condenser vacuum. Prior to the scram, multiple trips of the Unit 1 Circulating Water Intake Pumps (CWIPs) occurred due to high differential pressure across the circulating water traveling screens. The high differential pressure was caused by aquatic plant life which clogged the fine mesh screens installed on the inservice CWIP traveling screens during low tide. Following the shutdown, reactor vessel water level decreased below the low level 1 setpoint (162.5') resulting in Primary Containment Isolation System Groups 2 (Drywell Floor and Equipment Drains) and 6 (Containment Atmospheric Control) valve isolations. Additionally, an isolation signal to the normally closed Group 8 (Residual Heat Removal Shutdown Cooling) isolation valves was received. <br /><br /> To maintain reactor pressure and control the vessel cooldown rate the main steam line drain and isolation valves were closed. On May 20, 1995, at 1136 hours, following restoration of the Unit 1 Circulating Water system, reactor startup was commenced. This event had minimal safety significance in that the systems required to shutdown the plant responded as required. Corrective actions include the establishment of a task force to investigate and implement methods to prevent or mitigate biological impingement of the CWIP traveling screens. The cause of this event per NUREG 1022 criteria is C, External Cause.
325 | 3251995015 | 1995-07-13 | QR4 | Core Power Excursion (RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Brunswick 1 | B | GE | PO | 100 | On July 13, 1995, at 1158 hours, the Unit 1 reactor automatically shutdown (SCRAM) from 100% power when reactor pressure perturbations caused by a malfunctioning Electro-Hydraulic Control (EHC) pressure regulator created reactor power fluctuations. Average Power Range Monitors E and F generated a full Reactor Protection System (RPS) trip as a result of the fluctuating reactor power. The automatic isolation and/or actuation of the primary containment isolation system groups 1,2,3,6, and 8 occurred as designed. With the reactor stable and SCRAM signals reset, a full RPS actuation and the expected Engineered Safety Feature (ESF) actuations occurred on Unit 1 at 1433 hours due to a momentary shrink in reactor water level below the low level 1 setpoint. The EHC malfunction was localized to four pressure regulator 'A' circuit boards. The cause of the component malfunction is still indeterminate following failure mode testing by General Electric Co. The second event occurred following the cycling of a safety relief valve which was being used to control reactor pressure. Prior to Unit 1 startup with the reactor in hot shutdown, two additional full RPS logic actuations and expected ESF actuations occurred on July 14, 1995, at 2254 hours, and on July 15, 1995, at 0425 hours, when a momentary perturbation of the reactor water low level channels A2/B2 instrument sensing lines resulted in an invalid low level 1 trip signal. The momentary perturbations resulted from pressure spikes on the 'B' reference leg sensing line, which occurred when actual reactor water level was being lowered to a point below the reactor pressure vessel reference leg nozzle.
325 | 3251995018 | 1995-09-30 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Brunswick 1 | B | GE | PO | 58 | On September 30, 1995, at 0700 hours, the Unit 1 reactor automatically shutdown from 58% power. Automatic isolation and/or actuation of the Primary Containment Isolation System groups 2,3,6, and 8 also occurred. In addition, the Reactor Building Ventilation System isolated and the Standby Gas Treatment System initiated. Just prior to the event, maintenance technicians removed a conductivity cell installed on the condensate pump suction piping in support of corrective maintenance activities. Air in-leakage occurred during the conductivity cell replacement, resulting in vapor binding of the operating condensate pumps. Subsequent loss of pressure and flow in the condensate and feedwater systems decreased reactor water level below the low level 1 and 2 trip setpoints. The High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems initiated as designed. RCIC injected and reactor water level recovered before HPCI automatically injected. Event investigation determined that uneven packing distribution around the shaft of the conductivity cell resulted in excessive air inleakage during the conductivity cell replacement. This event has minimal safety significance in that the plant responded as designed. The NUREG-1022 cause classification for this event is D, Defective Procedures.
325 | 3251996002 | 1996-01-23 | QR6 | Manual Reactor Trip | [45 empty] | Brunswick 1 | B | GE | PO | 28 | On January 23, 1996, with the Unit 1 reactor operating at 28% power and undergoing a planned reactor shutdown to correct previously identified control rod slow scram insertion times, main turbine bearings experienced increasing vibration. When vibration levels approached the procedural limits, a manual reactor scram was initiated at approximately 0657 hours. Reactor water level momentarily decreased below the low level 1 setpoint (162.5'), resulting in Primary Containment Isolation System (PCIS) Group 2 (Drywell Floor and Equipment Drains) and Group 6 (Containment Atmospheric Control) valve isolations. In addition, a Group 8 (Shutdown Cooling) isolation signal occurred; however, the Group 8 valves were already closed at the time of the shutdown. The plant responded as expected. Following completion of repairs to the Unit 1 hydraulic control units and Plant Nuclear Safety Committee review of the event recovery effort, Unit 1 reactor power ascension commenced. On January 25, 1996, at 0435 hours, the Unit 1 main generator was synchronized to the electrical grid system.<br /><br /> Investigation into the cause of the increased turbine vibration determined that diaphragm packing rubs on the recently installed monoblock low pressure turbine rotors caused hot spots on the rotor shaft which created bowing of the rotor shaft and subsequently resulted in increased turbine bearing vibration levels. The primary cause of the slow control rod scram insertion times has been isolated by diagnostic and laboratory testing to be adherence of the SSPV's exhaust diaphragm to the valve seat. Additional procedural guidance for coping with increased main turbine vibration will be incorporated into the plant shutdown procedure. Corrective actions related to the control rod slow scram insertion times include replacement of the Scram Solenoid Pilot Valve (SSPV) exhaust diaphragms with Buna-N diaphragm material and implementation of an accelerated SSPV monitoring program. <br /><br /> The safety significance of the scram event is minimal in that the plant responded as designed and the Emergency Core Cooling Systems were operable at the time of event.
325 | 3251999002 | 1999-01-23 | QR6 | Manual Reactor Trip | [45 empty] | Brunswick 1 | B | GE | PO | 25 | On January 23, 1999, at 0638 hours, with Unit 1 reactor power at approximately 25 percent, a manual reactor trip was inserted. Prior to the insertion of the manual reactor trip, operation with a single loop of the reactor recirculation system resulted in reactor vessel bottom head stratification and operation near the vessel pressure and temperature limits. Based on these conditions, the decision was made to insert the manual reactor trip signal. Reactor water level decreased below the reactor water low level 1 trip setpoint (i.e., 166 inches), resulting in the actuation of Primary Containment Isolation System (PCIS) Groups 2, 6, and 8 (i.e., isolation of the Drywell Floor and Equipment Drains, Containment Atmospheric Control system valves and the Shutdown Cooling system). Plant systems responded as designed. The causes of the event are attributed to (1) the failure to adequately evaluate the impact of a recently installed thermal hydraulic instability modification on plant operations and (2) the lack of awareness by control room personnel of the effects of longer than anticipated single loop operations at minimum flow conditions and the impact of such conditions on reactor vessel bottom head stratification. Corrective actions include establishing the necessary procedural controls and training to preclude recurrence. This event is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(iv) in that the condition resulted in the manual and automatic actuation of an Engineered Safety Feature systems.
325 | 3251999009 | 1999-11-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Brunswick 1 | B | GE | PO | 100 | On November 5, 1999, at approximately 1050 hours, with Unit 1 operating at rated power, the Unit 1 reactor feed pump (RFP) 1B tripped during the performance of feed pump testing activities. As a result of the RFP trip, reactor water level decreased. Prior to reaching the automatic reactor water level trip low level 1 setpoint, a manual reactor trip was inserted. The required system actuations occurred as a result of reaching the low level 1 setpoint. By 1105 hours, the 1B RFP trip logic was reset and the pump operated in conjunction with the Startup Level Control valve to control reactor water level. The most likely cause of the occurrence is attributed to a man-machine interface issue or a possible intermittent electrical malfunction of the overspeed control circuit. Corrective actions include incorporation of the lessons learned into the pre-job brief database, additional testing of the Unit 1 and 2 RFP trip lockout control switches and associated overspeed test circuit, and implementation of equipment enhancements as needed. This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(iv) in that the RFP tri p resulted in the actuation of Engineered Safety Feature systems.
325 | 3252003001 | 2003-01-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Brunswick 1 | B | GE | PO | 94 | On January 12, 2003, at approximately 1552 hours, decreasing reactor coolant level, due to a reactor feedwater pump turbine (RFPT) trip, resulted in the actuation of the reactor protection system (RPS), as well as Group 2 and Group 6 primary containment isolation valve closures. After the plant trip, the four emergency diesel generators (EDGs) started due to an invalid signal generated by switchyard equipment. In addition, the Reactor Core Isolation Cooling system was manually operated to maintain coolant level in the reactor vessel. At the time of the event, Unit 1 was initially operating at 94 percent of rated thermal power. The cause of the RPS and subsequent equipment actuations was attributed to the decrease in reactor vessel level caused by a RFPT 1B trip which was the result of insufficient lube oil pressure margin on the RFPT 1B bearing header during a Main Oil Pump (MOP) trip. With proper margin, the standby MOP would have been able to maintain bearing header oil pressure, thereby avoiding RFPT trip and the event. The cause of the automatic start of the EDGs is the failure of a Power Circuit Breaker (PCB) to open on its initial trip signal, which resulted in the invalid automatic EDG start signal. The safety significance of this occurrence is considered minimal. RFPT 1B is being operated with both MOPS in operation until further investigation can be performed to resolve the rapid oil pressure decrease noted when an MOP is tripped in single MOP operation. The PCB was tested to ensure proper operation and returned to service.
325 | 3252004002 | 2004-08-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Brunswick 1 | B | GE | PO | 67 | On August 14, 2004, while experiencing severe weather due to Hurricane Charley, a fault occurred on the Weather spoon 230 kV transmission line (i.e., one of four lines connecting Unit 1 to the grid). Subsequent failure of a power circuit breaker (PCB) associated with the 230 kV 1B bus resulted in a 230 kV 1B bus lockout, and ultimately, a loss of power to the reactor recirculation pumps. By procedure, the loss of these pumps necessitated a manual reactor protection system actuation. As designed, the four emergency diesel generators auto-started and the required emergency buses re-energized. All primary containment isolation actuations occurred as designed. The high pressure injection and reactor core isolation cooling systems were manually started to maintain reactor water level and pressure within acceptable limits. Following restoration of the required systems and completion of the event reviews necessary to support startup, reactor startup was commenced on August 17, 2004. The cause of the event is attributed to a combination of conditions involving the failure of PCB 24B and the switchyard breaker scheme in affect at the time of the event. Corrective actions include replacement of degraded PCB components, leak checks of site PCBs, revision to the PCB maintenance process to adequately address moisture intrusion, and revisions to operating procedures controlling the switchyard breaker scheme.
325 | 3252005005 | 2005-07-13 | QR5 | Turbine Trip | [45 empty] | Brunswick 1 | B | GE | PO | 100 | On July 13, 2005, at 0917 hours, Unit 1 received a Main Turbine trip followed by an automatic Reactor Protection System (RPS) actuation. The cause of the Main Turbine trip was the failure of the B phase of the Main Generator No Load Disconnect Switch (NLDS). Plant systems responded per design. All control rods fully inserted. An expected Reactor Pressure Vessel coolant level shrink resulted in the coolant level decreasing below the Reactor Vessel Water Level - Low Level 1 setpoint, which resulted in appropriate Primary Containment Isolation System (PCIS) isolations. Additionally, coolant level momentarily satisfied the Low Level 2 actuation logic requirements, at which point an additional PCIS isolation occurred and the High Pressure Coolant Injection (HPCI) system initiated but did not inject. Safety/Relief valves B, C, D, and E operated to control pressure. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in valid actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). The root cause of this event is inadequate design and testing of the NLDS by the vendor, resulting in the NLDS not meeting its nameplate design rating. A temporary modification has been installed on both Unit 1 and Unit 2 which replaced the NLDSs with removable bus bars.
325 | 3252008007 | 2008-11-26 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Brunswick 1 | B | GE | PO | 22 | On November 26, 2008, at approximately 1200 hours Eastern Standard Time (EST), Unit 1 experienced a primary containment Group 1 isolation which resulted in an automatic actuation of the Reactor Protection system. The Pressure-Load Gate Amplifier (PLGA) circuit board (A58), in the Electro-Hydraulic Control system, operated erroneously which caused a sensed Main Steam Line low pressure on Main Steam Line Low Pressure instruments B21-PT-N015A through D. The sensed low pressure while in Mode 1 resulted in the Group 1 isolation. Following the scram, an expected reactor vessel coolant level shrink occurred. As a result of the low water level, primary containment Groups 2 and 6 isolation signals were received. All required isolations occurred as a result of the reactor low water level isolation signals. All control rods fully inserted on the scram and safety-related systems responded as designed. The Reactor Core Isolation Cooling System was manually started to restore reactor water level to the normal band. The erroneous operation of the PLGA circuit board was due to loose connection(s) within the blade / blade receptacle connection. The root cause of the loose connection was that the key slot in circuit board A58 was not squared at the bottom mating surface. Resin at the bottom mating surface, present since original manufacturing of the circuit board, prevented full seating with the terminal receptacle. Corrective actions to prevent reoccurrence include: (1) visual verification of Unit 1 and Unit 2 EHC circuit board engagement at the next opportunity and (2) procedural enhancements to ensure circuit board engagement after maintenance work is performed.
325 | 3252010003 | 2010-05-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Brunswick 1 | B | GE | PO | 100 | On May 5, 2010, at approximately 11:44 hours Eastern Daylight Time (EDT), an automatic reactor scram occurred on Unit 1 following a trip of the 1B Reactor Feed Pump (RFP). The Reactor Recirculation pumps did not run back as expected following the 1B RFP trip. The resulting water level shrink caused level in the Reactor Pressure Vessel (RPV) to drop to Low Level 1, causing the activation of the Reactor Protection System (RPS) and the Primary Containment Isolation System (PCIS). All control rods properly inserted. PCIS Group 2, Group 6, and Group 8 isolation signals were received on Low Level 1. Actuations of the Primary Containment Isolation Valves (PCIVs) were completed and the affected equipment responded as designed. Water level in the RPV momentarily reached Low Level 2, which initiated the High Pressure Coolant Injection (HPCI) System, the Reactor Core Isolation Cooling (RCIC) System, and a partial Group 3 (i.e., Reactor Water Cleanup (RWCU)) PCIS isolation. The HPCI and RCIC systems did not inject to the RPV. The RWCU inboard isolation valve isolated and, in accordance with plant design, 1-G31-F004 (i.e., RWCU outboard isolation) did not automatically isolate. Unit 2 was not affected by this event. The safety consequences of this event were minimal. All Emergency Core Cooling Systems (ECCS) were operable and available to provide adequate core cooling if needed. The investigation concluded that the adverse condition was a historical problem and no root cause could reasonably be determined.
325 | 3252012001 | 2012-02-22 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Brunswick 1 | B | GE | PO | 73 | On February 22, 2012, at 2319 hours Eastern Standard Time (EST), a manual Reactor Protection System (RPS) actuation was inserted on Unit 1 in anticipation of a loss of condenser vacuum. Shortly before the manual RPS actuation, Circulating Water Intake Pump (CWIP) 1B tripped due to high delta-pressure across the intake traveling screen. This caused the trip of the remaining Unit 1 CWIPs. Previously, at 1859 hours, balance of plant (BOP) bus Common C unexpectedly de-energized. This resulted in a loss of power to the CWIP traveling screen motors which, in turn, lead to the high delta-pressure across the traveling screens. As a result of the scram, reactor water level reached the Reactor Vessel Water Level - Low Level 1 actuation set point and Primary Containment Isolation System (PCIS) Groups 2 and 6 isolations occurred. Additionally, the Main Steam Isolation Valves (MSIVs) (i.e., PCIS Group 1) were manually closed prior to reaching the Condenser Vacuum - Low actuation set point. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the RPS system and automatic and manual actuations of PCIS. The root cause of this event is inadequate preventive maintenance (PM) for the 4160/480 V transformer associated with the Common C BOP bus. Corrective actions include the establishment of appropriate PM tasks for the 4160/480 V transformers.
325 | 3252016001 | 2016-02-07 | B1 | Loss of Offsite Power (LOOP) |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Brunswick 1 | B | GE | PO | 88 | On February 7, 2016, at 1312 Eastern Standard Time (EST), Unit 1 was in Mode 1 (i.e., Run) at 88 percent of rated power in end-of-cycle coastdown. At that time, an electrical fault occurred on a balance of plant 4160-volt bus, resulting in a lockout of the Startup Auxiliary Transformer (SAT) and a loss of both Reactor Recirculation pumps. Licensed personnel inserted a manual scram per procedure. Emergency Diesel Generators supplied emergency electrical busses until offsite power was restored at 1628 EST. The loss of power and reactor water level changes resulted in automatic closures of various Primary Containment Isolation Valves (PCIVs). The electrical fault resulted in an electrical explosion; therefore, an Alert was declared at 1326 EDT. The immediate cause of this event was a fault in a non-segregated electrical bus connected to the SAT. The root causes were insufficient detail in applicable maintenance instructions for inspecting the non-segregated bus housing and inadequate instructions for terminating electrical cables in a circuit breaker cubicle. Corrective actions include repairing equipment damaged by the electrical fault and revising the procedures and work instructions.
325 | 3252018002 | 2018-04-07 | QR5 | Turbine Trip | [45 empty] | Brunswick 1 | B | GE | PO | 100 | On April 7, 2018, at 0836 Eastern Daylight Time (EDT), Unit 1 automatically tripped during realignment of the Stator Cooling System. The trip was uncomplicated with all systems responding normally. Reactor water level reached low level 1 (LL1) due to the reactor trip. Per design, the LL1 signal resulted in Group 2, Group 6, and Group 8 Primary Containment Isolation System (PCIS) actuations. The Reactor Protection System (RPS) and PCIS actuations are being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).<br /><br /> The direct cause of this event was a design deficiency which resulted in an unanticipated Turbine Protection System actuation that caused a main turbine trip and subsequent automatic reactor trip. The root cause of the design deficiency was determined to be human performance related. Corrective actions include training and procedure revisions.
325 | 3252019003 | 2019-04-21 | QR5 | Turbine Trip | [45 empty] | Brunswick 1 | B | GE | PO | 100 | At 23:07 Eastern Daylight Time on April 21, 2019, with Unit 1 in Mode 1 at approximately 100 percent power, the Main Turbine and both Reactor Feed Pumps (RFPs) tripped resulting in a reactor scram and reactor water level dropping below Low Level (LL) 1 and 2. The LL1 resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves), and Group 8 (i.e., shutdown cooling isolation valves) isolations. The LL2 resulted in Group 3 (i.e., Reactor Water Cleanup) isolation, a secondary containment isolation signal, and High Pressure Coolant Injection and Reactor Core Isolation Cooling (RCIC) automatically starting and injecting into the vessel. All control rods inserted as expected during the scram and all systems responded as designed. <br /><br /> The Main Turbine and both RFPs tripped due to two out of three level instruments sensing a false high reactor water level. The false signal was a result of hydrogen deflagration in the reactor level condensing chamber due to a flaw in the original design. <br /><br /> There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to actuations of the Reactor Protection System, Primary Containment Isolation System, Emergency Core Cooling System, and RCIC.
325 | 3252020001 | 2020-03-22 | QR6 | Manual Reactor Trip | [45 empty] | Brunswick 1 | B | GE | SU | 2 | At 12:55 Eastern Daylight Time (EDT) on March 22, 2020, with Unit 1 in Mode 2, stabilized at 2% power, during startup from a refueling outage, all four main turbine Bypass Valves (BPVs) fully opened unexpectedly. This created an unexpected reactor depressurization and cooldown which resulted in the operating crew inserting a manual reactor scram. The scram was uncomplicated and all control rods inserted as expected during the scram. <br /><br /> All BPVs fully opened as a result of the Turbine Control System (TCS) pressure setpoint not being set correctly. This error went undetected until the low main condenser vacuum isolation signal to the BPVs cleared during the startup sequence, at which time the BPVs fully opened. <br /><br /> There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to manual actuation of the Reactor Protection System (RPS).
325 | 3252020003 | 2020-08-03 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Brunswick 1 | B | GE | PO | 19 | At 23:02 Eastern Daylight Time on August 3, 2020, with Unit 1 in Mode 1 at approximately 19% power during Hurricane Isaias, a loss of the transformer bus powering the Startup Auxiliary Transformer (SAT) resulted in a Loss of Offsite Power (LOOP). By design, all Main Steam Isolation Valves closed and an automatic reactor scram occurred. All control rods inserted as expected on the scram. At the time of this event the main generator was removed from service due to unrelated generator ground issues and all plant loads were being supplied by the SAT.<br /><br /> By design, the LOOP resulted in automatic actuation of Primary Containment Isolation System (PCIS) Group 1, 2, 3, 6, and 8 isolation valves. In addition, all four emergency diesel generators (EDGs) started, with EDGs 1 and 2 loading to their respective emergency buses per design. Reactor water level reached low level 1 following the scram resulting in automatic actuation of PCIS Groups 2, 6, and 8, by design. <br /><br /> The electrical fault that caused the transformer bus powering the SAT to trip and subsequent LOOP was determined to be a result of storm generated debris. <br /><br /> There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to valid actuation of the Reactor Protection System, PCIS, and EDGs.
327 | 3271988045 | 1988-11-18 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 72 | This LER is being revised in its entirety to provide the root cause and corrective action associated with this event. <br /><br />On November 18, 1988, at 1004 EST, the unit 1 reactor tripped from a steadystate condition of 72-percent rated thermal power as a result of the main turbine being tripped due to the actuation of the main generator protective relay for neutral overvoltage. This relay monitors the secondary voltage of the generator neutral transformer and actuates when this voltage exceeds a setpoint of 10 volts for one second, indicating a phase-to-ground fault. Subsequent to the trip, Operations personnel responded by performing the appropriate emergency and general operating instructions to stabilize the unit. During the reactor coolant system (RCS) cooldown following the reactor trip, RCS average temperature (Tave) decreased below the no-load Tave of 547 degrees F due to an excessive mass loss from the steam generators via the steam dump control system. A shutdown margin calculation was performed following the trip which determined Technical Specifications shutdown margin limits were maintained. Testing of the main generator revealed a phase-toground fault internal to the generator on "C" phase stator coil T-17. The neutral winding of "B" phase, stator coil T-13, failed during testing of the main generator. The stator bars were removed and transported to Westinghouse for analysis. This analysis concluded the fault associated with T-17 was due to a breakdown of coil insulation by either ingress of water from outside the coil or leakage of a hollow, water carrying strand. T-13 had a hollow strand leakage which occurred due to corrosion, which was also observed in T-17. The main generator has been repaired, and further recurrence controls have been taken to limit the RCS cooldown. Shutdown margin was maintained throughout this event.
327 | 3271988047 | 1988-12-25 | QP5 | Excessive Feedwater Flow | [45 empty] | Sequoyah 1 | P | WE | PO | 18 | On December 26, 1988, at 0051 EST, unit 1 reactor tripped from 7-percent power on lo-lo level in S/G loop 4 following a feedwater isolation (FWI) on hi-hi level in S/G loop 2. Before this event, the main turbine was rolled at 0004 EST and reached 1700 RPM at 0037 EST. During this time, sparks were noted in the No. 10 bearing area on the turbine/generator. At 0040 EST, the shift operations supervisor elected to manually trip the turbine and then initiate a controlled reduction in power. Approximately 10 minutes later, a FWI occurred on hi-hi level in loop 2. With the reactor at approximately 22-percent power, the operator attempted to reduce reactor power to less than 5-percent to be within the capabilities of auxiliary feedwater (AFW) since main feedwater was isolated. However, as a result of a combination of the FWI, the cold AFW, and the rapid reduction in power, S/G levels dropped sharply and the unit tripped on lo-lo level in loop 4. Immediately following the trip, the balance of plant operator took manual control of AFW to limit the reactor coolant system (RCS) cooldown in accordance with ES-0.1, "Reactor Trip Response." As average temperature (Tavg) dropped to 540 degrees F, the lead operator started an emergency boration at 75 gpm as required. Tavg decreased to 538 degrees F before turning around and slowly increasing. The unit returned to no-load temperature and pressure and the boration was secured. The trip was a result of erratic level control on all S/G's main and bypass regulator valves for feedwater. The controllers for the bypass valves were not fine-tuned to allow for automatic operation. This forced the operator to simultaneously use manual control on the bypass and main regulator valves and consequently, resulted in the lo-lo level reactor trip. Corrective actions taken included fine-tuning the bypass valve controllers and verifying the correct operation of the main and bypass valves. <br /><br />Long-term corrective actions were detailed in TVA's letter of May 5, 1989.
327 | 3271989005 | 1989-02-10 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On February 10, 1989 with unit 1 in mode 1, a reactor trip occurred at 2036 EST. The trip signal was a result of a steam generator (SG) steam flow to feedwater flow mismatch of greater than 40 percent of the nominal value of steam flow at full power coincident with a low SG level (25 percent) signal on SG loop 3. Two Instrument Maintenance (IM) technicians were implementing work request (WR)-B238429 on flow recorder (FR)-2-200/201, "Condenser Bypass/Makeup Flow," which is located on main control room (MCR) panel 1-M-3. The recorder pen needed to be restrung which required it to be removed from the case. The technicians fully removed the recorder in its case which required lifting the power supply leads. After reinstallation, the technicians reterminated the power supply leads, at which time one technician determined the terminating leads were too close to each other. The technician inadvertently shorted a screwdriver between the terminals, tripping open breaker No. 39 on 120-VAC vital instrument board I-II which is the power supply to a plug mold supplying the recorder. The plug mold is also the common power supply to the flow indicating controllers (FIC)-3-35, -90, and -103 which control main feedwater regulating valves (MFWRVs) FCV-3-35, -90, and -103 for SG loops 1, 3, and 4. FIC-3-48 for MFWRV on SG loop 2 is powered from board I-III. The three MFWRVs closed, isolating main feedwater (MFW) to the SGs. This resulted in the solid state protection system reactor trip signal. The root cause of the reactor trip signal was personnel error, in that, appropriate precautions were not taken in performing terminations of energized equipment. To prevent recurrence of this event, this event was discussed with IM planners, technicians, and engineers to familiarize them with the root cause of the event. Additionally, open WRs and scheduled preventive maintenances on MCR recorders were retrieved by the Work Control Group for replanning to address precautions on equipment common power supplies. In addition to the above, SQM2, "Maintenance Management System," and SQM2.2, "Maintenance Management System Troubleshooting," will be revised to clarify the requirements for working on energized equipment.
327 | 3271989035 | 1989-12-10 | QP5 | Excessive Feedwater Flow | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On December 10, 1989, at 1051 Eastern standard time (EST) with Unit 1 in Mode 1, a turbine trip/reactor trip occurred. The trip resulted from a high-high feedwater level of 75 percent in the No. 3 steam generator (S/G). The trip was preceded by a secondary side transient and turbine runback to approximately 80-percent load as a result of a high level in the No. 3 heater drain tank (HDT). During the runback, a low feedwater flow was observed, and Main Feedwater Pump (MFP) 1A was placed in manual to boost feedwater flow to match steam flow. However, as the S/G levels recovered, No. 3 loop did not isolate until after the 60-percent setpoint, and the turbine/reactor trip occurred as the No. 3 S/G level reached 75 percent. Plant shutdown proceeded in an orderly manner consistent with procedures. A posttrip review teAm concluded that the trip was caused by a failure of S/G Loop 3 main feedwater regulating valve to close and maintain Loop 3 S/G at a 60-percent level; a contributing cause was the inability of the MFP 1A to adequately respond to changing feedwater demands. The initiating event was the failure of level control valves to maintain proper levels in the No. 3 HDT. Corrective actions taken consisted of troubleshooting, repair, and/or adjustments to malfunctioning equipment. Longer-term corrective actions include Eagle 21 installation to improve operating margins. <br /><br /> At 2003 EST, an engineered safety feature feedwater isolation signal was actuated during posttrip testing when an alligator clip-type jumper fell off a terminal point. Interim corrective action consisted of issuance of a training letter to applicable personnel; long-term corrective action will be to evaluate a more positive method of connecting temporary jumpers.
327 | 3271990012 | 1990-06-02 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Sequoyah 1 | P | WE | PO | 11 | On June 2, 1990, with Units 1 and 2 at approximately 11 and 100 percent power respectively, a reactor trip occurred on Unit 1 about 17 minutes after a generator/turbine trip had occurred as a result of electrical problems. Control room operators reduced reactor power and announced the turbine trip on the plant public access (PA) system. The plant was stabilizing as reactor power reached approximately 15 percent when main feedwater (MFW) flow was lost. Two auxiliary unit operators (AUOs) had misheard the PA announcement as "unit trip" rather than "turbine trip" and had isolated the steam supplies to the MFW pumps. Operators started the auxiliary feedwater pumps while continuing to reduce reactor power, but the reactor tripped on low-low steam generator level. The root cause of the reactor trip has been attributed to inadequate communication between control room operators and AUOs. As corrective action, Operations management has issued a night order clarifying what specific actions should be taken by AUOs following a reactor or turbine trip only with unit operator guidance. A related weakness in AUO training regarding actions to be taken following a turbine trip or reactor trip was identified and corrected during the investigation of this event. Operations will evaluate the adequacy of AUO procedural guidance and training for other events.
327 | 3271990021 | 1990-09-14 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Sequoyah 1 | P | WE | PO | 98 | This LER is being revised to update the corrective action resulting from continued evaluation of the event. On September 14, 1990, with Unit 1 in Mode 1, a reactor trip occurred at 1613 Eastern daylight time. The trip was generated from a low-low steam generator water level signal in Loop 2. The low level was the result of a feedwater transient initiated by the failure of a vital inverter. The inverter failure occurred after the completion of maintenance activities on the inverter and during the transfer of the inverter from its maintenance power supply to its normal power supply. During the transfer, the inverter output voltage dropped to zero because of the failure of the inverter's silicon-controlled rectifiers. This deenergized the 1-II vital instrument power board. The loss of power resulted in the main feedwater regulator valves closing and the main feedwater pumps dropping to minimum speed. This reduced feedwater flow to all four steam generators. Plant systems responded properly and the shutdown posed no danger to plant employees or the general public. The unit was stabilized in accordance with plant procedures. The vital inverter was repaired and returned to service on September 15, 1990.
327 | 3271990022 | 1990-09-19 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 60 | On September 19, 1990, with Unit 1 operating at approximately 60 percent reactor power, 2235 pounds per square inch gauge (psig), and 564 degrees Fahrenheit (F), a turbine trip followed by a reactor trip occurred at 0357 Eastern daylight time. The turbine tripped as a result of "A" phase main transformer differential relay (sudden pressure) operation caused from corroded and shorted terminals on the transformer gas relay. Because the reactor power was greater than the reactor trip interlock for automatic block of reactor trip on turbine trip permissive (P-9), a reactor trip occurred as a result of the turbine trip. Operators responded to the trip using Emergency Operating Procedure 1-E-0, "Reactor Trip or Safety Injection," and stabilized the reactor at hot standby conditions (Mode 3) at 547 degrees F and 2235 psig. All reactor protection systems operated as designed, and no anomalies occurred. The sudden pressure relay was replaced, and the equipment was returned to service.
327 | 3271992010 | 1992-04-28 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On April 28, 1992, at 2022 Eastern daylight time, with Unit 1 in power operation at approximately 100 percent, the turbine tripped as a result of a loss of load, followed by a reactor trip. The cause of the loss of load was attributed to a varying resistance ground within the gas-operated relay (GOR) on the Phase B main transformer. An 18-second delay in the turbine trip, following loss of load, resulted from an incomplete modification that did not remove a diode from an electrical circuit. The plant response to the transient following the turbine trip was as expected for a loss-of-load condition. A mercury switch, internal to the GOR, was replaced and the transformer was tested and returned to service. GORs on the remaining Unit 1 main transformers and the Unit 2 main transformer GORs were meggered and found acceptable. Subsequently, on May 23, 1992, the Unit 1 Phase C main transformer GOR developed a ground, and the relay was effectively isolated. Neither a turbine trip nor a loss of load was induced by the ground. An evaluation of the failure mechanism is pending an outage of sufficient duration to replace the GOR or to inter-tie the spare main transformer.
327 | 3271992012 | 1992-05-16 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Sequoyah 1 | P | WE | PO | 82 | On May 16, 1992, Unit 1 was manually tripped from 82 percent power as a result of a condensate and feedwater transient. The decision to manually trip the reactor was made by the shift operations supervisor. The equipment, required to operate after the reactor was manually tripped, performed as expected. The condensate transient was caused by a simultaneous loss of both No. 7 heater drain tank pumps (HDTPs). The cause of the trip of the No. 7 HDTPs was determined to be the failure of the No. 7 heater drain tank level control valve positioner. The level control valve positioner was repaired and returned to service.
327 | 3271992018 | 1992-10-26 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 81 | On October 26, 1992, at 1855 Eastern standard time, with Unit 1 in power operation at approximately 81 percent, the reactor tripped because of a turbine trip. The turbine trip resulted from a high-high feedwater level in the No. 3 steam generator. Before the trip, water was inadvertently introduced into the nonessential control air system, inducing secondary plant transients that resulted in turbine runbacks to 81 percent for Unit 1 and 67 percent for Unit 2. Before the Unit 1 turbine runback, steam generator No. 3 was experiencing low feedwater level. The unit operator placed the Loop No. 3 feedwater regulating valve flow indicating controller (FIC) in manual, attempting to gradually raise feedwater level. The valve went to full open, and attempts to close the valve were unsuccessful, resulting in a high-high steam generator level. The immediate cause of the trip was attributed to the automatic-manual switching relay (K-1) in the FIC not changing state; however, the water intrusion in the air system initiated the transient that eventually led to the trip. The unit was stabilized in the hot standby condition. The K-1 relays in the four Unit 1 feedwater regulating-valve FICs were replaced. The FICs were tested and returned to service.
327 | 3271992027 | 1992-12-31 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Sequoyah 1 | P | WE | PO | 100 | On December 31, 1992, at approximately 2148 Eastern standard time (EST), with Units 1 and 2 in power operation at approximately 100 percent, both units received a reactor trip signal because of reactor coolant pump bus undervoltage. The reactor trips were followed by turbine trips. Undervoltage on the 6.9-kV shutdown boards initiated board load stripping, diesel generator (D/G) starts, and D/Gs tying onto their respective shutdown board. Electrical loads were appropriately sequenced back to the boards. Main feedwater isolated and auxiliary feedwater pumps started. Loss of power to a radiation monitor resulted in an auxiliary building isolation. With limited staffing in the Unit 2 main control room, recovery evolutions for Unit 2 resulted in isolation of centrifugal charging pump suction and removal of both centrifugal charging pumps from service. Unit 2 entered LCO 3.0.3 for approximately one minute until a suction flow path was reestablished. The cause of the event was an internal fault in a switchyard power circuit breaker resulting from inappropriate testing methodology. Corrective actions include strengthening of switchyard controls and increasing minimum Operations control room staffing.
327 | 3271993002 | 1993-02-05 | QR3 | Reactivity Control Imbalance | [45 empty] | Sequoyah 1 | P | WE | SU | 1 | On February 5, 1993, at 0615 Eastern standard time, during a controlled shutdown with Unit 1 in Mode 2 operating at less than one percent power, the unit was manually tripped. Before the reactor trip, a rod urgent alarm annunciated in the main control room. This prevented the rod control system from allowing movement of the control rods in either manual or automatic modes. Based on procedural guidance, the control rods were maintained in manual during maintenance evaluation of the alarm. It was subsequently determined that the reactor would soon enter Mode 3 because of the negative reactivity insertion resulting from increasing Xenon concentration with the control rods in an abnormal withdrawn position. The decision was made to manually trip the reactor. The cause of the rod control system rod urgent alarm was determined to be in the rod control system timing circuitry. A glitch in the timing circuitry could cause the multiplexing cards to operate out of sequence and cause the rod urgent alarm to annunciate. Although no hardware problems were identified, it was concluded that the most likely component to have caused the rod control system problem was the input/output alternating current amplifier board. This board was replaced with a new board.
327 | 3271993003 | 1993-02-18 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On February 18, 1993, at 1336 Eastern standard time, with Unit 1 operating at approximately 100 percent power, a reactor trip occurred as a result of the exciter field breaker opening. The breaker opened when a senior reactor operator training instructor inadvertently actuated the trip latch on the exciter field breaker during a training exercise. The unit responded as expected following the trip and the Operations crew stabilized the unit in hot standby conditions. The reactor trip occurred as a result of the instructor failing to evaluate the risks and consequences associated with conducting training activities using operating plant components. Training on energized and/or sensitive equipment has been stopped until a policy on utilizing energized and/or sensitive equipment is established. An interim policy on opening cabinets for energized equipment has been developed and communicated to site employees. Additionally, appropriate disciplinary action has been taken.
327 | 3271994008 | 1994-05-01 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Sequoyah 1 | P | WE | PO | 50 | On May 1, 1994, at 0140 Eastern daylight time, with Unit 1 in power operation at approximately 50 percent power, the turbine tripped followed by a reactor trip as a result of the loss of the 1A main feedwater pump (MFP). Prior to the event, the 1B MFP was out of service for maintenance. During clearance tagging in support of the maintenance work on the 1B MFP oil pump, an assistant unit operator inadvertently deenergized the running oil pump on the in-service 1A MFP. The loss of the oil pump and the subsequent drop in the oil pressure resulted in a trip of the operating MFP. With both MFPs in a tripped condition, a turbine trip and the subsequent reactor trip was initiated. The cause of the event was personnel error. Appropriate disciplinary action was taken with the involved individual.
327 | 3271994011 | 1994-07-15 | QR6 | Manual Reactor Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 25 | On July 15, 1994, at 1352 Eastern daylight time (EDT), with Unit 1 at approximately 25 percent power and with the turbine offline, a manual reactor trip was initiated. As designed, the reactor trip initiated a feedwater isolation (FWI). Subsequent to the trip, at 1558 EDT, a second FWI occurred. The trip was initiated in accordance with procedures as a result of the loss of a reactor coolant pump (RCP). During implementation of a dispatch switching order (clearance tagging) for main generator voltage regulator repair, an individual inadvertently removed bus-side fuses instead of line-side fuses to the 1D 6.9-kilovolt unit board. The bus fuses provide power to the board's loss-of-voltage relays. When the fuses were removed, a loss of voltage was sensed, resulting in the tripping of motor breakers supplied by the board, including the Loop 4 RCP motor breaker. The condition was caused by personnel error. The individual performing the clearance did not realize that the wrong fuse compartment was accessed until after the fuses were removed. The appropriate disciplinary action was taken with the involved individual. The second FWI appears to have been caused by erratic operation of the Loop 4 steam generator power-operated atmospheric relief valve. Troubleshooting identified a problem with the valve controller. The controller was repaired and returned to service.
327 | 3271994014 | 1994-11-29 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On November 29, 1994, at 0713 Eastern standard time, with Unit 1 in power operation at approximately 100 percent power, the turbine tripped followed by a reactor trip as a result of the loss of both of the turbine 48-volt electrohydraulic control (EHC) power supplies. The cause of the loss of both 48-volt turbine EHC power supplies was attributed to an electrical spike on the power supply output. The power supply output overvoltage protection limiter setting for both power supplies had previously been reduced. The root cause of this event was inadequate technical review in changing the EHC overvoltage trip point. The trip point was changed based upon verbal communication from an onsite vendor representative. A contributing factor to this event was an increase in radio frequency interference resulting in the overvoltage trip point being exceeded, causing the loss of the EHC power supply. The overvoltage trip point was reset to the 10 percent preferred margin before returning the system to operation. The appropriate plant procedures will be revised to require vendor information, including verbal information, to be evaluated in accordance with the vendor manual program before the information can be utilized.
327 | 3271995008 | 1995-06-23 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On June 23, 1995, at 0327 Eastern standard time (EST), a reactor trip occurred on Unit 1 as a result of a lo-lo level signal on steam generator No. 2. During the process of establishing a clearance for a maintenance activity on a radiation monitor, an assistant unit operator (AUO) opened the wrong breaker. The radiation monitor is supplied from the 120-volt Vital Instrument Power Board 1-II, Breaker 48. However, the AUO placed the clearance on the 120-volt instrument Power Board 1-I, Breaker 48. This resulted in a loss of power to Reactor Protection Set 1. The loss of power to the protection set caused the mainfeed pumps to go to minimum speed, as designed. The reduction in feedwater flow resulted in decreasing levels in the steam generators and subsequent reactor trip. The root cause of this event was personnel error in that the AUO opened the wrong breaker. Corrective action for this event includes the appropriate disciplinary action.
327 | 3271995010 | 1995-07-17 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | This LER is being revised to provide root cause failure analysis information. On July 17, 1995, with Unit 1 in power operation at approximately 100 percent, a turbine trip occurred followed by a reactor trip. The event resulted from the initiation of a trip signal by a sudden pressure rely located on the 'A' phase main transformer. A review of the condition determined that a no fault condition existed in the transformer. The reactor protection systems responded to the trip as expected; no anomalies occurred. Operators responded to the trip as prescribed by procedures and stabilized the reactor in the hot standby condition. Subsequent to the event, the sudden pressure relay, Qualitrol Corporation Model No. 900-003-01, was tested and found to be defective. Testing was performed on two additional Qualitrol Series 900 sudden pressure relays. Those relays were found to be nonfunctional. After an examination of the internal components of the failed relays, it was determined that the nonorificed control bellows was distended in each of the relay assemblies. Subsequent to the event, Qualitrol Series 900 sudden pressure relays that are located on transformers in use were either disabled or replaced with relays of a different design. Root cause failure analysis determined that the bellows is being deformed when the sudden pressure relay is isolated and heated. The heat source could be solar, transformer operation, or the oil purification process. Lessons learned have been provided to the appropriate personnel. New Qualitrol relays are being installed and placed in service.
327 | 3271995017 | 1995-12-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On December 8, 1995, at 2156 Eastern standard time (EST), a manual reactor trip was initiated on Unit 1 as a result of a low level in the No. 4 steam generator. At 2122 EST, a low steam generator level alarm was recieved in the main control room. An assistant unit operator was dispatched to the feedwater regulator valves to investigate. It was determined that an air line on the Loop 4 feedwater regulator valve was leaking and causing the feedwater regulator valve to drift closed. The root cause of this event was a lack of controls for maintenance activities that affect vibration through system configuration changes. A 1/8-inch brass close nipple that connected the air line to the valve positioner had failed. The configuration of the four Unit 1 feedwater regulating valves was changed by installing new tubing and fittings. The appropriate procedures and/or program will be revised to address maintenance activities that affect vibration through system configuration changes. The appropriate Maintenance personnel will be trained on the revised procedures/program.
327 | 3271995019 | 1995-12-25 | QR6 | Manual Reactor Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On December 25, 1995, at 0713 Eastern standard time (EST), with Unit 1 at 100 percent power, a manual reactor trip was directed by the shift operations supervisor (SOS). The unit had received a Generator 1 Exciter Field Overcurrent alarm and was experiencing oscillating meter indications associated with the main generator excitation system, including meter indications that the electrical megawatt output on the main generator was fluctuating 100-150 megawatts. The manual reactor trip was directed when the SOS determined that control of the generator excitation system had been lost and could not be regained. The reactor protection systems responded to the trip as expected. Operators responded to the trip as prescribed by procedures and stabilized the reactor in the hot standby condition. The root cause of this event was a field pole failure in the main generator exciter. The corrective action was to replace the exciter. This action is complete.
327 | 3271996006 | 1996-06-23 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | Sequoyah 1 | P | WE | PO | 100 | On June 23, 1996, at 1714 Eastern daylight time, a turbine trip, followed by a reactor trip, occurred on Unit 1 as a result of an actuation of the generator backup/transformer feeder relay. An initial switchyard fault occurred when a coupled capacitor potential device (CCPD) failed. This fault was cleared by the bus differential relay. A second fault occurred when the CCPD catastrophically failed and caught fire. The smoke from the fire caused a second fault, resulting in the actuation of the generator backup/transformer feeder relay. The actuation of the generator backup/transformer feeder relay tripped the turbine generator and caused the subsequent reactor trip. The cause of this event was a failure of the CCPD. The most probable cause of the CCPD failure was that the lower capacitor module began to conduct current because of internal degradation. The CCPD is a stacked capacitor consisting of three modules utilized to provide voltage indication in order to allow sychronization comparision for breaker closure. This put stress on the other two modules until the leakage current, resulting from the degraded module, caused the CCPD failure. The plant condition was diagnosed, and action was taken to stabilize the unit. The fire brigade responded to the fire and extinguished the fire. The failed CCPD has been removed from service and is being replaced.
327 | 3271996010 | 1996-11-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 1 | P | WE | PO | 36 | On November 16, 1996, at 0031 Eastern daylight time, with Unit 1 in power operation at approximately 36 percent, the reactor was manu pressure feedwater heaters because of high-high feedwater heater shell level. Before the unit was tripped, operators were performing a controlled unit shutdown for scheduled maintenance. After shutting down the No. 3 heater drain tank pumps, heater drain tank level abnormal alarms and heater abnormal level alarms were received in the main control room. An isolation of the feedwater heaters occurred resulting in a loss of feedwater to the main feedwater pumps. A decision was made to manually trip the reactor in anticipation of an automatic reactor trip on low steam generator level. This event occurred as a result of the No. 3 heater drain tank by-pass valve failing to respond to the increase in level in the No. 3 heater drain tank. The proportional controller on the valve was set at 50 percent in order to obtain a quicker response from the valve. Setting the proportional controller at 50 percent results in a decrease in the operational range of the controller. The setpoint (point at which the valve actuates) for the controller was set outside the operational range resulting in the failure of the valve to open when the No. 3 heater drain tank level had increased to a level above the setpoint. Appropriate procedures and the vendor manual will be revised to address the affects that changing the proportional band has on the operational range of the valve controller.
327 | 3271997012 | 1997-08-01 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Sequoyah 1 | P | WE | PO | 100 | While implementing a modification to improve the materiel condition of the control and Service Air System at Sequoyah Nuclear Plant (SQN), the control air header pressure dropped rapidly after modifications personnel cut into a six-inch control air header located inside an equipment clearance boundary. The loss of control air pressure resulted in a runback of the Unit 1 and Unit 2 Turbines and instabilities in Unit 1 secondary side flows sufficient to warrant a manual trip of the Unit 1 reactor. The immediate cause of the loss of control air header pressure was corrosion products (rust debris) that inhibited full closure of one of the six-inch gate valves used as a clearance boundary. The root cause of this event is an inadequate work boundary during performance of work on the Control and service Air System. The inadequate work boundary was the result of the poor materiel condition in this portion of the Control and Service Air System. Corrective actions include the following: 1) Operations personnel isolated the breach within approximately 7 minutes following the manual trip of Unit 1, 2) TVA will remove the corrosion buildup in the affected portions of the Control and Service Air System and will inspect other portions of the air system, as appropriate, for excessive corrosion, and 3) TVA will evaluate the adequacy and frequency of preventative maintenance (PM) on the affected portions of the Control and Service Air System and revise the PMs, as appropriate.
327 | 3271998001 | 1998-05-19 | QC4 | Loss of ac Instrumentation and Control Bus. | [13 empty] | X | [30 empty] | X | Sequoyah 1 | P | WE | PO | 100 | On May 19, 1998, with Unit 1 operating at 100 percent power, at 1043 Eastern daylight time (EDT), an automatic reactor trip occurred. During the performance of a relay functional test for 480-volt Shutdown Board 1A1-A, supply power was transferred from the normal feeder breaker to the alternate feeder breaker. The alternate feeder breaker failed, initiating a loss of Instrument Power Board 1-I and de-energizing Channel I reactor protection racks. The loss of Instrument Power Board 1-I caused a loss of power to the steam flow instrumentation, resulting in a closure of the feedwater regulator valves. The loss of feedwater caused a low-low steam generator level and subsequent reactor trip. The cause of the event was the failure of the alternate feeder breaker to the 1A1-A 480-volt shutdown board. The C phase of the alternate feeder breaker did not close properly resulting in arcing. The 480-volt shutdown board was inspected and no damage was identified. The normal feeder breaker was placed in service and the 480-volt shutdown board was returned to operation.
327 | 3271998003 | 1998-11-09 | QR8 | Spurious Reactor Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | This LER is being revised to provide an additional condition of an oscillator board with a bad solder joint. On November 9, 1998, at 1139 Eastern standard time (EST), an automatic reactor trip occurred. The reactor trip was initiated by an overpower differential temperature reactor trip caused by the loss of vital power to the power range neutron detectors. The silicon controlled rectifier in the bridge circuit of Vital Inverter 1-IV failed causing the inverter to fail. With a nuclear instrumentation system power range channel out of service for testing, the logic necessary to initiate the reactor trip was completed. Control room operators responded to the unit promptly, diagnosed the condition, and took necessary actions to stabilize and maintain the unit in a safe condition. The inverter bridge circuit was replaced and the inverter was returned to an operable status. On November 25, 1998, at 0924 EST, Vital Inverter 1-IV tripped. The inverter trip was caused by a failed oscillator board with a bad solder joint, attributed to a manufacturer's defect. The component was replaced and the inverter was returned to an operable status. On April 28, 1999, during an extent of condition review, an oscillator board with a bad solder joint was identified on the 2-IV vital inverter. The remaining Units 1 and 2 inverters were verified to be acceptable. The oscillator board was repaired and returned to service.
327 | 3272000003 | 2000-03-21 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 76 | On March 21, 2000, at 0440 Eastern standard time (EST), Unit 1 experienced an automatic reactor trip. The reactor trip was initiated by a turbine trip which was caused by a detected loss of excitation field to the main generator. The turbine trip signal was caused by the actuation of two protective relays that were installed during the refueling outage. A wiring error contained in the design change package resulted in improper installation in the field. The wiring error resulted in actuation of the relays during unit restart when a loss of excitation condition did not exist. The root cause of the design error was an error by the package preparer that was not detected by the barriers in place to prevent the design deficiency. The design change checking, design verifications, and reviews were not completed to the proper level. The design error was corrected. A standdown meeting, to clarify expectations for design checkers and design verifiers, was held with Design Engineering personnel. A training letter, addressing expectations for design checkers and design verifiers, was issued to the SQN Design Engineering personnel.
327 | 3272000004 | 2000-09-25 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On September 25, 2000, at 1033 Eastern Daylight Time, Unit 1 experienced an automatic reactor trip on low-low steam generator level. The reactor trip was preceded by a turbine runback because main feedwater pump (MFP) 1A tripped on low control oil pressure. Following the 1A MFP trip and turbine runback, the remaining MFP (1B) was not able to provide sufficient feedwater flow to maintain steam generator level, resulting in the automatic reactor trip. The root cause for the turbine runback was lower motor bearing failure on the lA MFP main oil pump, resulting in the motor tripping on thermal overload. The root cause of the reactor trip was incorrect adjustment of the 1B MFP turbine governor, resulting in a lower control signal output and inability of the pump to provide sufficient feedwater flow. The lA MFP turbine main oil pump motor bearing was replaced, the motor tested and returned to service. Calibration methodology of the MFP turbine governor was changed to ensure that during a transient, where one MFP is required to pickup load, the governor valve will open to provide adequate steam flow to run the pump near its maximum speed.
327 | 3272002004 | 2002-07-12 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On July 12, 2002, at 2223 Eastern Daylight Time, an automatic reactor trip occurred on Unit 2 as a result of an undervoltage condition on two reactor coolant pumps. The undervoltage resulted from the loss of power to Start Bus 2B, when the alternate feeder breaker attempted to close while being racked into the connect position. This closure attempt caused the normal feeder breaker to trip open, resulting in a loss of bus voltage initiating the reactor trip. When Start Bus 2B deenergized one offsite power source became inoperable. Operations personnel did not verify the availability of the remaining offsite power sources. The main control room operators took appropriate actions to stabilize the reactor in hot standby. The cause of the reactor trip was the failure of the alternate feeder breaker for Start Bus 2B to function properly when being returned to its normal configuration. The cause of failing to verify the availability of the remaining offsite power sources was supervisor duties were improperly focused, as priorities were placed on restoring off-site power and the diesel generators to normal alignment. A diagnostic of the breaker is being performed. The breaker will be repaired or replaced as necessary.
327 | 3272003001 | 2003-08-28 | QR6 | Manual Reactor Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On August 28, 2003, at approximately 1603 Eastern daylight time, main control room (MCR) operators initiated a manual reactor trip as a result of a loss of load event. Preceding the manual reactor trip, plant personnel were performing quarterly simulated oil trip tests on the main turbine. During performance of the thrust-bearing trip test section of the procedure, a main generator trip occurred resulting in a 100-percent loss of load to the unit. MCR operators diagnosed the plant condition, determined that a loss of load event had occurred, tripped the reactor, and took actions to stabilize and maintain the unit in hot shutdown, Mode 3. The turbine tripped as a result of the manual reactor trip. Based on information that the reactor had not tripped and the successful manual trip, MCR operators made an Alert emergency declaration (failure of reactor protection). The immediate cause of the event was a closed instrument isolation valve to the Unit 1 turbine auto-stop oil pressure switch. The event analysis identified two likely causes: 1) failure to properly implement the valve verification process, or 2) failure to maintain a configuration control process. Immediate actions were taken to verify valve positions identified in the extent of condition evaluation. Individuals involved with auto-stop oil pressure switch maintenance were counseled and disciplined. Site personnel were provided event lessons learned that reinforced configuration control requirements. A design change was implemented to add visual indication of auto-stop oil pressure switch actuation.
327 | 3272004001 | 2004-03-15 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On March 15, 2004, at approximately 1517 Eastern standard time, automatic turbine and reactor trips occurred. The trips were the result of a main generator trip. The generator trip occurred because of inadvertent protection relay actuation. Relay actuation occurred as a result of a ground loop (a positive side and negative side ground) on the non-safety related 250 Volt direct current (Vdc) Battery Board 2 system. Following the reactor trip, reactor coolant system (RCS) temperature decreased below 550 degrees Fahrenheit (F). Based on this RCS temperature coincident with a reactor trip, a main feedwater isolation occurred as expected. As designed, auxiliary feedwater was automatically initiated on steam generator low-low level following the reactor trip. The immediate cause of the event was inadvertent actuation of the Unit 1 generator main bank transformer protective relay. The root cause of the event was that a negative ground was created by an improperly abandoned cable. Contrary to the design change, only one end of the cable was lifted and insulated during design change implementation in 1999 by TVA’s Transmission Group. Since completion of the design change in 1999, TVA has taken steps to improve work standards in its Transmission Group by documenting management observations of work activities and implementation of the Substation and Switchyard Construction Standards Manual.
327 | 3272005001 | 2005-04-09 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On April 9, 2005, at approximately 1111 Eastern daylight time, an automatic reactor trip occurred followed by a turbine trip. The reactor trip was initiated by low ASO pressure input to the reactor protection system. The unit was operating with no abnormal indications prior to the trip. The reduction in pressure was the result of the failure of a red rubber gasket installed between the turbine protective trip block and the turbine governor pedestal. A tear in the gasket allowed oil in the ASO supply port to bypass the trip block and bleed directly to the drain port. The root cause of the event is improper machining of the turbine front pedestal oil ports during original manufacturing by Westinghouse Electric Company. This resulted in oil port misalignment and oil seepage between the turbine protective trip block and the turbine governor pedestal. Because of oil port misalignment, sheet gasket material had been used in place of the originally designed O-rings to seal the mating surfaces. The gasket material was not fully compatible with turbine oil and design of the connection did not support use of sheet gasket material. To correct the condition, the trip block and governor pedestal were reassembled with O-rings at the oil ports and gasket sealant on the metal to metal surfaces. Follow-up inspection found the interface to be leak free.
327 | 3272008001 | 2008-01-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On January 16, 2008, at 1925 Eastern standard time, the Unit 1 reactor was manually tripped as a result of a low steam generator level on Loop 3. Maintenance personnel were performing a transmitter calibration on a Loop 3 steam generator pressure transmitter. During performance of the calibration, Maintenance personnel made an incorrect assumption that a place-keeping aid placed in the procedure was intended to be the procedure start point when in fact they should have started two pages previous to the place-keeping aid location. The two missed pages resulted in Operations not being notified to remove the channel being tested as a controlling channel. This resulted in performing testing on the pressure transmitter on a controlling channel, causing closure of the Loop 3 main feedwater regulating valve. Operations placed the feedwater regulating valve in manual to open the valve. However, before steam generator water level began to increase, the pre-established low steam generator level trigger-point was reached and the operating crew initiated a manual reactor trip. The cause was determined to be a failure to follow procedure because of personnel not performing proper place keeping during performance of a calibration procedure. Corrective actions include establishing and proceduralizing standard placekeeping requirements, strengthening and proceduralizing standard pre-job brief requirements, and training on these standard requirements.
327 | 3272009003 | 2009-03-26 | QR7 | Other Reactor Trip (Valid RPS Trip) | [10 empty] | X |  |  | X | [26 empty] | X |  |  |  | X | Sequoyah 1 | P | WE | PO | 96 | The enclosed LER is being revised to indicate a condition where SQN failed to perform a technical specification (TS) action within the required timeframe. The enclosed LER is being revised to indicate that the condition resulted in an unplanned scram with complications. On March 26, 2009 at 0452 Eastern daylight time (EDT), Sequoyah Units 1 and 2 received an automatic reactor trip on reactor coolant pump (RCP) buses undervoltage. A loss of Common Station Service Transformer (CSST) C caused a loss of power to two unit boards on each unit that feed RCPs. CSST B continued to supply offsite power to the Train B safety-related shutdown boards for both units. The emergency diesel generators started and powered the Train A safety-related shutdown boards for both units. Both units were stabilized in hot standby (Mode 3). CSST C was isolated from CSST D and reenergized from the switchyard PCBs. Offsite power was then restored to the Train A safety-related shutdown boards for both units. The cause of the bus fault was determined to be degraded bus bar insulation and water intrusion into the CSST D secondary bus duct: Corrective actions include replacement of a section of the CSST D bus and inspection of the other CSSTs and cooling tower transformers (CTT). Repairs to degraded insulation of CSST C, CTT A, and CTT B were made as a result of the inspections. After the dual unit trip, with one offsite power source inoperable, the remaining offsite power source was not demonstrated operable within one hour as specified by TS 3.8.1.1 Action a. The TS action was subsequently completed.
327 | 3272009004 | 2009-04-28 | QR6 | Manual Reactor Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 18 | On April 28, 2009, at 2159 Eastern daylight time, SQN Unit 1 reactor was manually tripped following automatic isolation of two intermediate pressure feedwater heater strings. Prior to the reactor trip, the control room was notified that a moisture separator relief valve (MSR) had lifted. Upon notification of the condition of the valve, Operations personnel entered applicable abnormal operating procedures. Unit power was reduced from 27 percent to approximately 18 percent in an attempt to close the MSR relief valve. Since the reduced power level did not close the valve, the turbine was manually tripped. Following the turbine trip, two intermediate pressure feedwater heater strings automatically isolated. Operations manually tripped the reactor and entered the applicable emergency procedures. The plant safety systems responded as designed. The cause of the MSR valve lifting was determined to be failure of a gland sealing steam check valve to isolate because of foreign material. The cause of the isolation of the intermediate heater strings was determined to be the backflow of inventory from Heater Drain Tank (HDT) No. 3 into the No. 2 heater, which interfered with the ability of No. 2 heater to maintain proper level. As an interim action applicable plant operating procedures have been revised to ensure that when the plant is operating below 50 percent RTP, HDT No. 3 is maintained in full bypass to the condenser. The corrective action will perform a study of the necessary design change options and implement a solution.
327 | 3272009005 | 2009-05-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On May 6, 2009, at 2256 Eastern daylight time with Unit 1 operating at 100 percent reactor power, the reactor was manually tripped because of imminent loss of steam generator level induced by the closure of the Loop 1 main feedwater regulating valve. During normal power operations, the control room received a steam flow/feedwater flow mismatch alarm. Operations placed the Loop 1 main feedwater regulating valve in manual and attempted to open the valve. Operations observed that there was still no flow to the Loop 1 steam generator. Operators took action to manually trip the reactor. The Loop 1 main feedwater regulating valve actuator diaphragm was found to be ruptured. The diaphragm failure is attributed to an improper clamping force of the diaphragm to the actuator stem. This insufficient clamping force was a result of insufficient torque applied to the fastening screw. The insufficient clamping force allowed stress concentrations at the diaphragm hole, which caused an initial tear in the diaphragm composite material and led to an instantaneous failure of the diaphragm.
327 | 3272010002 | 2010-11-16 | QR6 | Manual Reactor Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 26 | On November 16, 2010, at 2210 Eastern Standard Time, SQN Unit 1 was manually tripped based on decreasing steam generator (SG) level in Loop 4. Prior to the reactor trip, reactor power was at 26 percent and ascending following completion of a scheduled refueling outage. A manual turbine trip was initiated, because a moisture separator reheater safety relief valve lifted and would not reseat. Following the manual turbine trip, the Loop 4 SG feedwater level controller was unable to control the feedwater level because of an inoperable main steam dump valve controller. Manual actions were taken by Operations personnel, but level could not be recovered and the reactor was tripped. The root cause was determined to be a failure to identify and perform adequate installation testing on the main steam dump valve controller. During the refueling outage that ended on 11/15/2010, a digital feedwater design change was implemented requiring relocation of the main steam dump valve controller. Relocating the controller required the power cord to be unplugged, the controller moved, and the power cord to be reinstalled. There was no installation testing identified for this controller in the design change notice or the associated work order. When the power cord was reinstalled, it was not properly latched. This resulted in the controller becoming unplugged. An immediate corrective action required components that were moved during the modification to be inspected. Corrective actions include revising the modification installation and installation testing procedures to add additional verifications and reviews.
327 | 3272010003 | 2010-12-20 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | Sequoyah 1 | P | WE | PO | 100 | On December 20, 2010, at 0050 Eastern Standard Time, SQN, Unit 1 reactor was manually tripped as a result of a fire associated with the main generator. Site personnel reported smoke in and around the main generator of the turbine building. Operations personnel witnessed a fire in the neutral bus duct housing of the main generator and initiated an emergency alarm. Operation personnel entered into the abnormal operating procedure for plant fires. The fire brigade and the Incident Commander responded to the fire alarm and validated a fire present inside a vent/inspection opening of the neutral bus duct housing. After validation of the fire, operations personnel manually tripped the reactor and turbine to support the fire brigade actions to arrest the fire. The fire brigade extinguished the fire. The safety systems performed as designed for the reactor trip. The unit was stabilized in Mode 3. The cause of the fire on the main generator bushing was identified as a cyclic vibration induced failure of the neutral bushing porcelain, which allowed a hydrogen leak that ignited. The failed neutral bushing was replaced. Corrective actions include developing a preventive maintenance instruction to define a service life for refurbishment/replacement of SQN, Unit 1 and Unit 2 main and neutral bushings. Another action involves the visual inspection of the SQN, Unit 2 bushings during the next scheduled refueling outage.
327 | 3272011003 | 2011-06-26 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On June 26, 2011, at 1615 Daylight Saving Time (DST), Sequoyah Nuclear Plant (SQN) Unit 1received an automatic reactor trip as a result of the failure of a turbine control analog electro-hydraulic (AEH) signal conditioning card. The card failure created an indication that the main turbine had tripped (auto stop latch signal) resulting in the governor and throttle valves closing. When the throttle valves closed, an automatic reactor trip was received from the turbine trip at greater than 50 percent rated thermal power. An immediate corrective action was to replace the failed AEH signal conditioning card. The root cause of this event was determined to be a failure to eliminate and mitigate single point vulnerabilities in AEH signal conditioning printed circuit boards.
327 | 3272011004 | 2011-07-20 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On July 20, 2011, at approximately 2129 Daylight Saving Time (DST), Sequoyah Nuclear Plant (SQN) Unit 1 automatically tripped as a result of loss of the Unit 1 Preferred Inverter. The loss of the preferred inverter caused the turbine governor valves to close, and the load rejection caused a Power Range Neutron Flux High Negative Rate Reactor Trip signal. At the time of the reactor trip, plant personnel were installing test equipment inside the preferred inverter to monitor frequency. A ground was introduced on the preferred inverter output when the frequency check was performed, which caused the preferred inverter output to be lost. The direct cause of the event was that the acting Maintenance foreman incorrectly decided to perform missed steps in a preventative maintenance procedure. This resulted in the preferred inverter frequency check steps being performed out of sequence from the sequence in the test procedure. The root cause of this event was that Operations has not sustained written guidance for supervisory review of applicable work documents prior to returning equipment to service. Corrective actions will include establishing procedural guidance for Operations supervisory review of applicable work documents prior to returning equipment to service.
327 | 3272011005 | 2011-08-18 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On August 18, 2011, at approximately 2250 Daylight Saving Time (DST), Sequoyah Nuclear Plant (SQN) Unit 1 automatically tripped as a result of reactor coolant pump (RCP) 1 and 3 bus undervoltage. The undervoltage condition on the two unit boards that feed RCPs 1 and 3 was caused by a slow transfer of the 1A Start Bus from normal to alternate supply. A failure of the 1A Start Bus potential transformer (PT) secondary side fuse initiated the slow transfer of the 1A Start Bus. Unit 1 was stabilized in hot standby following the automatic reactor trip. The cause of the fuse failure was determined to be mechanical separation of end plate from end cap due to inadequate manufacturing aggravated by age. The root cause was determined to be no preventative maintenance to address periodic replacement of fuses for the Start Bus protective relay circuits. The corrective actions will include creating preventative maintenance procedures to address replacing fuses in locations that are trip risk sensitive or could result in engineered safety feature actuations.
327 | 3272015001 | 2015-03-11 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Sequoyah 1 | P | WE | PO | 99 | On March 11, 2015, at 0621 Eastern Daylight Time Sequoyah Nuclear Plant Unit 1 reactor automatically tripped due to a Negative Rate Trip as a result of Control Bank D Control Rod H-8 dropping into the core. Initial investigation revealed Control Rod H-8 dropped into the core approximately one second before the reactor trip. The dropped control rod caused a rapid decrease in power which was sensed by all four nuclear instrumentation system power range channels. Reactor trip logic is two out of four channels. No power changes or control rod motion were in progress prior to the reactor trip. All safety related equipment operated as designed, all control rods fully inserted as required, and auxiliary feedwater automatically initiated as expected. Unit 1 was stabilized in hot standby following the automatic reactor trip. The cause of the reactor trip was due to Control Rod H-8 failing to maintain its commanded position. Trouble shooting was performed on the electrical components associated with Control Rod H-8. The direct cause was a compressed four-pronged pin inside a connector for the control rod drive mechanism (CRDM) circuit. The root cause was failure of a maintenance procedure to provide inspection guidance and acceptance criteria on CRDM vertical panel connections. The corrective action to prevent recurrence includes revising the maintenance procedure and periodic preventive maintenance of CRDM connections. Unit 2 was unaffected by this event.
327 | 3272015002 | 2015-07-24 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On July 24, 2015, at 1351 Eastern Daylight Time (EDT), Sequoyah Nuclear Plant (SQN) Unit 1 reactor automatically tripped following a turbine trip due to actuation of the generator backup relay. The relay actuation was a result of voltage variations on the main generator. A malfunctioning base adjuster follower card was identified on the main generator voltage regulator. After replacement of the base adjuster circuit card, Unit 1 was connected to the grid and ascending in power. On July 27, 2015, at 1040 EDT SQN Unit 1 reactor was at 82 percent power when it automatically tripped following a turbine trip due to actuation of the generator backup relay. An improperly terminated wire was found in the voltage regulator logic drawer which caused high resistance. Prior to restart, the wire was properly connected. Following each of the reactor trips, all safety related equipment operated as designed, all control rods fully inserted as required, and auxiliary feedwater automatically initiated from the feedwater isolation signal as expected. The cause of each of the reactor trips was determined to be inadequate standards for multi-wire terminations and verification at the time of the original improper wire termination event in the mid-1990s. Corrective actions to prevent recurrence include adding guidance for multi-wire terminations to Modifications and Additions Instruction M&AI-7.1, Cable Terminations and Repairing Damaged Cables. The condition described in this LER did not have an impact on SQN Unit 2.
327 | 3272015002 | 2015-07-27 | QR5 | Turbine Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On July 24, 2015, at 1351 Eastern Daylight Time (EDT), Sequoyah Nuclear Plant (SQN) Unit 1 reactor automatically tripped following a turbine trip due to actuation of the generator backup relay. The relay actuation was a result of voltage variations on the main generator. A malfunctioning base adjuster follower card was identified on the main generator voltage regulator. After replacement of the base adjuster circuit card, Unit 1 was connected to the grid and ascending in power. On July 27, 2015, at 1040 EDT SQN Unit 1 reactor was at 82 percent power when it automatically tripped following a turbine trip due to actuation of the generator backup relay. An improperly terminated wire was found in the voltage regulator logic drawer which caused high resistance. Prior to restart, the wire was properly connected. Following each of the reactor trips, all safety related equipment operated as designed, all control rods fully inserted as required, and auxiliary feedwater automatically initiated from the feedwater isolation signal as expected. The cause of each of the reactor trips was determined to be inadequate standards for multi-wire terminations and verification at the time of the original improper wire termination event in the mid-1990s. Corrective actions to prevent recurrence include adding guidance for multi-wire terminations to Modifications and Additions Instruction M&AI-7.1, Cable Terminations and Repairing Damaged Cables. The condition described in this LER did not have an impact on SQN Unit 2.
327 | 3272015003 | 2015-09-14 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On September 14, 2015, at 0426 Eastern Daylight Time, Sequoyah Nuclear Plant (SQN) Unit 1 reactor was manually tripped due to a loss of power to the Vital Instrument Power Board (VIPB) 1-II. Prior to the reactor trip, operators were in the process of realigning Vital Inverter 1-II for planned maintenance. During this evolution, VIPB 1-II became de-energized. Operators entered Abnormal Operating Procedure AOP-P.03, "Loss of Unit 1 Vital Instrument Power Board" which required a manual reactor trip. Following the reactor trip, operators restored power to VIPB 1-Il with the normal supply at 0550. All plant safety systems responded as designed, all control rods fully inserted, and auxiliary feedwater automatically initiated from the feedwater isolation signal as expected. It was determined that an Alternating Current (AC) output switch failed causing the loss of power to the VIPB 1-II. The direct cause of the switch failure was due to increased friction of bearing surfaces caused by lack of appropriate lubrication. The lack of lubrication was related to a failure to implement a corrective action following an operating experience review at SQN in 2000 of a similar event at McGuire Nuclear Station. The failure to implement a corrective action was determined to be the root cause of this event. Corrective actions to prevent recurrence include ensuring the existing requirement for management review of all corrective action closures remains in the Corrective Action Program. Unit 2 was unaffected by this event.
327 | 3272015004 | 2015-11-23 | QL5 | Partial Closure of MSIVs | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On November 23, 2015, at 0844 Eastern Standard Time, Sequoyah Nuclear Plant (SQN) Unit 1 reactor was manually tripped due to plant parameters indicating that the Loop 3 Main Steam Isolation Valve (MSIV) had started drifting in the closed direction. Prior to the reactor trip, the open light indication on the main control board for the Loop 3 MSIV was noted to be extinguished. The light bulb was replaced with no change in indication. At the same time, the Post Accident Monitoring panel indicator for the Loop 3 MSIV displayed full open; however, within two to three minutes, the panel provided dual indication. Subsequently, Operators noted that the reactor coolant system temperature and Loop 3 Steam Generator (SG) pressure were both rising, and the Loop 3 SG flow was lowering. These indications confirmed the Loop 3 MSIV was drifting closed. Following the reactor trip, all plant safety systems operated as designed, all control rods fully inserted, and auxiliary feedwater automatically initiated from the feedwater isolation signal, as expected. Troubleshooting identified a loose termination associated with the Loop 3 MSIV handswitch that would result in a slow loss of air pressure and cause the MSIV to slowly drift in the closed direction. The direct cause was determined to be a loose electrical connection on the MSIV handswitch. The root cause was determined to be inadequate work practices during replacement of the MSIV handswitch in 1994 that resulted in the loose electrical connection. The corrective action to prevent recurrence is revision of the work control planning procedure to ensure specific connection fastener torque values are utilized during work order planning. SQN Unit 2 was unaffected by this event.
327 | 3272019001 | 2019-04-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On April 14, 2019, at 0320 eastern daylight time (EDT), Sequoyah Nuclear Plant, Unit 1, experienced an automatic reactor trip. The reactor trip was preceded by a turbine runback, because main feedwater pump (MFP) 1A tripped on low lube oil pressure. In response to the 1A MFP trip, the Auxiliary Feedwater (AFW) System actuated, as designed; however, AFW and the remaining main feedwater pump (1B) were not able to provide sufficient feedwater flow to maintain steam generator level. This resulted in an automatic reactor trip due to low-low level in the Loop 3 steam generator (SG). The causes of the reactor trip were previous MFP turbine hydraulic control system modifications coupled with an unvalidated turbine runback setpoint resulting in the inability to supply adequate feedwater flow to the SGs during the loss of a MFP transient. The corrective actions to prevent recurrence are: (1) implement digital feed pump control upgrade via an engineering change package, and (2) implement a revised turbine runback setpoint, as determined, as part of an engineering change package.
327 | 3272019003 | 2019-08-27 | QR3 | Reactivity Control Imbalance | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On August 27, 2019, at 0109 eastern daylight time, Sequoyah Nuclear Plant, Unit 1, automatically tripped as a result of Control Bank D Control Rod H-8 dropping into the core. All safety related equipment operated as designed, all control rods fully inserted as required, and auxiliary feedwater automatically initiated as expected. Additionally, during a post trip review, it was identified that the Steam Generator #3 pressure transmitter, 1-PT-1-23, demonstrated sluggish behavior. This pressure transmitter had previously been identified as inoperable during a Unit 1 reactor trip occurring April 14, 2019. Maintenance was performed following the April event and the transmitter was declared operable. After further review, it was determined that the transmitter was inoperable since November of 2015. <br /><br /> For Control Rod H-8, the root cause was determined to be that excessive wear to the H-8 stationary gripper latch mechanism resulted in the inability to maintain the control rod in the fully, or nearly fully, withdrawn position for an extended period of time. The corrective action is to submit a license amendment request and develop an engineering design change to permanently remove Control Rod H-8. For 1-PT-1-23, the cause was determined to be the procedure associated with post maintenance testing did not identify that maintenance can affect the response time of the transmitters. The corrective action is to revise the procedure to note response time aspects should be considered when developing post maintenance testing for these transmitters.
327 | 3272020002 | 2020-05-13 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On May 13, 2020, at 0208 eastern daylight time, Sequoyah Nuclear Plant, Unit 1, was at 100 percent power when an automatic reactor trip signal was received concurrent with a low steam line pressure safety injection signal. The low steam line pressure safety injection signal was actuated from the steam rate of decrease feature. Following the reactor trip, all plant safety systems responded as designed with the exception of the following components: Pressure Transmitter, 1-PT-1-23, was found to have a failed power supply and Glycol Inboard Isolation Valve, 1-FCV-61-122, failed to automatically isolate on the Phase A containment isolation signal (the corresponding outboard isolation valve actuated as designed such that the penetration was isolated, as required). A post-trip troubleshooting team determined that the cause of the event was the failure of a Speed Error Channel B card associated with the Analog Electro-Hydraulic (AEH) Control System for the Main Turbine. The card was replaced, calibrated, and successfully passed functional testing. <br /><br /> The failure of the Speed Error Amplifier B Card was caused by a failed chip on the card identified because of an over heated resistor. The corrective action to reduce similar events is to replace the Main Turbine AEH Control System.
327 | 3272021001 | 2021-05-24 | QR8 | Spurious Reactor Trip | [45 empty] | Sequoyah 1 | P | WE | PO | 100 | On May 24, 2021, at 0915 eastern daylight time (EDT), SQN Unit 1 experienced an automatic reactor trip. Approximately 0.5 seconds before the reactor trip, an unexpected Rod Control Urgent Failure alarm annunciated and Control Bank B, Group 2 rods began to lower. The reactor trip first out alarm indicated the trip was from a Power Range High Neutron Flux Rate detected by the Power Range Nuclear Instruments. <br /><br /> During troubleshooting, it was discovered that there were bad pin connections on the backplane of the phase card associated with Control Bank B (the card connection between the Control Bank B, Group 2 stationary gripper phase control card and the backplane of its card cage). <br /><br /> All plant safety systems responded as designed. All rods fully inserted as required. <br /><br /> The direct cause of the failure has been attributed to the card connection between Control Bank B Group 2 stationary gripper phase control card and the backplane of the card cage. Periodic instruction procedure, PI-674 Periodic Calibration of the Full Length Rod Control Power, directs activities to remove phase control cards during calibration which can result in pin deformation. Therefore, the corrective action for this event is to revise the procedure to modify how calibration activities are performed based on learnings obtained from the equipment failure evaluation.
328 | 3281988023 | 1988-05-19 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 72 | This LER is being revised to update the corrective action section of this report. On May 19, 1988, with unit 2 at 71.7 percent reactor power, a reactor trip occurred at 1413 EDT. At 1350 EDT, a senior reactor operator (SRO) and an instrument mechanic (IM) started the process of making adjustments to the No. 3 heater drain tank (HDT) level controllers. The SRO and IM proceeded to troubleshoot the problem in an attempt to reduce the level in the subject tank. After three or four manipulations, the SRO noted the HDT pumps began to cavitate, and a subsequent trip of the pumps occurred. At 1405 EDT, the balance of plant (BOP) operator noted fluctuations in the No. 3 HDT discharge flow. At 1408 EDT, both No. 3 HDT pumps tripped. The BOP started a reduction in turbine load. At this time it was noted that steam generator (S/G) No. 1 level was dropping. The operator took manual control of the feedwater regulator valve and went to full open to regain level. Level dropped to 21 percent in the No. 1 S/G before level turned around and started to ascend. The "A" main feedwater pump backed off in speed as it was in the automatic control. However, "B" main feedwater pump continued in manual control causing feedwater flows to be high. Level continued to increase to 60 percent at which point the regulator valves automatically closed as designed. This resulted in a steam/feedwater flow mismatch. The S/G loop 3 low level bistable was already tripped as a result of 2-LT-3-97 being out of service. Therefore, a reactor trip signal was generated due to a steam/feedwater flow mismatch coincident with low S/G level in loop 3. The mismatch was caused by a S/G level transient induced by a manual BOP runback as a result of No. 3 HDT level manipulation and subsequent loss of the No. 3 HDT pump. The low S/G level was caused by bistable 2-LS-3-97 being in the tripped condition due to environmental qualification concerns. The trip was reviewed with Operations personnel to ensure familiarization with the event and to detail the lessons that could be learned from the transient.
328 | 3281988024 | 1988-05-23 | QR8 | Spurious Reactor Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 70 | On May 23, 1988, at 0028 EDT with unit 2 at 70 percent power, a reactor trip occurred from a low flow signal on reactor coolant system (RCS) loop 4 (2 out of 3 channels tripped on any one RCS loop above 35 percent power). At the time of the trip, Surveillance Instruction (SI)-246, "Recalibration Procedure for Reactor Coolant Flow Channels," was in progress to recalibrate the loop 4, channel II transmitter (2-FT-68-71B). The reactor trip "Sequence of Events Record" showed the trip being initiated from RCS loop 4, channel III bistable 2-FS-68-71D. Investigation into the cause of the trip revealed that the transmitter being calibrated was attached to a common sense line with loop 4, channel III transmitter, 2-FT-68-71D. It was discovered that the instrument mechanics (IMs) performing SI-246 had not complied with procedure when valving out the transmitter 2-FT-68-71B. SI-246 instructs the performer to relieve RCS system pressure by cracking open the transmitter high side test tee. Contrary to this instruction the IMs relieved system pressure through the drain valve which routes to a closed drain system which made it impossible to determine the amount of fill fluid (RCS water) lost when the drain valve was open. It was theorized that when the final step was performed to open the high side isolation valve, the void in the drain line caused a pressure drop in the common sense line and subsequent drop in the output of 2-FT-68-71D. This drop in the 2-FT-68-71D output caused the low flow bistable 2-FS-68-71D to actuate and since the 2-FS-68-71B bistable was already tripped under SI-246, this completed the necessary 2 out of 3 logic for the reactor trip. A reenactment of the procedure steps, confirmed the theory as discussed above and proved the reactor trip was caused by the procedure deviation. To provide assurance that an adverse trend does not exist on common interactions of equipment, TVA will review past reactor trips at SQN for a similar occurrence of a common interaction between equipment that has caused a reactor trip.
328 | 3281988027 | 1988-06-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 98 | This LER is being revised to update the corrective actions and to more accurately reflect the minimum reactor coolant system temperature that occurred following the reactor trip described herein. On June 6, 1988, at approximately 1415 EDT with unit 2 at 98 percent power, a reactor trip occurred from loop 4 steam/feedwater flow mismatch coincident with low steam generator (S/G) level. Instrument personnel were performing Surveillance Instruction (SI)-618, "Engineered Safety Features Actuation System Block Tests," to verify output continuity of the solid state protection system (SSPS) slave relays for feedwater isolation, turbine trip, and main feedwater (MFW) pump trip (train B). When test switch S801 in the safeguards test cabinet was depressed and released, the loop 4 MFW flow control valve (2-FCV-3-103) closed and feedwater was lost to this loop. As a result, S/G No. 4 level dropped, and the reactor tripped. The blocking circuitry of the above mentioned ESF functions incorporates test switch S801 and is designed to energize slave relay K601 and K621 while simultaneously providing a current path through diodes to block the final equipment actuation. It was discovered, subsequent to this trip, that the diode was missing in the blocking circuit for loop 4 feedwater flow control solenoid valve 2-FSV-3-103B. When the slave relays K601 and K621 were energized via the S801 switch, no current path was provided to maintain 2-FSV-3-103B energized and consequently the associated feedwater flow control valve 2-FCV-3-103 closed. A review of maintenance records did not identify any work associated with the missing diode, and past testing on this circuitry was always performed in a mode where the feedwater control valve would have already been closed. It is believed that the diode was most likely missing when the cabinet was received on site. The diode was replaced under Work Request (WR) B231541. The performance requirements of SI-618 were also reviewed, and it was determined that the performance of SI-618 is no longer required; thus, SI-618 was canceled.
328 | 3281988028 | 1988-06-08 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Sequoyah 2 | P | WE | PO | 15 | This report details two reactor trips, one on June 8 and one on June 9, 1988. Both trips occurred immediately after startup during power ascension and were a result of steam generator (S/G) No. 2 Lo-Lo level. On the June 8, 1988 event, the plant was at approximately 15 percent power and was in the process of changing over to automatic speed control on the "A" main feedwater pump (MFP). The MFP speed controller was placed into automatic but S/G levels were dropping, and the MFP ran back to minimum speed. The speed controller was then placed back in manual to increase pump speed, and the S/G levels began to overfill. The main regulating valves were manually being closed to prevent overfill when a turbine trip/feedwater isolation occurred from a High-High level (75 percent) in S/G No. 4. The MFP was reset to reestablish main feedwater (MFW) flow, but before the pump could start, the reactor tripped on Lo-Lo level in S/G No. 2. <br /><br />On the June 9, 1988 event, the plant was at approximately 19.7 percent power and was experiencing gland sealing steam pressure fluctuations because of inoperable pressure control valves. Because of the sealing steam pressure increasing to the No. 7 heater drain tank, the low pressure heater strings began isolating on high level conditions. The cycling of the heater isolation valves caused feedwater flow and S/G level perturbations. The unit operator attempted to maintain control of the S/G levels but the reactor tripped on S/G No. 2 Lo-Lo level. <br /><br />The major causes of the events were insufficient attention to secondary side maintenance and insufficient guidelines for MFW control during startup. To help prevent recurrence, a work control center has been established to maintain a more comprehensive control of outstanding work orders and additional guidelines for controlling S/G level during startup have been placed in operating procedures.
328 | 3281988028 | 1988-06-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 20 | This report details two reactor trips, one on June 8 and one on June 9, 1988. Both trips occurred immediately after startup during power ascension and were a result of steam generator (S/G) No. 2 Lo-Lo level. On the June 8, 1988 event, the plant was at approximately 15 percent power and was in the process of changing over to automatic speed control on the "A" main feedwater pump (MFP). The MFP speed controller was placed into automatic but S/G levels were dropping, and the MFP ran back to minimum speed. The speed controller was then placed back in manual to increase pump speed, and the S/G levels began to overfill. The main regulating valves were manually being closed to prevent overfill when a turbine trip/feedwater isolation occurred from a High-High level (75 percent) in S/G No. 4. The MFP was reset to reestablish main feedwater (MFW) flow, but before the pump could start, the reactor tripped on Lo-Lo level in S/G No. 2. <br /><br />On the June 9, 1988 event, the plant was at approximately 19.7 percent power and was experiencing gland sealing steam pressure fluctuations because of inoperable pressure control valves. Because of the sealing steam pressure increasing to the No. 7 heater drain tank, the low pressure heater strings began isolating on high level conditions. The cycling of the heater isolation valves caused feedwater flow and S/G level perturbations. The unit operator attempted to maintain control of the S/G levels but the reactor tripped on S/G No. 2 Lo-Lo level. <br /><br />The major causes of the events were insufficient attention to secondary side maintenance and insufficient guidelines for MFW control during startup. To help prevent recurrence, a work control center has been established to maintain a more comprehensive control of outstanding work orders and additional guidelines for controlling S/G level during startup have been placed in operating procedures.
328 | 3281989005 | 1989-04-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 30 | This report details three unit 2 reactor trips which occurred on April 15, 16, and 19, 1989 following the completion of the unit 2 cycle 3 refueling outage. For all three events operator actions (performed in accordance with plant procedures) caused steam generator (SG) water levels to begin fluctuating and, subsequently, a reactor trip due to low-low water level in one of the SGs. For the April 15 event, unit 2 was at 30-percent reactor power and in the process of performing a main turbine overspeed test when the reactor tripped due to low-low water level in SG No. 4. For the April 16 event, Operations was in the process of performing a swapover from auxiliary feedwater (AFW) to main feedwater (MFW) supply to the SGs when the reactor tripped due to low-low water level in SG No. 1. For the April 19 event, during normal power escalation (18-percent reactor power), Operations was in the process of swapping over from the MFW bypass valves to the MFW main regulating valves when the reactor tripped due to low-low water level in SG No. 2. The April 15 cause was allowing SG level conditions to degrade (wide swings) to where recovery was extremely difficult, before terminating nonessential activities, discussing alternative methods of level control, and regaining control of plant conditions. The April 16 cause was an out-of-calibration condition on 2-PT-3-1 (MFW pump discharge pressure). The cause for the April 19 trip was operating loops 1 and 2 bypass valves in manual and not allowing sufficient time for the system to stabilize after each transient. Numerous corrective actions are planned to be taken as detailed in TVA's letter to the NRC dated May 5, 1989.
328 | 3281989005 | 1989-04-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 16 | This report details three unit 2 reactor trips which occurred on April 15, 16, and 19, 1989 following the completion of the unit 2 cycle 3 refueling outage. For all three events operator actions (performed in accordance with plant procedures) caused steam generator (SG) water levels to begin fluctuating and, subsequently, a reactor trip due to low-low water level in one of the SGs. For the April 15 event, unit 2 was at 30-percent reactor power and in the process of performing a main turbine overspeed test when the reactor tripped due to low-low water level in SG No. 4. For the April 16 event, Operations was in the process of performing a swapover from auxiliary feedwater (AFW) to main feedwater (MFW) supply to the SGs when the reactor tripped due to low-low water level in SG No. 1. For the April 19 event, during normal power escalation (18-percent reactor power), Operations was in the process of swapping over from the MFW bypass valves to the MFW main regulating valves when the reactor tripped due to low-low water level in SG No. 2. The April 15 cause was allowing SG level conditions to degrade (wide swings) to where recovery was extremely difficult, before terminating nonessential activities, discussing alternative methods of level control, and regaining control of plant conditions. The April 16 cause was an out-of-calibration condition on 2-PT-3-1 (MFW pump discharge pressure). The cause for the April 19 trip was operating loops 1 and 2 bypass valves in manual and not allowing sufficient time for the system to stabilize after each transient. Numerous corrective actions are planned to be taken as detailed in TVA's letter to the NRC dated May 5, 1989.
328 | 3281989005 | 1989-04-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 18 | This report details three unit 2 reactor trips which occurred on April 15, 16, and 19, 1989 following the completion of the unit 2 cycle 3 refueling outage. For all three events operator actions (performed in accordance with plant procedures) caused steam generator (SG) water levels to begin fluctuating and, subsequently, a reactor trip due to low-low water level in one of the SGs. For the April 15 event, unit 2 was at 30-percent reactor power and in the process of performing a main turbine overspeed test when the reactor tripped due to low-low water level in SG No. 4. For the April 16 event, Operations was in the process of performing a swapover from auxiliary feedwater (AFW) to main feedwater (MFW) supply to the SGs when the reactor tripped due to low-low water level in SG No. 1. For the April 19 event, during normal power escalation (18-percent reactor power), Operations was in the process of swapping over from the MFW bypass valves to the MFW main regulating valves when the reactor tripped due to low-low water level in SG No. 2. The April 15 cause was allowing SG level conditions to degrade (wide swings) to where recovery was extremely difficult, before terminating nonessential activities, discussing alternative methods of level control, and regaining control of plant conditions. The April 16 cause was an out-of-calibration condition on 2-PT-3-1 (MFW pump discharge pressure). The cause for the April 19 trip was operating loops 1 and 2 bypass valves in manual and not allowing sufficient time for the system to stabilize after each transient. Numerous corrective actions are planned to be taken as detailed in TVA's letter to the NRC dated May 5, 1989.
328 | 3281989008 | 1989-07-10 | QR3 | Reactivity Control Imbalance | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On July 10, 1989, at 1134 EDT, with Unit 2 in mode 1 (100 percent reactor power, approximately 2,235 psig, and Tavg at 578 degrees F), a reactor trip occurred. The trip occurred on high negative flux rate as noted on the first-out annunciator. Plant shutdown proceeded in an orderly manner consistent with procedures with no overcooling transient. A Posttrip Review Team was formed that conducted personnel interviews and developed recommendations for immediate corrective/investigative actions. These actions are detailed in the report and include troubleshooting on the rod control system as well as other deficiencies noted by the operators. <br /><br /> Personnel statements, strip chart recorders, troubleshooting work requests, previous trip reports, Westinghouse Owner's Group trip data base, and a trip modeling routine of the Watts Bar simulator were part of the resources utilized in the team's evaluation. In addition, plant management requested Westinghouse to assist in providing expertise in troubleshooting the rod control system. The team's conclusion is that the trip was a dropped rod event because of a spurious control signal fault. Neither the trip itself nor the team's recommended restart plan pose any compromise to the safe operation of the unit. <br /><br /> At 1857 with Unit 2 in Mode 3 (0 percent reactor power, 2235 psig, and 547 degrees F), a second reactor trip signal was generated by a source range spike approximately seven hours after the high flux trip. The source range channel had previously been declared inoperable because of noise on the channel but had not been bypassed in accordance with procedural requirements. The unit was stable and in Mode 3 with all rods on bottom when the signal occurred. A training letter was issued to all licensed personnel and shift technical advisors on July 21, 1989, addressing the failure to comply with Abnormal Operating Instruction 4, "Nuclear Instrumentation Malfunctions," when the N31 source range monitor was declared inoperable.
328 | 3281990008 | 1990-04-10 | QR8 | Spurious Reactor Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On April 10, 1990, with Unit 1 defueled and Unit 2 in Mode 1 at 100 percent power, a reactor trip occurred on Unit 2 at 0134 Eastern daylight time. The trip resulted from a general warning alarm on both trains of the solid state protection system (SSPS) and was caused by surveillance test steps being performed out of sequence during a monthly SSPS Train B functional test. When the out-of-sequence situation was discovered, the process used to evaluate the situation was not as specified in plant instructions. As a consequence when the omitted steps were performed out of sequence, a reactor trip occurred. Plant systems responded properly and the shutdown posed no danger to plant employees or the general public. The root cause of the event has been attributed to personnel error on the part of the test director and his supervisor in not following procedures addressing an out-of-sequence situation. As corrective action, appropriate disciplinary action has been given to both the test director and the supervisor. In addition, a site wide message has been distributed to provide lessons learned from the event and to emphasize the proper response to problems encountered during work.
328 | 3281990017 | 1990-11-23 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | Sequoyah 2 | P | WE | PO | 10 | On November 23, 1990, at 0431 Eastern standard time with Unit 2 in Mode 1, a reactor trip occurred as a result of low-pressurizer pressure. Two minutes earlier, the 6.9kV Unit Board 2D had deenergized, leading to the loss of the No. 4 reactor coolant pump (RCP). The loss of the unit board has been determined to have been caused by sticking contacts on the fast transfer 62-224 relay. When the RCP tripped, Operations' personnel immediately began to take action to reduce power. The shift operating supervisor began searching for a procedure covering the loss of an RCP. Operations' personnel did not assume their normally assigned task, and they did not communicate effectively with one another while performing the tasks they assumed. The lead reactor operator (LRO) manually began reducing power faster than the turbine was being run back because of a perceived urgency to shut the unit down; this resulted in a power mismatch, the average temperature and reference temperature and, subsequently, low-pressurizer pressure. The cause of the reactor trip was a misunderstanding of the consequences of losing one RCP below 35 percent power by the LRO, and subsequent poor communication and command and control by Operations' personnel.
328 | 3281991006 | 1991-11-07 | QL5 | Partial Closure of MSIVs | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On November 7, 1991, at 1403 Eastern standard time, the Unit 2 reactor tripped on low-low steam generator level in Loop 4 during a routine performance of a main steam isolation valve (MSIV) partial stroke test in accordance with Surveillance Requirement 4.7.1.5. During the performance of the test, the MSIV fully closed because of the failure of a limit switch to actuate, which reopens the valve upon reaching the 90 percent open position. The control room staff responded as prescribed by emergency procedures. They promptly diagnosed the plant conditions and took actions necessary to stabilize the unit in a safe condition. Safety systems performed as expected with minor anomalies that did not affect the operators' capability to respond to the event. The 90 percent limit switch was replaced, and the MSIV was retested successfully.
328 | 3281992001 | 1992-02-10 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 89 | On February 10, 1992, at 0528 Eastern standard time (EST), the Unit 2 reactor tripped as a result of a turbine trip because of low auto stop oil pressure. The unit was operating with no abnormal indications before the trip. The turbine trip occurred as a result of a malfunction with a solenoid valve in the auto stop oil portion of the turbine electro-hydraulic control system. The solenoid valve was replaced. On February 10, 1992, at 0949 EST, while in hot standby, the Unit 2 reactor trip breaker was inadvertently actuated during performance of a reactor trip breaker test. Coincident with this actuation, an unplanned engineered safety feature (ESF) feedwater isolation and auxiliary feedwater start occurred due to loss of electrical continuity of an installed jumper. The signal causing the reactor trip was cleared and the jumper was modified to use a gripper-type connector, and the test was successfully completed. On February 10, 1992, at 2110 EST, while in hot standby, during unit startup, the Unit 2 reactor was manually tripped due to a malfunction of the shutdown bank "D" demand counter. The demand counter was replaced and the unit was restarted. The control room staff responded as prescribed by emergency procedures. Safety systems performed as expected.
328 | 3281992008 | 1992-06-27 | QR8 | Spurious Reactor Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | This LER is being revised to provide root cause failure analysis information. On June 27, 1992, at approximately 1053 Eastern daylight time, with Unit 2 in power operation at approximately 100 percent, the reactor tripped because of coincident logic (two out of four channels) of over temperature, differential temperature reactor protection. The coincident logic was developed when a reactor coolant system resistance temperature device (RTD) on Loop 3 went into a failed condition while a Loop 1 RTD was out of service (the channel was in trip), because of spurious alarms and indications. Investigations identified a varying resistance condition existed in the electrical penetrations through the containment vessel associated with the two RTD channels. It was determined that this condition has been experienced with Sequoyah canister-type electrical penetrations attached to low-voltage cables in RTD applications. In the process of troubleshooting the Loop 3 RTD failure, the resistance condition cleared. The problem RTDs were removed from scan (no longer part of the protection scheme), and a current was passed through the associated penetration leads, correcting the varying resistance condition. The RTDs were verified to be operating properly and were returned to service. A root cause failure analysis determined that the most probable cause of varying resistance readings is substandard workmanship (poor crimping practices resulted in some conductors displaying poor electrical continuity).
328 | 3281992011 | 1992-08-21 | QR8 | Spurious Reactor Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | At approximately 1322 Eastern daylight time, on August 21, 1992, with Unit 2 at 100 percent power, a reactor trip and a safety injection occurred from a low-pressurizer pressure signal. After plant conditions were stabilized, the safety injection was terminated, and the emergency core cooling-system pumps were returned to standby alignment. The apparent cause of the trip was determined to be from an inadvertent radio transmission in the incore instrument room seal table area near the pressurizer pressure transmitters. The procedure governing the use of radio equipment will be revised to better preclude radio transmissions inside containment during unit operation. In addition, alternate means of communications inside containment will be evaluated.
328 | 3271992027 | 1992-12-31 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Sequoyah 2 | P | WE | PO | 100 | On December 31, 1992, at approximately 2148 Eastern standard time (EST), with Units 1 and 2 in power operation at approximately 100 percent, both units received a reactor trip signal because of reactor coolant pump bus undervoltage. The reactor trips were followed by turbine trips. Undervoltage on the 6.9-kV shutdown boards initiated board load stripping, diesel generator (D/G) starts, and D/Gs tying onto their respective shutdown board. Electrical loads were appropriately sequenced back to the boards. Main feedwater isolated and auxiliary feedwater pumps started. Loss of power to a radiation monitor resulted in an auxiliary building isolation. With limited staffing in the Unit 2 main control room, recovery evolutions for Unit 2 resulted in isolation of centrifugal charging pump suction and removal of both centrifugal charging pumps from service. Unit 2 entered LCO 3.0.3 for approximately one minute until a suction flow path was reestablished. The cause of the event was an internal fault in a switchyard power circuit breaker resulting from inappropriate testing methodology. Corrective actions include strengthening of switchyard controls and increasing minimum Operations control room staffing.
328 | 3281993001 | 1993-03-01 | K1 | Steam Line Break Outside Containment | [9 empty] | X | [26 empty] | X | [8 empty] | Sequoyah 2 | P | WE | PO | 100 | On March 1, 1993, Unit 2 experienced a steam leak on the non-nuclear side of the plant. The No. 2 extraction line to the B2 feedwater heater ruptured, causing a 3- by 6-inch hole in the line. Steam escaping from the ruptured pipe flowed into the nearby main generator voltage regulator cubicle, resulting in regulator malfunction and voltage increasing to approximately 27 kilovolts (kV) (normal operating voltage is approximately 24 kV). As a result of the high voltage on the system and the inability to reduce the voltage, the reactor was manually tripped. The plant response during and after the manual reactor trip was consistent with responses described in the Final Safety Analysis Report. The root cause of this event was a programmatic failure of the erosion/corrosion (E/C) program resulting from insufficient management oversight and review of the program. Corrective actions include repair of affected piping and components; E/C program review and Engineering evaluation of other piping susceptible to erosion, including inspections and repairs/replacements; evaluation of impact of over-voltage condition on plant equipment; and review of other site technical programs.
328 | 3281993006 | 1993-12-03 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On December 3, 1993, at 1055 Eastern standard time, with Unit 2 operating at approximately 100 percent rated thermal power, Unit 2 experienced a turbine trip and subsequent reactor trip. Operations personnel observed erratic indications associated with the generator excitation system. Subsequently, a generator stator cooling failure alarm actuated. This circuit starts a 45-second time delay relay that results in a turbine/generator trip. Based on these conditions, the shift operations supervisor decided to manually trip the reactor. However, before manually tripping the reactor, the generator stator cooling failure relay actuated causing the turbine/generator trip and subsequent reactor trip. The root cause of the event was the overexcitation of the generator. The overexcitation was determined to have been caused by multiple grounds in the generator exciter. The Unit 2 exciter has been replaced.
328 | 3281995001 | 1995-01-05 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On January 5, 1995, at 0015 Eastern standard time, with Unit 2 operating at 100 percent power, the turbine tripped followed by a reactor trip as a result of operation of the gas-operated relay on the main bank transformer. Immediately before the trip, the 'Transformer 2 Cooling System Abnormal' alarm annunciated. During the response to the alarm by the control room operator (CRO), it was noted that one of the lights for the cooler groups on the C-phase main bank transformer was not lit, indicating that a cooler group was out of service. When the CRO attempted to remove the lens cover of the light, the lamp socket rotated and the control power for the main bank transformer cooler group shorted. This resulted in the cycling of the pumps in both cooler groups, causing pressure surges of the transformer cooling oil which actuated the gas-operated relay. The gas relay tripped the main transformer, resulting in subsequent turbine and reactor trips. The cause of this event was a failure to design the light socket with an adequate barrier to prevent the electrical short from occurring. The Unit 2 and common control room panel lamp sockets were inspected. Eight deficiencies were identified and corrected. A preventive maintenance instruction will be developed to periodically check the tightness of control room light sockets. The Unit 1 control room light sockets will be checked during the next refueling outage.
328 | 3281995002 | 1995-04-28 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 99 | On April 28, 1995, at 2031 Eastern standard time with Unit 2 operating at 99 percent power, the turbine tripped followed by a reactor trip as a result of operation of the main generator neutral overvoltage relay. The immediate cause of this event was attributed to a bus duct gasket that came loose and caused a ground. The ground was on the electrical bus leading from the main generator to the 'C' phase main transformer. The gasket provided a path for electrical leakage to ground that was detected by the neutral overvoltage relays. The actuation of the relays tripped the generator resulting in subsequent turbine and reactor trips. The relays actuated, as designed, to prevent damage to other components. The cause of this event is ineffective/inadequate corrective action of a previous similar event. As a result of a reactor trip in 1984, a preventive maintenance (PM) instruction was revised to periodically inspect the gaskets and bus alignments at the transformer doghouses and rework or replace as required. The PM lacked sufficient detail to ensure that the proper inspection and repairs were accomplished. The PM has been revised to provide sufficient detail to ensure proper inspection of the gasket. The Unit 1 transformers will be inspected during the next outage.
328 | 3281995003 | 1995-05-31 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 99 | On May 31, 1995, at 1809 Eastern standard time, the turbine tripped followed by a reactor trip as a result of an actuation of the main generator stator cooling water failure circuit. Prior to the trip, a temperature excursion on the stator cooling system was induced by the chlorination of the raw cooling water for the stator cooling system. Indications show that the stator cooling water temperature did not reach the setpoint associated with the trip circuit. The chlorination activity had been in progress for several weeks and was considered a routine activity with no threat to unit operation. not provide adequate guidance and control. The event occurred as a result of the temperature excursion caused by the performance of the chlorination activity and the early operation of the temperature switch because of the incorrect setpoint on the switch. The root cause for the premature initiation of the stator cooling failure circuit was the incorrect assembly and calibration of the outlet temperature switch. The temperature switch was replaced and installed correctly. An alternative approach to chlorination will be developed, and the appropriate procedures will be revised to eliminate the possibility of impacting plant operation.
328 | 3281995007 | 1995-12-21 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On December 21, 1995, at approximately 0629 Eastern standard time (EST), with Unit 2 in power operation at approximately 100 percent, a manual reactor trip was initiated because of a loss of condenser vacuum. At approximately 0626 EST, protection relays operated, opening breakers in the 161-kilovolt switchyard, clearing a ground fault on the Chickamauga 2 line in Power Circuit Breaker (PCB) 974. The ground fault duration was approximately five cycles. The electrical perturbation was sensed by protection circuitry on the synchronous motors of the condenser circulating water (CCW) pumps, resulting in the three Unit 2 pumps tripping and initiating the loss of condenser vacuum. When condenser pressure reached established limits, operators took manual control and tripped the unit. Main control room operators entered the appropriate procedures and stabilized the unit in hot standby (Mode 3). The reactor protection systems responded to the trip as expected; no anomalies occurred. Main feedwater isolated, and auxiliary feedwater pumps started as designed. The root cause of the ground fault was the failure of the C phase of PCB 974. A preliminary evaluation indicates that a potential latent defect was present in the ceramic insulator on the load side of the center head assembly. The failed PCB has been spared out and does not affect unit operation. A review of industry experience indicated that the failure was unique. Additionally, a study is in progress to develop economical solutions to alleviate the sensitivity of the CCW pump motor protection scheme without jeopardizing equipment or personnel safety.
328 | 3281996005 | 1996-10-11 | QR6 | Manual Reactor Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 47 | On October 11, 1996, at 0827 Eastern daylight time, with Unit 2 in power operation at approximately 47 percent, manually tripped as a result of an unexpected loss of load. controlled unit shutdown. The shutdown was initiated because of low No. 1 seal return flow on the No. 4 reactor coolant pump. The unit shutdown was progressing as expected up through removing the 'B' feedwater pump from service. After the pump was removed from service, Operations personnel determined that a turbine runback was in progress and that the auxiliary feedwater system had started. In response to the unexpected runback (loss-of-load) condition, the operator at the controls tripped the reactor. Subsequent to the reactor trip, a feedwater isolation occurred and Operations personnel observed the loop No. 4 feedwater isolation valve lose control room indication. Post trip evaluations determined that malfunction of the turbine impulse pressure switches resulted in the turbine runback condition. The loop No. 4 feedwater isolation valve failed to travel to the closed position because the valve's position retention brake did not release. The cause for the failure of the pressure switches resulted in the turbine runback condition. The loop No. 4 feedwater isolation valve failed to travel to the closed position because the valve's position retention brake was corrosion product buildup as a result of water intrusion. The pressure switches and the feedwater isolation valve motor and brake assembly were replaced, tested and returned to service. The root cause of the event was inadequate field inspection and corrective action for the water intrusion events. Lessons learned from the event were communicated to appropriate site personnel.
328 | 3281996006 | 1996-12-06 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On December 6, 1996, at 0033 Eastern standard time, with Unit 2 in power operation at approximately 100 percent, the reactor automatically tripped because of the loss of power to Start Bus 2A. When the 2A start bus lost power, a reactor trip was initiated as a result of a bus undervoltage condition for Reactor Coolant Pumps 1 and 3. Start Bus 2A lost power because the alternate source feeder breaker opened without a legitimate trip signal. The 2A start bus was being supplied by the alternate source, common station service transformer (CSST) B. The normal feeder (CSST A and the 2A start bus normal feeder breaker) was out of service for maintenance activities. At the time of the trip, maintenance personnel had opened the normal feeder breaker compartment to continue maintenance work in the compartment when the alternate feeder breaker opened. Investigation into the event did not identify any equipment failure or inappropriate personnel action. A refurbished breaker was installed in the 2A start bus normal feeder breaker compartment, the breaker was tested, found acceptable, and the bus was returned to service.
328 | 3281998001 | 1998-08-27 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On August 27, 1998, at 1357 Eastern Day light time, with Unit 2 in power operation at approximately 100 percent, a turbine trip occurred followed by a reactor trip. The event resulted from the initiation of a generator lockout (generator electrical trip) with a subsequent turbine trip initiated by failure of a sudden pressure relay on the 'B' phase main transformer. A review of the condition determined that the transformer did not experience a fault. The reactor protection systems, including feedwater isolation and auxiliary feedwater start, responded to the trip as expected; no anomalies occurred. Operators responded to the trip as prescribed by procedures and stabilized the reactor in the hot standby condition. Subsequent to the event, examination of the sudden pressure relay, Qualitrol Corporation Model No. 900-003-01, identified one rocker arm pin had worn to the degree that proper operation of the device was prevented. The remaining Qualitrol relays on the Units 1 and 2 plant transformers inservice were inspected and replaced, where necessary.
328 | 3281998002 | 1998-10-16 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On October 15, 1998, at 0501 Eastern Daylight time (EDT), a turbine trip occurred followed by a reactor trip. The event resulted from a generator lockout caused by a failure of a sudden pressure relay on the 'B' phase main transformer. Operators responded to the trip as prescribed by procedures and stabilized the reactor in a safe condition. On October 15, 1998, at 2309 EDT, during restart of the unit, Operators entered Limiting Condition for Operation (LCO) 3.0.3 when 4 rod position indicators in Control Bank C were more than 12 steps out from their respective demand position indicators. Operators withdrew the control rods correcting the indication problem. TVA believes that the sudden pressure relay failed because one of the control bellows had cracked and was leaking relay working fluid (Silicon). TVA considers that the crack in the control bellows was the result of vibration induced fatigue. The trip function of the sudden pressure relays was disabled from the main transformers and the unit station service transformers. A modification is being evaluated to physically isolate the relays from the vibration of the transformers and adding a two out of two logic for actuation of the sudden pressure relay trip function.
328 | 3282000001 | 2000-01-18 | QP2 | Partial Loss of Feedwater Flow | [10 empty] | X | [28 empty] | X | [5 empty] | Sequoyah 2 | P | WE | PO | 100 | This report is being revised to update the root cause analysis and provide additional corrective actions. On January 18, 2000, at approximately 1051 Eastern standard time (EST), an automatic reactor trip occurred. The reactor trip was initiated as a result of a low-low steam generator (SG) level. A momentary loss of power to Vital Instrument Power Board 2-IV occurred when plant personnel were performing a modification to the plant that involved lifting a lead on a synchronization signal cable for the static switch on Vital Inverter 2-IV. Lifting of the wire broke the ground reference in the static switch control circuit and provided an undervoltage condition to be sensed by the static switch control board. When the wire was lifted, a voltage spike developed across the relay coil energizing the relay and allowed a dead bus transfer to occur. An inadvertent safety injection (SI) actuation occurred on A-train. Investigation of the SI actuation indicates that this signal was caused by low SG pressure signals on Channels IV and II for SG No. 4. The Channel IV signal was attributed to the loss of power from Vital Instrument Power Board 2-IV and the Channel II signal was attributed to a noisy SG pressure transmitter. The control board to the static switch was replaced. This report includes information required by Technical Specification Limiting Condition for Operation 3.5.2 Action b for an emergency core cooling system injection.
328 | 3282000004 | 2000-11-17 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 53 | On November 17, 2000, at 0842 Eastern standard time (EST), Unit 2 experienced an automatic reactor trip. The reactor trip was initiated by a turbine trip, which was caused by the actuation of the sudden pressure relays on the `C' phase main transformer. The main control room operators took appropriate actions to stabilize the reactor in hot standby (Mode 3). An inspection of the main transformer revealed that a fault had occurred in the transformer. The electrical fault in the transformer was caused by a failure of a 24-kV bushing. A spare main transformer was placed in service for the faulted transformer, and the unit was returned to service.
328 | 3282002003 | 2002-05-31 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Sequoyah 2 | P | WE | PO | 71 | On May 31, 2002, at 0116 Eastern Daylight Time the Unit 2 turbine tripped followed by a reactor trip as a result of an actuation of the main generator stator cooling water failure circuit. Prior to the trip, Operations personnel observed increased temperature on the generator stator cooling water system. Indications show that the generator stator cooling water temperature reached the setpoint then actuated as required. The main control room operators took appropriate actions to stabilize the reactor in hot standby (Mode 3). The generator stator cooling water high temperature was the result of a raw cooling water isolation valve failure causing low flow to the stator cooling water system heat exchanger. The raw cooling water valve was replaced.
328 | 3282002004 | 2002-12-26 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On December 26, 2002, at 1620 Eastern Standard Time, the No. 3 reactor coolant pump (RCP) tripped because a neutral over-current condition on the No. 3 RCP motor. The loss of the No. 3 RCP resulted in a reactor coolant system low flow and subsequent automatic reactor trip. A feedwater isolation and auxiliary feedwater start occurred, as designed. Control room operators responded to the event in accordance with plant procedures. They promptly diagnosed the plant condition, took the actions necessary to stabilize the unit, and maintained the unit in hot standby, Mode 3. The cause of the event was a neutral over-current condition on the No. 3 RCP motor. The motor was replaced and the unit was returned to service.
328 | 3282003004 | 2003-03-10 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 88 | On March 10, 2003, at 0918 Eastern standard time (EST), Operations personnel manually tripped the reactor because of a low condensate pressure and the loss of the 2A main feedwater pump (MFP). The event began with the loss of the 2B hotwell pump (HWP) causing the condensate pressure to drop. Subsequently the No. 7 heater drain tank (HDT) pumps tripped off because of a low HDT level resulting from the HDT outlet valve being secured at approximately 60 percent open for maintenance. The 2A MFP and the 2A and 2C HWPs tripped followed by Operations personnel initiating a manual reactor trip. Control room operators responded to the event in accordance with plant procedures. They promptly diagnosed the plant condition, took the actions necessary to stabilize the unit, and maintained the unit in hot standby, Mode 3. The cause of this event was an inappropriate prioritization of the work order to repair the No. 7 HDT outlet valve coincident with the electrical failure of the 2B HWP motor resulting in low and unstable condensate system pressure. The 2B HWP motor was replaced and returned to service. The No. 7 HDT outlet valve was repaired and returned to service. Following the reactor trip, dose equivalent Iodine (DEI) was determined to have exceeded the technical specification (TS) limits. TS require sampling of the reactor coolant system (RCS) for DEI every 4 hours until the activity is within limits. During a review of the TS required actions, it was determined that one of the samples was not taken within the required frequency. The RCS was subsequently sampled and the DEI was determined to be within limits.
328 | 3282003005 | 2003-04-12 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 88 | On April 12, 2003, at 2221 Eastern daylight time, Unit 2 Operations personnel opened vibration power drawer No. 1, to reset a trip light alarm on the No. 7 turbine bearing. Operations personnel verified that the vibration trip cutout switch was in the cutout position. After resetting the trip light, Operations personnel proceeded to place the drawer back into its normal position. Upon sliding the drawer back into the panel, a spurious turbine vibration trip signal occurred, with a duration of less than one second, initiating an automatic turbine trip and subsequent reactor trip. The control room operators responded to the event in accordance with plant procedures. They promptly diagnosed the plant condition, took the actions necessary to stabilize the unit, and maintained the unit in hot standby, Mode 3. The root cause was determined to be a ground on the Unit 2 main turbine vibration drawer No. 1 causing the main turbine vibration trip relay to actuate. An investigation determined that the drawer wiring had been pinched and several wires had exposed conductors. When the drawer was inserted, it is suspected that one of the exposed conductors shorted against the cabinet casing or shorted with another exposed conductor that caused the relay coil actuation. The exposed conductors were repaired. A temporary modification was implemented on Unit 2 to prevent the main turbine vibration trip relay from actuating.
328 | 3282005001 | 2005-02-23 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Sequoyah 2 | P | WE | PO | 100 | On February 23, 2005, at approximately 2030 Eastern standard time (EST), Maintenance personnel were performing pre-refueling outage maintenance activities on a 125-Volt (V) direct current (dc) vital battery board molded case circuit breaker. After removing the breaker from the panel, Maintenance personnel began installation of a breaker board panel cover to its normal position. While aligning the cover, it shifted downwards, opening two adjacent breakers. One of the adjacent breakers controlled a fuse column providing power to all four main feedwater regulation valves, which subsequently closed on loss of control power. A reactor trip was initiated by the reactor protection system on low-low steam generator level. The control room operators responded to the event in accordance with plant procedures. They diagnosed the plant condition, took actions to stabilize the unit, and maintained the unit in Hot Standby, Mode 3. The root cause of the inadvertent closure of the trip sensitive breakers was determined to be insensitivity to trip risks. The maintenance procedure has been revised to provide positive position control of panels when working on molded case breakers. Moreover, SQN has implemented a procedure that provides additional processes for review and control of site work activities concerning potential nuclear safety and generation risk above and beyond that specified in the TVA nuclear online and outage work management procedures.
328 | 3282006001 | 2006-03-22 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On March 22, 2006, at 1624 Eastern standard time with Unit 2 operating at 100 percent power, the turbine tripped followed by a reactor trip as a result of operation of the main generator neutral overvoltage relay. The immediate cause of this event was attributed to an isolated phase bus duct gasket that came loose and caused a ground. The ground was on the electrical bus leading from the main generator to the 'C' phase main transformer. The gasket provided a path for electrical leakage to ground that was detected by the neutral overvoltage relays. The ground resulted in actuation of the main generator neutral overvoltage relay. The actuation of the relay stripped the main transformer resulting in subsequent turbine and reactor trips. The relays actuated, as designed, to prevent damage to other components. The cause of this event is ineffective corrective action of a previous similar event. The previous corrective actions from the 1995 event focused on methods to ensure retention of the gasket and did not focus on long-term equipment reliability. The Unit 2 bus duct gasket was reinstalled with additional tie-wraps to support the gasket and the bus was returned to service. The bus duct has been modified to no longer require the gasket on the Unit 1 bus ducts. The Unit 2 bus duct will be modified to remove the gasket during the upcoming refueling outage.
328 | 3282007001 | 2007-01-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On January 23, 2007, at 1244 Eastern standard time (EST) with Unit 2 operating at 100 percent power, an automatic reactor trip occurred because of a low-low steam generator level on Loop 2. The immediate cause was closure of the Loop 2 main feedwater regulating valve as a result of a failed control air line. At approximately 1030 EST, it was identified that the air line tubing to the Loop 2 main feed regulating valve appeared to be damaged and leaking. Operations discussed the condition with plant management and agreed to pursue dogging the valve open so maintenance could be performed online. During the evolution to open and place the bypass regulating valve in automatic, a swing in control signal was seen and feedwater flow decreased rapidly. The SRO directed that a manual reactor trip be initiated. The automatic trip occurred before the manual trip was initiated. Following the reactor trip, the plant systems responded as designed. The unit entered Mode 3 and an event investigation was initiated. The feedwater regulating valve's control air line was damaged as a result of improper routing of field tubing during a recent outage modification. The routing of the control air line did not sufficiently account for movement of the valve due to thermal growth.
328 | 3282007002 | 2007-03-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On March 13, 2007, at 1527 Eastern standard time with Unit 2 operating at 100 percent power, a manual reactor trip was initiated because of a partial loss of main feedwater flow to the steam generators. The immediate cause was failure of the 2A main feedwater pump control system. During normal power operations, Operations noticed that the steam generator levels on all four steam generators had begun to decrease. The 2A main feedwater pump speed controller output was noted to be decreasing. The controller was placed to manual but the controller failed to respond to the operator's attempt to increase output. The steam generator Loop 2 low-level alarm annunciated and the reactor was manually tripped. Following the reactor trip, the plant systems responded as designed. The unit entered Mode 3 and an event investigation was initiated. Troubleshooting determined the problem to be within the 2A main feedwater speed indicating controller. The root cause of the event was determined to be a faulty local/remote switch which is internal to the speed indicating controller.
328 | 3282008001 | 2008-11-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On November 3, 2008, at 2322 Eastern standard time with Unit 2 operating at 100 percent power, a manual reactor trip was initiated because of a partial loss of main feedwater flow to the steam generator Loop 4. The immediate cause was failure of the Loop 4 feedwater regulating valve controller. During normal power operations, operators received a steam generator level high-low deviation annunciation. An operator identified a decreasing level on the steam generator Loop 4. The controller was placed to manual, but the controller failed to respond to the operator’s attempt to increase level. Operators took action to manually trip the reactor. Following the reactor trip, an RCS leak occurred. The leak was from an instrumentation sensing line to the pressurizer. The plant systems responded as designed. The K1 Relay to the Unit 2 Loop 4 main feedwater regulating valve flow indicating controller has been determined as the most probable root cause of this event. The relay failure is attributed to a failing contact connection, which resulted in a slow closing drift of the main feedwater regulating valve.
328 | 3272009003 | 2009-03-26 | QR7 | Other Reactor Trip (Valid RPS Trip) | [10 empty] | X |  |  | X | [26 empty] | X |  |  |  | X | Sequoyah 2 | P | WE | PO | 96 | The enclosed LER is being revised to indicate a condition where SQN failed to perform a technical specification (TS) action within the required timeframe. The enclosed LER is being revised to indicate that the condition resulted in an unplanned scram with complications. On March 26, 2009 at 0452 Eastern daylight time (EDT), Sequoyah Units 1 and 2 received an automatic reactor trip on reactor coolant pump (RCP) buses undervoltage. A loss of Common Station Service Transformer (CSST) C caused a loss of power to two unit boards on each unit that feed RCPs. CSST B continued to supply offsite power to the Train B safety-related shutdown boards for both units. The emergency diesel generators started and powered the Train A safety-related shutdown boards for both units. Both units were stabilized in hot standby (Mode 3). CSST C was isolated from CSST D and reenergized from the switchyard PCBs. Offsite power was then restored to the Train A safety-related shutdown boards for both units. The cause of the bus fault was determined to be degraded bus bar insulation and water intrusion into the CSST D secondary bus duct: Corrective actions include replacement of a section of the CSST D bus and inspection of the other CSSTs and cooling tower transformers (CTT). Repairs to degraded insulation of CSST C, CTT A, and CTT B were made as a result of the inspections. After the dual unit trip, with one offsite power source inoperable, the remaining offsite power source was not demonstrated operable within one hour as specified by TS 3.8.1.1 Action a. The TS action was subsequently completed.
328 | 3282009001 | 2009-05-27 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On May 27, 2009, at 1904 Eastern daylight time, SQN Unit 2 reactor automatically tripped following a power range negative rate trip. An investigation revealed that one out of five rod control power cabinets had lost power as a result of lightning strikes onsite that induced a voltage on the electrical cables between the power cabinets and the reactor head. The Unit 2 power supplies in the rod control system contain a circuit that will sense a high voltage condition and will trip the power supply. When the high voltage condition occurred, the control rods (10) supplied from the affected cabinet inserted into the core causing the negative rate trip. The plant safety systems responded as designed. The root cause of this event has been determined to be the power supplies are susceptible to lightning induced overvoltage conditions because of a lack of a filter in the overvoltage protection circuit for the control rod drive system. The corrective actions include replacement of the existing overvoltage circuits with those less susceptible to voltage induced occurrences. An evaluation of lightning protection issues for the site is being conducted.
328 | 3282009002 | 2009-11-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 30 | On November 26, 2009, at 0242 Eastern standard time (EST), SQN Unit 2 reactor was manually tripped following indication of degrading main feedwater pump turbine (MFPT) condenser vacuum. At approximately 0239 EST, the shift manager was notified of a degrading vacuum in the 2A MFPT condenser. Operations manually tripped the reactor and entered the applicable emergency procedures. The cause of this event was determined to be the closure of two isolation valves for a level switch on the gland seal steam system that trapped water in the level switch and indicated a high gland steam level. With the level switch actuated, two associated gland seal steam drain valves failed open and allowed gland seal steam to be directly routed to the drain lines of the MFPT condenser. This allowed steam to be injected into the drain flow from the 2A MFPT and created a restricted flow condition because of the steam bound environment and subsequently challenged the drain capability of the 2A MFPT condenser. The root cause of this event was determined to be a deficiency in enforcing proper standards for status control during work development and execution. Corrective actions include revising the work control process procedure to strengthen status control requirements and additional training regarding status control for selected plant personnel.
328 | 3282012001 | 2012-08-16 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On August 16, 2012, at approximately 1926 Daylight Savings Time, Sequoyah Nuclear Plant (SQN) Unit 2 automatically tripped on a single loop loss of flow following reactor coolant pump (RCP) 2-4 trip. RCP 2-4 tripped as a result of the 250 volts direct current RCP control circuit energizing the trip coil for RCP 2-4 without a valid signal, resulting in a Unit 2 trip. No testing or surveillance was in progress at the time of the event. Unit 2 was stabilized in hot standby following the automatic reactor trip. The cause of the trip was determined to be the inadvertent operation of a GR-5 ground fault relay, designated as device 500. Failure of the GR-5 relay was caused by the failure of the metal oxide varistor, which is an internal component to the solid state GR-5 relay. The root cause for the failure of the metal oxide varistor was determined to be inadequate preventative maintenance instructions and implementation frequency on GR-5 relays in critical systems. The corrective actions include revising preventative maintenance procedures to address replacement of ABB/ITE relays for critical components. An additional action will replace Unit 1 and Unit 2 ABB/ITE relays, for critical components, that have been in service greater than five refueling cycles based on Operations review of critical components that are directly related to causing a plant trip or Limiting Condition for Operation entry for 8 hours or less. There were no actual safety consequences impacting plant or public safety as a result of this event.
328 | 3282013001 | 2013-02-24 | QR6 | Manual Reactor Trip | [10 empty] | X | [29 empty] | X | X |  |  |  | Sequoyah 2 | P | WE | PO | 19 | On February 24, 2013, at 1205 Eastern Standard Time, Operations personnel manually tripped the Sequoyah Unit 2 reactor from approximately 19 percent rated thermal power on imminent loss of condenser hotwell level. Specifically, Operations personnel entered an abnormal operating procedure based on indications of rising condenser pressure. When Operations personnel determined the hotwell level in "B" Condenser could not be maintained, a manual reactor trip was initiated. Prior to the manual reactor trip, the Unit 2 reactor had been at approximately 24 percent power with the main turbine offline for maintenance activities. All control rods fully inserted as required. The auxiliary feedwater system automatically initiated and provided feed water to the steam generators. No complications were experienced during or after the reactor trip. The loss of condenser vacuum indication was caused by the pressure indicator's drain line breaking under cyclic fatigue. It is suspected that initial damage to the drain line was caused during the previous refueling outage. The drain line was replaced prior to restart of the unit. Corrective actions will be performed to provide shielding of the condenser pressure transmitters' drain line, and the surrounding area will be marked as a unit trip hazard. Employees are to receive a briefing regarding the requirement for providing adequate spacing between stored items and sensitive equipment.
328 | 3282015001 | 2015-03-02 | QR5 | Turbine Trip | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On March 2, 2015, at 0645 Eastern Standard Time, Sequoyah Nuclear Plant (SQN) Unit 2 reactor automatically tripped following a turbine trip due to actuation of the main generator 287G differential relay. The relay actuation was a result of a failure of the main generator C-phase neutral current transformer (CT) cable. All safety related equipment operated as designed, all control rods fully inserted as required, and auxiliary feedwater automatically initiated from the feedwater isolation signal as expected. A broken splice connection was identified between the 287G differential relay and the C-phase CT. This main generator C-phase neutral CT cable failed open due to a combination of corrosion and periodic physical manipulation. The cause of this event was a lack of inspections in the preventive maintenance (PM) procedure to identify potential failure mechanisms. Prior to restart, both Unit 2 C-phase neutral CTs and one B-phase neutral CT along with all associated neutral side field cables were replaced. Corrective actions to prevent recurrence include replacement of all Unit 1 and Unit 2 main generator CT bolted connections with solder filled splices, covered in Raychem to prevent water intrusion. The condition described in this LER did not have an impact to SQN Unit 1.
328 | 3282019002 | 2019-12-12 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Sequoyah 2 | P | WE | PO | 100 | On December 12, 2019, at 0433 Eastern Standard Time (EST), Sequoyah Nuclear Plant Unit 2 was manually tripped as a result of a secondary system level control valve positioner failure. The failure of the valve led to reduced secondary system Heater Drain Tank flow and a unit down power. During the down power, manual reactor trip criteria was reached. All safety-related equipment operated as designed, all controls rods fully inserted as required, and the Auxiliary Feedwater system automatically initiated as expected. <br /><br /> The failed positioner was replaced with a newer model. Investigation revealed that a fine adjust screw had loosened, preventing the valve positioner from correctly responding to control signals. An extent-of-condition was performed to identify other susceptible components, and actions have been taken to replace a necessary component with a newer model.
331 | 3311988008 | 1988-07-24 | QR5 | Turbine Trip | [45 empty] | Duane Arnold | B | GE | PO | 81 | On July 24, 1988 at 1608 hours the reactor was operating at 81% power when a reactor scram occurred when a high vibration indication was received for the number ten Journal bearing of the Main Turbine- Generator. Per design the turbine tripped, initiating a rapid closure of the Main Steam Turbine Stop Valves. Stop valve closure indication initiated the reactor scram. All safety systems responded properly and reactor pressure was controlled via Main Steam Bypass Valves to the condenser. Investigation of the cause of the high vibration condition led to the determination that an internal failure had occurred within the vibration detector for the number ten journal bearing. This enabled a spurious signal of a high vibration condition to be generated of sufficient magnitude to exceed the turbine trip setpoint. The vibration transmitter was replaced and the plant successfully returned to power operation on July 27, 1988.
331 | 3311989001 | 1989-01-18 | QR6 | Manual Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 100 | On January 18, 1989 at 0337 hours an Electro Hydraulic Control (EHC) Reservoir low level alarm was received in the control room. The Auxiliary Operator was sent to investigate the low level alarm. The EHC Reservoir was low and there was a leak on a high pressure supply line to the Turbine Control Valve #3 (CV-3) which could not be isolated. Control Room personnel began lowering reactor power by reducing recirculation flow and inserting control rods. With reactor power at 41% and EHC Reservoir level decreasing, the reactor was manually scrammed at 0352 hours. <br /><br /> There were no component or system failures other than the leak in the EHC piping. The leak was in a flexible hose installed during the cycle 9/10 refueling outage. This hose was removed and examined for cracks using a liquid penetrant inspection. A 112" circumferential crack in the tubing was identified. A representative of the hose manufacturer was consulted and all of the flexible high pressure EHC tubing that was installed during the cycle 9/10 refueling was replaced.
331 | 3311989003 | 1989-02-02 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Duane Arnold | B | GE | PO | 100 | On February 2, 1989, with the plant operating at 100% power, during the preliminary steps of a hydrogen injection Special Test Procedure, a Reactor Scram occurred. The cause of this scram was high main steam line radiation levels caused by a larger than expected quantity of hydrogen being injected into the feedwater system. The root cause of this event was failure to reverify test rig construction following replacement of its fittings. This resulted in incorrect placement of the flow orifices going unnoticed. <br /><br /> Long term corrective action to prevent recurrence of this type of event will be a revision of the Special Test Administrative Control Procedure. The revision will include the requirement for independent verification of test rigs and special valve lineups which will be used during special tests. This requirement will be applied to special tests, except those which have no potential for affecting safety-related systems or structures. <br /><br /> The reactor scram occurred as designed upon receipt of multiple main steam line high radiation signals. All rods inserted to the full-in position. <br /><br /> Throughout the event, vessel level and pressure were maintained within safe operating limits via proper response of feedwater level control and the safety relief valves as well as appropriate response by Operations personnel. This event had no effect on the safe operation of the plant.
331 | 3311989008 | 1989-03-05 | QL5 | Partial Closure of MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Duane Arnold | B | GE | PO | 100 | On March 5, 1989 with the reactor operating at 100% power, calibration of the Main Steam Line Radiation Monitors was in progress when the 'B' Outboard Main Steam Line Isolation Valve (MSIV) unexpectedly closed due to a failed DC solenoid. The isolation of the B' Main Steam Line (MSL) resulted in flow in the remaining three main steam lines exceeding the high flow limit of 140%. In accordance with design this resulted in isolation of all Main Steam Lines. When MSIV's reached the less than 90% open position, an automatic reactor scram occurred. Reactor pressure peaked at approximately 1126 PSIG and was controlled with the use of four pressure relief valves. All safety systems performed as expected and operator response was appropriate.<br /><br /> The cause of the failed solenoid coil was moisture intrusion. The source for the moisture was condensation from a nearby minor steam leak. The solenoid enclosure was susceptible to moisture intrusion as a result of inadequate torquing of a threaded cover for the enclosure during previous maintenance activities in December 1988. The lack of proper torquing was due to an inadequate maintenance repair procedure. The failed solenoid was replaced. Other MSIV fast closure solenoids were inspected for moisture intrusion and the enclosures were properly torqued. The repair procedure has been revised.
331 | 3311989009 | 1989-06-12 | QR8 | Spurious Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 100 | On June 12, 1989, while at full power a Reactor Protection System (RPS) actuation and reactor scram occurred. Two ITT Barton Model 764 flow transmitters which help to determine the Average Power Range Monitor upscale setpoint were affected by hand-held radio frequency interference. Primary Containment Isolation System Groups II through V isolated and the Standby Gas Treatment System initiated as expected on low level following void collapse. Some feedwater control problems during recovery resulted in vessel level approaching the low level setpoint thirty-eight minutes after the reactor scram. Due to conservative instrument setpoints, an RPS trip and the aforementioned safety systems were initiated. The root cause of the scram was the unanticipated response of the flow transmitters to hand-held radio frequencies. The transmitters were in a low traffic area where radios are infrequently used. The root cause of the second low level event was inadequate preventive maintenance on a feedwater valve position indicator in the Control Room. A loose adjustment spring locknut on a feedwater valve pneumatic positioner also contributed. Corrective actions were to place further restrictions on hand-held radio use, shorten the calibration frequency of the position indicator, and require the use of Loctite when adjusting the pneumatic positioner.
331 | 3311989011 | 1989-08-26 | QR5 | Turbine Trip | [45 empty] | Duane Arnold | B | GE | PO | 100 | On August 26, 1989, at 1642 hours, with the plant operating at 100% power, Operations Procedure, "Power/Load Unbalance and Relay Circuits Test" was in progress. This test is performed for continued reliable operation of the main turbine. Contrary to what was expected, a trip of the main turbine control valves and subsequent reactor scram occurred at 1643 hours. Subsequent detailed investigations identified bridging of a mercury-wetted relay in the power/load unbalance circuitry as the most probable root cause for the turbine trip and subsequent reactor scram. Approximately five minutes following the scram, problems were encountered on the "B" essential and non-essential busses. Subsequent investigation revealed the root cause to be a failed trip coil on an associated breaker. <br /><br /> The plant was brought to a normal, safe shutdown condition and the appropriate notifications were made. There was no effect on the safe operation of the plant.
331 | 3311990002 | 1990-03-29 | QP5 | Excessive Feedwater Flow | [45 empty] | Duane Arnold | B | GE | PO | 100 | On March 29, 1990 with the reactor operating at 100% power, a manual reactor scram was initiated at 0407 hours in response to a rising reactor water level. The rising water was due to feed regulating valve lockup. <br /><br /> At approximately 0245 hours on March 29, 1990, operating air was isolated to an Instrument Air header isolation valve due to a personnel error made in the tagout preparation process. As this operating air pressure slowly bled off, the air header isolation valve failed shut. This loss of instrument air caused the feed regulating valves to lockup. Reactor level slowly increased to the 195" high level alarm point at 0405 hours. As actions to lower reactor level to within the normal operating range were unsuccessful and various other control valves began to fail due to the loss of instrument air, the Operations Shift Supervisor conservatively elected to direct initiation of a manual scram. <br /><br /> Following the reactor scram, all automatic functions and manual actions were completed satisfactorily. <br /><br /> Corrective actions for this event include a required independent review of Instrument and Service air tagouts, completion of drawing updates,.and a review of the design document change process focusing on potential process improvements.
331 | 3311990004 | 1990-04-01 | QR8 | Spurious Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 8 | On April 1, 1990 at 0532 hours, during reactor startup, a momentary increase in indicated flux on Average Power Range Monitor (APRM) channels "C" and "D" to greater than 15 percent of rated power resulted in an automatic reactor scram. The plant was at approximately eight percent thermal power. The APRM scram was originated from Local Power Range Monitor (LPRM) 32-09c, which feeds its output signal to APRM channels "C" and "D". These APRM channels feed opposite sides of the Reactor Protection System (RPS) logic. The most probable cause was metallic particles formed in the LPRM detector, which shorted the anode to the cathode. This resulted in a momentary spike which was sensed as a power increase by the APRMs, and subsequently the RPS logic. When the switch is in startup mode, the upscale trip setpoint is set at 15 percent of rated power. The plant responded to the scram as designed with no observed equipment failures.<br /><br /> Following the scram, a review of the event and troubleshooting of the failed LPRM were performed. The LPRM was bypassed and reactor startup commenced without further complications. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
331 | 3311990014 | 1990-09-10 | QR5 | Turbine Trip | [45 empty] | Duane Arnold | B | GE | PO | 27 | On September 10, 1990 with the reactor at approximately 27% power, a turbine trip occurred as a result of a sensed high level in a Moisture Separator Reheater. Reactor steam production at the time of the turbine trip was slightly in excess of the bypass valve capacity, resulting in a rising reactor pressure, and a reactor scram approximately one minute later.<br /><br /> Plant response to the conditions present occurred appropriately. Primary Containment Isolation Groups 2-5 responded in accordance with design when reactor water level decreased as a result of void reduction in response to the reactor scram. <br /><br /> The root cause of the event was valve misalignment following maintenance. The corrective actions included an immediate valve lineup verification and enhancements to the valve lineup procedure.
331 | 3311990015 | 1990-09-13 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Duane Arnold | B | GE | PO | 37 | On September 13, 1990, with the reactor at approximately 37% power, Operations personnel manually scrammed the reactor (Reactor Protection System initiation) when rapidly decreasing Instrument Air pressure resulted in reactor vessel level control difficulties. The feedwater regulating valves, which receive their motive power from Instrument Air, "locked up" in their current position, resulting in a gradual increasing trend in reactor vessel level. Primary Containment Isolation System Groups Two through Five initiated as designed on reduced level following the scram. The plant was returned to a stable condition with no further problems. The cause of the Instrument Air pressure loss was the failure of a three-inch soldered copper fitting joint at an air dryer inlet. Examination of the joint found inadequate solder coverage. Larger joints are difficult to solder, and code-required visual examination and inservice testing may not detect reduced solder coverage. As corrective actions, all other air system joints soldered in the same time period were inspected and repaired as necessary, and a sampling inspection of other soldered joints is ongoing. Inspection criteria for certain difficult joints is being modified to include ultrasonic testing.
331 | 3311990016 | 1990-09-18 | QL5 | Partial Closure of MSIVs | [45 empty] | Duane Arnold | B | GE | PO | 50 | On September 18, 1990, with the plant operating at approximately 50% power, a reactor scram occurred when three inboard Main Steam Isolation Valves (MSIVs) closed unexpectedly. Just prior to the MSIVs closing, the 'A' side of the Main Steam Line Radiation Monitor (MSLRM) surveillance test had been satisfactorily completed with isolation signals reset. Upon initiating the 'B' side test, the 'B', 'C', and 'D' inboard MSIVs closed resulting in the scram. <br /><br /> The cause of this event was a loose wiring connection in the inboard MSIV control logic which effectively put the 'B', 'C', and 'D' inboard MSIVs in a half (A side) tripped condition (AC solenoids de-energized) even though the logic was reset. During performance of the MSLRM surveillance, when the 'B' logic trip was inserted, the DC solenoids on the inboard MSIVs de-energized causing the 'B', 'C' and 'D' inboard valves to go closed. <br /><br /> Immediate corrective actions were to repair the connection and perform an extensive inspection of appropriate control room panels for additional loose connections. Long term corrective action will involve periodic inspections of appropriate panels. <br /><br /> This event had no effect on the safe operation of the plant. Safety systems responded as designed in response to the scram signal and the plant was quickly brought to a stable condition.
331 | 3311990019 | 1990-10-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Duane Arnold | B | GE | PO | 65 | On October 19, 1990 the reactor was in single loop operation at approximately 65% power, two night shift electricians assigned to the task of troubleshooting the source of an apparent fault on the 'B' Recirculation MG system drive motor pulled what they perceived to be the potential transformer for the circuit. The potential transformer actually senses the available supply voltage from one winding of the Startup transformer to one of the essential electrical busses. This caused the bus to sense an undervoltage condition and automatically initiated a dead bus transfer from the Startup Transformer to the Standby Transformer. When power was restored to 1A4, loss-of-power relays in the condensate demineralizer system (EEIS code SG), caused 3 out of 4 inservice demineralizer beds (function component FDM) to isolate. This resulted in the loss of feedwater and a reactor scram on low reactor vessel level. <br /><br /> The initiating event, removal of the potential transformer, was caused by personnel error. The root cause of the scram was an undesirable design feature of the condensate demineralizer control logic.
331 | 3311991001 | 1991-01-06 | K1 | Steam Line Break Outside Containment | [9 empty] | X | [26 empty] | X | [8 empty] | Duane Arnold | B | GE | PO | 95 | On January 6, 1991, with the plant operating at 95% power, a controlled reactor shutdown was initiated due to a steam leak in the heater bay. At 1107 operators rapidly reduced recirculation flow to minimum in preparation for insertion of a manual scram. The decision to manually scram was conservatively made to ensure heater bay temperatures would not challenge the Main Steam Line isolation setpoint of 200 degrees F. At 1113, with reactor power at approximately 60%, a manual scram was inserted. The intermediate cause of this event was a break in a two inch extraction steam drain line just below the welded joint which attaches the drain line to a twelve inch extraction steam line. The cause for the break in the pipe was cyclic fatigue due to the relative movement of the two inch and twelve inch pipe during plant operation. The section of to inch pipe, where the break occurred, was replaced with a new pipe. The new pipe was constructed with an expansion loop to compensate for relative movement between the twelve and two inch pipes. This event had no effect on the safe operation of the plant. Following the scram the plant was quickly brought to a stable condition.
331 | 3311991003 | 1991-02-09 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Duane Arnold | B | GE | PO | 100 | On February 9, 1991 at 1659, a reactor scram from 100% power occurred due to a sensed low control oil pressure at the Main Turbine Control valves. Extensive troubleshooting following the event identified induced electrical noise in the Turbine Electro-Hydraulic Control (EHC) System which appeared to have ultimately caused the pressure fluctuation in EHC control oil. Corrective actions include shielding of appropriate cabling and additional, more frequent EHC system component preventive maintenance. All automatic actions occurred as designed as a result of the scram. Operator actions were appropriate and expeditiously returned the plant to a stable condition.
331 | 3311991005 | 1991-06-22 | QL5 | Partial Closure of MSIVs | [45 empty] | Duane Arnold | B | GE | PO | 100 | On June 22, 1991 with the reactor at approximately 100% power, a single outboard Main Steam Isolation Valve (MSIV) closed, resulting in a high flux automatic reactor scram. The root cause for this event was poor workmanship during original construction of a soldered copper joint in the non-safety related nitrogen supply piping to the outboard MSIVs. Corrective actions include replacement of the MSIV copper piping with stainless steel tubing and evaluation of the long term suitability of existing copper piping in systems related to plant safety or availability. <br /><br /> While proceeding to cold shutdown, on June 23, 1991, a partial Primary Containment Isolation System (PCIS) Group IV actuation isolated the Residual Heat Removal (RHR) system suction piping. This occurred while aligning RHR to enter shutdown cooling. When the RHR pump was started, a pressure surge, cause unknown, resulted in the PCIS actuation. Corrective actions include installation of instrument line snubbers, and testing and analysis of the RHR shutdown cooling system. <br /><br /> This report is submitted as a supplemental update on corrective actions taken and testing performed.
331 | 3311992013 | 1992-08-17 | QR8 | Spurious Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 100 | On August 17, 1992, with the plant operating at 100% power, an automatic reactor scram was initiated due to a perceived high average power range neutron flux level. The cause was a noise signal which affected the recirculation flow signals and reduced the flow-biased scram setpoint below the current operating power level. <br /><br /> This revision to the original LER incorporates changes to the corrective actions previously committed to. Specifically, the use of light-emitting diodes (LEDs) has been approved for use in the control rod indication because of their improved reliability over the the incandescent lamps that failed during this event. Therefore, the previous commitment to replace the installed indication quarterly has been changed to a commitment to periodically inspect or replace the installed indication with a frequency consistent with the expected service life.
331 | 3311992018 | 1992-11-13 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Duane Arnold | B | GE | PO | 100 | On November 13, 1992 at 0327, with reactor power in transition and decreasing from 100% of rated power, a turbine trip and reactor scram occurred due to the loss of condenser vacuum. The loss of vacuum was caused by the failure of the 'A' circulating water pump which allowed the flow from the remaining pump to recirculate back to the circulating water pump pit and bypass the condenser. Four (4) safety-relief valves lifted momentarily in response to the scram from high power. Plant and operator response to the transient was as expected. <br /><br /> The 'A' circulating water pump failed due to bolting failure on the pump bottom column - pump impeller case flange. The bolt failure was determined to be caused by stress corrosion cracking. The pump bolt material has been changed.
331 | 3311993010 | 1993-10-26 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Duane Arnold | B | GE | PO | 100 | On October 26, 1993, with the plant operating at 100% power, a full automatic reactor scram occurred. The scram signals were turbine control valve fast closure and average power range monitor high flux. An unknown ground at a turbine solenoid valve, combined with a momentary arc caused by maintenance on a fan in the electro-hydraulic control (EHC) cabinet in the control room, resulted in completion of the circuit to close one of the four turbine control valves. <br /><br /> All control rods inserted and vessel level dropped below the low level setpoint causing groups 2-5 primary containment isolations. Vessel level was restored and returned to normal. Reactor pressure was controlled by the turbine bypass - valves. There were no emergency core cooling system actuations and no safety relief valve openings. <br /><br /> The ground at the turbine solenoid valve was repaired and other turbine valve circuits were checked for grounds but none were found. The reactor was re-started on October 28, 1993.
331 | 3311994010 | 1994-07-10 | QR6 | Manual Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 68 | On Sunday, July 10, 1994, at 2201 hours, with the plant operating at 68% power, a manual scram was inserted in response to an impending loss of Electro-Hydraulic Control (EHC) reservoir level. The loss of EHC reservoir level was caused by a 210 degree crack in the 1' EHC tubing supplying the number 3 main turbine control valve (CV-3). <br /><br /> All control rods fully inserted and vessel level dropped below the low level setpoint causing groups 2-5 primary containment isolations. Vessel level was restored and returned to normal. Reactor pressure was controlled by the turbine bypass valves and main steam line drains. There were no emergency core cooling system actuations and no safety relief valve openings. <br /><br /> Corrective actions include repair of the ruptured tubing and installation of accumulators on the CVs to prevent reoccurrence of this event. The reactor was restarted on July 16, 1994.
331 | 3311995005 | 1995-05-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Duane Arnold | B | GE | PO | 100 | On May 14, 1995, with the plant operating at 100% power, a full automatic reactor scram occurred due to low reactor water level caused by a trip of the B reactor feedwater pump. The pump tripped due to loss of lube oil pressure caused by a lube oil pump drive shaft coupling failure. The coupling failed due to a lack of lubrication caused by a plugged lube oil supply orifice. <br /><br /> All control rods inserted and Primary Containment Isolation System (PCIS) isolations, Groups 2-5, occurred as designed. Reactor water level control following the scram was complicated by problems with the A feedwater regulating valve controller but vessel level and pressure were maintained within safe operating limits. There were no emergency core cooling system actuations and no safety relief valve openings. <br /><br /> The failed coupling and the plugged orifice were replaced and the coupling and orifice for the A feedwater pump were inspected. The maintenance procedure, the vendor manual, and plant drawings for the feedwater pumps are being revised to ensure proper lubrication of the coupling. The controller was modified and the part number description for the controller has been changed to ensure that required modifications are made. The plant was re-started on May 17, 1995.
331 | 3312000001 | 2000-01-05 | QR8 | Spurious Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 100 | On January 5, 2000, with the plant operating at 100% power, an automatic scram occurred when technicians attempted to restore a level transmitter to service after calibration. All control rods inserted, and primary containment isolations (Groups 2, 3 and 4) occurred as expected. A partial Group 5 isolation also occurred. Reactor water level control following the scram was complicated by a positive bias on a feedwater regulating valve and a recirculation motor generator runback failure, but vessel level and pressure were maintained within safe operating limits. There were no emergency core cooling system actuations and no safety relief valve openings. The plant was restarted on January 9, 2000. This event had no effect on the safe operation of the plant. The scram signal resulted from a false low level signal generated due to an inadequate instrument restoration process. Corrective actions will include enhancements to training and calibration practices, and procedure revisions.
331 | 3312000002 | 2000-06-23 | QR5 | Turbine Trip | [45 empty] | Duane Arnold | B | GE | PO | 100 | On June 23, 2000 at 1616, with the reactor operating at 100% power, the Duane Arnold Energy Center (DAEC) experienced a main generator lockout which caused a turbine trip and reactor scram. The plant and control room operator responses were as expected. The safety consequences were minimal. The cause of the event was a main generator backup lockout due to a unit differential current trip. Initial testing on the associated current transformers did not indicate the existence of equipment malfunction. Other potential causes of the transient, including lightning strike, were investigated and additional equipment walk downs and testing were performed. No definitive cause was determined. During the subsequent plant startup the generator output current transformer, which provides an input to the unit differential current relay, failed approximately 30 minutes after the generator was synchronized to the grid. Apparently, a loose connection on one of the current transformer secondary leads caused an increased voltage potential, which resulted in an arc that destroyed the lead.
331 | 3312001003 | 2001-08-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Duane Arnold | B | GE | PO | 100 | On August 12, 2001, while operating at 100% power, operators inserted a manual reactor scram due to decreasing reactor water level. The low level was caused by a reactor feedwater pump minimum flow bypass valve failing open. The "B" (affected) feed pump tripped on low suction pressure as operators attempted to restore level. All control rods fully inserted upon receipt of the manual scram signal. Primary containment isolations initially occurred as expected. A Group 1 isolation also occurred, after which all main steam isolation valves closed. This isolation was due to the decreasing reactor pressure with the mode switch in RUN and occurred quicker than expected. The root cause of the event was a failed resistor in the flow indicating controller that operates the minimum flow valve. Corrective actions include repair of the failed controller, preventive maintenance to the controller for the "A" feed pump, replacements of similar installed controllers, engineering analysis of the receipt of the Group 1 isolation, and a revision to the procedure for immediate actions in response to a reactor scram. There were no actual safety consequences or impact on public health and safety as a result of this event. The plant was re-started and returned to power operation on August 15, 2001.
331 | 3312001006 | 2001-10-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Duane Arnold | B | GE | PO | 100 | On October 17, 2001, while operating at 100%power, operators inserted a manual reactor scram due to decreasing reactor water level. The low level was caused by a sequence of events initiated by a loss of Division 1 Instrument AC bus 1Y11 due to a failure of inverter 1D15 coincident with the alternate power supply, regulating transformer 1Y1A, being out of service for preplanned maintenance. The loss of 1Y11 caused a plant transient that required the operating crew to insert a manual scram in anticipation of reaching an automatic scram setpoint on low Reactor Pressure Vessel (RPV) level. All control rods fully inserted upon initiation of the manual scram. Reactor level dropped low enough (+119.5") to initiate High Pressure Coolant Injection (HPCI), Reactor Core Isolation Cooling (RCIC), Low Pressure Coolant Injection-Loss of Offsite Power (LPCI-LOOP) select, and Reactor Water Cleanup (RWCU) outboard isolation. Reactor level was recovered using RCIC and "B" Reactor Feed Pump (RFP). HPCI was out of service for preplanned maintenance. "B"RFP and RCIC received trips when reactor level reached the high level trip setpoint (211"). RCIC was restarted for level control and a second manual scram was inserted in anticipation of a low level automatic scram. The "B" RFP was restarted for level control and was used to restore level. At 195"RCIC was secured, and at 211" the "B"RFP tripped for the second time. Three circuit boards in the inverter were determined to be the likely cause of the failure and were replaced. The three original boards were removed and sent to the vendor for failure analysis. No problems were detected. There were no actual safety consequences associated with this event. There was no impact on public health and safety.
331 | 3312009003 | 2003-01-04 | QR6 | Manual Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 100 | On April 3, 2009, while operating at 100% power, with no Technical Specification (TS) Required Actions in affect, instrument and controls (I&C) technicians were performing Surveillance Test Procedure (STP) 3.3.3.2-09, Reactor Water Level and Pressure Instruments Calibration. This STP was performed for the first time since the recorder had been replaced during Refueling Outage (RFO) 21 in February 2009. Step 7.1.20 directed lifting a lead on the positive terminal of channel 2 on Level Recorder Switch (LRS) 4559/4560. When the lead was lifted, the control loop for reactor vessel level control was opened, and indicated vessel level pegged low. The plant response, as designed, was to increase feed water flow to the reactor to compensate for the indicated lowering vessel level. This caused actual reactor vessel level to increase. As a result of the increasing reactor water level, operators inserted a manual scram at 0028. All safety systems responded as designed. Containment isolations signals were received for groups 2, 3, and 4 due to reactor level dropping below 170 inches. All isolations went to completion. This reactor level response is normal following a reactor scram. The cause of this event was an inadequate procedure change. There were no actual safety consequences and no effect on public health and safety as a result of this event.
331 | 3312003001 | 2003-02-01 | QL6 | Condenser Leakage | [45 empty] | Duane Arnold | B | GE | PO | 93 | At 2242 on January 31, 2003, while operating the plant at 93% power, Control Room operators began receiving a series of conductivity alarms. Conductivity levels in the condenser hotwell, reactor feedwater and reactor coolant systems exceeded action levels established in plant procedures. After starting a normal reactor shutdown in response to those procedures, a manual reactor scram was inserted at 0233 on February 1, 2003, due to the rate and magnitude of the continued conductivity increases. The plant was cooled down and Mode 4 (Cold Shutdown) was reached at 1620 the same day. The cause of the chemistry transient was a punctured tube in the main condenser, which allowed water from the Main Circulating water system to leak into the Condensate system. A condenser steam deflector plate was found broken off inside the condenser, and was the cause of the punctured tube. The deflector plate experienced a fatigue failure due to sustained plant operation with a feedwater heater dump valve controlling heater water level; a condition created by the failure of the heater's drain valve. Corrective actions include repair of the heater drain valve, restoration of chemistry parameters, removal of the punctured tube, plugging of other damaged tubes, repairs to the condenser deflector plate, and follow-up inspections of deflector plates in other parts of the condenser. Extensive evaluations were performed for reactor vessel internal components, nuclear fuel, and other plant systems for adverse effects from the chemical excursion. The evaluations concluded there was minimal impact from this event. There was no impact on public health and safety as a result of this event.
331 | 3312003005 | 2003-11-07 | QR6 | Manual Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 45 | On November 7, 2003, during a plant startup, a manual reactor scram was inserted due to increasing reactor water conductivity (>5.0 µmho/cm). Plant Abnormal Operating Procedures require a scram to be inserted when conductivity exceeds 5.0 µmho/cm. Conductivity increase begun on November 6, 2003. All plant systems responded as expected to this event including Primary Containment Isolation System groups 2, 3, and 4, which isolated due to reactor water level dropping below 170". The reactor water level drop is normal following a scram from 45% power due to void collapse in the reactor vessel. Reactor water level was restored to normal and the group isolations were reset. Extensive evaluations were conducted and determined the cause of the increasing conductivity to be attributed to a resin intrusion. Trouble shooting activities determined that a single condensate demineralizer, 1T013E, had several septa installed that were not manufactured to the appropriate length. These septa allowed resin to be transported out of the system and subsequently into the reactor vessel. The affected demineralizer was repaired and successfully returned to service. There were no actual safety consequences associated with this event. There was no effect on public health and safety as a result of this event. This event is reportable under 10CFR50.73(a)(2)(iv)(A).
331 | 3312003006 | 2003-11-25 | QL7 | Degraded condenser vacuum | [45 empty] | Duane Arnold | B | GE | PO | 20 | On November 25, 2003, while operating at approximately 20% power, a manual reactor scram was inserted due to degrading condenser vacuum. The plant was operating at reduced power to perform testing to determine a source of excessive air in-leakage. The manual reactor scram was inserted in anticipation of an automatic trip. All plant systems responded as expected to this event including Primary Containment Isolation System groups 2, 3, and 4, which isolated due to reactor water level dropping below 170". The reactor water level drop is expected following a scram from power due to void collapse in the reactor vessel. Reactor water level was restored to normal and the group isolations were reset. Extensive testing and evaluations were conducted and determined the cause of the degrading condenser vacuum was from excessive air in-leakage from a failed welded seam between the High Pressure Condenser and the crossover loop seal. The seam was repaired and a plant startup was commenced on December 4, 2003. There were no actual safety consequences associated with this event. There was no effect on public health and safety as a result of this event. This event is reportable under10CFR50.73(a)(2)(iv)(A).
331 | 3312006005 | 2006-11-06 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Duane Arnold | B | GE | PO | 100 | On November 6, 2006, at 0110, while operating at 100% power, during the performance of Main Turbine Operational Tests, Surveillance Test Procedure (STP) NS93001, Section 7.3, "Overspeed Trip Device and Mechanical Trip Valve Test (Test A)," a reactor scram occurred. Investigation into this event has determined that the scram was initiated by Reactor Protection System (RPS) actuation due to at least three Turbine Stop Valves less than 90 percent open. The cause of this Turbine Stop Valve closure was a noise spike, of some level, in combination with normally open relays being closed (possibly stuck). Corrective actions included the replacement of a suspect cable, that was determined to be the most likely cause of the noise spike, the burnishing of relay contacts, and the replacement of a relay board. There were no actual safety consequences and no effect on public health and safety as a result of this event.
331 | 3312007006 | 2007-03-18 | QR6 | Manual Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 28 | On March 18, 2007, while operating at 28% power, a chemistry excursion occurred shortly after Condensate Filter Demineralizer 1T-13D was placed in service. The magnitude of the chemistry excursion required operators to shutdown the reactor in accordance with abnormal operating procedure sand plant chemistry procedures. As a result of inserting the manual scram, Primary Containment Isolation System (PCIS) groups 2, 3, and 4 isolations occurred when reactor water level dropped below 170 inches. All isolations went to completion. The reactor water level decrease is normal following as cram from 28% power due to void collapse in the reactor vessel. Reactor water level was subsequently restored to normal and the PCIS group isolations were reset. Troubleshooting subsequently determined that the chemistry excursion was the result of resin intrusion from Condensate Filter Demineralizers into the Condensate System. There were no actual safety consequences and no effect on public health and safety as a result of this event.
331 | 3312007007 | 2007-04-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Duane Arnold | B | GE | PO | 98 | On April 2, 2007, while operating at 98% power, during performance of planned preventative maintenance on Non-essential Electrical 4160V AC Bus 1A2, a bus lockout occurred at 11:25. The loss of the 1A2 switchgear resulted in the loss of B Reactor Feed Pump and B Condensate Pump. At 11:25, a manual reactor scram was inserted due to Reactor Pressure Vessel level approaching 170 inches (automatic scram level). The scram went to completion. After the scram, vessel level rose to 211 inches, causing the A Reactor Feed Pump to trip. Before the ‘A’ Reactor Feed Pump could be restarted and adequate feed flow established, another scram signal was received when reactor level dropped below 170 inches. Control rods were already inserted and isolations had been completed prior to this second scram signal being received. The Reactor Operator successfully restored level using the Feedwater Regulating Valve as directed by the Operations Shift Manager. The cause of this event is the failure to recognize the risk associated with performing the maintenance on-line without putting physical and process protections in place. There were no actual safety consequences and no effect on public health and safety as a result of this event.
331 | 3312009001 | 2009-02-01 | QR6 | Manual Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 53 | On February 1, 2009, with the plant operating at 53% power, during plant shutdown evolutions in preparations for Refuel Outage (RFO) 21, operators were in the process of securing the 'A' cooling tower in accordance with Operating Instruction 442, Circulating Water System. While throttling the 'A' cooling tower riser isolation valves in preparations for securing the 'A' circulating water pump, a rupture of the '13' cooling tower west riser occurred. In anticipation of a loss of circ water pit level, a manual scram was inserted at 1800. Following the manual scram, the plant was stabilized per abnormal operating procedures. Containment isolation signals operated as designed with Groups 2, 3, and 4 received. The cause of this event was an inadequate procedure. Operating Instruction 442 was inadequate to prevent an inappropriate operational configuration that resulted in the failure of the cooling tower riser. A design change restored the failed riser with a more robust design, and enhanced the design of the remaining risers on both cooling towers. There were no actual safety consequences and no effect on public health and safety as a result of this event.
331 | 3312009004 | 2009-10-08 | QR8 | Spurious Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 100 | On October 8, 2009, while operating at 100% power, during the performance of Surveillance Test Procedure (STP) 3.3.3.2-09B, Reactor Water Level and Pressure Instruments (Loop B) Calibration, an automatic reactor shutdown occurred. The shutdown was caused by the failure to close an instrument isolation valve for a Reactor Vessel Pressure Transmitter. The failure to close this valve resulted in creating a sensed low reactor water level on Reactor Protection System (RPS) channels A2 and B2, and thus resulted in the automatic reactor shutdown. Primary Containment Isolation System (PCIS) Groups 2, 3 and 4 were received due to reactor water level dropping below 170 inches due to the expected level shrink immediately following the reactor scram. All isolations went to completion. Reactor water level was subsequently returned to normal as expected under post scram conditions. The cause of this event was that defenses in depth were inadequate to prevent the plant transient during the performance of STP 3.3.3.2-09B. There were no actual safety consequences and no effect on public health and safety as a result of this event.
331 | 3312010003 | 2010-04-26 | QR6 | Manual Reactor Trip | [45 empty] | Duane Arnold | B | GE | PO | 10 | On April 26, 2010, at 0300, while in day 1 of a 31 day Limiting Condition for Operation (LCO) for inoperable Primary Containment Isolation Valves (Traversing Incore Probe Drive Ball Valves), during the process of shutting down the plant for a planned outage to investigate an increase in Drywell leakage, a manual scram was inserted. The manual scram was inserted due to elevated vibration readings on Main Turbine Bearing number 6. The reactor scram and associated turbine trip was initiated at approximately 14% power in anticipation of reaching Main Turbine vibration limit. The cause of the increase in bearing vibration was determined to be from a turbine rub. Turbine rubs can be induced in operating configurations of high turbine gland seal pressure with low main condenser back pressure. This configuration existed during the April 26, 2010 shutdown. The catalyst for inducing the rub was an excessive Low Pressure Turbine cool down rate which allowed one of the two Low Pressure Turbine casings to cool more than the other. This difference in casing temperatures created the formation of a rub which resulted in localized heating of the turbine shaft and resulting increase in vibration readings. There were no Systems, Structures, or Components inoperable at the time of the scram that contributed to the event. There were no actual safety consequences and no effect on public health and safety as a result of this event.
331 | 3312018004 | 2018-10-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Duane Arnold | B | GE | PO | 100 | On October 19, 2018, at 1725 while operating at 100% power, the 'B' Feedwater Regulating Valve (FRV; CV1621) failed closed resulting in lowering reactor level and subsequent automatic reactor scram on low level. This resulted in a 4 hour event report to the NRC under 10CFR50.72(b)(2)(iv)(B) for actuation of the Reactor Protection System. This report also included reports for emergency core cooling systems (High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC)) discharge into the reactor coolant system under 10CFR50.72(b)(2)(iv)(A), and a valid actuation of the Primary Containment Isolation System under 10CFR50.72(b)(3)(iv)(A) (reference EN#53676). The FRV was subsequently repaired and the reactor was started up on October 21, 2018. The direct cause of the failure was a broken conductor within the FRV position modulator (ZM1621). The root cause of this event was the fact that design choices made by the vendor resulted in a less robust wire connection. This event was of low safety significance and had no impact on public health or safety. There were no systems, structures, or components inoperable at the time of the event and none that contributed to the event. This event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A). There were no radiological releases associated with this event.
331 | 3312019001 | 2019-04-20 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Duane Arnold | B | GE | PO | 100 | On April 20, 2019, while operating at 100% power, NextEra Energy Duane Arnold (DAEC) experienced a trip of both reactor feed pumps due to a loss of suction pressure. As a result, plant operators inserted a manual scram. All control rods inserted, as required. As a result of the feed pump trips and scram, the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) automatically injected. In addition, containment isolations occurred, as expected for this event. This resulted in a 4-hour event report to the NRC under 10 CFR 50.72 section 50.72(b)(2)(iv)(A) - ECCS Injection, 50.72(b)(2)(iv)(B) - RPS Actuation - Critical, 50.72(b)(3)(iv)(A) - Valid Specific System Actuation (reference EN#54012). The root cause of this event was brittle fracture of a condensate demineralizer in-line air filter bowl due to heat related age degradation. This event was of very low safety significance and had no impact on public health or safety. There were no systems, structures, or components inoperable at the time of the event and none that contributed to the event. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A). In addition to the event that occurred on April 20, 2019, this LER is reporting a related event that occurred on April 21, 2019 that resulted in an invalid Primary Containment Isolation System. There were no radiological releases associated with either of these event.
331 | 3312020001 | 2020-08-10 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Duane Arnold | B | GE | PO | 80 | On August 10, 2020, at 1246 CDT, while operating at 80% power, NextEra Energy Duane Arnold (DAEC) experienced a generator load reject and subsequent reactor scram as a result of a loss of offsite power (LOOP) due to extremely high winds. An Unusual Event was declared at 1258. All Safety Systems performed as designed. As a result of the LOOP, the 'A' and 'B' Emergency Diesel Generators automatically started and supplied power to the safety related busses. As a result, the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) automatically initiated and injected into the reactor. In addition, containment isolations occurred, as expected for this event. This resulted in a 4-hour event report to the NRC under 10 CFR 50.72 section 50.72(b)(2)(iv)(A) - ECCS Injection, 50.72(b)(2)(iv)(B) - RPS Actuation - Critical, 50.72(b)(3)(iv)(A) - Valid Specific System Actuation (reference EN#54826). The NOUE was exited at 1600 on August 11, 2020. The cause of the LOOP was an extremely severe storm (called a Derecho) with heavy rains and very high winds. This event had no impact on public health or safety. There were no systems, structures, or components inoperable at the time of the event that contributed to the event. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A), 50.73(a)(2)(v)(C) and 50.73(a)(2)(iii). There were no radiological releases associated with this event.
333 | 3331987008 | 1987-06-10 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | FitzPatrick | B | GE | PO | 100 | POWER LEVEL - 100%. ON 6/10/87 AT 0034, WITH THE PLANT AT 100% POWER, REACTOR TRIPPED. ALL OTHER SYSTEMS WERE IN THE NORMAL POWER OPERATION LINE-UP, EXCEPT THAT BOTH RECIRCULATION SYSTEM SCOOP TUBE POSITIONERS WERE LOCKED UP DUE TO CONTROL PROBLEMS WHILE OPERATING NEAR 100% FLOW. THE CONTROL ROOM OPERATOR RESET THE SCOOP TUBE POSITIONERS. THIS ALLOWED THE RECIRCULATION SYSTEM PUMPS TO RUNBACK TO 44% SPEED, WHICH REDUCED STEAM FLOW TO WITHIN THE CAPACITY OF ONE RFP. AS REACTOR VESSEL LEVEL APPEARED TO BEGIN TO INCREASE, A LOW LEVEL SCRAM OCCURRED. A FAILED PUMP SEAL ON THE RFP A WAS DISCOVERED. IT IS BELIEVED THAT A PUMP SUCTION PRESSURE TRANSIENT, CAUSED BY THE SEAL FAILURE, MAY HAVE CAUSED THE RFP A TRIP, WHICH LED TO THE LOW LEVEL SCRAM. OPERATION WITH THE SCOOP TUBE POSITIONERS LOCKED MAY HAVE INCREASED THE MAGNITUDE OF THE LEVEL TRANSIENT. THE IMMEDIATE ACTION WAS TO CARRY OUT THE SCRAM PROCEDURE, RESTORE LEVEL AND PLACE THE PLANT IN A STABLE CONDITION. PRIOR TO STARTUP ALL REACTOR PROTECTIVE SYSTEM LEVEL TRIP UNITS WERE VERIFIED TO BE OPERATING WITHIN REQUIRED RANGES. PRIOR TO RETURNING THE RFP A TO SERVICE THE OIL SYSTEM AND TRIP FUNCTIONS WERE VERIFIED TO BE OPERABLE AND THE SEAL WAS REPLACED. LONG TERM ACTION IS TO MODIFY THE RECIRCULATION SYSTEM SPEED CONTROL SYSTEM TO ALLOW OPERATION WITH THE SCOOP TUBES UNLOCKED.
333 | 3331987012 | 1987-08-28 | QR5 | Turbine Trip | [45 empty] | FitzPatrick | B | GE | PO | 100 | POWER LEVEL - 100%. AT 1357 ON 8/28/87 WHILE OPERATING AT A POWER LEVEL OF 100% A REACTOR SCRAM OCCURRED AS A RESULT OF A MAIN TURBINE TRIP. THE MAIN TURBINE TRIP WAS INITIATED BY AN UNKNOWN GENERATOR PROTECTIVE RELAY ACTUATION. AT 2237 ON 9/7/87 WHILE OPERATING AT A POWER LEVEL OF 100% A TURBINE TRIP, DUE TO ACTUATION OF THE MAIN GENERATOR FIELD GROUND PROTECTIVE RELAY, OCCURRED WHICH WAS VIRTUALLY IDENTICAL TO THE 8/28/87 EVENT. DURING BOTH EVENTS THE PLANT OPERATORS RESPONDED TO THE TRANSIENT BY UTILIZING APPROVED PLANT PROCEDURES. PLANT RESPONSE FOR BOTH EVENTS WERE WITHIN THE BOUNDS OF TRANSIENT ANALYSIS DISCUSSED IN THE FINAL SAFETY ANALYSIS REPORT. THE ROOT CAUSE OF THE MAIN GENERATOR TRIPS IS BELIEVED TO HAVE BEEN THE PRESENCE OF A CUPRIC OXIDE FILM ON THE INSULATED COOLING WATER TUBES TO THE RECTIFIER BANKS. THIS FILM APPEARS TO HAVE CAUSED A LEAKAGE PATH TO GROUND IN THE GENERATOR FIELD CIRCUIT. AFTER THE INSULATING TUBES WERE CLEANED, THE FIELD GROUND CURRENT RETURNED TO NORMAL. NO SIMILAR EVENTS INVOLVING GENERATOR FIELD GROUND FAULTS HAVE OCCURRED AT THIS FACILITY.
333 | 3331987017 | 1987-09-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | FitzPatrick | B | GE | PO | 100 | POWER LEVEL - 100%. ON 9/24/87 AT 0738, WITH THE PLANT AT 100% POWER, REACTOR SCRAMMED ON LOW WATER LEVEL FOLLOWING A REACTOR FEED PUMP (RFP) A TRIP ON HIGH VIBRATION. ALL SYSTEMS WERE IN A NORMAL LINE UP EXCEPT THE RECIRCULATION SYSTEM SCOOP TUBE POSITIONERS WERE LOCKED UP DUE TO CONTROL PROBLEMS. THE CONTROL ROOM OPERATOR RESET SCOOP TUBE POSITIONERS ALLOWING RECIRCULATION SYSTEM RUNBACK TO 44% SPEED WHICH REDUCED STEAM FLOW TO WITHIN THE CAPACITY OF ONE RFP. OPERATION WITH SCOOP TUBE POSITIONERS LOCKED MAY HAVE INCREASED THE MAGNITUDE OF THE LEVEL TRANSIENT. A DEFECTIVE VIBRATION DETECTOR SHAFT RIDER ON RFP A TURBINE INBOARD BEARING WAS DISCOVERED. PRIOR TO RETURNING RFP A TO SERVICE THE OIL SYSTEM, TRIP FUNCTIONS AND VIBRATIONS WERE THOROUGHLY EVALUATED. RFP A TURBINE INBOARD BEARING AND SHAFT RIDER WERE REPLACED. LONG TERM ACTION IS TO MODIFY THE RECIRCULATION SPEED CONTROL SYSTEM TO ALLOW OPERATION WITH SCOOP TUBES UNLOCKED AND RFP TURBINE BEARINGS VIBRATION DETECTORS WILL BE ON A PREVENTIVE MAINTENANCE PROGRAM. LER 84-009, 84-010, 84-023 AND 87-008 ARE SIMILAR.
333 | 3331987018 | 1987-11-08 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | FitzPatrick | B | GE | PO | 80 | POWER LEVEL - 080%. AT 1934 HOURS ON 1X1/8/87 WITH REACTOR THERMAL POWER AT 80% A REACTOR TRIP OCCURRED AS A RESULT OF AN AVERAGE POWER RANGE MONITOR (IG) HIGH FLUX TRIP. THE HIGH FLUX TRIP WAS INITIATED BY A SUDDEN REACTOR WATER RECIRCULATION SYSTEM (AD) PUMP SPEED INCREASE. DURING THE EVENT OPERATORS RESPONDED TO THE TRANSIENT BY UTILIZING APPROVED PLANT PROCEDURES. PLANT RESPONSE FOR THE EVENT WAS WITHIN THE BOUNDS OF TRANSIENT ANALYSIS AS DISCUSSED IN THE FINAL SAFETY ANALYSIS REPORT. THE ROOT CAUSE OF THE RECIRCULATION PUMP SPEED INCREASE IS BELIEVED TO HAVE BEEN A MALFUNCTION IN A PUMP SPEED CONTROLLER REMOTE SETPOINT/CASCADE SWITCH. THE MALFUNCTION APPEARS TO HAVE OCCURRED DUE TO THE AGE OF THE SWITCH. AFTER TROUBLESHOOTING OF THE SPEED CONTROL LOOP, THE CONTROLLER WAS REPLACED AND THE LOOP RETURNED TO NORMAL OPERATION. THE LER NUMBER OF A SIMILAR PREVIOUS EVENT IS LER 85-018-00.
333 | 3331987020 | 1987-12-09 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | FitzPatrick | B | GE | PO | 100 | POWER LEVEL - 100%. AT 0913 HOURS ON 12/9/87 WITH THE PLANT OPERATING AT 100% POWER, AND WHILE MAKING PREPARATIONS TO PERFORM A TECH SPEC TABLE 4.2-2 SURVEILLANCE TEST ON THE HIGH PRESSURE INJECTION COOLANT (HPCI) SYSTEM (BJ) REACTOR HIGH WATER LEVEL SWITCH (02-3-LIS-101D) A REACTOR TRIP WAS INADVERTENT INITIATED BY AN INSTRUMENT AND CONTROLS (I&C) TECHNICIAN. THE CAUSE OF THE REACTOR TRIP WAS NOT FULLY CLOSING INSTRUMENT PROCESS ISOLATION VALVES BEFORE VALVING IN TEST EQUIPMENT TO THE HPCI REACTOR HIGH WATER LEVEL SWITCH. THIS RESULTED IN A FALSE REACTOR WATER LEVEL TRANSIENT OCCURRING BETWEEN THE SWITCH AND REACTOR PROTECTION SYSTEM (JC) LOW WATER LEVEL TRIP INSTRUMENTATION ON THE COMMON LEVEL HEADER. CORRECTIVE ACTION WAS TO COUNSEL THE I&C TECHNICIAN ON ENSURING INSTRUMENT ISOLATION VALVES ARE FULLY CLOSED BEFORE PRECEDING INTO THE INSTRUMENT TESTING MODE. IN ADDITION INSTRUMENT ISOLATION VALVES WILL BE REPLACED. SIMILAR EVENTS HAVE BEEN REPORTED IN LER 85-007-00, 85-012-00 AND 86-016-00.
333 | 3331989020 | 1989-11-05 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | FitzPatrick | B | GE | PO | 100 | Update Report - Previous Report Date 12/05/89 - Results of EHC Board Tests <br /><br /> EIIS Codes are in ! <br /><br /> A reactor scram occurred from full power at 3:23 P.M. on November 5, 1989. An unidentified failure in an electronic control card of the Electro-Hydraulic Control (EHC) JJ! system for the main turbine TA! is believed to have opened the bypass valves and closed the intercept and control valves. This reduction in steam flow caused a pressure transient resulting in a reactor high flux scram signal from the Average Power Range Monitor (APRM) IG!. The High Pressure Coolant Injection (HPCI) BJ! system was inoperable prior to the scram. The automatic features of the plant responded normally to the scram except that one safety relief valve passed a small amount of steam at a pressure 5 percent below its design lifting pressure. The reactor core isolation cooling (RCIC) BN! system was used to restore reactor water level. One control rod was not fully inserted, requiring manual insertion from position 02. Selected electronic control cards were replaced in the EHC system. The plant was restarted 11/10/89, and scrammed 11/12/89 (LER-89-023) for unrelated reasons. The plant was restarted 11/13/89 and run at 25 percent power to observe the EHC system. It was shutdown 11/20/89 for further work on the EHC system. Following testing and replacement of additional electronic circuit boards, the plant was restarted on 11/22/89. <br /><br /> The circuit boards removed from the EHC system have been sent to the vendor for analysis and possible root cause determination. Factory testing showed that all nine analog speed control boards met original equipment standards. No defects were found.
333 | 3331989023 | 1989-11-12 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | FitzPatrick | B | GE | PO | 10 | EIIS Codes are in !<br /><br /> At 5:34 P.M. on November 12, 1989, a reactor scram occurred during a scheduled surveillance test of safety relief valves (SRV) AD!. In preparation for the test, indicated reactor power was at approximately 10% and pressure was being controlled at 575 psig using the main steam bypass valves. The first SRV was opened in accordance with procedure. Upon closing the valve, the reactor scrammed due to a pressure transient which resulted in a high flux 15% Average Power Range Monitor (APRM) IG! trip. In the start-up/hot standby mode, the APRM trip point is set at a nominal 15%. Actual trip point settings ranged from 13.5% to 14.5% to allow for instrument drift. This left a margin of only 3.5% between indicated reactor power of 10% and the trip point. The small pressure transient caused by opening and then closing the valve was sufficient to cause a neutron flux spike and scram the reactor. The surveillance test procedure did not provide instruction concerning an appropriate margin, nor did it provide a caution to the operator concerning the possible pressure transient and the need for an adequate margin. Corrective action revised the procedure to provide for valve testing at 940 psig when the reactor mode switch will be in the RUN mode. In the RUN mode, the flow biased scram will be in effect. The APRM high flux trip point of 120% will be in service. These safety system trip points provide adequate margin for the expected pressure transient resulting from cycling of safety relief valves.
333 | 3331990001 | 1990-01-19 | QR8 | Spurious Reactor Trip | [45 empty] | FitzPatrick | B | GE | PO | 100 | EIIS Codes are in ! <br /><br /> A reactor scram from full power occurred at 10:45 A.M. on January 19, 1990 during the calibration of reactor water level instrumentation. The instrument which was being calibrated shares common reference and variable legs with instruments of the Reactor Protection System (RPS) JE!. While isolating the instrument under test, a valve packing leak developed. During the response to this leak, valve actuation caused a false low water level to be sensed by the RPS. This false low level transient was caused by rapid valve movement by the field .technician performing the valve manipulations. Corrective actions include review of this event with all I&C technicians, grooming of the communication system to eliminate noise, and repair of equipment that malfunctioned during the transient. <br /><br /> Related LERs: 85-012 and 87-020
333 | 3331990009 | 1990-03-19 | QP5 | Excessive Feedwater Flow | [45 empty] | FitzPatrick | B | GE | PO | 100 | POWER LEVEL - 100%. THE REACTOR SCRAMMED FROM FULL POWER AT 3:54 P.M. ON 3/19/90. A FALSE LOW REACTOR WATER LEVEL SIGNAL IN THE FEEDWATER CONTROL CIRCUIT (JB) INCREASED FEED PUMP SPEED. THIS RESULTED IN HIGH REACTOR WATER LEVEL FOLLOWED BY A TURBINE TRIP AND AUTOMATIC REACTOR SCRAM INITIATED BY TURBINE STOP VALVE CLOSURE (SB). ALL SYSTEMS PERFORMED AS DESIGNED EXCEPT FOR FLOW OSCILLATIONS IN THE HIGH PRESSURE COOLANT INJECTION SYSTEM (HPCI) (BJ) (LER-90-010) AND ONE ROD INSERTING ONLY TO POSITION (02). HPCI INJECTION WAS CONTINUED USING MANUAL OPERATOR CONTROL. A NORMAL PLANT COOLDOWN FOLLOWED. THE CAUSE OF THE SCRAM WAS AN OVERSIGHT BY THE VENDOR IN THE ASSEMBLY OF THE AMPLIFIER COMPONENT (PURCHASED 10 YEARS AGO) OF THE STRIP CHART RECORDER FOR NARROW RANGE WATER LEVEL. A ONE-QUARTER INCH METAL STAR LOCK WASHER WAS FOUND WEDGED BETWEEN THE PRINTED CIRCUIT BOARD AND THE MOUNTING TRACK GROOVE IN THE METAL AMPLIFIER BOX. THE WASHER WAS ALSO IN CONTACT WITH A SIGNAL WIRE ON THE BOARD. THE RESULTING ELECTRICAL GROUND CREATED A SHORT CIRCUIT TO AN INSTALLED GROUND ON THE FEEDWATER LEVEL CONTROL CIRCUIT AND A FALSE LOW REACTOR WATER LEVEL SIGNAL. THE PLANT WAS RETURNED TO SERVICE WITH THE GENERATOR ON LINE AT 8:27 P.M. ON MARCH 23, 1990.
333 | 3331990023 | 1990-10-19 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | FitzPatrick | B | GE | PO | 45 | At 0912 on 10/19/90 the reactor was manually scrammed from 45 percent power as a conservative measure due to inability to clear the circulating water system traveling screens. The rate of supply of circulating water had been reduced due to clogging of the cooling water intake screens KE! by leaves and lake weeds. One of three 50% capacity screens was out of service for scheduled preventive maintenance. A shift in wind direction contributed to an unusually large debris accumulation on the remaining two screens. The screen differential pressure alarm and screenwash systems, which would have provided early indication of fouling, had been unintentionally disabled during the maintenance of the out of service screen due to a procedural deficiency. Shear pins on the remaining two screens failed. It was necessary to remove two of the three main condenser circulating water pumps KE! from service to clear and repair the screens. This necessitated the power reduction and subsequent manual scram. The plant returned to service at 0418 on 10/21/90 (43 hours, 6 minutes off line). <br /><br /> Appropriate steps have been added to procedures. The differential Pressure instrumentation has been added to operator log sheets, plant flow diagrams, and instrument calibration schedules.
333 | 3331990026 | 1990-12-12 | QR8 | Spurious Reactor Trip | [45 empty] | FitzPatrick | B | GE | PO | 100 | UPDATE REPORT - PREVIOUS REPORT DATED JANUARY 11, 1991 <br /><br /> EIIS Codes are in ! <br /><br /> A reactor scram from full power occurred at 1352 on 12/12/90 during calibration of reactor water level instrumentation. The instrument being calibrated shared common reference and variable level legs with instruments of the reactor protection system JC!. The reactor scrammed as the instrument high pressure isolation valve was being cracked open during return to service. The scram resulted from a false low reactor water level signal. During the actual level transient following the scram difficulty was experienced with restarting the reactor feedwater pumps and a failure of the reactor feedwater low flow control valve occurred. A second scram occurred due to an actual low reactor water level at 1416 due to failure of the reactor feedwater low flow control valve air operator diaphragm. The plant returned to service at 0658 on 12/17/90 after being off line for 4 days, 17 hours, and 6 minutes. A root cause investigation of the initial scram has been completed. Corrective action is in the progress of being implemented. Related LERs: 90-007, 90-001, 90-027, 87-020 and 85-012.
333 | 3331990027 | 1990-12-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | FitzPatrick | B | GE | PO | 6 | EIIS Codes are in ! <br /><br /> A reactor scram from six percent power occurred during a start-up on December 15, 1990 at 2140. The cause was a failure of a fabric-woven Buna-N diaphragm which had been in service for 15 years in the air operator for the reactor feedwater low flow control valve and air leakage from the operator stem packing gland. The failure of the valve to stroke full open resulted in an inability to supply sufficient feedwater flow to the reactor. This resulted in decreasing reactor water level and the necessity to use the reactor feed pump. (RFP) discharge valve to control water level. After several controlled jogs in the open direction of the RFP discharge valve, the increase in water flow resulted in a high neutron flux scram of the reactor due to exceeding the 15 percent power limit while the mode switch was in the start-up mode position. <br /><br /> Corrective action included repairing the reactor feedwater low flow control valve operator, revising the start-up procedure to verify full stroke capability of the valve, adding a caution limiting the acceptable open demand signal for the valve to 70 percent. The plant was restored to service at 0658 on 12/17/90. <br /><br /> Related LER: 90-026.
333 | 3331991006 | 1991-05-07 | QR6 | Manual Reactor Trip | [45 empty] | FitzPatrick | B | GE | PO | 100 | Between 0400 and 0500 on 5/7/91 a monthly Technical Specification check found one of the two primary containment isolation valves in both residual heat removal BO! low pressure coolant injection (LPCI) BO) subsystems to be inoperable. One valve operator torque switch tripped in both directions preventing both full closure and full opening. The other valve had excessive seat leakage. The inoperability of both RHR/LPCI systems required a reactor shutdown within 24 hours which was initiated and an Unusual Event declared at 1237. The reactor was manually scrammed at 1820 achieving cold shutdown on 5/8/91 at 0330. The Unusual Event was terminated at 0400. In LPCI loop B the threads of the gate valve stem nut in the motor operator were worn and broken causing the valve to lock in a partially open position. The stem nut was replaced and LPCI loop B restored to service at 1410 on 5/12/91. The stem of an angle globe throttle valve in loop A was broken inside the valve body. The disc, disc guides, and seat were severely damaged. The valve was removed from the system and repaired. Analysis determined stem nut wear out may have been accelerated by mechanical overload caused by high differential pressure across the valve. The valve stem failed due to throttle flow induced vibration causing cyclic fatigue.
333 | 3331993004 | 1993-02-25 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | FitzPatrick | B | GE | PO | 100 | EIIS Codes are in !<br /><br /> On 2/25/93 at 0130 hours with the plant operating at 100 percent power, operators observed condenser SG! inlet temperature to be 58F (lake temperature was 33F). The increased temperature was apparently caused by a buildup of ice on the plant intake bar racks which restricted flow from the lake to the screenwell NN! intake. 80 of 88 intake bar rack heaters were operating. The screenwell water was being tempered by returning circulating water discharge to the intake where it mixed with lake water. As the ice blocked the intake, the amount of water flowing in from the lake decreased which caused the ratio of tempering water to lake water to increase. This caused the circulating water inlet temperature to increase. Load was reduced to 70 percent power and one circulation water pump was tripped. At 0140 hours, when the screenwell level was noted to be approximately ten feet below normal level, the reactor was scrammed. <br /><br /> A second circulating water pump was removed from service and the screenwell level returned to near normal. Computer alarm points have been established to alarm whenever the screenwell or condenser inlet temperature increases by 5 degrees F per hour. A continuous water level watch has been posted and an abnormal operating procedure has been developed to provide guidance if symptoms of icing conditions are observed.
333 | 3331993009 | 1993-04-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | FitzPatrick | B | GE | PO | 100 | Update report: Previous reports dated 10/25/94, 12/06/93, and 05/19/93. On 4/20/93 at 1654, while operating at 100 percent power, abrupt reduction in feedwater [SJ] flow resulted in rapidly decreasing Reactor water level. A Reactor Scram occurred at 177 inches above top active fuel. Plant operators attempted to restore reactor water level by taking manual control of the reactor feed pumps [JK], but were unsuccessful due to component failures. The event was caused by a loose electrical connection on the A Reactor Feed Pump [JK] Turbine Governor Control. The transient was compounded by a failed discharge check valve [SJ] on Reactor Feed Pump A. These failures allowed feedwater flow to be reduced and flow to be diverted causing a scram on low Reactor water level. All control rods fully inserted on the scram and plant systems responded as designed to decreasing and then increasing reactor water level. A Post Trip Evaluation was conducted to determine the root cause of the event and recommend corrective actions to prevent recurrence: The evaluation identified that the Technical Specification Pressure - temperature cooldown and heatup limit of 100 degrees per hour had been exceeded. All necessary repairs and corrective actions identified through the evaluation were completed prior to plant restart.
333 | 3331993013 | 1993-05-25 | QR8 | Spurious Reactor Trip | [45 empty] | FitzPatrick | B | GE | PO | 6 | EIIS Codes are in !<br /><br /> On May 25, 1993, at 2045 hours, an automatic reactor scram took place when Average Power Range Monitor (APRM) IG! E spiked while indicated power level was approximately 6 percent with the plant in the startup mode. Main Steam Line Radiation Monitor (MSLRM) IL! D had been intentionally tripped approximately 5 minutes prior to the APRM E spike after being declared inoperable due to intermittent downscale alarms. Systems performed as designed, no isolations or other engineered safety feature actuations took place and no significant reactor temperature, pressure or level transient took place. A Local Power Range Monitor (LPRM) detector spike was the probable cause of the APRM. LPRMs susceptible to spiking were tested per vendor recommendations to reduce spiking. Stronger radiation sources were placed adjacent to the MSLRM detectors to increase the detected radiation level above the downscale alarm setpoint. No previous LERs have been submitted for scrams due to APRM spikes.
333 | 3331993020 | 1993-09-24 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | FitzPatrick | B | GE | PO | 17 | On September 24, 1993, at 0709 hours, an automatic reactor scram took place when the Main Turbine Bypass Valves partially closed during the conduct of troubleshooting. Due to the potential risk of initiating a turbine trip, reactor power had been reduced, and the Main Turbine had been taken out of service to support troubleshooting an electrical ground in the Turbine Electrohydraulic Control System (EHC). The plant was at 17.5 percent power in the RUN mode with reactor pressure being controlled automatically by the Main Turbine Bypass Valves. While lifting individual leads in the Main Turbine Alarm and Trip circuit, a partial closure of the Turbine Bypass Valves occurred. The Bypass Valve partial closure caused reactor pressure to increase and an automatic scram on high reactor pressure. The event was caused by personnel error. Personnel performing the troubleshooting did not adequately verify plant response. The use of electrical drawings that did not adequately support troubleshooting contributed to the event cause. The electrical drawings will be upgraded.
333 | 3331995010 | 1995-05-30 | QG9 | Primary System Leak | [45 empty] | FitzPatrick | B | GE | PO | 16 | On 05/29/95 at 2216 hours, with the plant operating at 100 percent rated power, operators at the James A. FitzPatrick Nuclear Power Plant (JAFNPP) observed Drywell Floor Sump level recorder readings indicating an increase in the Drywell floor drain leakage rate. The reactor coolant leakage rate slowly increased and at 0538 hours, with the leakage rate at 1.37 gallons per minute (gpm), the decision was made to commence a normal plant shutdown to identify the source of the leakage. At 1200 hours, with the plant operating at approximately 16 percent power, Primary Containment reactor coolant leakage rate had reached and exceeded Technical Specification (T.S.) limit of 2gpm increase within any 24 hour period and an Unusual Event was declared. At 1235 hours, operators inserted a manual reactor scram to expedite reactor cooldown and depressurization. <br /><br /> The cause was identified as a packing leak on a 3/4 inch Reactor Water Recirculation System (RWR) valve located on piping connecting the 'B' Recirculation pump suction line to the Jet Pump Instrument drain line. The plant was brought to cold shutdown condition, entry was made into the primary containment, and corrective maintenance was completed on the RWR valve.
333 | 3331995013 | 1995-09-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | FitzPatrick | B | GE | PO | 100 | On 9/05/95 at 1303 hours, with the plant operating at 100 percent power, a feedwater control system fuse was mistakenly removed due to personnel error. Removal of the fuse caused a rapid reduction in feedwater flow and a reactor scram due to low reactor water level. Isolation of the containment, initiation of high pressure coolant injection and reactor core isolation cooling systems, and initiation of alternate rod insertion and recirculation pump trip signals occurred in response to lowering reactor water level. The safety significance of this event was minimal because the plant responded as designed to lowering reactor water level and the event is bounded by the previously analyzed loss of feedwater flow transient. A post transient evaluation was performed in order to determine the cause of the event, evaluate plant and personnel response, and provide corrective actions. All corrective actions required for continued plant operation were completed prior to restart.
333 | 3331996003 | 1996-02-22 | QR6 | Manual Reactor Trip | [45 empty] | FitzPatrick | B | GE | PO | 7 | On 02/22/96 at 0333 hours, with the plant operating at 60 percent of rated power, results from control rod scram time testing revealed an increased scram time to Notch Position 46 for 19 out of 20 control rods tested. Based on an evaluation of the test results, a normal reactor shutdown was commenced. On 02/22/96, during the controlled shutdown, at 1406 hours, with the plant operating at approximately seven percent of rated power in the Startup/Hot Standby mode, a manual scram was initiated. The manual scram was initiated in anticipation of loss of main turbine bypass valve control due to an Electro-Hydraulic Control (EHC) system leak. The EHC leak was caused by damaged tubing. Results of an engineering evaluation indicate that the subject tube had been damaged due to fatigue. The stainless steel Fluid Actuator Supply (FAS) tubing to all four Turbine Bypass Valves was replaced. The primary cause of the delayed scram time response is attributed to the adherence of the Scram Solenoid Pilot Valves (SSPV) exhaust diaphragms to the valve seats. The 03SOV-118 SSPV exhaust diaphragms for all control rods were replaced.
333 | 3331996010 | 1996-09-16 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | FitzPatrick | B | GE | PO | 100 | On 9/16/96, with the plant operating at 100% power, the UPS M-G set removed from service for maintenance and protective relay calibration in progress, the screwdriver a technician was using slipped and inadvertently connected two terminals of a 24KV iso-phase bus ground fault protective relay. This relay is in service when back-feeding plant loads from the 345 KV line. The short circuit simulated relay contact closure and caused the Main Unit Output Transformer load side circuit breakers to open which resulted in a generator load reject from 100% power. The short circuit also inhibited (by design) the fast transfer of station loads to their reserve power source. The subsequent residual transfer resulted in a loss of circulating water flow and subsequent loss of condenser vacuum. Condenser pressurization resulted in actuation of rupture disks on a LP Turbine Hood and one of the RFPT exhaust manifolds. An Unusual Event was declared based on indication of main turbine seal failure. RPV level and pressure were controlled using HPCI, RCIC and SRVs. The EDGs started as designed but were not required to supply electrical loads.
333 | 3331996014 | 1996-12-15 | QR6 | Manual Reactor Trip | [45 empty] | FitzPatrick | B | GE | PO | 36 | POWER LEVEL - 036%. On 12/15/96 at 0058 with the plant operating at approximately 36 percent power, a manual scram was initiated. At the time of the event the plant was in the process of performing post refuel outage startup/power ascension testing. The manual scram was initiated in anticipation of a potential loss of automatic reactor pressure control due to an identified Electro-Hydraulic Control (EHC) system fluid leak from number 4 turbine bypass valve (29BPV-4) actuator seal. The actuator seal, which was installed during the recently completed refuel outage, was replaced and satisfactorily retested prior to plant restart. Results of an engineering evaluation of the failed seal indicate that the primary actuator seal was most likely damaged during installation.
333 | 3331997001 | 1997-01-23 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | FitzPatrick | B | GE | PO | 100 | On January 23, 1997 at 2210 hours with the plant operating at 100 percent, power reduction was commenced due to potential loss of water inventory in the Circulating Water System's (CWS) intake bays. A high differential water level annunciator indicated fouling of the CWS traveling screens. Attempts to clean the screens resulted in the screens becoming inoperable due to shear pin failures. At 2224 hours, with power level reduced to approximately 57 percent, and following unsuccessful attempts to start the screens, a manual scram was initiated. <br /><br /> Cause of the event was a potential loss of CWS intake water due to restriction of flow through the three CWS traveling screens. A contributing cause was less than adequate work scheduling. <br /><br /> Actions taken included reviewing event lessons learned with plant personnel, revising Operating Procedure OP-4, "Circulating Water System", and evaluating the adequacy of the shear pins used on the screens.
333 | 3331997005 | 1997-05-25 | QR6 | Manual Reactor Trip | [45 empty] | FitzPatrick | B | GE | PO | 70 | On May 24, 1997 at 2102 hours, operators commenced a reactor shutdown from 100 percent power due to number three Main Turbine Control Valve (TCV-3) failing in the fully opened position. Power level was reduced and maintained at approximately 70 percent while unsuccessful attempts were made to close the valve. At 0456 hours on May 25, 1997, operators initiated a manual reactor scram followed by a manual turbine trip to support a reactor shutdown while maintaining reactor pressure control. Following the manual scram, a Primary Containment Isolation System (PCIS) Group II isolation occurred (Reactor Building Ventilation System isolation, and initiation of the Standby Gas Treatment System trains A and B) on low reactor water level. <br /><br /> The TCV failure was the result of a damaged valve spring can coupling. The cause for the damaged coupling was identified as a result of improperly installed bolting material. <br /><br /> Corrective actions included valve spring can coupling bolt replacement on the four TCVs and the four Combined Intermediate Valves (CIVs).
333 | 3331998004 | 1998-05-01 | QR6 | Manual Reactor Trip | [45 empty] | FitzPatrick | B | GE | PO | 100 | On 05/01/98, 12:32 (EDT) a manual reactor scram from approximately 100% power was initiated due to multiple control rod drift indications in the control room. It was subsequently determined that the rods had not drifted and the cause of the rod drift indications and alarm was a Rod Position Information System (RPIS) power supply failure. The Control Room Operators demonstrated conservative decision making when faced with the unexpected indications and inserted a manual reactor scram. Following the scram, six control rods did not immediately indicate "full in" and Emergency Operating Procedure EOP-3, "Failure to Scram" was entered. At 12:45, all rods were verified fully inserted and EOP-3 was exited. Emergency plan entry conditions were reviewed and no entry was required. An Equipment Failure Evaluation, including extent of conditions, was completed for the RPIS power supply failure. Corrective actions include a preventive maintenance evaluation for this and similar power supplies to determine appropriate preventive maintenance tasks and frequencies.
333 | 3331998008 | 1998-08-03 | QP4 | Partial Loss of Condensate Flow | [45 empty] | FitzPatrick | B | GE | PO | 70 | On 08/03/98, at 5:27 PM (EDT), an automatic reactor scram occurred while operating at_approximately 70% power due to low reactor pressure vessel (RPV) water level following a degradation in feedwater flow. The degradation of feedwater flow was due to an inadequate filling and venting operation for the "A" condensate pump during restoration of the pump from a maintenance activity. When the "A" condensate pump suction valve was partially opened the operating condensate pumps became air bound. This caused one of two operating condensate booster pumps to trip on low suction pressure. The reactor subsequently tripped automatically on low RPV water level. The plant responded as designed following the automatic scram and the transient response was bounded by previous analysis contained in the James A. FitzPatrick Final Safety Analysis Report. Corrective actions include a Post Transient Evaluation that was completed prior to start up, a correction to the filling and venting procedure for the condensate pumps, and an engineering evaluation and walkdown of the feedwater and condensate system to assess the affects of the resulting transient.
333 | 3331999010 | 1999-10-14 | QR5 | Turbine Trip | [45 empty] | FitzPatrick | B | GE | PO | 100 | On October 14, 1999 at 17:44, an automatic Main Turbine trip followed by a Reactor Scram occurred due to a short circuit between conductors in a control cable in the Main Generator anti-motoring protective relay circuit. (Figure 1). The plant was at 100% power at the time of the Main Turbine Trip. During the event the HPCI system tripped on overspeed. Corrective actions include repairs of the Main Generator anti-motoring circuit and repairs to the HPCI system.
333 | 3331999012 | 1999-11-05 | QR5 | Turbine Trip | [45 empty] | FitzPatrick | B | GE | PO | 83 | On 11/5/99, at 1051 hours with the mode switch in the “RUN” position and the plant operating at approximately 83 percent power during power ascension, an automatic Reactor scram occurred as a result of a Main Turbine trip. The Turbine trip initiation was a result of high water level trip signals from both Extraction Steam System Moisture Separator Reheater 31MS-1B and Extraction Steam System Moisture Separator Reheater Drain Tank 31TK-2B. The cause for the excessive water inventory in 31MS-1B and 31TK-2B was the combination of (1) a Feedwater Heater level transient during power ascension resulting in a closure signal to a Feedwater Heater control valve and (2) a failed pneumatic signal line on a 31TK-2B drain line control valve. The degraded line resulted in the drain line control valve failing in the closed position. Corrective actions include a Post Transient Evaluation that was completed prior to plant start up, an Equipment Failure Evaluation to determine the cause for the failed pneumatic line, and an extent of condition review to evaluate other equipment with potential similar failure characteristics.
333 | 3332000003 | 2000-04-01 | QL7 | Degraded condenser vacuum | [45 empty] | FitzPatrick | B | GE | PO | 25 | On April 1, 2000, with the reactor at approximately 25 percent power an automatic scram occurred due to a manual trip of the main turbine. Planned maintenance was in progress to repair a small main steam drain line pipe leak, which required the condenser air ejector recombiner to be removed from service. At approximately 17:04 when the recombiner was removed from service, the recombiner bypass valve, 01-107AOV-104, failed closed, isolating the condenser off gas system from the main condenser. This caused a lowering trend in condenser vacuum. Operators entered the associated Abnormal Operating Procedure AOP-31. At approximately 17:31 condenser vacuum had degraded to the "manual turbine trip region" contained in Figure 1 of AOP-31. The CRS assumed the reactor protection system turbine trip scram was bypassed, based on current power level, ordered a manual trip of the turbine. Upon initiation of the turbine trip an automatic reactor scram occurred from the turbine trip scram logic. The associated transient is bounded by analysis contained in the Final Safety Analysis Report. Corrective actions included repair of the failed valve, an Equipment Failure Evaluation, and evaluations of additional training required to improve some identified personnel performance errors.
333 | 3332003001 | 2003-08-14 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | FitzPatrick | B | GE | PO | 100 | On August 14, 2003 at 1611 hours, with the reactor operating at 100 percent power, a reactor scram occurred due to unstable conditions on the transmission grid causing rapid cycling of Turbine Control Valves (TCVs). This resulted in low turbine Electro-hydraulic Control System (EHC) oil pressure which caused a "Turbine Control Valve Fast Closure, EHC Oil Pressure - Low" Scram as instrumentation sensed conditions similar to a TCV fast closure - generator load rejection. A Main Turbine trip and generator trip followed approximately thirty-five seconds later, accompanied by a normal fast transfer of plant 4 kV busses to the offsite 115 kV supply. A subsequent loss of offsite power followed approximately two minutes later. Plant Emergency Diesel Generators (EDG) started and provided power to safety related plant loads. A cooldown was conducted using Safety Relief Valves, High Pressure Coolant Injection, and Reactor Core Isolation Cooling. MODE 4 was achieved on August 15, 2003 at 2220 hours. On August 29, 2003 at 1015 hours, during surveillance testing, the A EDG subsystem was determined to be inoperable due to out of tolerance no-load frequency, traceable to recovery from the August 14 event. A plant start-up had occurred subsequent to August 14, with an accompanying plant MODE change prohibited by Technical Specifications.
333 | 3332005005 | 2005-09-14 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | FitzPatrick | B | GE | PO | 100 | On September 14, 2005, at approximately 0213, with the plant operating at 100% power, an automatic reactor scram on low reactor water level occurred following a momentary loss of the Uninterruptible Power Supply (UPS) system. The power loss resulted in a lockout of the Reactor Feed Pump (RFP) controls, as designed. Following reset of the RFP controls, a level transient occurred causing reactor water level to lower, resulting in an automatic reactor scram on low reactor pressure vessel (RPV) water level (Level Ill). A Group 2 Primary Containment Isolation System (PCIS) isolation occurred, resulting in multiple system isolations. The Reactor Core Isolation Cooling system (RCIC) and the High Pressure Coolant Injection system (HPCI) auto initiated on "low-low" RPV water level (Level II). All systems operated as designed during and after the reactor scram. The level transient was caused by a RFP controller low output signal which is a design characteristic of the controller following a momentary loss of power. The operator did not verify the output signal prior to resetting the RFP control,which would have identified the low signal. Contributing to this human error was an inadequate abnormal operating procedure. As part of the corrective actions, the applicable procedure has been revised and the requirement to verify the controller output signal prior to resetting has been reinforced.There were no safety system functional failures or other safety consequences associated with this event.
333 | 3332007002 | 2007-09-12 | QR6 | Manual Reactor Trip | [45 empty] | FitzPatrick | B | GE | PO | 100 | On September 12, 2007, while the plant was operating at 100 percent power, operators inserted a manual reactor scram due to low intake flow caused by traveling water screen (TWS) blockage. All equipment responded as expected and the plant condition was stable in MODE 3, Hot Shutdown. While transitioning to Mode 4, the Reactor Protection System (RPS) automatically actuated when Reactor Pressure Vessel (RPV) level decreased to less than 177 inches above top of active fuel (TAV). This event was reported as NRC Event 43635 pursuant to 10CFR50.72(b)(2)(iv)(B) for RPS actuation (manual scram) (4 hour report) and 10CFR50.72(b)(3)(iv)(A) for specified system actuation (Group 2 PCIS isolations) (8 hour report). The cause of the manual scram was determined to be due to environmental debris induced overloading of the traveling screens, and the cause of the RPS signal was determined to be sluggish operation of the feed water startup flow control valve. The safety significance of this event is considered low and did not decrease the effectiveness of plant barriers from providing safety to the public. On October 28, 2007, while the root cause evaluation was in progress for the TWS blockage event, a similar event involving TWS screen blockage occurred that resulted in a manual scram (NRC Event 43752).
333 | 3332012007 | 2012-11-04 | QR5 | Turbine Trip | [45 empty] | FitzPatrick | B | GE | PO | 100 | On November 4, 2012, at 9:53 pm, with the plant operating at 100% power in Mode 1, the James A. FitzPatrick Nuclear Power Plant experienced a reactor scram. The scram was due to a failure of the main turbine emergency lockout valve (94SOV-LV) which caused the main turbine stop valves to begin to close. Once the main turbine stop valves reached 85% open, a reactor scram signal was generated. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the reactor protection system. Corrective actions included replacing the failed valve, testing the lockout circuit electrically, and shipping the failed valve offsite to have an equipment failure evaluation performed. There was no industrial or radiological safety significance associated with this event. The nuclear safety significance was minimal because all safety systems responded as designed when the scram signal was received.
333 | 3332012008 | 2012-11-11 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | FitzPatrick | B | GE | PO | 100 | An unplanned, automatic reactor scram occurred at 0355 on November 11, 2012, caused by a fire in the main transformer 71T-1A. All Reactor Protection Systems operated to shutdown the reactor without any complications. Offsite power transmission lines were Operable and onsite emergency power remained available during this event. At 0545 the emergency plan was entered by declaring a Notification of Unusual Event (HU 6.1). The fire was declared extinguished at 0632 and at 0801 the Notification of Unusual Event was exited. There was no release of radioactivity or personal injury. This event was caused by arcing; possibly originating by either a connection or coil failure internal to the transformer or by internal insulation breakdown or both. 71T-1A was replaced, tested, and returned to service.
333 | 3332016001 | 2016-01-23 | QL7 | Degraded condenser vacuum | [10 empty] | X | [28 empty] | X | [5 empty] | FitzPatrick | B | GE | PO | 89 | On January 23, 2016, James A. FitzPatrick Nuclear Power Plant (JAF) was ascending in power when screenwell water level started to lower. At 89 percent power, at 22:23, Operators began taking compensatory measures to reduce power and mitigate water level lowering. At 22:40, a manual scram was initiated.<br /><br /> The scram was complicated by a residual transfer that resulted in non-vital equipment trips. This event resulted in the manual actuation of the Reactor Protection System, High Pressure Coolant Injection, Reactor Core Isolation Cooling, Main Steam Isolation Valves and automatic actuation of Emergency Diesel Generators, Emergency Service Water, and containment isolations in multiple systems, reportable per 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> The lowering screenwell water level was caused by frazil ice blockage at the intake structure. The frazil ice stopped affecting screenwell water level after the manual scram. Corrective actions include strengthening mitigating actions in response to frazil ice. <br /><br /> The residual transfer was caused by lubrication hardening in the lower control valve assembly of the 71PCB-10042 breaker. Corrective actions included replacing or reworking the lower control valve assembly.
333 | 3332016004 | 2016-06-24 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | FitzPatrick | B | GE | PO | 100 | On June 24, 2016, at 1205, several 600V electrical busses lost power when James A. FitzPatrick Nuclear Power Plant was operating at 100% power. A fault in transformer 71T-5 caused a trip of circuit breaker 71-10340. Power was lost to 2 of 3 Reactor Building Closed Loop Cooling (RBCLC) pumps and 2 of 3 lube oil pumps for the Motor-Generator (MG) Set for 'A' Reactor Water Recirculation (RWR). The 'A' RWR pump tripped immediately causing reactor power to reduce to approximately 50%. The remaining RBCLC pump was inadequate to maintain the MG Set fluid drive oil temperature for the 'B' RWR pump so Operators initiated a manual scram at 1236. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> The power loss also affected Reactor Building Ventilation (RBV). This system supports the requirement of Technical Specification Surveillance Requirement 3.6.4.1.1 for a differential pressure in Secondary Containment. At the loss of RBV, Secondary Containment automatically isolated and the Standby Gas Treatment system was manually initiated. However, during this short transition the differential pressure requirement was not met. This report is being submitted per 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The apparent cause of the 71T-5 fault was inadequate preventative maintenance which allowed the transformer to remain in service beyond expected service life.
333 | 3332020001 | 2020-01-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | FitzPatrick | B | GE | PO | 38 | On January 31, 2020, an automatic scram occurred as a result of a main turbine trip on high Reactor Pressure Vessel (RPV) water level. The plant was at reduced power in preparation for maintenance activities. When the ‘A’ Reactor Feed Pump (RFP) was removed from service, the ‘A’ RFP discharge check valve (34FWS-4A) failed to immediately close resulting in a rapid increase in RPV level. A high RPV level trip signal resulted in the ‘B’ RFP trip and Main Turbine trip. <br /><br /> This event resulted in the automatic actuation of the Reactor Protection System and containment isolations in multiple systems, reportable per 10 CFR 50.73(a)(2)(iv)(A). When Secondary Containment automatically isolated, a differential pressure excursion momentarily exceeded Technical Specification limits, a condition reportable in accordance with 10 CFR 50.73(a)(2)(v)(C). <br /><br /> The cause of the event was determined to be due to a failure of the A’ RFP discharge check valve (34FWS-4A) to close. <br /><br /> There were no actual safety consequences as a result of this event. The ‘B’ RFP was restored to service and the condensate and feedwater systems remained available for post-scram recovery.
334 | 3341987001 | 1987-01-11 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 1/11/87, WITH THE PLANT AT 100% POWER, OPERATIONS PERSONNEL WERE PERFORMING THE MAIN TURBINE PEDESTAL CHECKS. DURING THE PERFORMANCE OF THE THRUST BEARING OIL TRIP DEVICE TEST, AT 0039 HOURS, A TURBINE TRIP OCCURRED. A REACTOR TRIP WAS INITIATED BECAUSE POWER WAS GREATER THAN 10 PERCENT AND THE P-9 PERMISSIVE WAS IN EFFECT. OPERATIONS PERSONNEL FOLLOWED THE APPLICABLE EMERGENCY PROCEDURES AND STABILIZED THE PLANT IN HOT STANDBY. THE CAUSE OF THE TURBINE TRIP WAS ATTRIBUTED TO LOW AUTO STOP OIL PRESSURE. TO MISINTERPRETATIONS OF THE PRECAUTIONS IN THE SURVEILLANCE PROCEDURE. THE OPERATORS HAVE BEEN COUNSELLED AND THE SURVEILLANCE PROCEDURE WILL BE REVISED TO PROVIDE ADDITIONAL GUIDANCE. ON 1/11/87, DURING THE PLANT RECOVERY/STARTUP, THE REACTOR WAS TAKEN CRITICAL AT 1258 HOURS AND ENTERED THE POWER OPERATION MODE AT 1445 HOURS. ON 1/12/87 AT 1000 HOURS, IT WAS DISCOVERED THAT THE POWER RANGE LOW POWER REACTOR TRIP SETPOINT WAS NOT VERIFIED OPERABLE IN ACCORDANCE WITH TECHNICAL SPECIFICATION 4.3.1.1.2.B, PRIOR TO ENTERING THE POWER OPERATION MODE. THE MISSED SURVEILLANCE WAS ATTRIBUTED TO PROCEDURE DEFICIENCIES. THE PROCEDURES USED DID NOT REQUIRE THE VERIFICATION OF THE POWER RANGE LOW POWER SETPOINT AND HAVE SUBSEQUENTLY BEEN REVISED TO INCLUDE THIS VERIFICATION.
334 | 3341987002 | 1987-02-07 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | POWER LEVEL - 100%. THE UNIT WAS AT 100% POWER ON 2/7/87 WHEN, AT 0201 HOURS, STEAM GENERATOR LOW LEVEL ANNUNCIATORS WERE RECEIVED FOR ALL THREE GENERATORS. WITHIN FIVE (5) SECONDS, A REACTOR TRIP OCCURRED ON LO-LO LEVEL IN THE 'C' GENERATOR, FOLLOWED BY A PRESSURIZER POWER OPERATED RELIEF VALVE (PORV) OPENING FOR 1.4 SECONDS. PLANT OPERATING PERSONNEL IMMEDIATELY IMPLEMENTED EMERGENCY OPERATING PROCEDURE E-0, REACTOR TRIP OR SAFETY INJECTION, AND STABILIZED THE PLANT IN HOT STANDBY AT 0207 HOURS. ALL PLANT SAFETY SYSTEMS PERFORMED AS DESIGNED. SUBSEQUENT INVESTIGATIONS TRACED THE FAULT TO A COMPARATOR CARD IN THE ELECTRO HYDRAULIC CONTROL (EHC) SYSTEM, MANUFACTURED BY WESTINGHOUSE, WHICH CAUSED A SPURIOUS ACTUATION OF THE OVERSPEED PROTECTION CONTROLLER. THIS ACTUATION RESULTED IN A TURBINE RUNBACK AS THE OVERSPEED SETPOINT DRIFTED LOW. THE RUNBACK INCREASED STEAM HEADER PRESSURE WHICH CAUSED STEAM GENERATOR LEVELS TO SHRINK TO THE LO-LO REACTOR TRIP SETPOINT. WITH THE ROD CONTROL SYSTEM IN MANUAL (NORMAL OPERATION FOR BEAVER VALLEY 1), THE PRIMARY TO SECONDARY ENERGY IMBALANCE RESULTED IN A PRIMARY PLANT HEATUP AND PRESSURIZATION WHICH OPENED THE PRESSURIZER PORV FOR 1.4 SECONDS. THE COMPARATOR CARD WAS REPLACED AND ALL EHC TESTING ON THE FOLLOWING STARTUP WAS PERFORMED SATISFACTORILY.
334 | 3341987012 | 1987-06-01 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 95 | POWER LEVEL - 095%. ON 6/1/87, WITH THE STATION AT 95% REACTOR POWER, A LOW ELECTRO-HYDRAULIC CONTROL (EHC) FLUID PRESSURE CONDITION OCCURRED. AN INVESTIGATION REVEALED THAT THE AUTO STOP OIL (ASO)/EHC INTERFACE VALVE WAS LEAKING BY. TROUBLESHOOTING ACTIVITIES ON THE MAIN TURBINE PEDESTAL TRIP BLOCK WERE INITIATED TO IDENTIFY THE CAUSE OF THE LOW ASO PRESSURE, AND IT WAS DETERMINED THAT THE ASO DRAIN VALVE, IN THE PEDESTAL TRIP BLOCK, WAS NOT FULLY SHUT. TO ALLOW MANIPULATION OF THE ASD DRAIN VALVE, THE MANUAL OVERSPEED TRIP TEST LEVER WAS PLACED IN THE TEST POSITION. SEVERAL ATTEMPTS TO SHUT THE ASO DRAIN VALVE WERE UNSUCCESSFUL, SO IT WAS DECIDED TO OPEN THE ASO DRAIN VALVE TO SWEEP THE SEAT OF SUSPECTED DEBRIS. UPON OPENING, FURTHER DEGRADATION OF THE LOW ASO PRESSURE CONDITION OCCURRED INITIATING THE LOW ASO TURBINE TRIP SETPOINT AND DRAINING EHC FLUID. THIS CAUSED A TURBINE TRIP AND A RESULTANT REACTOR TRIP (P-9 INTERLOCK) AT 1137 HOURS. THE ROOT CAUSE FOR THIS EVENT WAS ATTRIBUTED TO THE AUTO STOP OIL DRAIN VALVE NOT BEING FULLY SHUT. THE PEDESTAL TRIP BLOCK WAS DISASSEMBLED AND THE AUTO STOP OIL DRAIN VALVE WAS INSPECTED. MINOR MECHANICAL ADJUSTMENTS WERE MADE WHICH ALLOWED THE ASO DRAIN VALVE TO FULLY CLOSE. THERE WERE NO SAFETY IMPLICATIONS AS THE PLANT WAS PLACED IN A STABLE CONDITION (HOT STANDBY) BY 1236 HOURS.
334 | 3341987013 | 1987-06-09 | QR3 | Reactivity Control Imbalance | [45 empty] | Beaver Valley 1 | P | WE | PO | 33 | POWER LEVEL - 033%. AT 0305 HOURS ON 6/9/87, WITH THE STATION AT 33% POWER, IT WAS NOTICED THAT 4 CONTROL RODS HAD ANALOG POSITION INDICATION DEVIATING MORE THAN 12 STEPS FROM THEIR BANK DEMAND COUNTER. PRIMARY VOLTAGE READINGS TAKEN IN ACCORDANCE WITH TECH SPECS CONFIRMED MISALIGNMENT OF ONE ROD. FURTHER READINGS, TAKEN AT 0420 HOURS, INDICATED A TOTAL OF SIX TECH SPEC 3.1.3.5 WAS EXCEEDED AND TECH SPEC 3.0.3 WAS APPLICABLE. ACTION WAS INITIATED TO PLACE THE PLANT IN HOT STANDBY; HOWEVER, NO POWER REDUCTION WAS COMMENCED AS THE RODS WERE SUCCESSFULLY REALIGNED BY 0915 HOURS. AT 1345 HOURS, 6/9/87, AN AUTOMATIC REACTOR TRIP OCCURRED AT 35 PERCENT POWER DUE TO HIGH POWER RANGE NEGATIVE FLUX RATE. THERE WERE NO SAFETY IMPLICATIONS, SINCE THE REACTOR PROTECTION SYSTEM FUNCTIONED AS DESIGNED AND THE PLANT WAS STABILIZED IN HOT STANDBY AT 1405 HOURS. A FIRING CIRCUIT CARD IN THE ROD CONTROL POWER CABINET, WHICH ALSO EXPLAINS THE MISALIGNMENT. THIS CARD AND THREE OTHERS WERE REPLACED. SINCE TEMPERATURE IN THE AREA CONTRIBUTED TO CARD DEGRADATION, TEMPORARY COOLING WAS PROVIDED. THE REACTOR WAS TAKEN CRITICAL AT 0957 HOURS ON 6/10/87. A MODIFICATION TO THE EXISTING AREA VENTILATION SYSTEM WILL BE IMPLEMENTED TO PREVENT RECURRENCE OF THESE EVENTS.
334 | 3341988007 | 1988-06-07 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | On 6/7/88, at 2155 hours, with Unit I at 100 percent reactor power, an operator inadvertently tripped the 'C' Reactor Coolant Pump Breaker while performing an air compressor test. The loss of the RCP caused a Reactor Trip on low flow in a single loop. An excessive cooldown due to a combination of design features led to a low pressurizer pressure safety injection 29 seconds after the trip. These factors include modifications to the Main Feedwater Regulation Valves to increase their flow and stagnant flow in a 'C' loop instrument manifold. The operators followed the plant's emergency procedures to stabilize the plant in Hot Standby. An Unusual Event was declared at 2206 hours and terminated at 2400 hours. Several minor problems were noted during the trip. After equipment repair, the reactor was taken critical at 2200 hours on 6/8/88. Design changes to the main feedwater regulating valves and instrument manifolds will be made to prevent similar excessive cooldowns. The root cause of this event was a cognitive error on the part of a non-licensed operator who, through inattention to labeling, did not notice that he was tripping the wrong breaker. The operator was disciplined, and this event will be reviewed by all Operations personnel to emphasize the lessons learned.
334 | 3341988008 | 1988-06-09 | QP5 | Excessive Feedwater Flow | [45 empty] | Beaver Valley 1 | P | WE | PO | 17 | On 6/9/88, a unit startup was in progress with the main feedwater regulating valves closed and the bypass feedwater regulating valves (BFRV) being controlled in auto. The level in the 'C' BFRV was taken to stop the level increase. At 0149 hours, two of the three level channels in the 'C' steam generator reached their high-high level setpoint (75%) causing a turbine trip, feedwater isolation and a trip of the operating main feedwater pump (FW-P-1B). The motor driven auxiliary feedwater pumps (FW-P-3A and 3B) auto-started on the trip of the main feedwater pump. The 'B' auxiliary feedwater pump was subsequently shutdown. Before resetting the feedwater isolation signal, the 'A' main feedwater pump was started and then the 'A' auxiliary feedwater pump was shutdown. At 0153 hours, two of the three level channels in the 'A' steam generator reached their low-low setpoint (12%) causing a reactor trip. The turbine driven auxiliary feedwater pump (FW-P-2) started followed by the motor driven auxiliary feedwater pumps. There were no safety implications resulting from this event because all protection features (turbine trip, feedwater isolation, reactor trip, auxiliary feedwater pumps start) actuated properly in accordance with valid actuation signals.
334 | 3341988009 | 1988-06-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Beaver Valley 1 | P | WE | PO | 13 | On 6/11/88, during a Reactor Startup, the Main Feedwater Regulating Valves (MFRVs) automatic Steam Generator level control was unstable. This caused Steam Generator levels to increase to their Hi-Hi Level setpoint on two occasions, initiating Feedwater Isolation (FWI) signals, as per design. The FWIs shutdown/isolated the Normal Feedwater System and actuated the Auxiliary Feedwater System. After the first event, operators successfully restored Normal Feedwater. After the second event, while attempting to restore Normal Feedwater, the breaker for the 'B' Main Feed Pump's discharge valve tripped while the valve was opening, degrading Feed flow. Operators restored Normal Feedwater flow with the 'A' Main Feed Pump. This action was insufficient to prevent the 'A' Steam Generator level from decreasing to its Lo-Lo Level/Reactor Trip Setpoint. Operators stabilized the plant using the Reactor Trip response procedure. The Steam Generator level instabilities were caused by: 1) using the MFRVs to control level without having the Turbine/extraction steam inservice, 2) improper condenser steam dump response. A Special Operating Order has been issued to prevent the above configuration. The affected steam dump valves have been isolated. The Main Feed Pump discharge valve functioned properly after its breaker was reset. Its failure is under further investigation. The erratic Steam Generator level control and degraded Normal Feedwater Flow events are bounded by UFSAR analysis.
334 | 3341989001 | 1989-01-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Beaver Valley 1 | P | WE | PO | 90 | On 1/17/89, post-maintenance testing of the "C" Bypass Feedwater Regulating Valve (BFRV) was in progress. The Reactor Operator reviewed the test procedure and located the step that stroked the "C" BFRV. The Reactor Operator requested the Plant Operator to perform this step and showed him the procedure, inadvertently pointing to the wrong step. The Plant Operator read the step indicated by the Reactor Operator, noted the breaker number in that step and went to open it. This resulted in the inadvertent de-energization of the "A" Main Feedwater Regulating Valve (MRFV). The "A" MFRV closed, isolating feedwater to the "A" Steam Generator, resulting in a Reactor Trip. The Auxiliary Feedwater pumps started and restored level to the "A" Steam Generator. The operators stablized the plant using the Reactor Trip Response procedures. The involved operators have been counseled concerning this event. There were no safety implications due to this event. This event is bounded by Beaver Valley UFSAR Safety Analysis section 14.1.8, Loss of Normal Feedwater.
334 | 3341989002 | 1989-02-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Beaver Valley 1 | P | WE | PO | 90 | On 2/13/89, the "C" Main Feedwater Regulating Valve (MFRV) stroked partially closed during Power Operation. This resulted in a Feedwater Flow/Steam Flow Mismatch. Operators, unsuccessfully attempted to manually reopen the valve. "C" Steam Generator level decreased to its Low Level setpoint causing a Reactor Trip due to Feed/Steam flow mismatch , coincident with the Low Level. Auxiliary Feedwater actuated and, restored level in the "C" Steam Generator. Operators stabilized , the plant using the Reactor Trip Response procedure. Investigation determined that the "C" MFRV elector-pneumatic transducer had failed, preventing the valve from opening beyond 25%. The transducers on all three MFRVs were changed out. The station is revising its Preventive Maintenance program to periodically change out these transducers. There were no safety implications due to this event. This event is bounded by UFSAR Safety Analysis, "Loss of Normal Feedwater", Section 14.1.8.
334 | 3341989007 | 1989-05-18 | QR7 | Other Reactor Trip (Valid RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Beaver Valley 1 | P | WE | PO | 90 | On 5/18/89, with the Unit in Power operation (Operating Mode 1) at 90 percent reactor power, a breaker labeling verification evolution was in progress. During this verification, at 0232 hours, the electrical supply breaker to the Anticipated Transient Without Scram (ATWS) Mitigating System Actuation Circuitry (AMSAC) panel was accidently opened. This loss of power to AMSAC resulted in a loss of turbine impulse pressure signal to the Steam Dump Control System, opening steam dumps valves, and lowering steam line pressure. This caused a low steam line pressure rate compensated safety injection signal and a reactor trip, at 0235 hours. The operators Utilized the Emergency Operating Procedures to stabilize the plant in Hot Standby (Operating Mode 3). An Unusual Event was declared at 0235 hours and terminated at 0310 hours. The root cause for this event was a design deficiency. This deficiency was corrected by modifying the process instrumentation circuitry to make the impulse pressure channel signals (control) independent of AMSAC. There were no safety implications to the public as a result of this event. The AMSAC system is a non safety related backup to the reactor protection system. The AMSAC system is designed to assure that the reactor coolant system will not be overpressurized during an ATWS event.
334 | 3341989018 | 1989-12-27 | QR3 | Reactivity Control Imbalance | [45 empty] | Beaver Valley 1 | P | WE | PO | 29 | On 12/27/89, at 0001 hours, the Unit was in Power Operation Operating Mode 1) at 29% following the initial startup from the refueling outage. The 1A Rod Drive motor Generator (RDMG) set was in operation and the 1B RDMG set was out of service awaiting post maintenance testing. Outage maintenance activities on the 1B RDMG set included bearing replacement and breaker trip checks. A Caution Tag had been placed on the 1B RDMG set output breaker stating that trip checks were still required. At 0121 hours, a reactor trip occurred on Power Range High Negative Rate Flux Trip. The operators stabilized the plant in Hot Shutdown (Operating Mode 3) utilizing Emergency Operating Procedures E-0 and ES-0.1. The cause for the trip was due to a trip of the 480 Volt AC feeder breaker (1A5) to the 1A RDMG sets. Upon a loss of power to the 1A RDMG set, the control rods dropped into the core causing a negative rate reactor trip. Electrical Maintenance was requested to investigate the cause of the feeder breaker trip. There were no safety implications as a result of this event. The Updated Final Safety Analysis Report discusses similar events of this type in Section 14.1.3 "Rod Cluster Control Assembly Misalignment".
334 | 3341990007 | 1990-03-30 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | On 3/30/90 at 1541 hours, with the Unit in Power Operation at 100% reactor power, alarms indicating a Loop "C" steam flow/feedwater flow mismatch, followed by a "C" steam generator (SG) level deviation were received. The operators noted closure of the "C" Main Feedwater Regulating Valve, FCV-FW-498. The operator tried to manually open FCV-FW-498, however, the valve would not respond. At 1544 hours, a reactor trip on "SG "C" Low Level & Feedwater Flow Low" occurred. Control Room personnel entered Emergency Operating Procedures, E-0 and ES-0.1, to stabilize the plant in Hot Standby. The cause for the reactor trip was the closure of FCV-FW-498, in response to insufficient instrument air pressure supplying the valve positioner. Air pressure had degraded due to moisture in the filter in the instrument air regulator for the valve positioner. High moisture was present due to the instrument air dryer being unavailable. The moisture in the instrument air system has been removed and the instrument air dryer has been returned to service. There were no safety implications as a result of this event. The plant systems responded as designed (all rods inserted, turbine trip occurring and auxiliary feedwater initiating on low SG level), with the exception of FCV-FW-498, to place the plant in Hot Standby. This event is bounded by Updated Final Safety Analysis Report, Section 14.1.8.
334 | 3341991022 | 1991-07-20 | QP5 | Excessive Feedwater Flow | [45 empty] | Beaver Valley 1 | P | WE | PO | 21 | On 7/20/91, the station was at 21 percent power and preparing to increase load. The operators placed the Main Feedwater Regulating Valves (MFRV) in service using the Station Startup Procedure. When the C MFRV was placed in operation, it opened rapidly, causing C steam generator level to increase to the Hi-Hi Level/Feedwater Isolation (FWI) setpoint. The main turbine and feedpump tripped and the FWI valves closed. Level in the A steam generator decreased to the Lo-Lo Level/Reactor Trip setpoint. All control rods automatically fully inserted. Auxiliary feedwater initiated in response to the main feedpump trip and Lo-Lo steam generator levels. One auxiliary feed recirculation valve failed to open, but did not affect auxiliary feed operation. Investigation found the control circuit for the C MFRV had been mis-wired during a recent control loop calibration. The control circuit was rewired and the other MFRV circuits were checked and verified to be correctly wired. A Human Performance Enhancement System evaluation of this event has been initiated. This event will be covered in Instrumentation personnel training. There were no safety implications due to this event. A FWI due to Hi-Hi steam generator level and a reactor trip due to Lo-Lo steam generator level are bounded by Feedwater System Transient analyses in Beaver Valley's UFSAR sections 14.1.8 and 14.1.9.
334 | 3341991023 | 1991-07-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Beaver Valley 1 | P | WE | PO | 30 | On 7/26/91 at 1930 hours in operating Mode 1 at 30 percent power, the unit began to experience turbine governor control oscillations from the turbine Electro-Hydraulic Control (EHC) system. Between 1930 hours 7/26/91 and 0655 hours 7/27/91, three load rejections of between 100 and 150 MWe were experienced. Operators stabilized the plant after each load rejection. EHC troubleshooting by plant personnel and contractor technicians began after the first occurrence. After the third occurrence, station management decided to remove the turbine from service in accordance with the Abnormal Operating Procedure for a load rejection. During preparations for shutdown, a fourth load rejection, accompanied by erratic turbine governor valve control, occurred. The reactor tripped at 0713 hours, due to a low level coincident with a low feedwater flow in the "B" steam generator. Control room personnel stabilized the plant in Operating Mode 3. The spurious governor valve signals were due to a faulty circuit card in the EHC system. There were no safety implications to the public as a result of this event. All shutdown and control rods inserted, and all plant systems responded as designed.
334 | 3341992009 | 1992-10-09 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Beaver Valley 1 | P | WE | PO | 90 | On 10/09/92, Unit 1 was operating at Power Operation at 90 percent reactor power. At 1654 hours, the 1A reactor coolant pump (RC-P-1A) tripped on an indicated electrical ground fault. The trip of RC-P-1A generated a one of three reactor coolant pump low flow reactor trip. The reactor trip signal generated a turbine trip signal. operations personnel performed the Emergency operating Procedures and stabilized the plant in Hot Shutdown at 1709 hours. Auxiliary Feedwater initiated as expected due to the low-low steam generator levels following the reactor trip. At 1822 hours, the Nuclear Regulatory Commission was notified of the event using the Emergency Notification System. The cause of the trip was a failed top coil in the stator for RC-P-1A. The plant was placed in Cold Shutdown and the stator for RC-P-1A was removed and repaired. There were no safety implications as a result of this event. The reactor trip signal actuated as designed on a low flow condition in one reactor coolant loop. Auxiliary feedwater actuated as designed and expected on the low steam generator levels following the reactor trip.
334 | 3341993013 | 1993-10-12 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Beaver Valley 1 | P | WE | PO | 100 | On 10/12/93 Unit 1 was operating at 100 percent power and Unit 2 was in a refueling outage with all fuel removed from the reactor vessel. At 1507 hours, Unit 1 experienced a large loss of offsite load when ten offsite feed breakers in the Beaver Valley switchyard opened as a result of an inadvertent underfrequency system separation actuation. The load reduction caused the Unit 1 turbine to trip on mechanical overspeed and resulted in a High Flux Rate Reactor Trip. The opening of the switchyard feed breakers and the resultant Unit 1 generator trip resulted in a loss of offsite power to Units 1 and 2. Both Unit 1 Emergency Diesel Generators (EDGs), and the required Unit 2 EDG, started and supplied their required loads. Unit 1 Auxiliary Feedwater actuated due to Low-Low Steam Generator Levels resulting from the Reactor Trip. Unit 1 was stabilized using the Emergency Operating Procedures. Following realignment of switchyard breakers, offsite power was restored to both units by 1522 hours. On 10/13/93, following a Unit 1 containment inspection, a Reactor Coolant System Pressure Boundary Leak was discovered on the Loop 1A cold leg vent valve RC-27. A Technical Specification Required cooldown was initiated and Mode 5 was entered at 0304 hours on 10/14/93.
334 | 3341994005 | 1994-06-01 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | On 6/01/94 at 1455 hours, an insulating bushing failure on the Unit 1 Main Unit Transformer initiated an immediate generator/turbine trip followed by a subsequent reactor trip. The transformer fault initiated a voltage disturbance on the electrical grid which caused an inadvertent protective relay actuation on a circuit monitoring the 138 kilovolt (KV) AC line supplying the Unit 2 System Station Service Transformer (SSST)2A. Unit 2 4KV AC busses were being supplied by the offsite electrical grid. The loss of the 2A SSST resulted in the actuation of two reactor coolant pump underfrequency protective relays on two of the 4KV AC busses. This initiated a Unit 2 reactor trip. Both Units were stabilized in Hot Standby. The cause for this event was a single-phase insulating bushing failure on the Unit 1 Main Unit Transformer, which initiated a voltage disturbance on the electrical grid which affected Unit 2. Corrective actions have been initiated at both Units to address identified concerns. There were no safety implications as a result of this event. The reactor protection systems at both Units actuated as designed to place the reactors in safe shutdown conditions (Hot Standby). Engineered Safety Features systems actuated as required upon receipt of the initiation signals.
334 | 3341994008 | 1994-07-19 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | On July 19, 1994 at 1610 hours, with Unit 1 operating at 100% power, an insulating bushing external flash-over on the Unit 1 Main Unit Transformer initiated an immediate Unit 1 generator/turbine trip followed by subsequent Unit 1 reactor trip. The flash-over of the insulating bushing on the Main Unit Transformer occurred during a transformer fire protection system actuation. Water spray from the fire protection nozzles allowed flash-over from the 'C' phase bushing to its base and grounded fire protection piping and conduit beneath the bushing. This damaged the bushing, caused protection relays to isolate the transformer from the electrical grid, and initiated a generator/turbine trip. The unexpected fire protection system actuation that initiated this event occurred when heat detectors sensed conditions that exceeded their actuation setpoint, even though no fire protection system actuation was required. The suspect heat detectors were subsequently tested and verified to be actuating prematurely. Actions have been implemented to improve main transformer fire protection compatibility with the high voltage transformer application. There were no safety implications as a result of this event. The reactor protection system actuated as designed. The Engineered Safety Feature Systems actuated as required. This report is being submitted in accordance with 10CFR50.73.a.2.iv.
334 | 3341996008 | 1996-05-31 | QR8 | Spurious Reactor Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | POWER LEVEL - 100%. On May 31, 1996, Unit 1 reactor tripped due to an inadvertent turbine trip signal generated during solid state protection system testing. Both reactor trip breakers opened and all control rods fully inserted. All auxiliary feedwater pumps automatically started as designed on low-low steam generator water level. The 1B first point feedwater heater relief valve opened and did not immediately reclose due to a combination of setpoint drift and internal debris. automatically started, but was not required to load, in response to a momentary undervoltage condition on the B train emergency bus. Both emergency busses remained energized at all times. Post-trip review showed that the Anticipated Transient Without Scram Mitigating System Actuation Circuitry (AMSAC) did not function as expected due to a design deficiency, and the main generator trip and automatic fast bus transfer actuated early due to a timer setpoint drift. At the time of the occurrence, Unit 1 was in Mode 1, operating at 100 percent power.<br /><br /> A comprehensive investigation has shown that the most likely cause of this trip was a test circuit that was applying more test current than the amount actually required to test this solenoid coil. Corrective actions include performing a modification which will reduce the test current for this circuit to the lowest practical value.
334 | 3341997005 | 1997-03-19 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | On March 19, 1997, at approximately 0606 hours, while operating at 100% nominal power, Beaver Valley Power Station (BVPS) Units 1 and 2 experienced simultaneous reactor trips due to the opening of the output breakers for both units. The event was initiated by an inadvertent operation of the Bus Backup Timer relay on the #3-345 KV bus in response to a phase to ground fault which occurred on the Ohio Edison system's Mansfield-Hoytsdale 345 KV line. An Emergency Notification System (ENS) report was made pursuant to the requirements of 10CFR50.72(b)(2)(H) at 0922 hours on March 19, 1997. This event is also reportable pursuant to the requirements of 10CFR50.73(a)(2)(i) and 10CFR50.73(a)(2)(iv). <br /><br /> Operations responded to the dual unit trip by entering the appropriate plant Emergency Operating Procedures (EOPs). Stabilization of Unit 1 was completed at approximately 0608 hours on March 19, 1997, with the mitigating equipment operating in the expected manner to control the transient. Unit 1 Emergency Diesel Generator (EDG) EE-EG-1 started due to momentary undervoltage on 4 KV emergency bus AE, but was not required to load, since bus AE did not lose power. Unit 1 EDG EE-EG-2 did not start and was conservatively declared inoperable as of 0606 hours on March 19, 1997, until testing was completed which demonstrated that the undervoltage condition on bus DF was of insufficient duration to start EDG EE-EG-2. Both Unit 1 EDGs functioned as designed. <br /><br /> Stabilization of Unit 2 was completed at approximately 0610 hours on March 19, 1997, with the mitigating equipment operating in the expected manner to control the transient with the exception of "B" Steam Generator Auxiliary Feedwater (AFW) flow indicating lower than normal. Subsequent investigation indicated that this was due to the concurrent event failure of a check valve in the "B" AFW injection header. The "B" AFW injection header was declared inoperable at 1206 hours on March 19, 1997, and, pursuant to the requirements of Technical Specifications (TS), Unit 2 commenced a boration and cooldown towards Mode 4 at 1731 hours on March 19, 1997. An update to the ENS notification pursuant to the requirements of 10CFR50.72(b)(1)(i)(A) was made at 1302 hours. Unit 2 entered Mode 4 at 1731 hours on March 19, 1997. An evaluation of the AFW check valve failure pursuant to the requirements of 10CFR21 was completed April 24, 1997. ENS Notification of 10CFR21 reportability was made at 1403 hours. <br /><br /> The root cause of the dual unit trip event was inadequate implementation of design specifications and design review which resulted in incorrect wiring between the Unit 2 Static Breaker Failure Unit Relay and its associated Static Relay Unit Bus Backup Timer. Both units were safely shut down in accordance with the applicable procedures. There were no implications to the health and safety of the public as a result of this event.
334 | 3341997025 | 1997-08-07 | QP5 | Excessive Feedwater Flow | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | On August 7, 1997, at 2018 hours, Beaver Valley Power Station Unit 1 was in Mode 1 at 100% power when the unit experienced an automatic turbine trip, reactor trip and feedwater isolation (FWI). The feedwater regulating valve for "A" steam generator (S/G) failed open during the replacement of a resistor block in the S/G level control circuit by Instrumentation and Controls (I&C) technicians. The spurious feedwater regulating valve opening resulted in a rapid rise in S/G level. When Control Room Operators attempted to take manual control of the valve, it would not respond.<br /><br /> When 2 out of 3 level channels on the "A" S/G reached the Hi-Hi setpoint, a full FWI was generated, which also tripped the turbine. The FWI secured both main feedwater pumps and closed the feedwater isolation valves. The turbine trip initiated a reactor trip at 2018 hours. The Control Room crew responded by implementing the required emergency operating procedure (EOP) for reactor trip. S/G level shrinkage from the secondary pressure rise resulted in the expected automatic start of all three auxiliary feedwater pumps. Approximately 30 seconds after the turbine trip, the main generator tripped and a fast bus transfer to the system transformers occurred. The emergency diesel generators started automatically due to a transient bus undervoltage condition, but load shedding and sequencing of loads onto the emergency buses was not required. The reactor trip EOP was exited approximately 3 minutes after the trip and the unit was stabilized and placed in a safe, controlled shutdown condition with no safety implications to the health and safety of the public. <br /><br /> At 2220 on August 7, 1997, a four hour non-emergency notification was made pursuant to the requirements of 10CFR50.72(b)(2)(ii). This report is being made pursuant to the requirements of 10CFR50.73(a)(2)(iv). <br /><br /> An Event Response Team was formed on August 8, 1997 to investigate the reactor trip. The ERT determined that I&C and Operator actions were correct and did not cause the trip. The root cause of the trip was determined to be the existence of excess solder on a circuit card in the S/G feedwater flow control module. The excess solder came in contact with the module chassis, creating an internal ground on the feedwater control loop. Ground current initiated a full open demand signal to the "A" main feedwater regulating valve and also prevented operators from taking manual control of the valve. A new module was installed to replace existing S/G feedwater flow control module FC-FW-478 and was demonstrated to function properly via post maintenance testing on August 9, 1997.
334 | 3341998028 | 1998-08-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Beaver Valley 1 | P | WE | SU | 20 | On 8/11/98 at about 1512 hours, while placing Unit 1 'A' Steam Generator (SG) feedwater (FW) flow control valve FCV-FW-478 into service, SG level decreased and an automatic reactor trip at about 20% power occurred due to SG low level (25%) coincident with a SG steam/feed flow mismatch. Prior to this event, the transmitter bistables of the SG Main Steam (MS) Channel IV flow indicator P-MS-475 had been manually tripped to comply with Technical Specifications due to downscale indication. Following the reactor trip, emergency operating procedures were entered and the Unit was stabilized. Investigation has determined, the root causes of this event are cognitive error (inadequate awareness) by the involved licensed and non-licensed shift operating personnel to fully recognize the consequences of tripping the F-MS-475 transmitter bistables and inadequacy of the procedure 1OM-52.4A for placing FCV-FW-478 into service. Event contributors: incomplete shift briefing following the decision to trip the F-MS-475 bistables, inadequate instrument failure (IF) procedure 1OM-24.4.IF for FMS-475, and a station decision to continue with plant startup based on inadequate expectations for SG level control during FW control transfer. F-MS-475 was repaired and returned to service. 1OM-52.4A has been revised. The adequacy of existing IF procedures will be evaluated to identify any required changes.
334 | 3341999001 | 1999-01-23 | QL7 | Degraded condenser vacuum | [45 empty] | Beaver Valley 1 | P | WE | PO | 73 | At approximately 1024 hours on 1/23/99, the Unit 1 Reactor was manually tripped from approximately 73% power, as a conservative and proactive step in response to continuing degradation of Main Condenser parameters. The Reactor control rods fully inserted and plant systems operated as expected. Emergency Operating Procedures were entered, the Unit was stabilized, and station recovery from the Reactor trip was satisfactorily completed. NRC 4-hour notification of this event was made, per 10 CFR 50.72(b)(2)(ii), at approximately 1251 hours (same day). The degraded Main Condenser parameters resulted from elevated air in-leakage through the valve seat of the closed outlet isolation valve of V Main Condenser waterbox and into the Cooling Tower pumps' suction piping. This resulted from eliminating the water seal over the waterbox outlet valve seat during routine waterbox maintenance due to failure of the on-shift operating crew to maintain adequate awareness of changes which altered level in the waterbox, with a direct contributor of procedure inadequacy. As part of corrective actions to this event, Operations Shift briefings were conducted, an Operations communication and written instructions to Maintenance were provided, and the procedure for isolating waterboxes was revised.
334 | 3341999010 | 1999-09-06 | QR6 | Manual Reactor Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | On September 6, 1999 with the Beaver Valley Power Station (BVPS) Unit No. 1 running at 100% power, the following four alarms were received at 1722: Generator Field Forcing, Generator Field Overcurrent, Voltage Regulator Firing Circuit #1 Blown Fuse/Power Loss, and Voltage Regulator Firing Circuit #2 Blown Fuse/Power Loss. Control room operators observed the main generator power factor, VAR and current meters to be fluctuating rapidly above and below normal values. The above four alarms then cleared and reoccurred within approximately two seconds. These alarms continued to clear and reoccur on an approximate two second frequency. The reactor was manually tripped 18 seconds after the receipt of the initial alarm. The control room operators followed station procedures to recover from a (manual) reactor trip. Safety related systems functioned properly following the reactor/turbine trip and the Unit was stabilized in hot standby conditions. This is an event that resulted in a manual actuation of the Reactor Protection System (RPS) and an automatic actuation of the Auxiliary Feedwater System which is an Engineered Safety Features System. These two actuations are reportable pursuant to 10CFR50.73(a)(2)(iv). A definitive root cause for this event could not be identified. However, the apparent cause of the event is an electronic circuit open/fault in the Voltage Regulator Logic Drawer of the Main Unit Generator. There were minimal safety implications to the health and safety of the public.
334 | 3342000005 | 2000-04-17 | QL7 | Degraded condenser vacuum | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | At 1309 hours on April 17, 2000, the Unit 1 reactor was manually tripped from approximately 100% power due to degrading condenser vacuum. The degraded condenser vacuum was caused by inadequate steam supply to the condenser air ejectors due to the malfunctioning of auxiliary steam pressure control valve PCV-1AS-100. The Unit was manually tripped after reaching the condenser vacuum low-low alarm setpoint. Unit response to the reactor trip and Unit recovery were uncomplicated. PCV-lAS-100 was repaired, tested, and returned to service. As part of corrective actions to this event, an evaluation of I&C task analysis documentation, and maintenance documentation of as found and as-left conditions will be performed. Performance of a manually initiated reactor trip constitutes a manual actuation of an engineered safety feature and is reportable per 10 CFR 50.72(b)(2)(ii), and 10 CFR 50.73 (a) (2)(iv). The calculated risk associated with this event is small.
334 | 3342000006 | 2000-07-05 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | At 1305 on July 5, 2000, Beaver Valley Power Station (BVPS) Unit 1 experienced a reactor trip from 100% power due to the four (4) Main Turbine throttle valves going closed. There were no turbine related activities ongoing at the time. The Sequence of Events recorder indicated a momentary loss of DC control power (18 milliseconds) to the Analog Electrohydraulic (AEH) control system associated with the Main Turbine. One second later, a computer point indicated that a Throttle Valve/Governor Valve transfer had occurred. All four Main Turbine throttle valves closed between 10 and 13 seconds after the momentary loss of DC power. Following initiation of the automatic reactor trip signal, all control rods fully inserted and the Unit was stabilized in mode 3 with decay heat being removed via the normal post-reactor trip method of using the steam bypass system into the Main Condenser. There were no radiological releases. The throttle valve mixing amp 3 card was the only failed component found in the AEH control cabinet. Though initially thought to be the cause, subsequent evaluation showed this failure was not responsible for the turbine trip. A new mixing amp 3 card was installed and tested satisfactorily with the original DC power supplies. It is known that the reactor trip was caused by a failure in the AEH control cabinet, though no specific cause has been identified.
334 | 3342001001 | 2001-06-22 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Beaver Valley 1 | P | WE | PO | 100 | On June 22, 2001, at approximately 0924, Beaver Valley Power Station Unit No. 1 received an alarm for Station Instrument Air Receiver Tank Discharge Pressure Low. Operators entered the Abnormal Operating Procedure and initiated action for Loss of Station Instrument Air. At 0930, the degrading instrument air pressure caused an air-operated isolation valve in the cooling water flow path to two Reactor Coolant Pumps (RCPs) to close, eliminating component cooling water flow to these RCPs. At 0931, the reactor was manually tripped due to the loss of cooling to two RCPs and the potential loss of cooling water to the third RCP. All RCPs were then secured and natural circulation was established in the Primary System. All control rods fully inserted into the reactor core and all required safety systems operated as designed. Emergency Operating Procedures for Reactor Trip were performed and the plant was stabilized in Mode 3. The initiation of a manual reactor trip is reportable pursuant to 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73 (a)(2)(iv)(A). The root cause of the rapid Instrument Air System depressurization was mechanical aging/cyclic fatigue of the spring in a blowdown valve associated with the air dryer for the Instrument Air System. This failure caused the output from the operating air compressor to be vented off rather than entering the Instrument Air System Receiver Tank, resulting in an Instrument Air System breach. The safety significance for this event was small.
334 | 3342001003 | 2001-11-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | At 1416 hours on November 6, 2001, Beaver Valley Power Station Unit No. 1 reactor automatically tripped from 100% power due to low-low level in the C Steam Generator. The Feedwater Level Control Valve on the C Steam Generator unexpectedly failed closed causing the C Steam Generator water level to rapidly drop and reach the low-low water level reactor trip setpoint. Prior to the reactor trip, the Control Board Operator attempted to open the Feedwater Level Control Valve in manual control and observed no increase in the demand signal indicator or feedwater flow. After the reactor trip, Emergency Operating Procedure E-0 for Reactor Trip was performed and the plant was stabilized in Mode 3. The automatic initiation of a reactor trip from 100% power via the Reactor Protection System on November 6, 2001, was a valid reactor trip and was not part of a pre-planned sequence during testing or reactor operation. Therefore this event is reportable pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 50.73(a)(2)(iv)(A). The cause of the unexpected closure of the C Main Feedwater Regulating Valve was a random failure of a diode in the 7100 process rack module that controls the valve actuator. The safety significance of the automatic reactor trip on November 6, 2001 was small.
334 | 3342001004 | 2001-12-07 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Beaver Valley 1 | P | WE | PO | 100 | At 1353 hours on December 7, 2001, the operating station air compressor 1SA-C-1A tripped while station air compressor 1SA-C-1B was de-energized for preventive maintenance. The running compressor tripped due to a blown fuse in its control circuitry. The blown fuse was caused by a short circuit that was the result of uninsulated screwdriver contact in an energized circuit between compressors 1SA-C-1A and 1SA-C-1B. The on-shift operations crew responded per the appropriate alarm response procedure, and entered Abnormal Operating Procedure (AOP) 1.34.1, “Loss of Station Instrument Air”. Operators were dispatched locally to compressor 1SA-C-1A, the compressor’s supply breaker and to the backup diesel air compressor 1SA-C-2. A local start of 1SA-C-1A was unsuccessful due to the blown control power fuse. The backup diesel air compressor was started and placed in service; however, system pressure had already reached an abnormally low level and the backup diesel compressor was unable to restore system pressure due to insufficient capacity. The low system air pressure caused Loop 1C main steam trip valve, TV-1MS-101C, to begin to close as indicated by alarm “Steamline Stop Valve Not Fully Open”. At 1401 hours, Beaver Valley Power Station (BVPS) Unit 1 reactor was manually tripped due to the loss of station air in accordance with AOP-1.34.1. All control rods fully inserted into the reactor core and all required safety systems operated as designed. Emergency Operating Procedure E-0 for Reactor Trip was performed and the plant was stabilized in Mode 3. The direct cause for the manual trip was a loss of station air due to the unavailability of both station air compressors. The root cause of the event was determined to be the failure of the station work process to adequately plan, review, control, assign risk significance, and provide adequate oversight for work activities. This event is reportable pursuant to 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as a valid reactor trip and was not part of a pre-planned sequence during testing or reactor operation. The safety significance of this event was low.
334 | 3342002002 | 2002-11-11 | QR6 | Manual Reactor Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 53 | On November 11, 2002, Beaver Valley Power Station (BVPS) Unit 1 was performing a planned power reduction from full power at a rate of approximately 12 percent per hour for a scheduled maintenance outage. At approximately 1946 hours, the plant was at 53 percent power and the Turbine Motoring Condition alarm was received. An automatic turbine trip will occur if this alarm is received for more than 30 seconds. An automatic reactor trip will also occur following a turbine trip signal, if the plant power level is above 49 percent power. After approximately 20 seconds from the time of the alarm, the Control Room Unit Supervisor directed a manual reactor trip. Control room personnel implemented Emergency Operating Procedure E-0 for a reactor trip. The Auxiliary Feed Water System actuated as expected and all other systems functioned as required. An investigation into the event determined that the turbine motoring condition alarm was caused by a failure of the turbine differential pressure instrument that measures the differential pressure between the turbine impulse pressure and the turbine exhaust. The failure was due to a misapplication of the instrument to the service conditions. The failed instrument was replaced with a new instrument more suited for the application. The manual initiation of a reactor trip via the Reactor Protection System by the BVPS Unit 1 control room operator on November 11, 2002, was a valid manual reactor trip signal and was not part of a pre-planned sequence during testing or reactor operation. Therefore this event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A). The safety significance of the manual reactor trip on November 11, 2002 was small.
334 | 3342003001 | 2003-02-24 | QL5 | Partial Closure of MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Beaver Valley 1 | P | WE | PO | 100 | On 2/24/03 at 1548 hours, Beaver Valley Power Station (BVPS) Unit 1 was operating at 100% power, end of core life at steady state conditions, with preliminary Refueling No. 15 work evolutions (scaffold erection) in progress, when the Control Room received Annunciator A1-56 "Steamline Stop Valve Not Fully Open". This alarm was followed by a safety injection and reactor trip due to low main steam pressure. All required safety related systems functioned as required. After the automatic actuation occurred, control room operators noted that all three steam generator pressures were stable at normal post reactor trip values. No indications of a steam leak were observed. The plant was stabilized in Mode 3. The cause for the safety injection and reactor trip was the sudden inadvertent closure of the 'C' Main Steam Isolation Valve (MSIV), which caused a Low Steam Line Pressure safety injection and reactor trip. The west air cylinder rupture disk on the MSIV was damaged due to human error by craft workers installing scaffolding in the area below the MSIV. The rupture disk failed, thereby venting the instrument air pressure resulting in closure of the MSIV. Steam flows in the A and B loops subsequently increased and steam line pressures dropped such that the rate of the steam line pressure decrease in the B loop initiated a safety injection and reactor trip signal. An Unusual Event was declared for this event. This event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an applicable system.
334 | 3342003007 | 2003-11-13 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | At 1135 hours on November 13, 2003, the Beaver Valley Power Station Unit 1 reactor received an unexpected automatic reactor trip signal while operating at 100 percent power. The reactor trip signal was inadvertently generated during the performance of a maintenance surveillance procedure on the Solid State Protection System. Instrument and Control Technicians connected a digital volt meter (DVM) across the incorrect terminals in the Reactor Trip Breaker Switchgear cabinet when verifying breaker position contact state. This incorrect action created a current path across an open contact and energized the turbine trip relay. The turbine trip initiated an automatic reactor trip. The operating crew entered Emergency Procedure E-0, and transitioned to ES-0.1 in response to the trip. During the event, all required plant safety systems responded as required. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B)(1). The cause was self-checking and peer checking that did not meet expectations. The `B' train of Solid State Protection System (SSPS) had just been returned to service, exiting the applicable Action of the technical specifications (a two hour allowed outage time). Because the crew had exited the time critical portion of the technical specification, they did not complete the remaining portion of the surveillance procedure with the same sense of rigor as was used in the prior steps. The safety significance of this event was low.
334 | 3342006004 | 2006-09-07 | QR8 | Spurious Reactor Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | On September 7, 2006, Beaver Valley Power Station (BVPS) Unit No. 1 experienced an unexpected reactor trip at 2157 due to an opening of the "B" Reactor Trip Breaker. All safety systems functioned as designed. All three Auxiliary Feedwater System pumps started as expected on low steam generator levels. The plant was stabilized in Mode 3 with primary and secondary parameters returned to normal hot standby values. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System. The cause of the reactor trip was due to the unexpected opening of the "B" Reactor Trip Breaker caused by a failure of universal logic card A312B output gate in the Solid State Protection System (SSPS) that produced an invalid SSPS signal to the trip breaker. The root cause was a manufacturing defect on the integrated circuit Z9 that was not identified by pre and post manufacturing testing. The plant risk associated with the BVPS Unit 1 reactor trip that occurred on September 7, 2006, is considered to be very low.
334 | 3342013003 | 2013-11-05 | QR6 | Manual Reactor Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Beaver Valley 1 | P | WE | PO | 47 | On November 5, 2013 at 1747 hours, Beaver Valley Power Station (BVPS) Unit 1 was operating at 47 percent power after the 1R22 Refueling Outage. The Unit 1 Control Room received multiple unexpected alarms. The Turbine/Generator tripped due to Unit Station Service Transformer (USST) "BV-TR-1C" differential protection relay actuation. This transformer was energized but not in service at the time. The reactor operator manually tripped the reactor due to multiple unexpected alarms. An automatic reactor trip signal was not generated due to the fact that the reactor was operating at a power level less than the turbine trip - reactor trip setpoint of 49 percent power. The Steam Driven Auxiliary Feedwater (AFW) pump automatically started due to low level in the "C" Steam Generator. The "B" Motor Driven AFW pump was manually started to assist in maintaining steam generator levels. An Unusual Event was declared at 1828 hours due to reports from the fire brigade that an explosion had occurred in a cable tray in the Unit 1 turbine building mezzanine. The cause of this event was determined to be a fault in the "B" 4KV bus supply cables from BV-TR-1C that resulted in an arc flash and subsequent fire. Corrective actions include planned replacement of the faulted supply cables and inspections of the remaining Unit 1 and Unit 2 4KV bus supply cables for signs of degradation and aging. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the valid manual and automatic actuation of systems listed in (a)(2)(iv)(B) - (1) manual Reactor trip, (6) manual and automatic Auxiliary Feedwater pump start. A 10 CFR 50.72 notification was made at 1927 hours on November 5, 2013 to report entry into an Unusual Event, RPS Actuation and a Specified System, Auxiliary Feedwater actuation (EN 49505).
334 | 3342014001 | 2014-01-06 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | On January 6, 2014 at 1659 hours, Beaver Valley Power Station (BVPS) Unit 1 was operating at 100 percent power. An automatic reactor trip occurred due to a main transformer differential protection main unit generator trip. All three Auxiliary Feedwater (AFW) pumps automatically started, as expected, due to lowering steam generator levels. The reactor trip response was as expected with no immediate complications. The main transformer differential protection actuation was determined to be caused by an internal winding fault in the 'B' phase windings due to a dielectric breakdown. The transformer has been replaced. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the valid automatic actuation of systems listed in (a)(2)(iv)(B) - (1) automatic Reactor trip, (6) automatic Auxiliary Feedwater pump start. A 10 CFR 50.72 notification was made at 1909 hours on January 6, 2014 to report an automatic reactor trip and a Specified System, Auxiliary Feedwater actuation (EN 49697).
334 | 3342015001 | 2015-04-15 | QP3 | Loss of Condensate Flow | [45 empty] | Beaver Valley 1 | P | WE | PO | 85 | At 0411 EDT on April 15, 2015 the Beaver Valley Power Station (BVPS) Unit 1 reactor was manually tripped from approximately 85 percent power following a condensate pump trip. Prior to the manual reactor trip the unit was performing an emergent power reduction after the identification of a degrading condition on the "A" condensate pump motor. All control rods fully inserted into the core. The auxiliary feedwater system actuated as designed. The unit was stabilized in Mode 3 with the normal main feedwater system in service and the auxiliary feedwater system properly secured.<br /><br /> The "A" condensate pump trip was caused by the failure of the inboard motor bearing due to lack of oil lubrication. The root cause evaluation determined that responses to technical questions were provided without the appropriate technical rigor or validation of assumptions regarding acceptable oil level for the pump motor.<br /><br /> This event was reported (EN 50985) as an event or condition that results in the actuation of the reactor protection system when the reactor is critical, 10 CFR 50.72(b)(2)(iv)(B) and specified system actuation, 10 CFR 50.72(b)(2)(iv)(A). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the manual actuation of the Reactor Protection System, 10 CFR 50.73(a)(2)(iv)(B)(1), and the automatic actuation of the Auxiliary Feedwater System 10 CFR 50.73(a)(2)(iv)(B)(6).
334 | 3342017003 | 2017-11-07 | QR5 | Turbine Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 100 | On November 7, 2017 at 05:04 EST Beaver Valley Power Station (BVPS) Unit 1 experienced an automatic Reactor Trip from 100 percent power due to an automatic Turbine Trip. The Turbine Trip was initiated by a Main Unit Generator Overcurrent Protection Trip. The Reactor Trip was without complications. All control rods fully inserted into the core. The Auxiliary Feedwater System automatically actuated as expected and performed as designed. The plant was stabilized in Mode 3 with the normal Main Feedwater System in service and the Auxiliary Feedwater System properly secured. <br /><br /> The Main Unit Generator trip was caused by foreign material in the isophase bus duct. The isophase bus ducts have been properly inspected and cleared of all foreign material. <br /><br /> This event was reported (EN 53056) as an actuation of the Reactor Protection system 10 CFR 50.72(b)(2)(iv)(B) and a Specified System Actuation (Auxiliary Feedwater System) 10 CFR 50.72(b)(3)(iv)(A). <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the automatic actuation of the Reactor Protection System (RPS) and the expected automatic actuation of the Auxiliary Feedwater System.
334 | 3342019002 | 2019-11-04 | QR6 | Manual Reactor Trip | [45 empty] | Beaver Valley 1 | P | WE | PO | 15 | On November 4, 2019, at 0535 Eastern Standard Time, the Beaver Valley Power Station Unit 1 reactor was manually tripped at approximately 15% reactor power due to secondary system perturbations that caused the 1A Main Steam Safety Valve (MSSV) to lift. The 1A MSSV opened, instead of the expected opening of the 1A Atmospheric Dump Valve (ADV), as the tolerance range for ADV pressure switch overlapped the tolerance range for 1A MSSV. The 1A MSSV closed just prior to the trip. <br /><br /> The Reactor Trip was without complications. All control rods fully inserted into the core. The plant was stabilized in Mode 3 with normal Main Feedwater System in service. <br /><br /> The reason for the MSSV opening prior to the 1A ADV opening was due to the as-left setpoint of the 1A ADV pressure switch during its calibration in the prior refueling outage. The setpoint drifted high and was found to be above the opening setpoint of the MSSV.<br /><br /> The pressure switch input to the 1A ADV was adjusted to within the tolerance band prior to reactor startup. An Engineering Evaluation established new setpoint and reset values for the three ADVs. <br /><br /> This event was reported per Event Notification 54369 as an actuation of the Reactor Protection System per 10 CFR 50.72(b)(2)(iv)(B). <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the manual actuation of the Reactor Protection System.
335 | 3351987002 | 1987-02-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 5 | POWER LEVEL - 005%. ON FEBRUARY 7, 1987, ST. LUCIE UNIT ONE WAS IN MODE ONE (CRITICAL, > OR = 5% POWER), REDUCING POWER TO ENTER A SCHEDULED REFUELING OUTAGE. AT 0020 HOURS, OPERATIONS PERSONNEL BEGAN EXPERIENCING DIFFICULTIES MAINTAINING MINIMUM FLOW THROUGH THE MAIN FEEDWATER (MFW) PUMP, AND THE PUMP TRIPPED SEVERAL TIMES DUE TO LOW FLOW. STEAM GENERATOR (S/G) LEVELS BEGAN TO DECREASE DUE TO UNEVEN FEED FLOW, AND DISCREPANCIES WERE NOTICED IN THE S/G LEVEL INDICATORS ON THE RTGB. THE REACTOR AUTOMATICALLY TRIPPED AT 0038 HOURS ON LOW S/G LEVEL. THE REACTOR TRIP WAS OBSERVED TO BE NORMAL, MFW FLOW WAS SUCCESSFULLY RESTORED, AND THE UNIT WAS STABILIZED IN MODE THREE BY 0050 HOURS. MANUAL CONTROL OF PRIMARY AND SECONDARY SYSTEMS DURING A CONTROLLED SHUTDOWN IS DIFFICULT; THE TRIPPING OF THE MFW PUMPS AND SOME CONFUSION CREATED BY DISCREPANCIES IN S/G LEVEL INDICATIONS RESULTED IN THE INABILITY TO CONTROL S/G LEVEL AND LED TO THE REACTOR TRIP. FOUR CORRECTIVE ACTIONS HAVE BEEN TAKEN: TROUBLESHOOTING AND REPAIR OF RTGB S/G LEVEL INDICATORS: EXPECTED INSTALLATION OF A LOW POWER FEEDWATER CONTROL SYSTEM DURING THE REFUELING OUTAGE IN PROGRESS; RESEARCH INTO IMPROVED OPERATION OF MFW PUMP RECIRCULATION VALVES, AND EVALUATION FOR APPROPRIATE TRAINING REQUIREMENTS AND METHODS BY PLANT TRAINING GROUP.
335 | 3351987011 | 1987-05-21 | QR5 | Turbine Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | POWER LEVEL - 100%. WHILE ST. LUCIE UNIT 1 WAS IN MODE 1 AND AT STEADY STATE CONDITIONS, THE REACTOR TRIPPED BY VIRTUE OF THE LOSS OF TURBINE LOAD TRIP. A TURBINE LOCKOUT TRIP WAS INITIATED BY THE TRIPPING OF THE GENERATOR LOCKOUT RELAY BY THE OVEREXCITATION PROTECTION LIMITER. THE CAUSE OF THE EVENT WAS DUE TO AN INCREASE IN EXCITER FIELD CURRENT WHICH EXCEEDED THE SETTING OF INSTANTANEOUS CURRENT LIMITER #3 WHICH DIRECTLY GIVES A GENERATOR LOCKOUT. THE ROOT CAUSE OF THE EXCITER FIELD CURRENT INCREASE WAS A FAILED TRANSDUCER. IMMEDIATE ACTIONS WERE PERFORMED TO BRING THE REACTOR TO A STABLE CONDITION. TWO DEFECTIVE WIRES WERE REPAIRED, THE FAILED TRANSDUCER WAS REPLACED, AND THE CURRENT LIMITER WAS RE-SET TO ITS SPECIFIED SETTING.
335 | 3351987013 | 1987-06-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | POWER LEVEL - 100%. ON JUNE 14, 1987, WHILE OPERATING AT 100% POWER (MODE 1), ST. LUCIE UNIT 1 EXPERIENCED A MAIN TURBINE RUNBACK TO 60% POWER DUE TO THE LOSS OF THE 1B STEAM GENERATOR FEED PUMP (SGFP). THE UTILITY LICENSED OPERATORS RESTARTED THE SGFP AND MANUALLY INSERTED CONTROL RODS TO REDUCE THE PRIMARY/SECONDARY POWER MISMATCH. THE UNIT AUTOMATICALLY TRIPPED ON HIGH PRESSURE APPROXIMATELY 22 SECONDS INTO THE EVENT. THE TRIP WAS UNCOMPLICATED AND THE UNIT WAS QUICKLY STABILIZED IN HOT STANDBY. THE CAUSE OF THE 1B SGFP TRIP HAS NOT BEEN CONCLUSIVELY IDENTIFIED; HOWEVER, A FAILURE OF THE DIFFERENTIAL CURRENT RELAY, TYPE SA-1, IN THE 1B SGFP IS BELIEVED TO HAVE BEEN THE CAUSE. AN UPGRADE HAS BEEN INSTALLED IN ALL UNIT #2 AND IN ONE UNIT #1 TYPE SA-1 RELAYS. THE REMAINING UPGRADES FOR UNIT #1 TYPE SA-1 RELAYS ARE ON ORDER. THE INTENTION OF THE MAIN TURBINE RUNBACK IS TO REDUCE THE TURBINE STEAM LOAD IN RESPONSE TO THE REDUCED FEEDWATER FLOW AND SUBSEQUENT DECREASE IN S/G INVENTORIES. IT IS NOT REQUIRED FOR REACTOR SAFETY. THE REACTOR PROTECTION SYSTEM WILL ASSURE REACTOR SAFETY BY AUTOMATICALLY TRIPPING THE UNIT AND THE MAIN TURBINE ON LOW S/G LEVEL OR HIGH PRESSURE AS IT DID IN THIS EVENT. THIS WILL ASSURE SUFFICIENT S/G INVENTORIES TO PROVIDE AN ADEQUATE PRIMARY HEAT SINK.
335 | 3351987016 | 1987-10-29 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | St. Lucie 1 | P | CE | PO | 20 | POWER LEVEL - 020%. ON OCTOBER 29, 1987, AT 0334 HOURS, ST. LUCIE UNIT ONE WAS IN MODE 1 REACTOR POWER >5%, AVERAGE COOLANT TEMPERATURE >325F), WHEN THE UNIT TRIPPED ON LOW STEAM GENERATOR LEVEL DUE TO THE LOSS OF THE 1A CONDENSATE PUMP. FEEDWATER WAS RESTORED TO THE STEAM GENERATORS BY THE MANUAL STARTING OF THE AUXILIARY FEEDWATER PUMPS. ALL SYSTEMS FUNCTIONED NORMALLY. AT 0542 HOURS, THE UNIT WAS IN MODE 3 (REACTOR NOT CRITICAL, RCS TEMPERATURE >325F) PREPARING TO RETURN TO FULL POWER OPERATION, WITH THE C CHANNEL OF WIDE RANGE NUCLEAR INSTRUMENTATION ON THE REACTOR PROTECTION SYSTEM (RPS) PLACED IN TRIP CONDITION IN ACCORDANCE WITH TECHNICAL SPECIFICATION 3.3.1.1. THE LICENSED REACTOR CONTROL OPERATOR HAD JUST BEGUN PULLING THE INITIAL GROUP OF SHUTDOWN CONTROL RODS WHEN A SPURIOUS SIGNAL WAS RECEIVED ON THE B CHANNEL WIDE RANGE NUCLEAR INSTRUMENTATION AND THE REACTOR WAS TRIPPED ON HIGH STARTUP RATE. ALL SYSTEMS FUNCTIONED NORMALLY. THE ROOT CAUSE OF THE LOSS OF THE CONDENSATE PUMP WAS DETERMINED TO BE AN INADEQUATE OPERATING PROCEDURE. THE ROOT CAUSE OF THE HIGH STARTUP RATE TRIP WAS DETERMINED TO BE ELECTRICAL NOISE.
335 | 3351987017 | 1987-12-21 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | POWER LEVEL - 100%. ON 12/21/87, WHILE OPERATING IN MODE 1 AT 100% POWER, ST. LUCIE UNIT #1 TRIPPED DUE TO THE LOSS OF THE 1MD 120 VOLT AC BUS. WITH THE REACTOR PROTECTIVE SYSTEM (RPS) HI START-UP RATE B CHANNEL BISTABLE IN TRIP, THE RPS LOGIC FOR HI START-UP RATE WAS 1 OF 3. THE LOSS OF THE 1D INSTRUMENT INVERTER CAUSED THE SUBSEQUENT LOSS OF THE 1MD 120 VOLT AC BUS, WHICH RESULTED IN THE ACTUATION OF THE DEENERGIZE TO ACTUATE FUNCTION OF THE RPS D CHANNEL TRIP BISTABLES THUS SATISFYING THE RPS TRIP LOGIC. THE ROOT CAUSE OF THE EVENT WAS A COGNITIVE PERSONNEL ERROR BY A UTILITY NON-LICENSED OPERATOR NOT ADEQUATELY FOLLOWING A PLANT APPROVED PROCEDURE FOR OPERATION OF THE 120 VOLT INSTRUMENT AC CLASS 1E SYSTEM. THE NON-LICENSED OPERATOR WAS COUNSELED BY HIS SUPERVISOR ON THE IMPORTANCE OF ADEQUATELY FOLLOWING APPROVED PROCEDURES AND THE NEED FOR GREATER ATTENTION TO DETAIL WHILE PERFORMING CRITICAL JOB RESPONSIBILITIES. A PROCEDURE FOR INFREQUENT OPERATIONS OR MANIPULATIONS IS BEING DRAFTED. THIS IS TO ASSURE A DETAILED REVIEW AND BRIEFING BY THE SHIFT SUPERVISOR WITH APPROPRIATE PERSONNEL FOR SAFE AND SATISFACTORY PERFORMANCE. THE PLANT TRAINING DEPARTMENT WILL EVALUATE THIS ITEM TO DETERMINE APPROPRIATE TRAINING METHODS AND REQUIREMENTS. A HUMAN PERFORMANCE EVALUATION IS BEING CONDUCTED TO IDENTIFY ANY AREAS THAT MAY BE OF CONCERN.
335 | 3351988003 | 1988-03-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On March 27, 1988, St. Lucie Unit 1 was in Mode 1, 100% power and at steady state conditions. All plant controls were in their normal operating line-up. At approximately 00:01 EDT, on March 28, 1988, a malfunction of the Main Feedwater Control System (EIIS:JB) was observed and the Main Feedwater regulating valve closed. The closure of the valve generated a low Steam Generator level signal from the Reactor Protection System and caused the Reactor to automatically trip. All systems functioned as designed and the plant was maintained at a stable condition. There were no radiological releases observed during the event. The health and safety of the public was not endangered throughout the event. The reactor trip was observed as an uncomplicated reactor trip. <br /><br /> The root cause of the event was due to the malfunction of the Feedwater regulating valve positioner causing the valve to overshoot its pre-set position on the closing stroke. Some of the contributing factors to the valve closure were (1) the steam flow/feed flow mismatch controller was sluggish and had low output signals, and (2) the electrical to pneumatic converter signals were not consistent. <br /><br /> Immediate corrective actions were (1) replace the steam flow/feed flow mismatch controller, (2) the electrical to pneumatic converter was cleaned and adjusted, and (3) the valve positioner was cleaned and adjusted.
335 | 3351988004 | 1988-06-30 | QP4 | Partial Loss of Condensate Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On June 30, 1988, St. Lucie Unit One was operating at 100 percent power steady state in Mode 1. At 0548 hours, St. Lucie Unit One experienced a main turbine runback to 60 percent power due to the loss of the 1B Steam Generator Feed Pump (SGFP). The 1B SGFP tripped due to an interlock with the running condensate pump that tripped on its equipment protective relay. The 1B Condensate Pump tripped on a Current Balance Relay actuation. The reactor automatically tripped on high pressurizer pressure. The trip was uncomplicated and the unit was quickly stablized in Hot Standby, Mode 3. <br /><br />The root cause for the 1B Condensate Pump to trip was a spurious actuation of its Current Balance Relay. <br /><br />The following corrective actions have been implemented: replaced the Current Balance Relay, failure analysis testing on the relay will be performed, modified the Current Balance Relay setpoints for both 1A and 1B Condensate Pump motors to reduce sensitivity to spurious actuation, and a Request for Engineering Assistance has been initiated to perform a study on the necessity of the Current Balance Relay and means to prevent unnecessary condensate pump trips.
335 | 3351988008 | 1988-09-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | Prior to the event on 20 September, 1988, Unit 1 was at 100% power, steady state operations. Instrumentation & Control (I&C) personnel were working on the 'B' Steam Generator Feed Regulating System (SG FRS) in an effort to minimize water level swings of 4% narrow range indication in the 'B' Steam Generator (SG). At 1152, a power supply wire lead, which was not shown on the vendor wiring diagram being used, was inadvertently lifted when I&C correctly removed another lead on the same terminal lug connection. Removal of the power supply lead deenergized the 'B' FRS control circuit, and caused the valve to shut. The loss of half of normal main feedwater supply caused SG water level to rapidly decrease. The unit was tripped on low SG level by the Reactor Protective System and the Reactor Operator Corrective actions were to upgrade the administrative procedure used, install a double lug terminal connection in the FRS circuitry to preclude accidental lead lifting, and to evaluate and repair the root cause of SG level swings before resuming power operations.
335 | 3351989003 | 1989-07-17 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | St. Lucie 1 | P | CE | SU | 4 | On 17 July, 1989, St. Lucie Unit 1 was in Mode 2 and performing a turbine startup. Steam Generator (SG) levels were maintained with the 1A and 1B Auxiliary Feedwater (AFW) Pumps. At 0254, the 1B Main Feedwater (MFW) Pump was started, AFW was secured and the turbine was rolled shortly thereafter. SG levels were observed to be decreasing, and AFW was restored. The unit automatically tripped at 0300 on low SG level due to mismatches between steam loads and feed flow rates. The audible annunciator for the low SG levels pre-trip alarms failed before the trip. Standard Post Trip Actions were performed and the unit was stabilized in Mode 3. <br /><br /> MFW flow to the SGs was prevented because the MFW block valves had not been opened. Procedures will be changed to verify their proper line up before starting the turbine. Affected audible annunciators were returned to service. A cognitive personnel error among the utility licensed operators led to the automatic reactor trip.
335 | 3351989005 | 1989-09-13 | QR5 | Turbine Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 98 | On September 13, 1989, at 1409, while in Mode 1 at 98% power, Unit 1 tripped on Loss of Load. Prior to the trip, there were two Nuclear Plant Work Orders (NPWO) being worked concurrently on the Reactor Plant Protection System (RPS). One of the NPWO's involved removing TCB-1 for maintenance while the other NPWO was for replacing a "C" channel power supply in the RPS cabinet. In order to replace the power supply, breaker CB-3 inside the RPS cabinet was opened. When this was done, TCB-7 and TCB-3 opened and with TCB-1 already open, a turbine and reactor trip occurred. The root cause of the reactor trip was determined to be an inadequate NPWO work description, inadequate communications to Operations by I&C and the procedure for Unit Reliability-Sensitive Systems did not clearly show that its use was required. Corrective actions: review/revise Sensitive Systems Procedures, write standard work descriptions to be attached to NPWO's for RPS power supply replacements, add caution statements to I&C procedures to check the TCB's position and expedite plant changes to replace RPS power supplies.
335 | 3351990007 | 1990-05-24 | QR6 | Manual Reactor Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 91 | On May 24, 1990 St. Lucie Unit 1 was in Mode 1 at 91% power performing main turbine maintenance on a hydraulic control valve (Moog) in the Digital Electro-Hydraulic (DEH) Control System on the #3 Governor valve. When DEH fluid was re-established to the valve, an excessive unisolable leak developed. The Assistant Nuclear Plant Supervisor instructed the Reactor Control Operators to manually trip the reactor and turbine at 0452. The Standard Post Trip Actions were performed and the unit was stabilized in Mode 3, Hot Standby. <br /><br /> The initiator of this event was the severe leakage of DEH fluid from the associated Moog valve of the #3 Governor valve. An investigation revealed the o-rings inside the base of the Moog valve which seal this valve to the #3 Governor valve mounting plate had ruptured. The cause of the rupture was due to the installation of improperly sized o-rings. The parts list used to obtain replacement o-rings for maintenance had the incorrect part number listed for these o-rings. The root cause for this event is inadequate tech manuals and drawings for the DEH system which lack the part numbers for replacement pads. <br /><br /> An official parts list was requested from the vendor for all o-rings used on the turbine/generator set, as well as all other supporting Westinghouse systems. The o-rings on all similar valves were inspected to ensure the correct o-rings were installed. A drawing change request has been submitted to have the o-ring pan numbers put on the appropriate drawings.
335 | 3351991003 | 1991-05-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 96 | On May 6, 1991, St. Lucie Unit 1 was in Mode 1 and holding power at 96% to complete a Nuclear Delta-T Power Calibration before resuming full power operation following a scheduled shutdown. The 1A Heater Drain Pump tripped at 0508 and, four seconds later, the 1A Steam Generator Feedwater Pump tripped causing a turbine runback. The unit was manually tripped at 0509 at the direction of the Nuclear Plant Supervisor in anticipation of an automatic reactor trip and Standard Post Trip Actions were performed. The unit was then stabilized in Mode 3, Hot Standby. <br /><br /> The manual reactor trip was the result of a turbine runback initiated when both the 1A Heater Drain Pump and the 1A Steam Generator Feedwater Pump tripped. An investigation revealed a possible grounding of the 5A Feedwater Heater Hi-Hi level switch which, in turn, opened Circuit Breaker 27 on the 120 VAC Vital Static Uninterruptible Power Supply. This would have caused the normal drain valves to close on several secondary Feedwater Heaters and the alternate drain valves to open. It was also found that the pressure sensing element setpoint for the 1A SGFP had drifted high from the normal value of 275 psig to 291 psig. The end result was a low suction pressure condition on the Feedwater Pump suction line and the trip of the 1A Steam Generator Feedwater Pump on low suction pressure. <br /><br /> The immediate Corrective Actions implemented as a result of this event include: testing and replacing Circuit Breaker 27 as a precautionary measure, cleaning and testing the 5A Feedwater Heater Hi-Hi level switch, and lowering the setpoint of the 1A Steam Generator Feedwater Pump to its normal value of 275 psig.
335 | 3351991005 | 1991-07-01 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On July 1, 1991, St. Lucie Unit 1 was operating in Mode 1 at 100% power. Utility Maintenance personnel were attempting to remove LIC-9013-B, the Channel B narrow range level indicator for the 1A Steam Generator. At 1137 FIC-9011, the 1A Feedwater Regulating Valve Digital Controller, lost all power. The 1A Steam Generator water level decreased, and the Reactor Control Operator opened the 100% Main Feedwater Bypass Valve in an attempt to regain level. At 1138 the reactor tripped automatically on low level in the 1A Steam Generator. Standard Post-Trip Actions were performed, and the plant was stabilized in Mode 3, Hot Standby. <br /><br /> The root cause of this event was due to a deficient procedure which did not completely isolate electrical power to LIC-9013-B during maintenance. With this indicator controller unisolated, two leads were inadvertently shorted, resulting in an overload and blown power supply fuse. As transfer to the back up power supply occurred, that power supply's breaker tripped resulting in a complete loss of power to FIC-9011. This loss of power resulted in a close demand signal from the controller to the 1A Feedwater Regulating Valve. The Feedwater Regulating Valve went closed, and water level decreased in the 1A Steam Generator to the reactor trip setpoint. <br /><br /> Corrective actions as a result of this event: a revision of plant maintenance procedures to direct the isolation of power to the steam generator level indicators, and a procedure revision to require supervisory and department head review of proposed work on sensitive systems. Also, a plant modification for replacing the steam generator level indicators with a model which has pin type connectors is under consideration.
335 | 3351991006 | 1991-09-18 | QR8 | Spurious Reactor Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On 18 September, 1991, with Unit 1 in mode 1 at 100%, operators prepared to return the 1A Control Element Drive Mechanism (CEDM) Motor Generator (MG) set to service following maintenance on its flywheel bearing. At 1043, while a utility non-licensed operator was manually synchronizing the 1A MG set to the CEDM bus, the generator output breaker was closed out of phase with the running MG set. This resulted in an instantaneous overcurrent condition on the CEDM bus. The overcurrent condition opened 7 Trip Circuit Breakers (TCBs) and removed power to the CEDMs. All Control Element Assemblies (CEAs) then fully inserted. The main turbine automatically tripped upon sensing an undervoltage condition on the CEDM bus and the 2 remaining TCBs opened. The operators then implemented Standard Post Trip Actions, and the normal Reactor Trip Recovery procedure. <br /><br /> The root cause for the out of phase synchronization of the MG set was that a non-licensed operator made a personnel error while attempting to manually synchronize the 1A MG set to the CEDM bus. The non-licensed operator closed the generator output breaker out of phase while he was in an incorrect section of the procedure. Contributing factors to this event included: on the scene supervision of this load threatening activity was absent, a lack of specific technical knowledge by the operator, no pre-evolution brief between maintenance and operating personnel was held, and the procedure for MG set operation contained some human factor deficiencies. <br /><br /> Corrective actions were to: counsel the individuals involved on this event, emphasize the importance of on the scene supervision and pre-evolution briefings, provide additional training on MG set operation to non-licensed operators, revise the procedure for CEDM MG Set Operation, and verify the proper operation of the 1A MG set.
335 | 3351992006 | 1992-09-24 | QR5 | Turbine Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 43 | On 24 September 1992, St. Lucie Unit 1 was holding power at 43% while awaiting the return to service of the 1B Steam Generator Feedwater pump. At 1138, the reactor automatically tripped on a Turbine Generator Loss of Load signal from the Reactor Protection System. Operators implemented EOP-1 Standard Post Trip Actions, stabilizing the unit in Mode 3 utilizing the Steam Bypass Control System and by manually starting the 1A and 1B Auxiliary Feedwater Pumps. Three sets of Safety Function Status Checks were satisfactorily accomplished as per EOP-2, Reactor Trip Recovery.<br /><br /> The cause of the turbine trip was a momentary interruption of 15VDC bus power to the turbine Digital Electro-Hydraulic (DEH) control system. Interruption of power to the + or - 15VDC bus will result in a turbine and reactor trip. The root cause of the momentary interruption of power to the 15VDC bus was most likely due to the failure of a filter capacitor in a turbine speed control circuit card. This capacitor is suspected to have shorted to common ground, momentarily dropping 15VDC voltage, and then failed open. <br /><br /> Corrective actions: The turbine speed control circuit board with the failed capacitor was replaced; the utility maintenance instrumentation & Controls (I&C) department verified the operability of the remaining turbine DEH control circuit cards, looking for similar filter capacitor failures; I&C verified the operability of the six DC power supplies in the turbine control system; the vendor for the turbine control system was consulted to assist in troubleshooting and to validate the root cause of this event; the circuit board with the failed filter capacitor will be evaluated to determine the specific cause of the failure and any generic implications.
335 | 3351993007 | 1993-09-18 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | St. Lucie 1 | P | CE | PO | 75 | On September 18, 20, and 22, 1993, while Unit 1 was at 100%, 63%, and 60% power respectively, a large number of jellyfish were drawn from the Atlantic Ocean into the intake canal. This condition created a large differential pressure across the intake traveling screens necessitating the removal of non-safety related circulating water pumps from service. In accordance with Off-Normal Operating Procedure 1-0620030, Circulating Water System, manual reactor and turbine trips were initiated on Unit 1 at power levels of 75%, 63%, and 11% respectively as cooling water to one of the main turbine condensers was removed from service. In each case the Standard Post Trip Actions of EOP-1 led to a diagnosis of an uncomplicated reactor trip. EOP-1 was exited and upon completing EOP-2, Reactor Trip Recovery, the Unit was stabilized in Mode 3, Hot Standby. During this time period, the safety related intake cooling water system remained in service.<br /><br /> The root cause of the event was that an abnormal influx of jellyfish was greater than the intake traveling screen system could efficiently handle. <br /><br /> Interim corrective actions for this event were: The unit was maintained at reduced power or kept offline at appropriate times to prevent equipment damage. The intake traveling screens were manned and operated as necessary with the Circulating Water Pump discharge valves throttled to minimize the jellyfish influx at the intake structure. The influx of jellyfish subsided on 29 September.
335 | 3351993007 | 1993-09-20 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | St. Lucie 1 | P | CE | PO | 63 | On September 18, 20, and 22, 1993, while Unit 1 was at 100%, 63%, and 60% power respectively, a large number of jellyfish were drawn from the Atlantic Ocean into the intake canal. This condition created a large differential pressure across the intake traveling screens necessitating the removal of non-safety related circulating water pumps from service. In accordance with Off-Normal Operating Procedure 1-0620030, Circulating Water System, manual reactor and turbine trips were initiated on Unit 1 at power levels of 75%, 63%, and 11% respectively as cooling water to one of the main turbine condensers was removed from service. In each case the Standard Post Trip Actions of EOP-1 led to a diagnosis of an uncomplicated reactor trip. EOP-1 was exited and upon completing EOP-2, Reactor Trip Recovery, the Unit was stabilized in Mode 3, Hot Standby. During this time period, the safety related intake cooling water system remained in service.<br /><br /> The root cause of the event was that an abnormal influx of jellyfish was greater than the intake traveling screen system could efficiently handle. <br /><br /> Interim corrective actions for this event were: The unit was maintained at reduced power or kept offline at appropriate times to prevent equipment damage. The intake traveling screens were manned and operated as necessary with the Circulating Water Pump discharge valves throttled to minimize the jellyfish influx at the intake structure. The influx of jellyfish subsided on 29 September.
335 | 3351993007 | 1993-09-22 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | St. Lucie 1 | P | CE | PO | 11 | On September 18, 20, and 22, 1993, while Unit 1 was at 100%, 63%, and 60% power respectively, a large number of jellyfish were drawn from the Atlantic Ocean into the intake canal. This condition created a large differential pressure across the intake traveling screens necessitating the removal of non-safety related circulating water pumps from service. In accordance with Off-Normal Operating Procedure 1-0620030, Circulating Water System, manual reactor and turbine trips were initiated on Unit 1 at power levels of 75%, 63%, and 11% respectively as cooling water to one of the main turbine condensers was removed from service. In each case the Standard Post Trip Actions of EOP-1 led to a diagnosis of an uncomplicated reactor trip. EOP-1 was exited and upon completing EOP-2, Reactor Trip Recovery, the Unit was stabilized in Mode 3, Hot Standby. During this time period, the safety related intake cooling water system remained in service.<br /><br /> The root cause of the event was that an abnormal influx of jellyfish was greater than the intake traveling screen system could efficiently handle. <br /><br /> Interim corrective actions for this event were: The unit was maintained at reduced power or kept offline at appropriate times to prevent equipment damage. The intake traveling screens were manned and operated as necessary with the Circulating Water Pump discharge valves throttled to minimize the jellyfish influx at the intake structure. The influx of jellyfish subsided on 29 September.
335 | 3351994001 | 1994-01-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On January 9, 1994 at 1940 hours with St. Lucie Unit 1 in mode 1 at 100% power, the 1B Steam Generator Feedwater Pump tripped. Subsequently the reactor was manually tripped due to decreasing Steam Generator water levels. Emergency Operating Procedure-01, Standard Post Trip Actions, was performed and Steam Generator water levels were regained using the Auxiliary Feedwater System. Emergency Operating Procedure-02, Reactor Trip Recovery was completed, confirming an uncomplicated reactor trip. The plant was stabilized in Mode 3, Hot Standby.<br /><br /> The reactor was manually tripped by the utility licensed operators in anticipation of an automatic reactor trip due to low Steam Generator water level. The cause of the low Steam Generator water level was the 1B Steam Generator Feedwater Pump trip. The most likely cause of the 1B Steam Generator Feedwater Pump trip was a spurious signal from the pump protective low flow switch or its associated time delay relay. The purpose of the low flow switch is to protect the pump in the event of a low flow condition. <br /><br /> Corrective Actions for this event: 1) Instrumentation and Control Maintenance replaced the 1B Steam Generator Feedwater Pump low flow switch, 2) Electrical Maintenance replaced the low flow trip time delay relay, 3) Electrical Maintenance performed electrical continuity and ground checks, 4) Electrical and Instrumentation and Control Maintenance groups replaced the wiring between the low flow switch and the time delay relay, 5) System Engineers monitored Steam Generator Feedwater Pump operation prior to and following unit restart and 6) FPL Engineering has performed an autopsy of the low flow switch and the time delay relay and no specific component failure was identified.
335 | 3351994003 | 1994-03-28 | QR5 | Turbine Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 68 | On March 28, 1994, St. Lucie Unit 1 was at 68% power for Condenser waterbox cleaning activities and Unit 2 was shutdown for a scheduled refueling outage. Utility Electrical Maintenance personnel requested a clearance for the Unit 2 main generator exciter switchgear breaker for preventive maintenance. The chief electrician requesting the clearance went to the work control center and signed on to the clearance which specified that the Unit 2 exciter breaker was in the open position. He then went to the Unit 1 exciter switchgear room and found the breaker closed . Unaware that he was on the wrong unit, the chief electrician tried to verify what he thought was the appropriate position by attempting to open the breaker. The breaker opened and Unit 1 immediately experienced a reactor trip by turbine trip. An uncomplicated automatic reactor trip was verified and Unit 1 was subsequently stabilized in mode 3. <br /><br /> The root cause of the event was due to cognitive personnel error by a member of the utility Electrical Maintenance department in failure to adhere to the clearance procedure. The procedure governing clearance orders provides direction to verify deenergization of the system prior to work proceeding. Station practices restrict personnel other than Operations from manipulating in-service equipment without a valid clearance boundary. A contributing factor was the lack of an identifier on the exciter switchgear housing or the exciter field breaker. <br /><br /> Corrective actions included: 1) Operations stabilized the unit in mode 3. 2) The individual responsible was counseled and disciplined. 3) Reviews will be held with plant maintenance personnel to re-emphasize the foreman's responsibilities in the clearance procedure. 4) Unit 1 and Unit 2 main generator exciter switchgear housings and breakers have been labeled. 5) Additional postings to ensure unit awareness will be installed.
335 | 3351994004 | 1994-04-03 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | St. Lucie 1 | P | CE | SU | 19 | On April 3,1994 at 0036 hours with St Lucie Unit 1 in mode 1, the Control Element Drive Mechanism (CEDM) bus was deenergized, which tripped the reactor. The utility licensed operators carried out Emergency Operating Procedure-01, Standard Post Trip Actions. Emergency Operating Procedure-02, Reactor Trip Recovery, was completed confirming an uncomplicated reactor trip. The plant was stabilized in mode 3, Hot Standby.<br /><br /> The cause of the plant trip was an overcurrent condition on the CEDM bus caused by the CEDM Motor Generator (MG) sets being out of phase due to a procedural error. temporary change to an approved plant procedure, to isolate the 1A2 4.16 KV bus for repair of the 1A2 4.16 KV Startup Transformer Breaker. The running 1A Emergency Diesel Generator (EDG) switched to the isochronous mode when the 1A3 4.16 KV bus was separated from the grid. The electrical frequency of all components supplied by the 1A EDG then became independent from the B train components. The resulting phase mismatch between the A train MG and B train MG sets caused an overcurrent condition on the CEDM bus. Trip Circuit Breakers (TCBs) 4, 8, 9 and the A MG set output breaker opened as designed on instantaneous overcurrent. The root cause of the procedural error was due to personnel focusing on issues other than the potential for phase mismatch between the MG sets during the review of the temporary procedure change. <br /><br /> Corrective actions for this event: 1) Checks were performed on the CEDM system, MG sets, MG set output breakers, and TCBs with satisfactory results, 2) Training will be provided to reviewers of temporary changes to procedures to reinforce the need for prior Facility Review Group review of complex changes to procedures. 3) the affected breaker and associated components were replaced, 4) Onsite breaker cubicles of large frame breakers were inspected with satisfactory results.
335 | 3351994005 | 1994-06-06 | QR5 | Turbine Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 97 | On June 6, 1994, at 1508 with Unit 1 at 97% power, during a period of thunderstorm and high wind activity a piece of aluminum facia from a storage building became airborne and struck the Unit 1A Main Transformer. The aluminum facia contacted two phases on the output of the 1A Main Transformer which caused a Main Transformer differential current trip. The Unit 1 Main Turbine tripped from the Main Generator lockout and resulted in an automatic reactor trip. Standard post trip actions were performed, the normal Reactor Trip Recovery procedure was implemented and all safety functions were satisfactory. <br /><br /> The root cause of the reactor trip was due to natural phenomenon in the form of high winds from localized thunderstorm activity. Gusting winds from the thunderstorm tore loose a piece of aluminum facia from a permanent storage building in the vicinity of the 1A Main Transformer and caused it to become airborne and strike the transformer output bushings. <br /><br /> Corrective actions for this event include: 1) Operations stabilized the unit in mode 3. 2) A visual inspection for loose materials on buildings nearby the Main Transformers has been performed with satisfactory results. 3) An internal visual inspection was performed on the Main Generator with satisfactory results. 4) Electrical tests were performed on the Main Generator, Isophase buses, and the 1B Main Transformer with no damage observed. 5) The 1A Main Transformer will be restored and tested prior to ascension to full rated power. 6) The facia on the storage facility was secured using additional fasteners. 7) Additional review criteria will be developed for periodic inspections of buildings in the vicinity of the transformers.
335 | 3351994007 | 1994-10-26 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | St. Lucie 1 | P | CE | PO | 100 | On October 26, 1994, Unit 1 was in mode 1 and operating at 100% steady state power. At 1426 utility personnel observed a flash in the area of the 240 KV switchyard near the Unit 1 synchronizing potential transformer. At this time Unit 1 experienced an automatic reactor trip on Loss of Electrical Load predicated by Main Generator differential current condition. Standard post trip actions were performed, the normal Reactor Trip Recovery procedure was implemented and all safety functions were satisfactory. Subsequently a fire was reported at 1445 in the 240 KV switchyard at the affected synchronizing potential transformer outside the protected area. The fire was controlled and allowed to extinguish itself. <br /><br /> The root cause of the failed potential transformer is attributed to an external fault to the transformer across its insulator. This fault was most likely induced by marginal component design insulation level and contributed to by salt contamination of the insulator. <br /><br /> Corrective actions were: 1) Operations stabilized the unit in mode 3. 2) The affected potential transformer has been replaced. 3) Contamination preventive coatings are scheduled for both units synchronizing potential transformers 4) The unit 1 Main Transformers and Isophase bus have been tested. 5) The Main Generator was visually inspected with satisfactory results.
335 | 3351995003 | 1995-07-08 | QR5 | Turbine Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On July 8, 1995, Unit 1 was operating at 100 percent reactor power. Operations personnel were conducting a scheduled Turbine overspeed trip surveillance per an approved plant procedure. During the portion of the surveillance that tests a solenoid valve for Overspeed Protection Control (20-1 OPC) a utility non-licensed operator failed to close an isolation valve as directed by the procedure. Failure to close this valve allowed electro-hydraulic (EH) fluid from the Governor valves (GV) and Intercept valves (IV) to drain when the solenoid valve was opened in a subsequent step. Draining of the EH fluid caused closure of the Main Turbine Governor and Intercept valves which resulted in an automatic reactor trip. <br /><br /> The root cause of this event was cognitive personnel error on the part of a utility non-licensed operator who failed to properly implement a procedural step during performance of a surveillance.<br /><br /> Corrective actions for this event: 1) Operations personnel involved with the event were counselled. 2) Procedure changes are being made to incorporate human factors improvements and additional step verifications. 3) Other load threatening surveillances are being reviewed to determine if generic change are warranted. 4) A technical subcommittee is evaluating this event for additional corrective actions to prevent reoccurrence. 5) Site management held a trip review meeting open to all disciplines for lessons learned from this event.
335 | 3351995010 | 1995-11-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On November 16, 1995, at 1741 hours, St. Lucie Unit 1 was manually tripped from 100 percent power due to decreasing water level in the 1B Steam Generator. The level in the 1B Steam Generator was restored immediately following the reactor trip, and Auxiliary Feedwater was used to supply. feedwater to both Steam Generators. All safety function status checks were satisfactorily completed and the plant was stabilized in Mode 3 following the trip. <br /><br /> The event was caused by a degraded 24 volt DC power supply to the 1B Steam Generator Main Feedwater Controller. The degraded power supply, coupled with a momentary voltage drop associated with the start of a plant fire pump, resulted in a voltage loss to the feedwater controller. Loss of voltage to the controller caused the partial closure of the Main Feedwater Regulating Valve supplying feed to the 1B Steam Generator. Subsequent testing showed that the power supply had degraded, and was supplying voltages incompatible with proper controller operation. <br /><br /> Corrective actions: 1) The power supply for the 1B feedwater controller was tested and replaced. 2) The 1A and Unit 2 feedwater power supplies were tested and found to be satisfactory. 3) The failure mode of the power supply is being evaluated. 4) A plant modification was developed to provide a vital source of power to the controller which is less susceptable to voltage fluctuatuations. 5) Plant staff is evaluating the Feedwater and Condensate systems for additional power supplies which could represent single point trip vulnerabilities. 6) Plant staff is evaluating the cause of additional alarms which were received during the momentary voltage drop.
335 | 3351996002 | 1996-02-22 | QP5 | Excessive Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On February 22, 1996, while at 100 percent power, a Control Element Assembly (CEA) dropped on Unit 1 during periodic testing due to a failed silicon control rectifier (SCR). The CEA could not be recovered and a unit shutdown was initiated in accordance with Technical Specification (TS) 3.0.3. An Unusual Event notification was made due to the TS required shutdown and inability to realign the CEA within the action time. At approximately 25 percent power the unit was manually tripped due to increasing Steam Generator (SG) levels caused by a failed main feedwater regulating valve (MFRV). Additionally, a steam bypass control valve operated improperly during the event. The plant was stabilized in Mode 3 and the Unusual Event was terminated. <br /><br /> The cause of the dropped CEA was a failed SCR in the upper gripper power switch module. Entry into TS 3.0.3 was caused by the inability to realign the dropped CEA within the allowable TS action time. The cause of the feedwater regulating valve failure was a leaking instrument air line. The steam bypass control valve improper operation was due to an air booster relay misadjustment. <br /><br /> Significant Corrective Actions: 1) Power switch modules for the CEA were replaced and additional CEA testing was performed. is being performed by the vendor. 2) Air lines were replaced on MFRVs and preventive maintenance (PM) enhancements are being made. 3) Steam Bypass Control System (SBCS) valves were inspected and repaired and actuators and positioners are being upgraded. SBCS procedure enhancements were made.
335 | 3351996012 | 1996-08-31 | QR6 | Manual Reactor Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 58 | On August 31,1996, St. Lucie Unit 1 was operating in Mode 1 at 100 percent reactor power. At 1848, accumulated gas was detected in the 1B main transformer and a Unit shutdown was commenced as required by plant operating procedures. During the plant shutdown, gas accumulation in the 1B main transformer continued to increase, and the reactor and turbine were manually tripped at 2018 to preclude a potential failure of the main transformer. The reactor trip was uncomplicated and all systems functioned as designed. <br /><br /> The cause of the increased gas accumulation in the transformer was attributed to the intrusion of outside air into the transformer oil cooling system through a leak in an oil cooler. This was confirmed by oil analysis which was conducted following the Unit shutdown. <br /><br /> Corrective actions include: 1) A detailed inspection was performed of the 1B main transformer cooling system and the affected oil cooler was replaced. 2) A modification was performed on the 1B main transformer to reduce negative pressure areas within the cooling system susceptible to air in-leakage. 3) The main transformer was pressure tested to verify leak tightness and returned to service. 4) Metallurgical analysis is being performed to determine the leak failure mechanism. 5) Additional monitoring of transformer gas accumulation is being performed. 6) Additional transformers are being evaluated for generic applicability. 7) Substation guidelines for transformer assembly and pre-installation testing are being reviewed and revised as necessary.
335 | 3351997003 | 1997-03-04 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On March 4, 1997, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. Reactor Protective System (RPS) following the loss of a reactor coolant pump (RCP). Operation of the RCP was interrupted when the electrical supply breaker for the pump opened. Following the trip, a main feedwater regulating valve failed to close as designed and operator action was taken to mitigate excess feedwater flow. The plant was stabilized in Mode 3 and subsequently returned to Mode 1 operation on March 7, 1997, following replacement of the RCP breaker and repair of the main feedwater regulating valve control circuit relay. <br /><br /> The automatic reactor trip was caused by the loss of the 1A2 RCP when an electrical supply breaker for the pump opened. Loss of the RCP resulted in a valid actuation of the RPS low reactor coolant flow trip. The opening of the supply breaker was evaluated by FPL and an experienced vendor and a specific cause was not determined. Corrective actions were taken for the potential root causes identified. The failure of the main feedwater regulating valve to close was caused by the malfunction of a K2 relay in the control circuitry for the valve. <br /><br /> Corrective actions include: 1) The RCP breaker was replaced and the pump was returned to service. 2) Breaker inspection and testing was performed. 3) Similar breakers were inspected and adjusted. 4) Visual monitoring was installed in the RCP breaker area. 5) The feedwater regulating valve was returned to service following replacement of a failed relay in the valve control circuit. 6) Additional failure analysis is being performed for a relay which was replaced in the feedwater valve circuitry. 7) Unit 2 main feedwater regulating valve testing will be performed during the next scheduled refueling outage.
335 | 3351998003 | 1998-01-10 | QR6 | Manual Reactor Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 60 | On January 10, 1998, St. Lucie Unit 1 was operating in Mode 1 at 60 percent reactor power. The Unit 1 reactor was manually tripped in response to Digital Electro-Hydraulic (DEH) system alarms, which indicated that a fault had occurred within the DEH system. An operator observed and reported a DEH oil leak immediately prior to the alarms. The plant was stabilized in Mode 3. Following the Unit 1 manual trip, it was observed that both main feedwater pumps had tripped due to low pump flow conditions. The DEH test block leakage was repaired and the unit was returned to Mode 1 operation. The root cause of the DEH test block leakage was determined to be o-ring extrusion caused by inadequate joint closure between the test block and the trip block. During the investigation of the leakage, a gap was discovered under the test block, indicating that the test block was not fully seated to the trip block. O-ring groove machining and the length of the original bolting did not allow for proper closure of the joint. Corrective Actions include: 1) Shortening the bolts by 0.125" and reinstalling at the correct torque values. 2) Increasing the trip block bolt holes depth from 1.00" to 1.25" per the drawing. 3) Revising Maintenance Procedures to include a step for verifying, with feeler gauges, that the test blocks are completely mated to the trip blocks, and that appropriate torque values are applied. 4) Reviewing the event for inclusion in the Instrument and Control Maintenance continuing training program. 5) Evaluating potential plant changes to prevent loss of Main Feedwater Pumps following a reactor trip.
335 | 3351999003 | 1999-08-23 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | St. Lucie 1 | P | CE | PO | 100 | On August 23, 1999, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. At approximately 1234 hours, the control room received annunciation that the turbine generator gland seal steam pressure was abnormal. Two minutes later annunciator D-13, Turbine Vacuum Low, was also received. With main condenser backpressure approximately 5.0 inches Hg increasing, licensed operators entered off normal procedure (ONP) -1- 0610031, "Loss of Condenser Vacuum," and prepared for a rapid downpower. An operator was dispatched in an attempt to place the hogging air ejector in service. However, within 20 seconds, the main condenser backpressure reached the administrative limit of 5.5 inches Hg, at which time the nuclear plant supervisor directed that the reactor be tripped. The plant was manually tripped at 1236 hours and stabilized in Mode 3. The trip was determined to be uncomplicated with respect to safety system functions and operating parameters. Loss of condenser vacuum was caused by the malfunction of the pilot control valve for the turbine gland seal steam regulating valve, PCV-08-850, for the number 2 low pressure turbine, north end. The malfunction of the PCV caused a breach of the condenser envelope that rapidly degraded the condenser vacuum. Repairs were implemented, and St. Lucie Unit 1 entered Mode 1 operation on August 26, 1999.
335 | 3351999006 | 1999-10-29 | QR5 | Turbine Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On October 29, 1999, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. At 0105 hours the St. Lucie Unit 1 control room received annunciation of D-12 "Turbine Bearing Oil Pressure Low." Operations personnel discovered that a small amount (approximately two drops per minute) of oil was leaking from the cover of the turbine protective device trip block. The turbine/generator and reactor automatically tripped at 0129 hours. Standard post trip actions were carried out and the reactor was stabilized in Mode 3. The cause of this event was the installation of a Westinghouse supplied defective diaphragm for the turbine low bearing oil trip protective device. The failure of this diaphragm dumped the autostop oil pressure and tripped the turbine/generator. The loss of autostop oil pressure resulted in the opening of the DEH interface valve, dumping all DEH oil pressure. The loss of DEH oil pressure resulted in the automatic trip of the reactor. The faulty diaphragm was replaced and miscellaneous minor equipment issues were dispositioned.
335 | 3351999007 | 1999-10-30 | QR6 | Manual Reactor Trip | [45 empty] | St. Lucie 1 | P | CE | SU | 3 | On October 30, 1999, St. Lucie Unit 1 was in the process of a reactor startup. While Operations personnel were performing turnover activities, the level of the 1A steam generator began dropping and attempts to recover the 1A steam generator level were unsuccessful. Upon receiving annunciation of steam generator low level pre-trip alarms the reactor was manually tripped at 0641 hours. The plant was stabilized in Mode 3. There were no significant equipment issues during or after the manual reactor trip. The cause for the manual reactor trip was personnel error. Operators paid insufficient attention to detail regarding the 1A steam generator steam flow/feed flow mismatch that resulted from unbalanced operation of the atmospheric dump valves. Operations Management reinforced expectations regarding the role of control room supervisors and the conduct of crew turnovers. The plant was restarted later the same day. Procedural enhancements will be made with regard to the role of control room supervisors and atmospheric dump valve operation.
335 | 3352001007 | 2001-06-05 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On June 5, 2001, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. At 1048 hours, St. Lucie Unit 1 experienced an unexpected trip of the 1A2 reactor coolant pump (RCP). This was immediately followed by an automatic reactor trip from the reactor protection system (RPS) on low reactor coolant flow. The Unit 1 turbine generator tripped following the reactor trip. Plant electrical distribution systems automatically transferred from the unit auxiliary transformers to the unit start up transformers as required for onsite power. Approximately one minute later, the 1B main feedwater pump (MFP) tripped and the auxiliary feedwater system actuated to provide cooling flow to the steam generators. All safety-related equipment operated per design. FPL determined that the most probable cause of the 1A2 reactor coolant pump trip was the spurious actuation of a Westinghouse SA-1 motor protective relay device. This determination was based on vendor notifications, known industry history, and the symptoms of the trip. FPL replaced the SA-1 relay and a main feedwater recirculation valve positioner, and at power operations for St. Lucie Unit 1 resumed on June 7, 2001.
335 | 3352002002 | 2002-10-24 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | St. Lucie 1 | P | CE | PO | 6 | On October 24, 2002, St. Lucie Unit 1 was in Mode 1 at approximately 6 percent reactor power during power ascension at the end of refueling outage SL1-18. Attempts to "latch" the turbine were unsuccessful, and the resultant turbine trip signal drove the 15 percent main feedwater bypass valves to the post-trip position. Steam generator levels rose and the operating main feedwater pump tripped on high steam generator -water level. The operators tripped the reactor when the steam generator water levels dropped below the procedural trip requirements during the efforts to restore feedwater. The cause of this event was the failure of the turbine valves to latch and latent procedural weaknesses in that the adverse consequences of a "partial latch" condition were not addressed. The failed turbine latch initiated the chain of events that ultimately led to the manual reactor trip. Corrective actions include the completed repair of the turbine front standard latch function, procedure enhancements, continuing training, and potential plant modifications to the 15 percent main feedwater bypass valve controller.
335 | 3352010006 | 2010-06-16 | QR6 | Manual Reactor Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 45 | On June 16, 2010, St. Lucie Unit 1 was in Mode 1 returning from a scheduled refueling outage when a manual reactor trip was initiated. Due to the control element drive mechanism (CEDM) system not being able to effectively maintain two control element assemblies (CEAs) in the withdrawn and aligned position. This event required Operations to manually trip Unit 1 due to greater than one CEA being misaligned from other CEAs greater than twenty inches. All control systems responded as required. A root cause evaluation (ROE) determined the cause to be a failure of the snubber network capacitors to perform its designed function. Contributing causes included ineffective maintenance on the cable spreading room air conditioners and a weakness in purchasing the correct capacitors for the power switches. Corrective actions included replacement of the under rated network capacitors on the upper gripper power switches which are normally energized (holding) on all CEDMs and the lower gripper, lift, and load transfer power switches for the lead group CEDM's, and reduction of the temperature and humidity within the cable spreading room.
335 | 3352011001 | 2011-08-22 | QL7 | Degraded condenser vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | St. Lucie 1 | P | CE | PO | 89 | On August 22, 2011, St. Lucie Unit 1 was operating in Mode 1 at 89% when it was manually tripped due to rising condenser back pressure. All control element assemblies (CEAs) fully inserted into the core. The cause of the rising back pressure was an influx of jelly fish into the intake structure degrading Unit 1 circulating water system performance. Decay heat removal was initially from the main feedwater and steam bypass to the main condenser. However, subsequent to the manual trip, the 1B main feedwater pump was manually secured due to a leak on the pump casing. The 1A main feedwater pump subsequently tripped due to low suction pressure after manually securing the 1B condensate pump and decay heat removal was transitioned to the atmospheric dump valves and auxiliary feedwater. Root cause evaluation determined the jellyfish intrusion rate exceeded the current capacity of the traveling water screens and trash pits. In addition, procedural guidance did not anticipate the possible rapidly escalating jellyfish intrusion rate and the urgency for response regarding the negative effect of the rapid jelly intrusion on condenser back pressure was not recognized. Contributing causes included: plant maneuvering did not account for condenser back pressure margin, equipment degradation and malfunctions, and design deficiencies. Corrective actions include procedure revisions and design changes to address procedure deficiencies and correct design deficiencies.
335 | 3352011002 | 2011-10-19 | QL7 | Degraded condenser vacuum | [45 empty] | St. Lucie 1 | P | CE | PO | 86 | On October 19, 2011, St. Lucie Unit 1 was operating in Mode 1 at 86% when the unit was manually tripped due to rising condenser backpressure. The cause of the rising backpressure was an unplanned trip of the 1A1 circulating water (CW) pump. Condenser backpressure reached procedural limits which required a manual unit trip. The 1A1 CW pump breaker tripped as a result of an internal motor fault. Unit 1 was in a planned power reduction at the end of the cycle. All control element assemblies (CEAs) fully inserted and decay heat removal was achieved through main feedwater and steam bypass to the main condenser. A root cause evaluation (RCE) concluded that ineffective condition monitoring of the 1A1 CW pump motor for degraded air flow passages prior to scheduled motor overhauls, resulted in a buildup of salt and corrosion products in the rotor cooling air flow passages, restricting air flow. Contributing causes included previous actions to implement quarterly resistance temperature detector measurements for the CW pump motors were ineffective. Corrective actions will implement temperature monitoring using the CW pump motor winding resistance temperature detectors (RTDs) .
335 | 3352012003 | 2012-03-31 | QR6 | Manual Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | St. Lucie 1 | P | CE | PO | 10 | On March 31, 2012 at 0022 EDT, St. Lucie Unit 1 was in Mode 1 at 10% reactor power and performing post modification testing (PMT) of the steam bypass control system (SBCS) when the reactor was manually scrammed after a steam bypass control valve opened unexpectedly at 0019 EDT. Immediately following the reactor scram the steam bypass control valve closed, terminating the cooldown. Additionally, Operators closed the main steam isolation valves in accordance with Emergency Operating Procedure (EOP-01), "Standard Post Trip Actions" due to steam generator pressure decreasing to less than 750 psia. All control element assemblies (CEAs) fully inserted. No automatic safety system actuations were required and none occurred. RCS heat removal was maintained with auxiliary feedwater and atmospheric dump valves. The offsite power grid was available and stable. The root cause for failure of the control valve was less than adequate analyses supporting a recently implemented design change and less than adequate post modification testing that failed to provide appropriate contingency actions to mitigate potentially unfavorable SBCS test responses. Corrective actions include isolating the malfunctioning SBCS valve until it can be redesigned and replaced. SBCS capability is provided by the remaining four SBCS valves.
335 | 3352012005 | 2012-06-22 | QR5 | Turbine Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On June 2, 2012 at 1935 with St. Lucie Unit 1 in Mode 1 at 100% power the reactor automatically tripped from normal full power operation due to a loss of load following a failure of the turbine control system (TCS). The reactor trip was uncomplicated and all control rod assemblies (CEAs) fully inserted. No automatic safety system actuations were required and none occurred. The reactor coolant system (RCS) heat removal was maintained with main feedwater (MFW) and steam bypass to the condenser. The Offsite power grid was available and stable.<br /><br /> The reactor trip on turbine trip was caused by loss of communications of the Drop 3 and Drop 53 controllers in the recently installed Ovation turbine control system (TCS). The direct cause for the failure of the primary controller (Drop 53) was an intermittent fault in the Remote Node Controller (RNC) or the Media Attachment Unit (MAU). The back up controller (Drop 3) failed due to a failed fiber optic (FO) cable field connector. The root cause of this event was ineffective design control for the TCS upgrade.<br /><br /> Immediate corrective actions taken included removing all questionable control modules and controllers. Corrective actions to prevent reoccurrence included providing additional guidance to operators in the annunciator response procedure and implementing a new normal operating procedure for the TCS.<br /><br /> This event had no effect on the health and safety of the public.
335 | 3352013001 | 2013-03-12 | QL5 | Partial Closure of MSIVs | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On March 12, 2013 at 1451 EDT, St. Lucie Unit 1 was in Mode 1 at 100% reactor power when the spurious closure of HCV-08-1B, 1B Main Steam Isolation Valve (MSIV), resulted in an automatic reactor trip. Upon troubleshooting and valve disassembly, it was discovered that interference between the internal tail link and the valve body prevented the valve disc from fully opening. This allowed unintentional loading of internal parts resulting in the failure of the valve's lower shear pin. The pin failure led to spindle/disc separation and inadvertent closure of the valve.<br><br> This reactor trip event is reportable pursuant to 10 CFR 50.73(a) (2) (iv) (A) as an automatic actuation of the reactor protection system (RPS). This event had no significant safety consequence since the RPS successfully performed its intended safety function upon the failure of the 1B MSIV.<br><br> The internal interference was caused by an oversized tail link supplied by the valve manufacturer. To correct the problem, the tail link was reworked to eliminate the body interference, and the MSIV was reassembled.<br><br> This event had no effect on the health and safety of the public.
335 | 3352013002 | 2013-11-12 | QR6 | Manual Reactor Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 90 | On November 12, 2013 St. Lucie (PSL) Unit 1 was manually tripped due to a digital-electro-hydraulic (DEH) fluid leak from a tubing fitting in the turbine control system. Prior to the reactor trip, PSL Unit 1 was at 90% power ascending to 98% power following the SL1-25 refueling outage. Following the reactor trip, emergency operating procedures were successfully completed and the unit was stabilized in Mode 3. The reactor trip was uncomplicated. All systems functioned as designed. There were no automatic safety system actuations as a result of the trip. <br /><br /> A root cause evaluation was performed which identified the cause as failure of a DEH tubing fitting as the result of high cycle fatigue fracture and inadequate tubing support following a DEH pump replacement. <br /><br /> Corrective actions include: 1) update of the engineering procedure for post-modification testing and 2) update of the maintenance procedure for post-maintenance testing, to inspect for vibration and inadequate support of adjacent tubing/piping after a change to a vibration inducing component (pump, fan, etc.) <br /><br /> This reactor trip event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of reactor protection system (RPS). This event had no significant safety consequence. Given the response of the plant and the actions taken, the health and safety of the public was not affected by this event.
335 | 3352015001 | 2015-08-09 | QR8 | Spurious Reactor Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On August 9, 2015 with St. Lucie Unit 1 in Mode 1 at 100% reactor power, an unplanned reactor trip occurred. The trip occurred while Operators were performing a reactor protection system (RPS) logic matrix test in which the individuals performing the test did not follow the procedure steps in sequence resulting in a loss of configuration control. As a result, a set of reactor trip circuit breakers (TCBs) was opened before ensuring that all TCBs tested in the previous test section had been closed.<br /><br /> Corrective actions include procedure revisions to the test methodology to ensure configuration control of the TCBs is maintained through additional verification techniques. <br /><br /> This reactor trip event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the reactor protection system (RPS). This event had no significant safety consequence since the RPS successfully performed its intended safety function upon opening the trip circuit breakers.<br /><br /> This event had no effect on the health and safety of the public.
335 | 3352016003 | 2016-08-21 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | St. Lucie 1 | P | CE | PO | 38 | On August 21, 2016, during Unit 1 restart following a maintenance outage, an unexpected actuation of the Main Generator Inadvertent Energization Lockout Relay caused the main generator to trip, resulting in an automatic reactor trip. The generator lockout prevented the automatic transfer of station auxiliaries to the available startup transformer power, requiring the emergency diesel generators to start and power the safety related buses. Reactor coolant pumps normally powered through the non-safety buses were deenergized, and decay heat removal was via natural circulation and Auxiliary Feedwater. The lockout relay actuation was caused by a latent error introduced during a 2013 design modification where the maintenance configuration control procedure did not prevent a wire from being inadvertently removed from the circuit. <br /><br /> Corrective actions included restoration of the affected circuit, implementation of procedure guidance to verify the inadvertent energization relay state following Main Generator manual synchronization and revisions to the maintenance configuration control procedure. <br /><br /> This licensee event report is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) for system actuations of the reactor protection system, the emergency diesel generators and the auxiliary feedwater system. <br /><br /> This event had no effect on the health and safety of the public.
335 | 3352018001 | 2018-10-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On October 29, 2018, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. At 1258 hours the control room was alerted to abnormal water levels in the 4B feedwater heater. Troubleshooting was unable to determine the cause and at 1304 hours the 1B steam generator water level began to decrease. The operators initiated a rapid downpower at 1308 hours. At 1317 hours the operators executed a manual reactor scram due to 1B steam generator water level approaching procedural limits. <br /><br /> Malfunctioning feedwater heater system controllers caused the inadequate main feedwater flow and loss of steam generator water level. Legacy foreign material was removed from the 4B feedwater heater normal drain valve controller restoring that component to service; remaining susceptible controllers will be visually inspected for foreign material. Preventative maintenance practices allowed abnormal wear on the normally closed 4B feedwater alternate drain valve controller and the controller was replaced; preventative maintenance practices are being revised to account for this failure mechanism.<br /><br /> The operators and plant responded as trained and designed for the feedwater system failures. The resultant trip was uncomplicated and plant risk remained green. There was no adverse effect on the health and safety of the public.
335 | 3352019001 | 2019-04-25 | QR5 | Turbine Trip | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On April 25, 2019, St. Lucie was in Mode 1 at 100 percent reactor power. At 0918 hours the reactor tripped due to a generator lockout during reactive power lagging capability testing. The trip was uncomplicated and all safety systems responded as designed. The plant was stabilized in Mode 3 with decay heat removal via the main feedwater system and condenser steam bypass system. <br /><br /> The direct cause of the generator lockout was attributed to a localized breach in the ground wall insulation of stator bar B17. The quarantined equipment was tested at the original equipment manufacturer (OEM) testing facility. The causal analysis could not establish a root cause for the defect. <br /><br /> The generator repairs and post maintenance testing were successfully completed. <br /><br /> Automatic reactor trips are analyzed events in the Updated Final Safety Analysis Report (UFSAR). The trip and post trip actions were uncomplicated. Therefore, this event had no impact on the health and safety of the public.
335 | 3352019002 | 2019-09-07 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On September 7, 2019, St. Lucie was in Mode 1 at 100 percent reactor power. At 0824 the Unit 1 Reactor tripped automatically on a low Reactor Coolant System flow actuation of the Reactor Protection System. The trip was uncomplicated and all safety systems responded as designed. The plant was stabilized in Mode 3 with decay heat removal via the main feedwater system and condenser steam bypass system.<br /><br /> The direct cause was an electrical fault in the 1A1 Reactor Coolant Pump (RCP) motor. The electrical fault was initiated after a cooling water pipe for the 1A1 RCP motor's upper bearing failed and the leaking water entered the motor enclosure. The root cause evaluation determined there were inadequate technical controls over the use of generic reuse specifications and engineering quality instructions during a 2010 modification of RCP motor cooling water piping. <br /><br /> The 1A1 RCP motor was replaced, and post maintenance testing was successfully completed. St. Lucie Unit 1 was returned to service on September 21, 2019. <br /><br /> Automatic reactor trips are analyzed events in the Updated Final Safety Analysis Report (UFSAR). The trip and post trip actions were uncomplicated. Therefore, this event had no impact on the health and safety of the public.
335 | 3352021001 | 2021-12-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 1 | P | CE | PO | 100 | On December 10, 2021 at 1024 EST with Unit 1 in Mode 1 at 100% power, the reactor was manually tripped due to lowering level in the steam generators. The trip was uncomplicated with all systems responding normally post trip. Operators restored steam generator level utilizing main feedwater and stabilized the reactor in Mode 3. <br /><br /> The event occurred while replacing a feedwater heater control Pressure Differential Indicating Switch (PDIS). In the process of landing the wires from the new PDIS on the terminal strip, the technician made inadvertent contact with the enclosure housing resulting in a blown supply fuse which caused a loss of high pressure heater level control and a reduction of Steam Generator feedwater flow. <br /><br /> Due to the emergent nature of this work, some of the normal preplanned mitigation measures were not in place. Corrective actions include maintenance procedure revisions. <br /><br /> Manual reactor trips are analyzed events in the Updated Final Safety Analysis Report. The trip was uncomplicated. Therefore, this event had no impact on the health and safety of the public.
336 | 3361987002 | 1987-01-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 100 | POWER LEVEL - 100%. ON JANUARY 2, 1987 AT 0840 AN AUTOMATIC TRIP OCCURRED FROM 100% POWER OPERATION. SYSTEM WHEN 2 OUT OF 4 CHANNELS REACHED THEIR TRIP SETPOINT FOR LOW STEAM GENERATOR LEVEL. OPERATIONS PERSONNEL RESPONDED TO THE TRIP BY PERFORMING EMERGENCY OPERATIONS PROCEDURES 2525, 'STANDARD POST TRIP ACTIONS' AND 2526, 'REACTOR TRIP RECOVERY'. PERFORMANCE OF THESE PROCEDURES PLACED THE UNIT IN A STABLE CONDITION WITH LEVEL IN THE #2 STEAM GENERATOR IN ITS NORMAL RANGE. ROOT CAUSE OF THIS EVENT WAS THE FAILURE OF THE #2 STEAM GENERATOR FEEDWATER REGULATING VALVE, 2-FW-51B, TO GO TO A LOCKED UP CONDITION ON A LOSS OF POWER. THE FEEDWATER REGULATING VALVE WAS REPAIRED AND THE UNIT WAS TAKEN CRITICAL ON 1/3/87 AT 0600, AND THE UNIT WAS BACK AT 100% POWER ON 1/4/87 AT 1350. LOSS OF POWER TO 2-FW-51B OCCURRED WHEN ITS POWER SUPPLY, NON-VITAL REGULATED 120VAC INSTRUMENT PANEL, 2-IAC-2, AUTOMATICALLY SWITCHED FROM ITS PRIMARY TO ALTERNATE SUPPLY. THIS CHANGE IN POWER SUPPLIES UTILIZES A BREAK BEFORE MAKE AUTOMATIC SWITCH LOGIC. THIS TRANSFER RESULTS IN A MOMENTARY POWER LOSS. THE POWER TRANSFER WAS INITIATED WHEN AN ARC WAS DRAWN IN THE FIRE SUPPRESSION ALARMS PANEL, C-26. THE ARC RESULTED IN A DIRECT SHORT IN 2-IAC-2, WORK IN C-26 WAS PERFORMED IN SUPPORT OF APPENDIX R MODIFICATIONS.
336 | 3361987007 | 1987-04-16 | QR5 | Turbine Trip | [45 empty] | Millstone 2 | P | CE | PO | 100 | POWER LEVEL - 100%. ON 4/16/87 AT 0717 HOURS, AN AUTOMATIC REACTOR TRIP OCCURRED FROM 100% POWER OPERATION. THE TRIP WAS DUE TO A TURBINE TRIP WHICH WAS CAUSED BY THE GENERATOR EXCITER FIELD BREAKER OPENING. OPERATIONS PERSONNEL RESPONDED TO THE TRIP BY PERFORMING EMERGENCY OPERATIONS PROCEDURE 2525, 'STANDARD POST TRIP ACTIONS' AND 2526, 'REACTOR TRIP RECOVERY'. PERFORMANCE OF THESE PROCEDURES PLACED THE UNIT IN A STABLE CONDITION. THE CAUSE OF THE EVENT WAS THE ACTUATION OF GENERATOR VOLTS/HERTZ RELAY (59X2) WHICH IS A COMMON TRIP FOR BOTH THE GENERATOR EXCITER FIELD BREAKER AND GENERATOR FIELD BREAKER. PROVIDES BACKUP PROTECTION WHEN THE GENERATOR IS EXCITED AND NOT SYNCHRONIZED TO THE GRID. THE REASON FOR THE ACTUATION OF RELAY 59X2 IS UNKNOWN. WITH RELAY 59X2 WAS NOT ACTUATED, THEREFORE THE NORMAL SEQUENCE TO ACTUATE THE 59X2 RELAY WAS NOT USED. THE TWO REMAINING METHODS OF ACTUATION ARE ELECTROMAGNETIC INTERFERENCE (EMI) AND MANUAL ACTUATION OF THE RELAY. ALL EQUIPMENT RESPONDED AS REQUIRED FOR AN UNCOMPLICATED REACTOR TRIP.
336 | 3361987011 | 1987-07-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 80 | POWER LEVEL - 080%. ON JULY 23, 1987 AT 0546, AN AUTOMATIC REACTOR TRIP OCCURRED FROM 80% POWER, 2075 PSIA. THE EVENT BEGAN WITH A STUCK SPRAY VALVE CAUSING DECREASING REACTOR COOLANT SYSTEM (RCS) PRESSURE. DURING THE RESPONSE TO DECREASING PRESSURE, THE TRIP WAS INITIATED BY LOW LEVEL IN #1 STEAM GENERATOR (S/G). OPERATIONS STAFF RESPONDED BY PERFORMING EMERGENCY OPERATIONS PROCEDURES EOP 2525 'STANDARD POST TRIP ACTIONS' AND EOP 2526 'REACTOR TRIP RECOVERY'. THE SPRAY VALVE WAS ISOLATED MANUALLY. PERFORMANCE OF THESE PROCEDURES PLACED THE UNIT IN A STABLE CONDITION. THE CAUSE OF THE EVENT WAS LOW LEVEL IN #1 S/G. A FAULTY FEED REGULATING VALVE DIFFERENTIAL PRESSURE INDICATOR CONTROLLER, PDIC 5270, CONTRIBUTED TO THE TRIP. THE SPRAY VALVE 2-RC-1OOF WAS REPAIRED; PDIC 5270 WAS REPLACED. THE UNIT WAS TAKEN CRITICAL ON JULY 23, 1987 AT 1903. THE UNIT RETURNED TO 100% POWER ON JULY 24, 1987 AT 1805.
336 | 3361987009 | 1987-09-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 91 | POWER LEVEL - 091%. WHILE OPERATING AT 91% POWER ON SEPTEMBER 2, 1987 AT 2015 THE UNIT EXPERIENCED AN AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL IN THE #1 STEAM GENERATOR. THE OPERATION'S STAFF WAS PERFORMING A ROUTINE REDUCTION IN POWER LEVEL FROM 100% TO 90%. DURING THIS EVOLUTION THE SECONDARY PLANT OPERATOR OBSERVED THE FEED FLOW TO THE #1 STEAM GENERATOR LESS THAN THE STEAM FLOW. THE OPERATOR TOOK MANUAL CONTROL OF THE FEEDWATER REGULATING VALVE, 2-FW-51A, AND THE FEEDWATER REGULATING BYPASS VALVE, 2-FW-41A, IN AN ATTEMPT TO RESTORE LEVEL IN THE #1 STEAM GENERATOR. LEVEL CONTINUED TO DECREASE IN THE #1 STEAM GENERATOR AND THE UNIT TRIPPED. OPERATIONS RESPONDED TO THE TRIP BY PERFORMING EOP 2525, 'STANDARD POST TRIP ACTIONS' AND EOP 2526 'REACTOR TRIP RECOVERY'. NO OTHER SYSTEMS WERE AFFECTED AND THE UNIT WAS PLACED IN A STABLE CONDITION. THE #1 FEEDWATER REGULATING VALVE, 2-FW-51A, WAS DISASSEMBLED AND REPAIRED. DURING THE DISASSEMBLY IT WAS DISCOVERED THAT THE STEM HAD SEPARATED FROM THE PLUG. THIS EVENT IS BEING REPORTED PURSUANT TO THE REQUIREMENTS OF PARAGRAPH 50.73(A)(2)(IV) DUE TO THE AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR LEVEL. SIMILAR LER'S: NONE.
336 | 3361987012 | 1987-11-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 100 | POWER LEVEL - 100%. WHILE OPERATING AT 100% POWER ON NOVEMBER 16, 1987 AT 0211 THE UNIT EXPERIENCED AN AUTOMATIC REACTOR TRIP DUE TO A LOW STEAM GENERATOR LEVEL IN THE #1 STEAM GENERATOR. FOLLOWING TURBINE VALVE TESTING, THE OPERATOR RESPONDED TO AN INDICATED HIGH LEVEL IN #1 STEAM GENERATOR BY TAKING MANUAL CONTROL OF THE #1 FEEDWATER REGULATING VALVE. THE VALVE FAILED TO RESPOND TO ALL MANUAL CLOSED SIGNALS UNTIL A HIGH STEAM GENERATOR LEVEL INITIATED A RAMP CLOSING SIGNAL, CLOSING THE VALVE. THIS RESULTED IN A LOW STEAM GENERATOR LEVEL AND SUBSEQUENT REACTOR TRIP BEFORE RAMP OVERRIDE COULD BE INITIATED. ALL SAFETY SYSTEMS RESPONDED NORMALLY WITH THE EXCEPTION THAT THE 'A' AUXILIARY FEED PUMP (AFP) FAILED TO START ON THE AUTO AUXILIARY FEED ACTUATION SIGNAL AND WAS STARTED MANUALLY. THE 'SPRING-RETURN-TO-NORMAL', 'A' AUTO AUXILIARY FEED OVERRIDE SWITCH WAS IN AN INTERMEDIATE POSITION, PREVENTING THE START. OTHER EVENTS SUBSEQUENT TO THE REACTOR TRIP INCLUDED THE LOSS OF THE A AND C REACTOR COOLANT PUMPS (RCPS) WHEN THE 25A (6.9KV) BUS FAILED TO TRANSFER FROM THE NORMAL STATION SERVICE TRANSFORMER TO THE RESERVE STATION SERVICE TRANSFORMER. THIS WAS CAUSED BY A DAMAGED COMPONENT PREVENTING FULL RACKING IN OF THE BREAKER.
336 | 3361988011 | 1988-10-25 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Millstone 2 | P | CE | PO | 100 | On October 25, 1988 at 0719 hours with the plant in Mode 1 at 100 percent power, a loss of normal power (LNP) on both 4160 volt vital AC buses caused a reactor trip and ESF actuation. As designed, all loads were shed from both safety buses, both emergency diesels automatically started and all safe shutdown loads were sequenced onto the diesel powered safety buses. The plant functioned as expected during the reactor trip and subsequent plant recovery. <br /><br />The event occurred while unit electrical maintenance personnel were preparing to remove the Facility Z2 Service Water pump motor from service for preventive maintenance. The event was caused by personnel error when workers improperly connected a grounding device to the "BUS" side of the 4160 volt breaker compartment in bus 24D, causing a symmetrical three phase fault. The fault cleared when the feeder breakers to the bus were opened and the bus was de-energized. <br /><br />Immediate action was taken to verify all equipment was responding as required and the plant was in a safe condition.
336 | 3361990006 | 1990-05-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 100 | On May 8, 1990 at 00:49 hours with the Unit in MODE 1 at 100% power, plant operators manually tripped the reactor due to decreasing levels in the #1 steam generator. The secondary plant operator observed a rapidly decreasing level in the #1 steam generator, with the feedwater regulating valve, 2-FW-51A, indicating full open. With control of main feed flow to #1 steam generator apparently lost and since steam generator level was decreasing, the unit was manually tripped. Operators then performed EOP 2525, "Standard Post Trip Actions" and EOP 2526, "Reactor Trip Recovery". All equipment responded as expected and the unit was placed in a stable condition. Main feed flow to the #1 steam generator was restored and controlled with the feedwater regulating bypass valve, 2-FW-41A. The #1 feedwater regulating valve, 2-FW-51A, was disassembled and inspected. During the disassembly it was discovered that the stem had separated from the plug. This event is being reported pursuant to the requirements of paragraph 50.73(a)(2)(iv) due to the manual reactor trip on decreasing steam generator level. <br /><br /> Similar LER's : 87-009
336 | 3361990012 | 1990-08-27 | QR8 | Spurious Reactor Trip | [45 empty] | Millstone 2 | P | CE | PO | 100 | On August 27, 1990, at 0100, with the reactor plant in MODE 1 (100% power, 575 degrees F, 2263 psig), while performing Surveillance Procedure SP 2601D "Power Range Safety Channel and Delta T Power Channel Calibration" with 'A' RPS (Reactor Protection System) channel inoperable (tripped), the plant operator did not bypass the second channel before testing it, which caused an automatic plant trip. Operators then performed Emergency Operating Procedure EOP 2-25, "Standard Post Trip Actions". All equipment responded as expected and the unit was placed in a stable condition. The cause of the event was operator error in that the operator failed to perform the prescribed steps when initiating the daily, Power Range Safety Channel and Delta T Power Channel Calibration. The licensed Reactor Operator involved has been instructed in the proper sequence of bypass switch operations and the entire Operations Department has discussed the importance of evaluating plant conditions and self-verification at subsequent department meetings. In addition, procedure SP 2601D has been revised to incorporate a separate section on performing, the calibrations with one RPS channel inoperable, including a signature requirement for verification that the bypass lights are energized on the channel to be tested. This event is being reported pursuant to the requirements of paragraph 50.73(a)(2)(iv), reporting any event or condition that resulted in manual or automatic actuation of any Engineered Safety, Feature System.
336 | 3361991001 | 1991-01-10 | QR5 | Turbine Trip | [45 empty] | Millstone 2 | P | CE | PO | 92 | On January 10, 1991 at 1612 hours, with the unit operating at 92% power, the main turbine tripped on low Electro-Hydraulic Control (EHC) pressure. The Reactor Protection System initiated a Reactor trip following the turbine trip. Normal post-trip procedures were followed. There were no safety implications since the unit experienced a normal Reactor trip shutdown.
336 | 3361991004 | 1991-02-16 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Millstone 2 | P | CE | PO | 100 | On February 16, 1991, with the unit operating at 100% power, the 'B' Steam Generator Feed Pump (SGFP) unexpectedly tripped at 1731 hours. The pump was reset and the speed of the 'A' SGFP was raised from 4430 to 5100 RPM. As the 'B' SGFP was accelerated, it caused low suction pressure for both pumps. The 'B' SGFP tripped again, was reset, tripped and reset again. The 'A' and 'B' pump suction pressures again alarmed low. The 'A' SGFP then tripped. Low level alarms occurred in both steam generators. At 1733 hours, the reactor was manually tripped because of decreasing SG levels. The cause of the initial 'B' SGFP trip is unknown.
336 | 3361991012 | 1991-11-06 | K2 | Feedwater Line Break | [9 empty] | X | X | [26 empty] | X |  | X | [5 empty] | Millstone 2 | P | CE | PO | 100 | On November 6, 1991, with the plant operating at 100% power, an eight inch diameter pipe ruptured at approximately 0643. The subject line contains pressurized, heated water and serves as a drain line from the first stage reheater drain tank no. 1B to the 1B high pressure feedwater heater. The water in this line is normally 470 psig at 463 degrees F. The leak released steam into the turbine building. The control room received a call that there was a "loud noise" in the turbine building. This initiated a review of control room instrumentation which indicated: Moisture separator reheater changes, slight cooldown, slight MWe output decrease and a 15 second calorimetric increase to 2722 MWth. A visual inspection of the turbine building confirmed the steam leak. At 0649 the SCO ordered a manual reactor trip based on alarms and indications. The reactor and turbine were tripped. The shift carried out EOP 2525, "Standard Post Trip Actions." Approximately one minute after the trip the SS ordered the main steam isolation valves shut and the opening of the condenser dump valves to depressurize the main steam header. After EOP 2525 was completed, and in-hand verified, the shift entered EOP 2536, "Excess Steam Demand." In order to assess the source of the leak, the remaining condensate pump was secured and condenser vacuum was broken. With the plant stable the operators exited EOP 2526 "Reactor Trip Recovery."
336 | 3361993004 | 1993-02-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 100 | On February 22, 1993, at 0144 hours, with the plant in Mode 1 at 100% power, the 'A' steam generator atmospheric steam dump valve (ADV) failed open. During the subsequent transient plant conditions, the 'B' main feedwater pump automatically tripped on low suction pressure, and an automatic reactor trip on low steam generator water level occurred at 0151 hours. Operators then performed Emergency Operating Procedure EOP 2525, 'Standard Post Trip Actions.' All safety related equipment responded as expected and the unit was placed in a stable condition. The cause of the reactor trip was the inability to recover the water level in the 'A' steam generator following the trip of the 'B' main feedwater pump. <br /><br /> During the subsequent plant startup on February 23, 1993, at 2037 hours, with the plant in Mode 1 at 18% power, high vibration of several main turbine bearings required shutdown of the main turbine. Reactor power was quickly reduced to approximately 14% power and the main turbine was tripped at 2040 hours. During the subsequent transient plant conditions, an automatic reactor trip on low steam generator water level occurred at 2043 hours. Operators then performed Emergency Operating Procedure EOP 2525, 'Standard Post Trip Actions.' All safety related equipment responded as expected and the unit was placed in a stable condition. The cause of the reactor trip was insufficient feedwater flow to the steam generators for the existing reactor power level. <br /><br /> These events are being reported pursuant to the requirements of Paragraph 50.73(a) (2) (iv), reporting any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature System.
336 | 3361993004 | 1993-02-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 14 | On February 22, 1993, at 0144 hours, with the plant in Mode 1 at 100% power, the 'A' steam generator atmospheric steam dump valve (ADV) failed open. During the subsequent transient plant conditions, the 'B' main feedwater pump automatically tripped on low suction pressure, and an automatic reactor trip on low steam generator water level occurred at 0151 hours. Operators then performed Emergency Operating Procedure EOP 2525, 'Standard Post Trip Actions.' All safety related equipment responded as expected and the unit was placed in a stable condition. The cause of the reactor trip was the inability to recover the water level in the 'A' steam generator following the trip of the 'B' main feedwater pump. <br /><br /> During the subsequent plant startup on February 23, 1993, at 2037 hours, with the plant in Mode 1 at 18% power, high vibration of several main turbine bearings required shutdown of the main turbine. Reactor power was quickly reduced to approximately 14% power and the main turbine was tripped at 2040 hours. During the subsequent transient plant conditions, an automatic reactor trip on low steam generator water level occurred at 2043 hours. Operators then performed Emergency Operating Procedure EOP 2525, 'Standard Post Trip Actions.' All safety related equipment responded as expected and the unit was placed in a stable condition. The cause of the reactor trip was insufficient feedwater flow to the steam generators for the existing reactor power level. <br /><br /> These events are being reported pursuant to the requirements of Paragraph 50.73(a) (2) (iv), reporting any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature System.
336 | 3361993012 | 1993-05-24 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Millstone 2 | P | CE | PO | 100 | On May 24, 1993, at 0943 hours, with the plant in Mode 1 at 100% power, a reactor trip occurred due to a turbine trip. The turbine trip was caused by high generator stator cooling water temperature resulting from mussel cooking (thermal backwash) operations on the 'B' condenser waterbox. During the subsequent transient, a malfunction caused the 'A' feedwater regulating valve to stay at approximately 56% open which caused the #1 steam generator water level to increase to the high level setpoint. The reactor operator tripped the running feedwater pump based on the high steam generator water level. Steam generator water levels were subsequently controlled using the auxiliary feedwater system, Operators performed Emergency Operating Procedure 2525, "Standard Post Trip Actions." All safety related equipment, with the exception of the main feedwater regulating valves, responded as expected and the unit was placed in a stable condition. During the event investigation subsequent to the trip, it was discovered that during the mussel cook, Reactor Building Closed Cooling (RBCCW) temperatures momentarily exceeded 85 degrees F which potentially resulted in the plant being outside of its design basis. RBCCW temperatures immediately returned to normal.<br /><br /> These events are being reported pursuant to the requirements of Paragraph 50.73(a)(2)(iv) and Paragraph 50.73(a)(2(ii)(B) reporting any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature System including the Reactor Protection system and to report an event or condition that potentially resulted in the nuclear power plant being in a condition outside the design basis of the plant.
336 | 3361993013 | 1993-06-03 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Millstone 2 | P | CE | PO | 100 | On June 3, 1993, at 1624 hours, with the plant in mode 1 at 100% power, the main turbine generator Electro-Hydraulic Control (EHC) system initiated a signal that caused the main turbine to rapidly, decrease load. The sudden load drop caused an increase in pressurizer pressure, resulting in a reactor trip. The EHC signal has been attributed to spurious relay actuations as a result of operations within the EHC cabinet.<br /><br /> Operators performed Emergency Operating Procedure EOP 2525, "Standard Post Trip Actions" and all safety related equipment performed as expected. <br /><br /> This is being reported pursuant to requirements of Paragraph 50.73(a)(2) (iv), reporting any event or condition that resulted in manual or automatic actuation of any, Engineered Safety Feature system, including the Reactor Protection System (RPS).
336 | 3361993019 | 1993-08-12 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Millstone 2 | P | CE | SU | 2 | On August 12, 1993, the plant was operating in Mode 2. At 13:44 a reactor trip occurred due to low Steam Generator (SG) level. Approximately one hour prior to the trip the plant had entered mode 2 (reactor critical) and SG levels were being maintained by one auxiliary feedwater pump. Reactor power had just been increased to 2% and preparations were being made to start a main feedwater pump and begin the turbine warming process. Following the reactor trip Emergency Operating Procedure EOP 2525, Standard Post Trip Actions, was performed. All safety related equipment responded as expected, and the unit was placed in a stable condition.
336 | 3361994009 | 1994-04-23 | QR3 | Reactivity Control Imbalance | [45 empty] | Millstone 2 | P | CE | PO | 1 | On April 22, 1994, at 2100 hours, with the plant in Mode 1 at 99.8% power, a planned shutdown was commenced to repair a degraded Reactor Coolant Pump seal. At 2113 hours, it was identified that Control Element Assembly (CEA) 7-65 not inserting with the other CEAs in its group. The Shift Supervisor had the indication investigated and declared the reed switch CEA position indicator channel for CEA 7-65 inoperable at 2143 hours and logged into the applicable Technical Specification action statement. The downpower had been terminated when the CEA 7-65 indication problem was identified and was recommenced at 2207 hours. <br /><br /> At 0055 hours on April 23, 1994 with reactor power at approximately 25% and CEA Group 7 at approximately 110 steps, the operators began to suspect that CEA 7-65 was at the fully withdrawn position. At 0115 hours the Shift Supervisor declared CEA 7-65 immovable and logged into the applicable Technical Specification action statement. <br /><br /> At approximately 0230 hours, it was identified that the Technical Specification action statement requirements for an immovable CEA had not been performed within the specified time. <br /><br /> At 0250 hours with the reactor in Mode 2 at approximately 10**-5% power and Group 7 CEAs at approximately 90 steps (with the exception of CEA 7-65), power was removed to the Control Element Drive Mechanism (CEDM) for CEA 7-65 and the CEA fully inserted into the core. At 0251 hours the reactor was manually tripped.
336 | 3361995032 | 1995-08-08 | K1 | Steam Line Break Outside Containment | [9 empty] | X | [26 empty] | X | [8 empty] | Millstone 2 | P | CE | PO | 60 | On August 8, 1995, at 1459 hours with the plant in mode 1 at 60% power, the RCS temperature at 556 degrees and RCS pressure at 2265 PSI, the reactor was manually tripped from the control room due to a steam leak in a secondary system within the turbine building. Plant response was within norm and no automatic actuation of safety systems occurred. Examination of the area where the steam leakage occurred revealed a 14" vertical rupture in the B" diameter recirculation line from the discharge of the B Heater Drain Pump to the Heater Drain Tank. <br /><br /> Immediate corrective action consisted of manually tripping the reactor and placing the plant in mode 3, and stopping the steam leak and restricting access to the local area for personnel protection. <br /><br /> An event review team (ERT) was formed to investigate the cause of the pipe rupture. The ERT corrective actions were provided on a short term and long term basis (see Section IV of this LER). All short term and all but one long term corrective actions have been completed.<br /><br /> This event is being reported pursuant to the requirements of 10CFR50.73(a)(2)(iv), any event or condition that resulted in a manual or automatic action of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS).
336 | 3361999009 | 1999-05-25 | QR6 | Manual Reactor Trip | [45 empty] | Millstone 2 | P | CE | PO | 100 | On May 25, 1999, (Mode 1, 100% power) at 1512, a manual reactor trip was initiated due to a report of a steam leak in the turbine building. The steam leak occurred following erratic feedwater heater level response. The steam leak was located at the inlet flange to the shell side relief valve for the 1A feedwater heater. All safety related equipment performed as expected and the plant was stabilized at normal post trip parameters. Additionally, the Main Steam Isolation Valves were shut to isolate steam to the turbine building. The event was caused by inadequate controls associated with the adjustment and grooming of the feedwater heater level control valves which resulted in an overpressure condition when the shell side relief valve lifted. The resultant force caused a steam leak at the relief valve flange. Inadequate gasket compression was caused by improper torquing of the feedwater heater 1A shell side relief valve flange studs which resulted from unclear guidance in the procedure used for determining the torque values. Corrective actions pertaining to this event include refining of controls for adjusting feedwater heater string controls and clarifying guidance concerning torqued connections when significant dynamic piping loads are expected from events such as water hammer's or the opening of pressure relief devices.
336 | 3362000001 | 2000-01-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 100 | On January 27, 2000 at approximately 1427 hours with the unit in Mode 1 at 100 percent power, a manual reactor trip was initiated due to a rapid decrease in the "B" Steam Generator (SG) level to approximately 57 percent and the trip of a SG feedwater pump. The plant response was uncomplicated with safety systems performing as expected. The plant was stabilized at normal post trip parameters (Mode 3) and operating shift personnel reacted appropriately. Operators manually initiated the auxiliary feedwater system to restore SG water levels. It was determined that this event was caused by the loss of all heater drain flow to the suction of the SG feedwater pumps as a result of bulk flashing in the heater drain tank. As event precursors, it was determined that the transient was initiated due to the restoration of the 2A feedwater heater's sight glass causing oscillations in the feedwater control system that adversely affected the systems' ability to recover from the transient. Also, it was concluded that the heater drain tank vent control valve 2-HD-104 control logic wiring did not permit the valve to function properly in order to mitigate the consequences of a loss or rapid reduction of extraction steam pressure on the heater drain tank. Completed corrective actions include optimizing the feedwater heater system performance by improving the stroke time for the level controller valve, and correcting the control logic for 2-HD-104 such that the valve will close to prevent depressurization of the heater drain tank.
336 | 3362000003 | 2000-02-11 | QR6 | Manual Reactor Trip | [45 empty] | Millstone 2 | P | CE | PO | 96 | On February 11, 2000 at approximately 1346 hours with the unit in Mode 1 at 96 percent power, a manual reactor trip was initiated during Control Element Assembly (CEA) insertion testing after the second of two CEAs unexpectedly dropped into the core. Immediately prior to the trip, Operators were reducing power in accordance with Technical Specification Action Statement 3.1.3.1(e) after the first CEA had dropped into the core. During this power reduction action, the second CEA dropped into the core approximately 17 minutes after the first. As directed by procedure, the Operators then manually tripped the reactor immediately after the second CEA inserted at which time all remaining CEAs inserted completely into the core. The Auxiliary Feedwater System automatically initiated as a result of the trip and other appropriate safety systems operated as expected. The plant was stabilized in hot standby (Mode 3) at normal post trip parameters and Operating shift personnel reacted appropriately throughout the trip event. The apparent cause of the first CEA failure was determined to be a ground in the circuit between the interposing cabling and the coil stack. In addition, the apparent cause of the second CEA failure was determined to be failed relays in the assembly's upper gripper circuit. As a contributing factor, it was determined that there were deficiencies in the CEA's preventive maintenance program. Prior to unit restart, several corrective actions were performed to both test and replace suspect equipment. In addition, a preventive maintenance program for periodic refurbishment of power switch modules will be established by September 1, 2000.
336 | 3362000010 | 2000-06-04 | QR5 | Turbine Trip | [45 empty] | Millstone 2 | P | CE | PO | 65 | At 0012 on June 4, 2000 with the plant in Mode 1 at 65 percent (%) power, a reactor trip occurred during the performance of the weekly test of the Main Turbine Generator Power-Load Unbalance (PLU) circuit by operations personnel. This test was being performed in accordance with the applicable plant procedure (SP-2651T, "Power to Load Unbalance (PLU) Circuitry Test"). In accordance with this procedure, the power load unbalance pushbutton was pressed to initiate the test. However, the turbine control valves were not disabled and as a result the turbine control valves received a fast closure signal. The fast closure signal dumped disk pressure from the control valves which in turn processed a reactor protection trip from the low turbine trip fluid pressure switches. This event resulted in the Control room receiving annunciation of a turbine trouble followed by a reactor trip and plant equipment responded as expected following the initiation of the turbine control valves fast closure signal. This event was reported in accordance with 10CFR50.72(b)(2)(ii) on June 4, 2000 and is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event or condition that resulted in a manual or automatic actuation of an engineered safety feature (ESF), including the reactor protection system (RPS). The root cause for this event was determined to be an inadequate circuit design which, along with other corrective actions, is being addressed via the Millstone Corrective Action Program.
336 | 3362001003 | 2001-04-29 | QL7 | Degraded condenser vacuum | [45 empty] | Millstone 2 | P | CE | PO | 97 | On April 29, 2001, with the plant at 97 percent power an automatic plant trip occurred due to a degraded condenser vacuum caused by both Circulating Water pumps (CWP) in one condenser not operating. In preparation for testing the "D" CWP following maintenance activities performed on it, electricians inadvertently caused the "C" CWP to trip when attempting to install a jumper in the "D" CWP breaker cubicle. The loss of circulating water resulted in a degrading condenser vacuum which then caused an automatic turbine trip. The turbine trip caused the reactor to automatically trip. Following the trip, all safety systems functioned as required. The auxiliary feedwater system auto started due to low steam generator (S/G) level caused by S/G level shrink following the reactor trip. The root cause of this event was determined to be inadequate procedures that did not include the correct information or require the correct verifications. Following the plant trip, work was stopped and briefs were conducted with the appropriate groups to reinforce work expectations. All lifting of leads or installation of jumpers not controlled by an approved procedure will require additional supervisor review. To prevent recurrence a procedure is being developed to provide guidance to control the running/bumping of motors following on-line maintenance.
336 | 3362001004 | 2001-05-07 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Millstone 2 | P | CE | PO | 96 | On Monday May 7, 2001, with the plant at 96 percent power, preventive maintenance work was being performed in the Unit 2 "A" Circulating Water bay. The "A" Circulating pump, "A" travelling screen, and travelling screen in the adjacent "B" bay were tagged off for diver protection which allowed an accumulation of seaweed on the "B" screen over a period of several hours. When the "B" screen differential pressure reached its setpoint of 30 inches, the "B" Circulating Water pump automatically tripped. The reactor was then manually tripped per procedure at approximately 1433 hours due to the loss of two Circulating Water pumps in one condenser. There were no significant complications following the trip and all safety systems functioned as designed. The root cause of this event was determined to be that the risks and consequences of non-safety related work management decisions are not completely identified or assessed. To prevent recurrence a risk assessment process is being developed that utilizes the collective knowledge of plant personnel to identify those activities having the potential to jeopardize the safe and continuous operation of the plant. Additional corrective actions are being addressed via the Millstone Corrective Action Program.
336 | 3362002002 | 2002-04-19 | QR5 | Turbine Trip | [45 empty] | Millstone 2 | P | CE | PO | 99 | On April 19, 2002, with the plant operating at approximately 99.5 percent power, a turbine trip resulted in an automatic reactor trip when a temperature switch in the Stator Water Cooling System tripped on a high value. The temperature switch in the Stator Water Cooling System was found with a trip setpoint value approximately 14°C lower than the acceptance criteria found in the calibration procedure. Following the reactor trip, main steam reheat valves, 2-MS-2A and 2-MS-2B, did not close as expected and had to be manually closed, resulting in an unexpected RCS cooldown. Auxiliary Feedwater automatically initiated to compensate for a low level in the Steam Generators caused by shrinkage. Required safety equipment functioned as expected and this event is considered to be of low safety significance. The cause of this event is indeterminate. The presumptive causes are either an equipment failure or insufficient oversight and controls that led to calibration errors. Following the reactor trip, the temperature switch was tested and re-calibrated to the proper setpoints prior to plant restart. To prevent recurrence the stator coolant temperature switch from both Millstone Unit Nos. 2 and 3 will be replaced. The Unit No. 2 device will then be sent to the vendor for a failure analysis. In addition, separate procedures will be developed for secondary plant instruments that are trip sensitive at Unit Nos. 2 and 3.
336 | 3362002005 | 2002-08-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 55 | On August 7, 2002, with the plant operating in Mode 1 and in power ascension at approximately 55 percent power, an automatic reactor trip occurred due to low steam generator level. Post trip procedures were followed and the plant responded normally without any engineered safety feature actuation. Prior to the event, feedwater was being supplied to the steam generators by the "A" steam generator feedwater pump (SGFP).The event took place during the startup sequence of the "B"SGFP. The discharge flow from the SGFPs is fed into a common header which in turn is sent through the No.1 feedwater heaters and then to the steam generators. The SGFPs are each protected from reverse flow by a check valve,2-FW-1A and B. Downstream of the check valves are motor operated isolation valves,2-FW-38A and B.As part of the startup sequence for placing the "B"SGFP in service, the operators opened the motor operated isolation valve, 2-FW-38B. Almost immediately, steam generator level deviation alarms were received. The operators commenced closing 2-FW-38B, but the time for the motor operated valve closure was not sufficient to recover steam generator levels prior to the reactor trip. The cause of the loss of feedwater flow to the steam generators was the failure of the "B"SGFP discharge check valve (2-FW-1 B) due to an inadequate anti-rotation weld. The root cause is that the organization failed to install adequate anti-rotation welds in the SGFP discharge check valves in 1990. The SGFP discharge check valves were inspected and repaired with improved anti-rotation welds.
336 | 3362003002 | 2003-03-07 | QR8 | Spurious Reactor Trip | [45 empty] | Millstone 2 | P | CE | PO | 100 | On March 7, 2003, at 1439, with the unit in Mode 1 at 100% power, an automatic reactor trip occurred during normal monthly Reactor Protection System (RPS) matrix testing due to a fault in the test circuitry. Specifically, Control Rod Drive trip circuit breaker (TCB) pair TCB-1 and TCB-5 tripped open in addition to the expected opening of TCB pair TCB-3 and TCB-7 when AC Matrix Relay Trip Select switch was rotated to position "3." The opening of both pairs of trip breakers resulted in a reactor trip from full power followed by an automatic turbine trip. All control rods inserted into the core and all electrical busses transferred properly following the trip. Auxiliary Feedwater (AFW) initiated as expected, on low steam generator level. The post-trip plant response was complicated by several additional equipment failures, the most notable being a malfunction of the charging system leading to a loss of all charging. This latter condition is addressed in a separate report. The root cause of the event was historical in nature and determined to be poor workmanship of the original RPS matrix test module dating back to plant startup. Specifically, the keying pin hole was drilled too large in the adapter plate for the AC matrix relay trip select switch (Micro switch model X6210-25AS4-7448) allowing excessive movement of the switch. This movement, in addition to poor quality of soldering and lack of wiring strain relief in the test module, caused strain failure of the wiring at the switch terminal joint. Corrective actions to prevent recurrence included re-drilling the switch keying pin hole to remove excessive switch play, and to inspect for and repair damaged wiring and provide adequate strain relief for wiring as necessary, in the RPS matrix test module. These actions were completed prior to startup.
336 | 3362003006 | 2003-11-27 | QR6 | Manual Reactor Trip | [45 empty] | Millstone 2 | P | CE | PO | 20 | On November 27, 2003, at approximately 0617 with the plant in MODE 1 at approximately 20 percent power, the reactor was manually tripped due to high vibration of the Main Turbine. Additionally, on November 28, 2003, at approximately 2205 with the plant in MODE 1 at approximately 11 percent power the reactor was also manually tripped due to high vibration of the Main Turbine. Following the manual reactor trips, all control rods inserted into the core. There were no safety system actuations. All electrical busses transferred properly following the trip, and all emergency diesel generators were operable, but not required. All other plant system responses were as expected. Therefore, these two events have low safety significance. The apparent cause of these two events is excessive turbine bearing vibration due to newly installed LP turbine monoblock rotors. Monoblock rotors are manufactured from a single forging with integral wheels formed by machining. The fact that the wheels are part of the rotor means that rubbing on the wheels can cause a rotor bow due to localized heating. This construction makes monoblock rotors more sensitive to rubbing than built-up rotors. In addition to the monoblock rotor sensitivity, the Millstone Unit No. 2 turbine rotor replacement includes all new packing. New packing also increases the possibility of a rub, as all the clearances are minimum.
336 | 3362003006 | 2003-11-28 | QR6 | Manual Reactor Trip | [45 empty] | Millstone 2 | P | CE | PO | 11 | On November 27, 2003, at approximately 0617 with the plant in MODE 1 at approximately 20 percent power, the reactor was manually tripped due to high vibration of the Main Turbine. Additionally, on November 28, 2003, at approximately 2205 with the plant in MODE 1 at approximately 11 percent power the reactor was also manually tripped due to high vibration of the Main Turbine. Following the manual reactor trips, all control rods inserted into the core. There were no safety system actuations. All electrical busses transferred properly following the trip, and all emergency diesel generators were operable, but not required. All other plant system responses were as expected. Therefore, these two events have low safety significance. The apparent cause of these two events is excessive turbine bearing vibration due to newly installed LP turbine monoblock rotors. Monoblock rotors are manufactured from a single forging with integral wheels formed by machining. The fact that the wheels are part of the rotor means that rubbing on the wheels can cause a rotor bow due to localized heating. This construction makes monoblock rotors more sensitive to rubbing than built-up rotors. In addition to the monoblock rotor sensitivity, the Millstone Unit No. 2 turbine rotor replacement includes all new packing. New packing also increases the possibility of a rub, as all the clearances are minimum.
336 | 3362004001 | 2004-03-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 100 | On March 6, 2004, at approximately 0050 with the unit in Mode 1 at 100 percent power, and with steam generator (SG) level approaching about 55 percent, operators initiated a manual reactor trip in anticipation of the low SG water level auto trip setpoint. The decreasing SG water level was due to a reduction in feedwater from the loss of the 'B' steam generator feedwater (SGFW) pump. The 'B' SGFW pump had tripped unexpectedly causing lowering SG water levels. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of any of the systems listed in 50.73(a)(2)(iv)(B). This includes Reactor Protection System actuation (RPS) and Auxiliary Feedwater System initiation (AFW). The apparent cause of the trip was agitation of a relay in the feedwater pump control system. This perturbed the relay's signal to the digital control system (MicroNet) sufficiently for it to sense a low pressure condition and initiate a trip of the feedwater pump, even though a low pressure condition did not exist. As a result of the Event Investigation Team (EIT) findings in response to the immediate issue of relay contact sensitivity, a relay's operation in the speed control circuit for the SGFW pumps was changed from an energized closed to an energized open configuration with the associated software changes. This reduces the HGA relay sensitivity to agitation and will avert additional SGFW pump trips.
336 | 3362004002 | 2004-03-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 100 | At approximately 2020 hours on March 15, 2004, with the unit in Mode 1 at 100 percent power, the reactor experienced an automatic reactor trip on low steam generator (SG) water level. The decreasing SG water level was due to a trip of the 'B' steam generator main feedwater (SGFW) pump that had occurred at approximately 2018 hours. The SGFW pump tripped in the course of performing the quarterly overspeed lockout test. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as any event that resulted in manual or automatic actuation of any of the systems listed in 50.73(a)(2)(iv)(B). This includes Reactor Protection System actuation (RPS) and Auxiliary Feedwater System initiation (AFW). It is believed that the use of the lockout control switch for the quarterly performance of a SGFW pump emergency governor and trip lockout exerciser test is problematic and resulted in a momentary opening of switch contacts. This caused a rapid depressurization of the hydraulic overspeed protection system and a trip of the 'B' SGFW pump. To prevent recurrence, the performance of applicable sections of the emergency governor and trip lockout exerciser test procedure at power levels that could challenge a reactor trip from a SGFW pump trip has been suspended until such time as an appropriate final resolution to this condition is specified.
336 | 3362006002 | 2006-02-23 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Millstone 2 | P | CE | PO | 100 | On February 23, 2006, with the plant in Mode 1 and 100% power, a Manual Reactor Trip was initiated due to a trip of both feed pumps following a loss of Instrument Air. Mechanics were attempting to replace a pipe clamp on a two-inch copper Instrument Air header on Millstone Power Station Unit 2 when an inadequately soldered joint failed on a 1/2 inch tee connection. The 1/2 inch line separated from the header and resulted in rapidly lowering Instrument Air pressure in a portion of the turbine building and shutting of an excess flow check valve, as designed. Numerous air operated valves shifted to their loss-of-air failure position. Feedwater heater high-level dump valves opened causing a reduction of heater drain flow and loss of suction pressure to the steam generator feed pumps (SGFP). Both SGFPs tripped and a manual reactor trip was initiated. The Auxiliary Feedwater System actuated as expected, however, the Number 1 Steam Generator AFW Regulating Valve went to its failed position (i.e. full open) allowing excessive flow to the Number 1 Steam Generator, which contributed to a greater than expected, cool down of the RCS. An operator was dispatched to take manual control of the regulating valve at which point RCS temperature was restored to the normal post-trip band of 530-535 F. All other safety systems functioned as designed. The plant was stabilized in Mode 3 at normal operating temperature and pressure. This event/condition is being reported pursuant to 50.73(a)(2)(iv)(A) as an event that resulted in the manual actuation of the Reactor Protection System as well as the automatic actuation of the Auxiliary Feedwater System.
336 | 3362008003 | 2008-05-22 | QR5 | Turbine Trip | [45 empty] | Millstone 2 | P | CE | PO | 100 | On May 22, 2008 at 1359 with the Millstone Power Station Unit 2 (MPS2) at 100% power in Mode 1, the reactor automatically shutdown following a loss of load and subsequent turbine trip. Investigation determined that a lightning strike on a transmission line created an over current condition to which the unit responded. The 345 kV main generator output breakers in the transmission switchyard opened causing a turbine trip on loss of load. A pre-existing mechanical failure of a connecting wire lug created an open circuit in the pilot wire circuitry. The power surge from the lightning strike coupled with this open circuit caused the pilot wire relay to act as an over current protection device which opened the breakers. The transmission switchyard breakers and associated interlocks operated as designed protecting station equipment. During the event, the in-house electrical buses were automatically transferred from the Normal Station Service Transformer (NSST) to the Reserve Station Service Transformer (RSST) causing a momentary loss of the nonsafety grade 120 volt power supplies (VR-11 and VR-21). This affected multiple components which required additional operator actions. The systems functioned as expected based upon the signals received. The operators took actions as trained and in accordance with procedures. No equipment was damaged as a result of this event. The unit was brought to a stable condition in hot-standby (Mode 3) and the lug was repaired. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10CFR50.73(a)(2)(iv)(B).
336 | 3362008005 | 2008-06-28 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Millstone 2 | P | CE | PO | 100 | On June 28, 2008, at 1146 with the Millstone Power Station Unit 2 in Mode 1 at 100% power, operators manually tripped the reactor when both main feedwater pumps tripped. Main turbine combined intercept valve (CIV) testing was in progress. The testing of the #3 CIV had just been completed when the 2A feedwater heater level began oscillating. The perturbations in the feedwater heater levels caused a feedwater pump suction pressure to decrease to the pump trip setpoint tripping both pumps. The operators manually tripped the reactor prior to reaching the steam generator low level automatic trip setpoint. During the event, the in-house electrical buses were automatically transferred from the Normal Station Service Transformer to the Reserve Station Service Transformer causing a momentary loss of the non-safety grade 120 volt power supplies (VR-11 and VR-21). This affected multiple components which required additional operator actions. The systems functioned as expected based upon the signals received. The operators took actions as trained and in accordance with procedures. No equipment was damaged as a result of this event. The unit was brought to a stable condition in hot-standby (Mode 3) and the feedwater heater level control valve was repaired. Ineffective configuration control of parts allowed parts to be installed in a feedwater level control valve causing it to operate incorrectly which caused divergent feedwater heater level oscillations and the main feedwater pumps to trip. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
336 | 3362009001 | 2009-07-03 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Millstone 2 | P | CE | PO | 100 | At 1304 on July 3, 2009, with the Millstone Power Station Unit 2 at 100% power in Mode 1, the reactor automatically tripped due to a high pressurizer pressure reactor trip signal. There was a grid disturbance coincident with the time of the trip. Approximately 5 seconds prior to the trip, the four main turbine stop valves and four intermediate stop valves went fully closed. With the main turbine stop valves closed, the reactor coolant system (RCS) pressure increased to the high trip setpoint. The reactor automatically tripped and both pressurizer power operated relief valves (PORVs) lifted to relieve pressure as designed. The reactor trip generated a turbine trip signal. The most probable cause of this event is that the 24VDC power supply to the electro-hydraulic control (EHC) of the turbine valves did not tolerate the July 3, 2009 grid disturbance. As a result of the grid disturbance, the master trip solenoid valves (MTSVs) provided fluctuating emergency trip system (ETS) hydraulic pressure to the turbine valves. This fluctuating hydraulic pressure caused the turbine stop and intermediate stop valves to close unexpectedly. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
336 | 3362010001 | 2010-02-26 | QR6 | Manual Reactor Trip | [10 empty] | X | [28 empty] | X | X |  |  |  |  | Millstone 2 | P | CE | PO | 100 | On February 26, 2010, with the unit in Mode 1, at 100 % power, the Millstone Power Station Unit 2 (MPS2) reactor was manually tripped as required by procedure due to a loss of circulating water (CW) flow to one of the two sections of the main condenser. All control rods fully inserted into the reactor and all emergency systems functioned as designed. At the time of the trip, the 'D' CW pump was out of service for planned maintenance. The loss of CW flow to a main condenser section occurred when the 'C' CW pump automatically tripped due to a larger than expected influx of debris causing a high differential level across the traveling screens. Following the trip, the operators closed the main steam isolation valves to protect the condenser from overpressure. There were no radiological challenges as a result of the event. The cause was determined to be the failure of the organization's individual departments to work together as a team to clearly identify the risks associated with the work evolution. The risk assessment and mitigation control process has been reviewed and the appropriate actions are being taken in accordance with the corrective action program. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
336 | 3362010002 | 2010-05-22 | QR6 | Manual Reactor Trip | [45 empty] | Millstone 2 | P | CE | PO | 100 | On May 22, 2010 at 1645 with the Millstone Power Station Unit 2 at 100% power in Mode 1, the reactor was manually tripped by operators due to a high water level condition in steam generator (S/G) number 2. Investigation determined that level oscillations occurred because of S/G level control problems associated with number 2 feedwater (FW) regulating valve. Safety systems functioned as expected based upon the signals received. The operators took actions as trained and in accordance with established procedures. No equipment was damaged as a result of the event. The unit was brought to a stable condition in hot-standby. The cause of the reactor trip was vibration induced wear of the number 2 FW regulating valve positioner beam screw. The degraded valve positioner was replaced and the frequency of on-line preventive maintenance was changed. Design changes are being evaluated to reduce FW regulating valve positioner beam screw wear. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10CFR50.73(a)(2)(iv)(B).
336 | 3362010003 | 2010-11-28 | QL7 | Degraded condenser vacuum | [45 empty] | Millstone 2 | P | CE | PO | 100 | On November 28, 2010, at 1515, Millstone Power Station Unit 2's (MPS2) reactor automatically tripped from 100% power MODE 1. Prior to the event, MPS2 was establishing conditions to perform a backwash of the "B" condenser [COND] waterbox. Operators pressed the stop pushbutton for the "B" circulating water (CW) pump [P] and were closing the "A" CW pump's water box outlet valve (2-CW-11A) [V] per established operating procedure OP-2325D when the "A" CW pump automatically ramped off. Upon loss of the second pump in the condenser, condenser pressure increased to the low condenser vacuum trip set point, causing an automatic turbine generator trip and a reactor trip. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). The cause of the event was an organizational failure to properly develop and train on the procedure needed to conduct backwashing operations using Variable Frequency Driven (VFD) CW pumps. Corrective actions to prevent recurrence being implemented will ensure proper development and training on procedures are made during plant modifications.
336 | 3362011002 | 2011-06-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 59 | At 1152 on June 20, 2011, with Millstone Power Station Unit 2 operating at 59 percent power in Mode 1, the reactor tripped automatically on low steam generator water level. The decreasing water level condition was due to a low suction pressure trip on the "B" steam generator feed pump (SGFP) that occurred while placing the "A" SGFP in service. The event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of any of the systems listed in 50.73(a)(2)(iv) (B). The actuation of the Auxiliary Feedwater Actuation System also is a reportable condition under the same paragraph. The cause of the event was gaps in the application of operator fundamentals and some procedure quality issues associated with operations procedure OP 2204, Load Changes. Procedure OP 2204 has been revised to ensure the second steam generator feedwater pump is placed in service at a lower power level. Additional corrective actions to address the underlying causes of the gaps in the application of operator fundamentals are being addressed in accordance with the station's corrective action program.
336 | 3362013004 | 2013-11-09 | QL7 | Degraded condenser vacuum | [45 empty] | Millstone 2 | P | CE | PO | 95 | On November 9, 2013, at 1514, Millstone Power Station Unit 2 (MPS2) experienced a turbine trip and an automatic reactor trip from 95% power MODE 1 due to loss of condenser vacuum. The Unit was in the process of condenser backwashing operations when condenser vacuum was lost due to unexpected pump ramp-down of the 'C' circulating water pump (CWP) when the 'D' CWP was secured as required by procedure.<br /><br /> All control rods inserted on the reactor trip. An auxiliary feedwater (AFW) automatic start occurred post trip, as expected per design, and all other safety systems functioned as required.<br /><br /> The direct cause of the event was the MPS2 'C' CWP ramped off due to failure of contacts on a time-delay relay to deenergize as designed.<br /><br /> The defective relay was replaced. Additional corrective actions are being taken in accordance with the station's corrective action program.<br /><br /> This event is being reported per 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). Actuations of the reactor protection system and the AFW system are reportable under this paragraph.
336 | 3362014006 | 2014-05-25 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Millstone 2 | P | CE | PO | 100 | On May 25, 2014, with Millstone Power Station (MPS) Unit 2 and 3 (MPS2 and MPS3) in operating MODE 1, operating at 100% reactor power, a total loss of offsite power occurred in the MPS switchyard. Both MPS2 and MPS3 experienced a turbine trip on power to load imbalance followed by an automatic reactor trip. Both units' safety related emergency diesel generators (EDGs) automatically started and supplied power to their respective safety busses. As designed, the motor driven auxiliary feedwater (AFW) pumps automatically started on MPS2 and all AFW pumps automatically started on MPS3.<br /><br /> MPS declared an Unusual Event (UE) following the reactor trips and the NRC was notified (EN50142 for MPS2 and EN 50141 for MPS3). Following stabilization of both MPS2 and MPS3, the UE was terminated.<br /><br /> With both MPS2 and MPS3 at full power and one of the Transmission Owner (TO) 345 kV lines out of service for scheduled work, a phase to ground fault occurred on one of the phases on a motor operated disconnect (MOD) on one of the three remaining TO 345 kV lines. The fault was caused by an insulator failure of a MOD switch at a TO substation (offsite). This fault was also sensed as an instantaneous ground in one of the two remaining TO 345 kV lines resulting in this line also tripping. With three of the four TO 345 kV lines out of service, the MPS total electrical output overloaded the single remaining TO 345 kV Line which then also tripped resulting in a total loss of offsite AC power to MPS.<br /><br /> The TO replaced the faulty components and is investigating additional corrective actions. Additional corrective actions are being taken in accordance with the station's corrective action program.<br /><br /> This event is being reported per 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B)(1), (6), and (8). Actuations of the reactor protection system, the AFW system, and the EDGs are reportable under this paragraph.
336 | 3362015003 | 2015-11-08 | QR6 | Manual Reactor Trip | [45 empty] | Millstone 2 | P | CE | PO | 100 | On November 8, 2015 during reactor start-up from refueling outage 2R23 with the reactor in mode 1 at approximately 57.5 percent power the operators received indication of an oil leak on the 'C' reactor coolant pump (RCP) motor lower oil reservoir. The operators monitored the 'C' RCP oil level and bearing temperatures. Upon noting the RCP oil level dropping at a rate of approximately 1.7 percent per hour and the lower RCP guide bearing temperature rising, the operators entered abnormal operating procedure (AOP) 2575, Rapid Downpower, and commenced a rapid downpower. The operators manually tripped the reactor at approximately 19 percent power in accordance with AOP 2575 and entered emergency operating procedures. The reactor trip was uncomplicated. All safety systems operated as designed. <br /><br /> The cause of the valid actuation of the reactor protection system (RPS) was the operators manually tripping the reactor via the manual reactor trip push button switches. The AOP was entered due to an oil leak from the tubing to the level transmitter on the 'C' RCP motor lower oil reservoir. The tubing failure mechanism was determined to be high cyclic fatigue. Repairs were completed, the unit was restarted, and returned to service. Additional corrective actions are being taken in accordance with the station's corrective action program. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of any of the systems (RPS) listed in paragraph 10 CFR 50.73 (a)(2)(iv)(B).
336 | 3362016002 | 2016-08-11 | QL7 | Degraded condenser vacuum | [45 empty] | Millstone 2 | P | CE | PO | 100 | On August 11, 2016 at 09:59 while operating in MODE 1 at 100% power, operators manually tripped the Millstone Power Station Unit 2 reactor due to degraded condenser vacuum caused by the loss of two out of four circulating water pumps (CWPs) ('A' and 'C' CWPs). The reactor trip was uncomplicated and decay heat removal was via the steam dumps to the condenser. All control rods inserted on the reactor trip. All safety systems functioned as required. <br /><br /> The 'A' and 'C' CWPs stopped due to a loss of normal control power in the associated variable frequency drive (VFD) system. Both backup uninterruptible power supplies (UPS) in the VFDs associated with the 'A' and 'C' CWPs failed to function resulting in the 'A' and 'C' CWPs stopping. This coincided with a grid disturbance that occurred during a storm. The loss of two out of four CWPs caused a reduction in condenser vacuum. The operators manually tripped the reactor due to degrading condenser vacuum. <br /><br /> The associated UPSs were replaced. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
336 | 3362019001 | 2019-12-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Millstone 2 | P | CE | PO | 100 | On December 27, 2019 at 0704 while operating in MODE 1 at 100 percent power, operators manually tripped the Millstone Power Station Unit 2 (MPS2) reactor due to lowering steam generator levels caused by a loss of flow from the 'A' Steam Generator Feed Pump (SGFP). <br /><br /> The direct cause was the failure of the coupling connecting the MPS2 'A' Steam Generator Feed Pump (M2P1A) to the Steam Generator Feed Pump Turbine (M2H-5A). <br /><br /> The failed 'A' SGFP coupling was replaced and MPS2 was returned to service. <br /><br /> The actuation of Reactor Protection System (RPS) and Auxiliary Feedwater System (AFW) is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of systems listed in 10 CFR 50. 73(a)(2)(iv)(B).
338 | 3381987004 | 1987-04-19 | QR3 | Reactivity Control Imbalance | [45 empty] | North Anna 1 | P | WE | PO | 67 | POWER LEVEL - 067%. ON APRIL 19, 1987, AT 1554 HOURS, NORTH ANNA UNIT 1 TRIPPED FROM APPROXIMATELY 67% POWER, 667 MWE, DURING A CONTROLLED RAMPDOWN INTO A REFUELING OUTAGE AFTER 170 DAYS OF CONTINUOUS OPERATION. THE INITIATING SIGNAL WAS NUCLEAR INSTRUMENTATION SYSTEM POWER RANGE HIGH NEGATIVE FLUX RATE CAUSED BY A SINGLE DROPPED ROD. THE ROD DROPPED WHEN A FUSE IN THE STATIONARY GRIPPER COIL CIRCUITRY OF THE ROD CONTROL SYSTEM FAILED. THE CAUSE OF THE BLOWN FUSE HAS BEEN ATTRIBUTED TO A RANDOM FAILURE. PLANT RESPONSE WAS AS EXPECTED FOLLOWING THE TRANSIENT. INTERMEDIATE RANGE NEUTRON FLUX DETECTORS WERE UNDERCOMPENSATED, REQUIRING MANUAL REINSTATEMENT OF THE SOURCE RANGE DETECTORS. ALL OTHER EQUIPMENT PERFORMED AS EXPECTED. INTERMEDIATE RANGE DETECTOR COMPENSATION VOLTAGE WAS ADJUSTED AND ALL STATIONARY GRIPPER COIL CIRCUIT FUSES ARE TO BE REPLACED AND THE ROD CONTROL SYSTEM FULLY TESTED DURING THE UNIT 1 REFUELING OUTAGE. THIS EVENT IS REPORTABLE PURSUANT TO 10CFR50.73(A)(2)(IV).
338 | 3381987015 | 1987-06-29 | QR5 | Turbine Trip | [45 empty] | North Anna 1 | P | WE | PO | 18 | POWER LEVEL - 018%. ON JUNE 29, 1987, AT 2248 HOURS, UNIT 1 TRIPPED FROM 18 PERCENT POWER. UNIT 2 WAS STABLE IN MODE 1 AT 92 PERCENT POWER. THE INITIATING SIGNAL FOR THIS REACTOR TRIP WAS A TURBINE SOLENOID TRIP WHICH RESULTED FROM A 5A FEEDWATER HEATER HIGH-HIGH LEVEL SIGNAL. THE HIGH-HIGH LEVEL IN THE 5A FEEDWATER HEATER WAS CAUSED BY AN IMPROPER VALVE LINE-UP FOLLOWING A REFUELING OUTAGE. THIS EVENT IS REPORTABLE PURSUANT TO 10CFR50.73(A)(2)(IV). THE ROOT CAUSE FOR THE IMPROPER VALVE LINE-UP IS FAILURE TO FOLLOW ADMINISTRATIVE CONTROLS FOR HANGING AND REMOVING DANGER TAGS AND RETURNING VALVES TO SERVICE.
338 | 3381987017 | 1987-07-15 | F1 | Steam Generator Tube Rupture PWR (SGTR) | [5 empty] | X | [18 empty] | X | [20 empty] | North Anna 1 | P | WE | PO | 100 | POWER LEVEL - 100%. AT APPROXIMATELY 0635 HOURS ON JULY 15, 1987, WITH UNIT 1 AT 100 PERCENT POWER AND UNIT 2 AT 81 PERCENT POWER, UNIT 1 WAS MANUALLY TRIPPED DUE TO INDICATIONS OF A STEAM GENERATOR TUBE RUPTURE IN THE 'C' STEAM GENERATOR. INJECTION SYSTEM AUTOMATICALLY INITIATED. AT 0639 HOURS, A NOTIFICATION OF UNUSUAL EVENT WAS DECLARED AND NOTIFICATIONS TO STATE AND LOCAL GOVERNMENTS WERE COMPLETED BY 0651 HOURS. THE EVENT WAS SUBSEQUENTLY UPGRADED TO AN ALERT AT 0654 HOURS AND ALL NOTIFICATIONS TO OFF-SITE AGENCIES AND THE NUCLEAR REGULATORY COMMISSION (NRC) WERE COMPLETED BY 0702 HOURS. COOLDOWN AND DEPRESSURIZATION OF THE REACTOR COOLANT SYSTEM (RCS) WAS CONDUCTED IN ACCORDANCE WITH STATION EMERGENCY OPERATING PROCEDURES. AT 1336 HOURS, THE RCS WAS COOLED DOWN TO BELOW 200 DEGREES F AND THE UNIT WAS PLACED IN MODE 5. AT THIS TIME, PLANT CONDITIONS WERE STABLE AND THE EMERGENCY WAS TERMINATED. THIS EVENT IS REPORTABLE PURSUANT TO 10 CFR 50.73(A)(2)(II), 10 CFR 50.73 (A)(2)(IV), AND WAS THE ELEVENTH ECCS ACTUATION REPORTABLE PURSUANT TO TECHNICAL SPECIFICATION 6.9.2. AT NO TIME DURING THIS EVENT WERE THE HEALTH AND SAFETY OF THE GENERAL PUBLIC AFFECTED.
338 | 3381987020 | 1987-11-23 | QR5 | Turbine Trip | [45 empty] | North Anna 1 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 0009 HOURS ON NOVEMBER 23, 1987, UNIT 1 TRIPPED FROM 100 PERCENT POWER (MODE 1). THE INITIATING SIGNAL FOR THIS REACTOR TRIP WAS A TURBINE SOLENOID TRIP WHICH RESULTED FROM A 5A FEEDWATER HEATER HI-HI LEVEL SIGNAL. THE 5A FW HEATER HI-HI LEVEL SIGNAL WAS GENERATED WHEN A LEVEL SWITCH FAILED. THIS EVENT IS REPORTABLE PURSUANT TO 10CFR50.73(A)(2)(IV). A FOUR HOUR REPORT WAS MADE IN ACCORDANCE WITH 10CFR50.72(B)(2)(II). THE CAUSE OF THE LEVEL SWITCH FAILURE WAS FATIGUE FAILURE OF A SPRING INSIDE THE MICROSWITCH. WHEN THE SPRING FAILED THE SWITCH CLOSED AND A TURBINE SOLENOID TRIP SIGNAL WAS GENERATED. AS CORRECTIVE ACTIONS, THE LEVEL SWITCH WAS REPLACED AND ALL OTHER FEEDWATER HEATER LEVEL SWITCHES WHICH INITIATE REACTOR TRIPS WERE INSPECTED WITH SATISFACTORY RESULTS. THIS EVENT POSED NO SIGNIFICANT SAFETY IMPLICATIONS BECAUSE ALL SAFETY RELATED EQUIPMENT FUNCTIONED AS DESIGNED AND KEY REACTOR PARAMETERS STABILIZED FOLLOWING THE REACTOR TRIP. ALSO, THE REACTOR TRIP SIGNAL WAS GENERATED FROM A SECONDARY PLANT PROTECTION SIGNAL FOR WHICH AN ACTUAL CONDITION DID NOT EXIST. THE HEALTH AND SAFETY OF THE GENERAL PUBLIC WERE NOT AFFECTED.
338 | 3381988002 | 1988-01-08 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | North Anna 1 | P | WE | PO | 100 | At 0438 hours on January 8, 1988, Unit 1 was manually tripped from approximately 100 percent power (Mode 1). The manual trip was initiated in anticipation of loss of the main condenser after the three running circulating water (CW) pumps tripped simultaneously and condenser vacuum was observed to be decreasing rapidly. <br /><br />Following the reactor trip, an electrical troubleshooting procedure was developed and performed to duplicate the events immediately prior to the simultaneous tripping of the three running CW pumps. No equipment problems (relays, timers, etc.) were identified which could account for the simultaneous tripping of the CW pumps. Additional testing was performed on the CW pump/condenser waterbox trip interlock protection circuitry in an attempt to determine the potential cause for the loss of all the CW pumps. As a result, the exact cause of the simultaneous tripping of the CW pumps could not be determined. <br /><br />This event posed no significant safety implications because all safety related equipment functioned as designed, with the exception of the steam driven auxiliary feedwater pump which successfully started and operated for about 40 minutes before tripping unexpectedly. Also, key reactor parameters stabilized, as expected, following the reactor trip. The health and safety of the general public were not affected. <br /><br />This event is reportable pursuant to 10CFR50.73(a)(2)(iv).
338 | 3381988005 | 1988-01-13 | QR5 | Turbine Trip | [45 empty] | North Anna 1 | P | WE | PO | 15 | At 0313 hours on January 13, 1988, Unit 1 automatically tripped from approximately 15 percent power (Mode 1). The initiating signal for this Reactor Trip was a turbine solenoid trip which resulted when a Hi-Hi level (greater than 75 percent) was detected on 2 out of 3 level channels in the "B" Steam Generator (S/G). The Hi-Hi level in the "B" S/G resulted from S/G level oscillations due to the low temperature of the FW (approximately 81 degrees F) entering the S/G's. This event is reportable pursuant to 10CFR 50.73(a)(2)(iv). <br /><br />When a Hi-Hi level was reached in the "B" S/G, a turbine solenoid trip occurred which resulted in a turbine trip, reactor trip, and a Main Feedwater (FW) isolation. As a result of the Main FW isolation, the auxiliary FW system automatically started, as designed. As corrective actions, Main FW was restored and Auxiliary FW was secured and then restored to the automatic position. To prevent recurrence of this type event, Operating Procedure 2.1, Unit Power Operation Mode 2 to Mode 1, will be revised to include a caution about FW temperature and increasing power above ten percent with S/G level oscillations. <br /><br />This event posed no significant safety implications because all safety related equipment responded as designed and key reactor parameters stabilized following the reactor trip. The health and safety of the public were not affected.
338 | 3381988013 | 1988-03-19 | QR5 | Turbine Trip | [45 empty] | North Anna 1 | P | WE | SU | 3 | At 0133 hours on March 19, 1988, Unit 1 experienced an automatic reactor trip from approximately 3.5 percent power, 0 MWe. The reactor trip occurred due to a spike in the turbine impulse (first stage) pressure which caused a turbine trip and enabled the logic for a reactor trip when a turbine trip condition existed. This event is reportable pursuant to 10CFR50.73 (A)(2)(iv). <br /><br />The turbine impulse pressure spike occurred while placing the turbine in operation. Internal bypass leakage in the Electro-Hydraulic Fluid Control System (EHC) was believed to have occurred in the servo control valves and valve actuators which control the position of the turbine governor valves. The increased bypass leakage allowed the turbine governor valves to close and resulted in a decrease in turbine impulse pressure. A second EHC pump was started to increase the EHC fluid pressure and reopen the turbine control valves. The reopening of the turbine control valves caused the impulse pressure to exceed the setpoints for a turbine trip if the generator output breaker is open and for a reactor trip from a turbine trip. <br /><br /> As a corrective action, the servo control valves for the four governor valves were replaced and tested satisfactorily. <br /><br /> This event posed no significant safety implications since safety related equipment responded as designed and key reactor parameters stabilized at their normal values following the reactor trip. The health and safety of the public were not affected.
338 | 3381988020 | 1988-08-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 1 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 2257 HOURS ON 8/6/88, UNIT 1 AUTOMATICALLY TRIPPED FROM APPROX. 100% POWER (MODE 1). THE INITIATING SIGNAL FOR THIS REACTOR TRIP WAS A 'B' STEAM GENERATOR FEED FLOW/STEAM FLOW MISMATCH COINCIDENT WITH A LOW LEVEL. THE FEED FLOW/STEAM FLOW MISMATCH RESULTED FROM CLOSURE OF THE 'B' MAIN FEEDWATER REGULATING VALVE. THIS EVENT IS REPORTABLE PURSUANT TO 10CFR50.73(A)(2)(IV). THE 'B' MAIN FEEDWATER REGULATING VALVE CLOSURE OCCURRED SUBSEQUENT TO A DEGRADED VOLTAGE CONDITION ON THE '1J' EMERGENCY BUS. THE DEGRADED VOLTAGE OCCURRED BECAUSE THE 'A' RESERVE STATION SERVICE TRANSFORMER (RSST) TAP CHANGER MOTOR BREAKER TRIPPED ON OVERCURRENT AFTER THE SHUNT REACTOR WAS PLACED IN SERVICE. THE 'A' RSST TAP CHANGER MOTOR BREAKER TRIPPED ON OVERCURRENT BECAUSE THE DYNAMIC BREAKING MECHANISM REMAINED ENGAGED DUE TO FAILURES WITHIN THE CONTROL CIRCUIT. AS A CORRECTIVE ACTION, THE 'A' RSST TAP CHANGER MOTOR AND CONTROL RELAYS WERE REPLACED, A CAM SWITCH WAS READJUSTED, AND THE 'A' RSST TAP CHANGER WAS SATISFACTORILY TESTED. THIS EVENT POSED NO SIGNIFICANT SAFETY IMPLICATIONS BECAUSE ALL SAFETY RELATED EQUIPMENT FUNCTIONED AS DESIGNED, AND KEY REACTOR PARAMETER STABILIZED FOLLOWING THE REACTOR TRIP. ALSO, THE PROTECTIVE FUNCTIONS REQUIRED FOR DEGRADED VOLTAGE WERE VERIFIED TO HAVE OCCURRED. THE HEALTH AND SAFETY OF THE GENERAL PUBLIC WERE NOT AFFECTED.
338 | 3381989005 | 1989-02-25 | QP2 | Partial Loss of Feedwater Flow | [6 empty] | X | [18 empty] | X | [19 empty] | North Anna 1 | P | WE | PO | 76 | At 1407 hours on February 25, 1989, Unit 1 automatically tripped from 76 percent power (Mode 1). The initiating signal for the reactor trip was "C" Steam Generator steam flow greater than feedwater flow mismatch coincident with a low Steam Generator level. The team flow greater than feedwater flow mismatch was caused by the closure of the "C" Main Feedwater Regulating Valve on the loss of control air. This event is reportable pursuant to 10CFR50.73(a)(2)(iv). <br /><br /> Following the reactor trip, indications of primary to secondary leakage were detected. "C" Steam Generator was identified as the source of the leakage. The Emergency Plan was entered and an ALERT was declared. The plant was subsequently cooled down and depressurized to Mode 5 and the ALERT was terminated. During the cooldown, a problem was encountered placing the Residual Heat Removal System in service due to a faulty auto-closure relay on the RHR Suction Isolation Valve (1-RH-MOV-1701). This is reportable pursuant to 10CFR50.73(a)(2)(v). Following the event, calculations were made that indicated that primary the secondary leakage was 74 GPM. This is reportable pursuant to 10CFR50.73(a)(2)(i)(A). <br /><br /> This event posed no significant safety implications because safety equipment functioned as designed. Radiological releases were well below Technical Specification limits. The health and safety of the general public were not affected during this event.
338 | 3381989014 | 1989-07-19 | QR5 | Turbine Trip | [45 empty] | North Anna 1 | P | WE | PO | 90 | At 1740 hours, on July 19, 1989, Unit 1 experienced an automatic reactor trip from 90 percent power. The reactor trip signal occurred due to a loss of electro hydraulic control (EHC) system pressure which generated a turbine trip and a subsequent reactor trip since power was greater than 10 percent. This event is reportable pursuant to 10CFR50.73(a)(2)(iv). A four hour report was made in accordance with 10CFR50.72(b)(2)(ii). <br /><br /> The loss of EHC system pressure was due to a failed o-ring on the turbine trip solenoid operated valve (SOV) 20-ET. The loss of EHC system pressure resulted in the closure of the turbine stop valves which generated the turbine trip signal. A reactor trip signal was automatically initiated, as designed, since power was greater than 10 percent. No safety injection signal (manual or automatic) was initiated or required during this event. Unit 1 was placed on line at 2136 hours on July 20, 1989. <br /><br /> A Root Cause Evaluation is being performed to determine the root cause of the turbine trip solenoid operated valve 20-ET o-ring failure. Recommendations resulting from the Root Cause Evaluation on the o-ring failure will be evaluated and implemented as necessary.<br /><br /> This event posed no significant safety implications because safety related equipment functioned as designed and key reactor parameters stabilized following the reactor trip. There was no release of radioactive materials due to the trip. The health and safety of the general public were not affected.
338 | 3381989017 | 1989-12-05 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | North Anna 1 | P | WE | PO | 7 | At 2236 hours on December 5, 1989, Unit 1 experienced an automatic reactor trip from approximately 7 percent power. The reactor trip occurred due to a Low Low level in the "B" Steam Generator (S/G). This event is reportable pursuant to 10CFR50.73(a)(2)(iv). <br /><br /> Prior to the reactor trip, reactor power was being reduced due to Electro Hydraulic Control (EHC) system pressure transients. Approximately 16 minutes before the reactor trip, the main generator output breaker was opened and the turbine was manually removed from service. <br /><br /> The EHC system pressure transient was caused by leaking turbine overspeed protection circuitry (OPC) valves. The OPC valves were replaced and other EHC system modifications/replacements were implemented. An event investigation is being performed to determine additional EHC system upgrades. Unit 1 was placed on line at 0434 hours on December 21, 1989. <br /><br /> This event posed no significant safety implications because safety related equipment functioned as expected and key reactor parameters stabilized following the reactor trip. The health and safety of the general public were not affected.
338 | 3381990001 | 1990-01-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 1 | P | WE | PO | 100 | At 1522 hours on January 23, 1990, Unit 1 experienced an automatic trip from 100 percent power. The initiating signal for the reactor trip was a low level in the "C" Steam Generator with a steam flow greater than feedwater flow mismatch. The mismatch resulted from closure of the 'C' Main Feedwater Regulating Valve. The closure was caused by a failed printed circuit driver card in the valve controller. After event investigation and corrective action, Unit 1 was returned to critical on January 24, 1990 at 0241 hours. <br /><br /> This event constitutes an automatic actuation of the Reactor Protection System and is reportable pursuant to 10 CFR 50.73 (a)(2)(iv). <br /><br /> No significant safety consequences resulted from the reactor trip because plant safety systems functioned as designed. The Reactor Coolant System parameters stabilized at their normal post trip values. There was no release of radioactive materials due to the trip.<br /><br /> The health and safety of the public were not affected at any time during this event.
338 | 3381991017 | 1991-08-08 | QL5 | Partial Closure of MSIVs | [45 empty] | North Anna 1 | P | WE | PO | 100 | On August 8, 1991, at 0242 hours, with Unit 1 at 99.8 percent power (mode 1) "A" main steam trip valve shut causing a safety injection and reactor trip. The initiating signal for the safety injection was high steam flow coincident with low steam line pressure in two out of three main steam lines. At 0250 hours a Notification of Unusual Event was declared, and the safety injection signal was reset in accordance with Emergency Procedures. Heat removal was accomplished through the atmospheric main steam power operated relief valves due to closure of the main steam trip valves. This event is reportable pursuant to 10CFR50.73 (a)(2)(iv), and was the twelfth ECCS Actuation reportable pursuant to Technical Specification 6.9.2. A one hour report was made pursuant to 10CFR50.72 (a)(i). <br /><br /> The cause of the event was water entering the control relay junction box for the "A" main steam trip valve. The source of water was determined to be rainfall entering the quench spray pump house due to a defective rain gutter. Inspection of the junction box revealed corrosion on the relay contacts which closed the gap between the seal-in contacts making it possible for water to create a short across the contacts.<br /><br /> No significant safety consequences resulted from this event because all safety systems responded appropriately. Therefore, the health and safety of the public was not affected at any time during this event..
338 | 3381995001 | 1995-01-27 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | North Anna 1 | P | WE | PO | 100 | On January 27, 1995, at 1601 hours, with Unit 1 in Mode 1, 100 percent power, an automatic reactor trip occurred. The reactor trip initiating signal was low flow in the 'B' reactor coolant loop with greater than thirty (30) percent power. This resulted in a reactor and turbine trip. A four (4) hour report was made to the NRC Operations Center at 1740 hours in accordance with 10 CFR 50.72 (b)(2)(ii). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv) for a condition that resulted in an automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS). <br /><br /> A fault in the motor leads box on the inboard motor of the 'B' main feedwater pump was not isolated by the motor supply breaker resulting in the loss of the 'B' station service bus. The loss of power to 'B' station service bus caused a loss of the 'B' reactor coolant pump and subsequent reactor trip on low loop flow. <br /><br /> This event posed no significant safety implications because core cooling was maintained and all safety systems responded appropriately. Therefore, the health and safety of the public were not affected at any time during this event.
338 | 3381996005 | 1996-08-27 | QR3 | Reactivity Control Imbalance | [45 empty] | North Anna 1 | P | WE | PO | 100 | On August 27, 1996, at 1004 hours, while performing a quarterly rod operability periodic test, Unit 1 experienced an automatic reactor trip from 100 percent power. The reactor trip initiating signal was 'Hi Flux Rate - Reactor Trip' which caused a reactor and turbine trip when multiple rods 'B' Control Bank, Group 2 tripped in from the fully withdrawn position of 225 steps. An ESF actuation subsequently followed, as designed, with the auto-starting of the Auxiliary Feed Water System on Steam Generator Low - Low level. <br /><br /> The cause of the event has been determined to be failure of the Control Rod Drive System to supply a full current - stationary current order to Group 2 of Control Bank 'B'. This allowed multiple rods in 'B' Control Bank, Group 2 to fall into the core and cause a high negative flux rate reactor trip. <br /><br /> A four (4) hour report was made to the NRC Operations Center at 1109 hours on August 27, 1996, in accordance with 10 CFR 50.72 (b) (2) (ii). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv) for a condition that resulted in an automatic actuation of an engineered safety feature, including the reactor protection system. <br /><br /> This event posed no significant safety implications since all safety systems responded as designed. Therefore, the health and safety of the public were not affected at any time during this event.
338 | 3381996010 | 1996-10-24 | QR5 | Turbine Trip | [45 empty] | North Anna 1 | P | WE | PO | 100 | On October 24, 1996, at 0319 hours, Unit 1 experienced an automatic reactor trip from 1 00 percent power. The reactor trip initiating signal was 'Turbine Trip/Reactor Trip' resulting from a main generator trip. Emergency procedures were entered and immediate actions were performed. All engineered safety feature (ESF) equipment responded as designed. The main generator trip was caused by the generator backup lockout relay (86-BU). Operation of the generator negative phase sequence relay actuated 86-BU. A non-emergency four hour report was made to the NRC at 0500 hours pursuant to 10 CFR 50.72 (b)(2)(ii). (a)(2)(iv). <br /><br /> The cause of the reactor trip is believed to be an internal problem to the generator negative phase sequence relay while operating in response to a transmission line fault. <br /><br /> No significant safety implications resulted from the reactor trip because the reactor protection safety systems responded as designed. Therefore, the health and safety of the public were not affected at any time during this event.
338 | 3382000004 | 2000-05-07 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | North Anna 1 | P | WE | PO | 100 | On May 7, 2000, at 0757 hours, with Unit 1 in Mode 1 operating at 100% power, a "Generator Lockout - Turbine Trip" occurred due to a malfunction (suspected ground) on the "A" phase of the generator output breaker, G-12. This resulted in an automatic reactor trip from a "Turbine Trip - Reactor Trip" signal. The Auxiliary Feedwater (AFW) System received an automatic start signal as expected for a full power reactor trip. Control Room personnel responded to the reactor trip in accordance with emergency procedure E-0, Reactor Trip or Safety Injection. Initially, Reactor Coolant System (RCS) pressure decreased to 1930 psig, pressurizer level decreased to 22 percent, and RCS temperature decreased to approximately 543 degrees F. Pressurizer pressure, level, and RCS temperature returned to their normal programmed values. All Engineered Safety Feature (ESF) equipment responded as designed. This event posed no significant safety implications because the reactor protection system and ESF systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
338 | 3382003003 | 2003-04-19 | QR6 | Manual Reactor Trip | [45 empty] | North Anna 1 | P | WE | PO | 74 | On April 19, 2003, at 2008 hours, with Unit 1 operating in Mode 1, at 74 percent power following a refueling and reactor vessel head replacement outage, a manual reactor trip was initiated. The manual reactor trip was initiated due to a loss of turbine electro-hydraulic control (EHC) system pressure which caused turbine control valves to drift shut. The cause of the EHC low pressure was a diaphragm failure on the auto stop oil side of the turbine auto stop oil EHC interface valve. At 2323 hours, a 4 hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made to the NRC in accordance with 10 CFR 50.72 (b)(3)(iv)(A). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in actuation of any engineered safety feature including the reactor protection system. This event posed no significant safety implications because the Reactor Protection System and Engineered Safeguards Features System functioned as designed. Therefore, the health and safety of the public were not affected by this event.
338 | 3382003004 | 2003-06-11 | QR5 | Turbine Trip | [45 empty] | North Anna 1 | P | WE | PO | 100 | On June 11, 2003, at 1453 hours with Unit 1 operating at 100 percent power an automatic reactor trip occurred as a result of a main transformer fault. The initiating signal was the Main Transformer Lockout Relay Turbine Trip resulting in a turbine trip/reactor trip. The cause of the main transformer fault was an unused electrical lead disengaging from the no-load tap changer and coming in contact with the transformer casing. At 1718 hours, a 4 hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made to the NRC in accordance with 10 CFR 50.72 (b)(3)(iv)(A). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in an automatic actuation of any engineered safety feature including the reactor protection system. This event posed no significant safety implications because the Reactor Protection and Engineered Safety Feature systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
338 | 3382007001 | 2007-01-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 1 | P | WE | PO | 100 | On January 3, 2007, at 1803 hours with Unit 1 operating at 100 percent power an automatic reactor trip occurred. The initiating signal was the "B" steam generator (SG) low level coincident with a steam flow greater than feed flow mismatch caused by closure of the "B" main feed regulating valve (MFRV). This resulted in a reactor and turbine trip. Closure of the "B" main feed regulating valve was due to a shorted capacitor on the final control card that provides input to the "B" MFRV. At 1932 hours a 4 hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made to the NRC in accordance with 10 CFR 50.72 (b)(3)(iv)(A). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in an automatic actuation of any engineered safety feature including the reactor protection system. This event posed no significant safety implications because the Reactor Protection System and Engineered Safety Features Actuation Systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
338 | 3382011003 | 2011-08-23 | QR7 | Other Reactor Trip (Valid RPS Trip) |  | X | [13 empty] | X | [29 empty] | North Anna 1 | P | WE | PO | 100 | On August 23, 2011, at 1351 hours, with both units in Mode 1 at 100% power, a magnitude 5.8 earthquake occurred approximately 11 miles WSW of North Anna Power Station. The earthquake caused an automatic reactor trip of both Units, and a loss of offsite power. At 1403 hours, an Alert was declared based on Shift Manager judgment, due to significant seismic activity onsite with the loss of offsite power. All Engineered Safety Feature equipment responded as designed with the exception of the Unit 1 turbine driven auxiliary feedwater pump, which was undergoing surveillance testing when the earthquake occurred. All 4 Emergency Diesel Generators (EDG) started as designed but the 2H EDG was manually tripped 49 minutes later due to a coolant system leak. The alternate AC diesel generator was subsequently aligned to re-energize the 2H emergency bus. Offsite power was fully restored at 2258 hours on August 23. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in system actuations. On August 26, 2011, at 1623, a non-emergency 8-hour report was made to the NRC Operations Center, in accordance with 10CFR50.72(b)(3)(ii)(B) due to the seismic activity potentially exceeding design basis levels. It was later determined that the seismic activity did exceed design levels at some frequencies. The event posed no significant safety implications and the health and safety of the public were not affected by the event.
338 | 3382013002 | 2013-10-11 | QR5 | Turbine Trip | [45 empty] | North Anna 1 | P | WE | PO | 48 | On October 11, 2013, at 1319 hours with Unit 1 operating at 48 percent power (Mode 1), an automatic turbine trip and subsequent reactor trip occurred due to a lockout relay actuation for the 1C Station Service Transformer (1-EP-SST-1C). The lockout occurred simultaneously with the start of the 1C Condensate Pump (1-CN-P-1C). The direct cause of the 1-EP-SST-1C lockout is that current transformer terminal block shorting screws were left installed inside the 1- EP-BKR-15C2 breaker cubicle. The root cause of the event was less than adequate written instructions for documenting the installation and removal of the terminal block shorting screws. All safety system responded as expected. The Auxiliary Feedwater Pumps actuated as designed following the reactor trip and provided makeup flow to the Steam Generators. 1-EP-SST-1C was inspected and no signs of damage or abnormal conditions were observed. At 1507 hours, a 4 hour report was made to the NRC in accordance with 10CFR50.72(b)(2)(iv)(B) for a Reactor Protection System (RPS) actuation and a 8 hour report in accordance with 10CFR50.72(b)(3)(iv)(A) for a Auxiliary Feedwater system actuation. The event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) for a condition that resulted in the automatic actuation of the RPS and AFW Systems. The health and safety of the public were not affected by the event.
338 | 3382015001 | 2015-02-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 1 | P | WE | PO | 96 | On February 26, 2015, at 1511 hours with Unit 1 operating at 96 percent power in an end of cycle coastdown, an automatic reactor trip occurred. The initiating signal was a low-low level on "B" steam generator caused by the closure of the "B" main feedwater regulating valve (MFRV). Closure of the valve was due to a loss of power on the final driver card for "B" MFRV. At 1639 hours, a 4-hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iv)(B) for "an event causing actuation of the Reactor Protection System when the reactor is critical" and an 8-hour report was also made in accordance with 10 CFR 50.72(b)(3)(iv)(A) for "an event causing actuation of the Auxiliary Feedwater System (AFW)." Approximately 30 minutes after the reactor trip with AFW flow throttled, the Turbine Driven (TD) AFW pump, 1-FW-P-2, discharge relief valve (RV) lifted and discharged approximately 200 gallons per minute (gpm) to the ground. The RV opened as a result of the inability of the governor valve for the pump to travel an additional 3/16" in the closed direction. An engineering evaluation determined that the loss of emergency condensate storage tank inventory was a condition reportable per 10 CFR 50.73(a)(2)(i)(B) for an "any operation or condition which was prohibited by Technical Specifications." The health and safety of the public were not affected by either event.
338 | 3382015002 | 2015-04-02 | QR6 | Manual Reactor Trip | [45 empty] | North Anna 1 | P | WE | PO | 100 | On April 2, 2015, at 0426 hours, with Unit 1 operating at 100 percent power, a manual reactor trip was initiated due to the inability to maintain main generator voltage in specification. This also resulted in a turbine trip. The operations crew entered the reactor trip procedure and stabilized Unit 1 in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the reactor trip. The inability to maintain generator voltage in specification was due to a failure of a component in a firing circuit downstream of the automatic voltage regulator (AVR). The root cause of the event was firing circuit design vulnerabilities in the AVR were not identified during the design change due to lack of rigor. At 0655 hours, a 4-hour Non- Emergency Report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iv)(B) for "an event causing actuation of the Reactor Protection System when the reactor is critical" and an 8- hour report was also made in accordance with 10 CFR 50.72(b)(3)(iv)(A) for "an event causing actuation of the Auxiliary Feedwater System (AFW)." Two of the AVR gate firing modules (GFMs) were replaced and the third GFM was evaluated to not be required and was disabled. The health and safety of the public were not affected by this event.
338 | 3382021001 | 2021-05-06 | QL7 | Degraded condenser vacuum | [45 empty] | North Anna 1 | P | WE | PO | 60 | On May 6, 2021 at 1223 hours, Unit 1 was manually tripped from 60% power due to degrading main condenser vacuum. Unit 1 was in the process of decreasing power due to increased secondary sodium levels identified earlier in the day. At 1400 hours on May 6, 2021, a 4-hour and 8-hour non-emergency report was made per 10 CFR 50.72(b)(2)(iv)(B) for RPS Actuation (scram) and 10 CFR 50.72(b)(3)(iv)(A) for a valid actuation of an ESF system, respectively. <br /><br /> The direct cause of the event was High Cycle Fatigue Piping Failure of the "A" High Pressure Heater Drain Receiver High Level Divert Line that caused damage to condenser tubes and degraded condenser vacuum. Unit 2 continued to operate at 100% power, Mode 1, during the event. The health and safety of the public were not affected by this event.
339 | 3391990010 | 1990-11-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 2 | P | WE | PO | 9 | At 1741 hours, on November 2, 1990, Unit 2 experienced an automatic reactor trip from approximately 9 percent power. The reactor trip was caused by a low low level in "A" Steam Generator. The reactor trip occurred approximately eight minutes following an automatic trip of the turbine from approximately 15 percent power. This event is reportable pursuant to 10CFR50.73 (b) (2) (iv). A four hour report was made in accordance with 10CFR50.72 (b) (2) (ii). <br /><br /> The cause of the event was personnel error since failure to reset the feedwater regulating bypass valves after reinitiation of Main Feedwater resulted in the low low the Steam Generator level and the subsequent reactor trip. A contributing cause of the event was that a specific procedure for responding to a turbine trip without a reactor trip was not available. As an immediate corrective action, Emergency Procedure 2-E-0, Reactor Trip or Safety Injection, was entered and the plant was stabilized. In addition, a root cause evaluation is being performed. Further corrective actions will be implemented, as required, based on the results of the root cause evaluation. <br /><br /> This event posed no significant safety implications because safety related equipment functioned as designed and key parameters stabilized following the reactor trip. There was no release of radioactive materials due to the reactor trip. The health and safety of the public were not affected at any time during this event.
339 | 3391991009 | 1991-09-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 2 | P | WE | PO | 100 | On September 20, 1991, at 0513 hours, with Unit 2 at 100 percent power, the "B" Main Feed Regulating Valve (MFRV) closed due to a driver card failure causing a reactor trip. The initiating signal for the reactor trip was "B" Steam Generator low level coincident with a steam flow greater than feed flow mismatch. After the reactor trip, an automatic Safety Injection (SI) was initiated. The SI was initially determined to be non-valid; however, a detailed investigation revealed that a malfunction in the steam dump control system resulting in a high steam flow with low-low Reactor Coolant System (RCS) average temperature generated the SI signal. This was the sixth SI to occur on Unit 2. This event is reportable pursuant to 10CFR50.73 (a) (2) (iv), and a four hour report was made pursuant to 10CFR50.72 (b) (2) (ii). A Notification of Unusual Event was declared upon determination that the SI signal was valid. <br /><br /> The "B" MFRV closure and subsequent reactor trip was caused by failure of the valve driver card. The SI signal was caused by a malfunction in the steam dump control system which prevented the valves from modulating closed. <br /><br /> No significant safety consequences resulted from this event because all safety systems responded appropriately. Therefore, the health and safety of the public was not affected at any time during this event.
339 | 3391992001 | 1992-01-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 2 | P | WE | PO | 89 | On January 29, 1992, at 0325 hours, with Unit 2 at 89 percent power, the "C" Main Feed Regulating Valve (MFRV) closed due to a driver card failure causing a reactor trip. The initiating signal for the reactor trip was "C" Steam Generator low level coincident with a steam flow greater than feedwater flow mismatch. This event is reportable pursuant to 10 CFR 50.73 (a) (2) (iv), and a four hour report was made pursuant to 10 CFR 50.72 (b) (2) (ii). <br /><br /> The "C" MFRV closure and subsequent reactor trip was caused by failure of the control system driver card. <br /><br /> No significant safety consequences resulted from this event because all safety systems responded appropriately. Therefore, the health and safety of the public was not affected at any time during this event.
339 | 3391992007 | 1992-08-06 | QL5 | Partial Closure of MSIVs | [45 empty] | North Anna 2 | P | WE | PO | 100 | On August 6, 1992, at 0751 hours, with Unit 2 at 100 percent power (mode 1), the "C" main steam trip valve (MSTV) failed shut causing a safety injection and reactor trip. The initiating signal for the safety injection was high steam line flow coincident with low steam line pressure in two out of three main steam lines. At 0756 hours a Notification of Unusual Event was declared and the Emergency Plan Implementing Procedures were entered. A one hour report was made pursuant to 10CFR 50.72 (a) (i). At approximately 0800 hours during the plant trip/SI recovery a leak was discovered on the downstream weld of a LHSI discharge line isolation vent valve. Since the piping could contain highly radioactive fluid during the post Loss Of Coolant Accident recirculation mode, the potential exists for an unmonitored gaseous release to the environment through a normally running exhaust fan. A four hour report was made pursuant to 10CFR50.72 (b) (2) (iii) (C). This event is reportable pursuant to 10CFR50.73(a)(2)(iv) and (v). <br /><br /> The cause of the C-MSTV closure has been attributed to failure of the C-MSTV air cylinder rupture disc. The valve weld failure is believed to be a result of an overstress condition when the LHSI pumps started on the SI signal. <br /><br /> No significant safety consequences resulted from this event because all safety systems responding appropriately and the unit never entered a post LOCA recirculation mode. Therefore, the health and safety of the public was not affected at any time during this event.
339 | 3391993002 | 1993-04-16 | QR5 | Turbine Trip | [45 empty] | North Anna 2 | P | WE | PO | 100 | On April 16, 1993, at 0717 hours with Unit 2 in Mode 1, 100 percent power, an automatic reactor trip occurred as a result of a turbine trip. Emergency procedures were entered and immediate actions were performed. Subsequently, the operating crew became concerned with the reactor coolant system (RCS) cooldown when temperature decreased to approximately 540 degrees F. To reduce the Steam Generator feedwater addition rate and stabilize the RCS temperature the ATWS Mitigation System Actuation Circuitry was reset and the Auxiliary Feed Water (AFW) pumps were secured before steam generator levels were restored above the automatic start setpoint. Defeating the automatic start capability of the AFW pumps is prohibited by Technical Specifications. A 4 hour report was made to the NRC at 1055 hours pursuant to 10CFR50.72 (b)(2)(ii) & (iii)(A). The event is reportable as an Engineered Safety Feature System actuation pursuant to 10CFR50.73 (a)(2)(iv) & (v). <br /><br /> The cause of the turbine trip/reactor trip was a malfunction in the main generator voltage regulator circuitry. The cause of defeating the AFW system during the event was a result of personnel error.<br /><br /> No significant safety consequences resulted from the reactor trip because reactor protection safety systems responded as designed. Disabling the AFW pumps did not present a significant safety consequence because the heat sink was maintained throughout the event. Therefore, the health and safety of the public were not affected at any time during this event.
339 | 3391993003 | 1993-04-24 | QR6 | Manual Reactor Trip | [45 empty] | North Anna 2 | P | WE | PO | 71 | On April 24, 1993, at 0530 hours with Unit 2 in Mode 1, 71 percent power, a manual reactor trip was initiated due to erratic feedwater flow indications to the "C" Steam Generator, abnormally high vibration alarms for the "B" Reactor Coolant Pump, and suspected water and steam leakage from the "C" Main Feedwater line. Emergency procedures were entered and immediate actions were performed. All Engineered Safety Feature system equipment responded as designed. At 0602 hours an "Alert" was declared, based on Shift Supervisor judgment, in accordance with Emergency Plan Implementing Procedures and the required notifications were made. A 1 hour report was made to the NRC at 0620 hours pursuant to 10CFR50.72 (a) (ii) (3). At 0816 hours with the unit in a stable condition the "Alert" classification was down graded to a Notification Of Unusual Event (NOUE). The NOUE was terminated at 1045 hours on April 24, 1993. The event is reportable pursuant to 50.73 (a) (2) (iv). <br /><br /> The cause of the event has been attributed to the inherent instabilities with the design of the main feedwater regulating valve and positioner controls. <br /><br /> No significant safety consequences resulted from the main feedwater concerns because auxiliary feedwater was available and provided cooling to the steam generators throughout the event. Therefore, the health and safety of the public were not affected at any time during this event.
339 | 3391994003 | 1994-01-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 2 | P | WE | PO | 100 | On January 22, 1994, at 0644 hours with Unit 2 operating at 95 percent power (Mode 1) an automatic reactor trip occurred. The initiating signal was the 'A' Steam Generator (SG) low level coincident with a steam flow greater than feedwater flow mismatch caused by closure of the 'A' Main Feedwater Regulating Valve (MFRV). This resulted in a reactor and turbine trip. A four hour report was made to the NRC at 1014 hours pursuant to 10 CFR 50.72 (b)(2)(ii) and (vi). This event is reportable pursuant to 10CFR50.73 (a)(2)(iv) as an automatic actuation of a Reactor Protection System. <br /><br /> The cause of the 'A' MFRV closure was due to a component failure of the upper pneumatic booster relay on the valve positioner. <br /><br /> No significant safety consequences resulted from this event because all safety systems responded appropriately. Therefore, the health and safety of the public were not affected at any time during this event.
339 | 3391995004 | 1995-11-11 | QR8 | Spurious Reactor Trip | [45 empty] | North Anna 2 | P | WE | PO | 100 | On November 11, 1995, at 1215 hours, with Unit 2 in Mode 1, 100 percent power, an automatic reactor trip occurred. The reactor trip initiating signal was 'Hi Flux Rate - Reactor Trip.' At 0220 hours on November 11, 1995, the 'A' Control Rod Drive System Motor Generator (MG) set tripped. The 'A' MG set was tagged out to support troubleshooting activities when the output breaker of the 'B' Motor Generator set tripped open causing the control rods to drop into the core. This resulted in the High Flux Rate Reactor Trip. <br /><br /> Loose fuses in the control power to the voltage regulators of each of the MG sets were determined to be the cause for the loss of the MG sets. <br /><br /> A four (4) hour report was made to the NRC Operations Center at 1445 hours on November 11, 1995 in accordance with 10 CFR 50.72 (b)(2)(ii). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv) for a condition that resulted in an automatic actuation of an engineered safety feature, including the reactor protection system. <br /><br /> This event posed no significant safety implications because all safety systems responded as designed. Therefore, the health and safety of the public were not affected at any time during this event.
339 | 3391996003 | 1996-11-12 | QR5 | Turbine Trip | [45 empty] | North Anna 2 | P | WE | PO | 100 | On November 12, 1996, at 0853 hours, Unit 2 experienced an automatic reactor trip from 1 00 percent power. The reactor trip initiating signal was a Turbine Trip/Reactor Trip resulting from a main generator trip. The main generator trip was the result of actuation of the generator stator ground overvoltage relay (59N) which picked up the generator differential lockout relay (86G). Emergency procedures were entered and immediate actions were performed. All engineered safety feature (ESF) equipment responded as designed. A non-emergency four hour report was made to the NRC at 1112 hours pursuant to 10CFR50.72(b)(2)(ii). This event is reportable pursuant to 10CFR50.73 (a)(2)(iv). <br /><br /> The cause of the reactor trip has been determined to be a failed generator stator coil due to overheating.<br /><br /> No significant safety implications resulted from the reactor trip because the reactor protection and engineered safety systems responded as designed. Therefore, the health and safety of the public were not affected at any time during this event.
339 | 3391998004 | 1998-09-17 | QR8 | Spurious Reactor Trip | [45 empty] | North Anna 2 | P | WE | PO | 100 | At 2032 hours on September 17, 1998, with Unit 2 in Mode 1 at 100 percent power, an automatic reactor trip occurred due to an Over-Temperature Delta-T protection actuation. Just prior to and at the time of the trip, a lightning storm was in progress whereby plant personnel noticed a lightning strike inside the protected area in the vicinity of Unit 2. A non-emergency four hour report was made to the NRC at 2305 hours pursuant to 10CFR50.72(b)(2)(ii). This event is reportable pursuant to 10CFR50.73(a)(2)(iv). The probable cause of the automatic reactor trip was due to the actuation of the Over-Temperature/Delta-T protection circuitry caused by a lightning strike. No significant safety implications resulted from the reactor trip because the reactor protection safety systems functioned successfully to trip the reactor safely as designed. Therefore, the health and safety of the public were not affected at any time during this event.
339 | 3391999004 | 1999-12-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 2 | P | WE | PO | 98 | On December 2, 1999, at 1647 hours, with Unit 2 in Mode 1 operating at approximately 98% power, the reactor was manually tripped due to the loss of two of three main feedwater pumps The main feedwater pumps tripped on low suction pressure due to the loss of discharge flow from the "A" high pressure heater drain pump following a secondary plant transient. The auxiliary feedwater pumps automatically actuated following the reactor trip to restore inventory in the steam generators. This event is reportable pursuant to 10CFR50.73 (a)(2)(iv) for any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS). The cause of the event is attributable to the failure of a feedwater heater level control switch to properly actuate. A root cause evaluation of the event is being performed. This event posed no significant safety implications. The reactor was safely shut down and ESF equipment operated properly. The health and safety of the public were not affected.
339 | 3392000001 | 2000-04-03 | QR5 | Turbine Trip | [45 empty] | North Anna 2 | P | WE | PO | 100 | On April 3, 2000, at 0857 hours, with Unit 2 in Mode 1 operating at 100% power, an automatic reactor trip occurred as a result of actuation of the 2C Station Service Lockout Relay resulting in a Turbine trip-Reactor trip. Actuation of the 2C Station Service Lockout Relay was due to a fault on a secondary feeder cable from the 2C Station Service Transformer to the 2C Station Service Bus. Control Room personnel responded to the reactor trip in accordance with emergency procedure E-0, Reactor Trip or Safety Injection. Initially, Reactor Coolant System (RCS) pressure decreased to 1985 psig, pressurizer level decreased to 23 percent, and RCS temperature decreased to approximately 542 degrees F. Pressurizer pressure, level and RCS temperature returned to their normal programmed values. All Engineered Safety Feature (ESF) equipment responded as designed. This event posed no significant safety implications because the reactor protection system and ESF systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
339 | 3392000002 | 2000-04-04 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | North Anna 2 | P | WE | SU | 7 | On April 4, 2000, at 1146 hours, with Unit 2 in Mode 1 operating at approximately 7% power, a manual reactor trip was initiated to comply with Technical Specification 3.4.1.1 due to the loss of the "C" reactor coolant pump. While preparing to install the potential transformer fuses for recovery of the 2C Station Service Bus (SSB), the drawer for the "F" emergency transfer bus was opened. This caused the "C" Reserve Station Service Transformer (RSST) to unload, deenergizing the 1 H and 2J emergency busses and also both Unit's "C" SSBs. The "C" Reactor Coolant Pumps on both units tripped due to the loss of the "C" SSBs. Both unit's SSB power was being provided from the RSST busses at this time. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(A) and (a)(2)(iv). The loss of the emergency busses was the result of personnel error when the incorrect potential transformer fuse drawer was opened. This event posed no significant safety implications because the Unit's Reactor Protection System and ESF systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event. Non-emergency one and four hour reports were made at 1225 hours on April 4, 2000, pursuant to 10 CFR 50.72(b)(1)(i)(A) and (b)(2)(ii).
339 | 3392001005 | 2001-12-22 | QR5 | Turbine Trip | [45 empty] | North Anna 2 | P | WE | PO | 100 | On December 22, 2001, at 1542 hours, with Unit 2 in Mode 1 operating at 100% power, an automatic reactor trip occurred due a to failure in the turbine control electro hydraulic control (EHC) power supply system. A momentary fault on the control system power supply created a situation where the EHC system controller changed operating modes and reset its demand to zero. Consequently, the turbine valves drifted closed. The loss of load transient caused a reactor trip on low-low steam generator level. The reactor trip signal initiated a turbine trip. A non-emergency 4-hour notification was made to the NRC, at 1920 hours, on December 22, 2001, in accordance with 10CFR50.72(b)(2)(iv)(B). During the event, the auxiliary feedwater (AFW) system and accident mitigation system actuation circuitry (AMSAC) actuated. A non-emergency 8-hour notification was also made to the NRC, at 1920 hours, on December 22, 2001, in accordance with 10CFR50.72(b)(3)(iv)(A). The cause of the event was a failure of components in both the normal and backup turbine control EHC power supplies. Repairs to the components in both the normal and backup turbine control EHC power supply were performed prior to unit startup. No significant safety consequences resulted from this event because the reactor protection system and ESF systems functioned as designed following the reactor trip. The health and safety of the public were not affected at any time during this event.
339 | 3392003001 | 2003-03-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 2 | P | WE | PO | 100 | On March 31, 2003, at 1259 hours with Unit 2 operating at 100 percent power an automatic reactor trip occurred. The initiating signal was the "C" steam generator (SG) low level coincident with a steam flow greater than feed flow mismatch caused by closure of the "C" main feed regulating valve. This resulted in a reactor and turbine trip. Closure of the "C" main feed regulating valve was due a blown fuse on the valve driver card. At 1540 hours a 4 hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made to the NRC in accordance with 10 CFR 50.72 (b)(3)(iv)(A). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv) for a condition that resulted in an automatic actuation of any engineered safety feature including the reactor protection system. This event posed no significant safety implications because the Reactor Protection and ESF systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
339 | 3392004004 | 2004-06-10 | QR8 | Spurious Reactor Trip | [45 empty] | North Anna 2 | P | WE | PO | 100 | On June 10, 2004, at 1313 hours, with North Anna Unit 2 operating at 100 percent power (Mode 1), an automatic reactor trip occurred during performance of 2-PT-36.1A (Train A Reactor Protection and ESF Logic Actuation Logic Test). An incorrect contact configuration in the cell switch for "A" Bypass Reactor Trip Breaker caused the event. The incorrect contact configuration created a Turbine Trip Signal which, in turn, resulted in a Reactor Trip Signal. At 1611 hours, a 4-hour Non-Emergency Report was made to the NRC in accordance with 10CFR50.72(b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made in accordance with 10CFR50.72(b)(3)(iv)(A) due to actuation of the Auxiliary Feedwater System. This event is reportable pursuant to 10CFR50.73(a)(2)(iv) for a condition that resulted in an automatic actuation of any engineered safety feature including the reactor protection system. The cell switch contact configurations for the Unit 2 Bypass Reactor Trip Breakers were corrected. No significant safety implications existed because the Solid State Protection System was fully capable of tripping the reactor if required.
339 | 3392005001 | 2005-08-05 | QR8 | Spurious Reactor Trip | [45 empty] | North Anna 2 | P | WE | PO | 100 | On August 5, 2005, at 2227 hours, North Anna Unit 2 experienced an automatic Reactor trip from 100 percent power during a severe thunderstorm. A lightning strike was the direct cause of this event. The lightning strike caused an Overtemperature Delta T (OTDT) Unit 2 Reactor Trip signal without an actual over temperature condition. The control room team responded to the reactor trip in accordance with procedure 2-E-0, Reactor Trip or Safety injection. All Engineered Safety Feature equipment responded as designed. A non-emergency 4-hour report was made to the NRC Operations Center at 0020 hours on August 6, 2005, in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8-hour report was also made in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to actuation of the Auxiliary Feedwater System (AFW). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in automatic actuation of the reactor protection system and the AFW system. This event posed no significant safety implications since the reactor protection systems functioned to trip the reactor safely. Therefore, the health and safety of the public were not affected by this event.
339 | 3392006001 | 2006-11-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 2 | P | WE | PO | 100 | On November 16, 2006, at 0226 hours with Unit 2 operating at 100 percent power an automatic reactor trip occurred. The initiating signal was the "B" steam generator (SG) low level coincident with a steam flow greater than feed flow mismatch caused by closure of the "B" main feed regulating valve. This resulted in a reactor and turbine trip. Closure of the "B" main feed regulating valve was due to failure of the isolation card that provides steam flow input to the "B" SG water level control circuit. At 0357 hours a 4 hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made to the NRC in accordance with 10 CFR 50.72 (b)(3)(iv)(A).This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in an automatic actuation of any engineered safety feature including the reactor protection system. This event posed no significant safety implications because the Reactor Protection System and Engineered Safety Features Actuation Systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
339 | 3392007003 | 2007-06-29 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | North Anna 2 | P | WE | PO | 100 | On June 29, 2007 at 1752 hours, with Unit 2 in Mode 1 at 100% power, an automatic turbine trip, reactor trip and Phase "A" Containment Isolation occurred due to an invalid Train "B" Safety Injection actuation. Following the trip, some Train "B" Safety Injection equipment would not reset from the Main Control Room. Manual actions were performed to secure Safety Injection flow. During this process, the Pressurizer filled and spilled over to the Pressurizer Relief Tank rupturing one of the rupture disks. This allowed Reactor Coolant System water to reach the Unit 2 Containment basement. The cause of this event was the failure of zener diode CR34 on Universal card A313 located in the "B" Train of the Solid State Protection System. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) for an event that resulted in the automatic actuation of the Reactor Protection System and Engineered Safety Function Systems. Unit 2 was cooled down to Mode 5 conditions at 0839 hours on June 30, 2007. The health and safety of the public were not affected at any time during the event.
339 | 3392007004 | 2007-12-25 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | North Anna 2 | P | WE | PO | 100 | On December 25, 2007 at 2110 hours, with Unit 2 in Mode 1 at 100% power, an automatic reactor trip occurred. The automatic reactor trip was a result of a loss of coolant flow with power greater than 30 percent. The loss of coolant flow was the result of the "B" Reactor Coolant Pump (RCP) motor trip. A review of the event determined that the breaker supplying the "B" RCP motor opened due to a response by the neutral over current protection relay. Post-event testing of the "B" RCP motor trip identified a "B" phase to ground fault. The ground fault of the motor winding was caused by a manufacturing defect leading to premature aging of the coil insulation system. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) for an event that resulted in the automatic actuation of the Reactor Protection System and Engineered Safety Features Actuation Systems. All Engineered Safety Feature equipment responded as designed with the exception of the steam driven auxiliary feedwater pump which tripped due to actuation of the over-speed trip valve and was manually reset and subsequently placed in service. The health and safety of the public were not affected at any time during the event.
339 | 3382009004 | 2009-12-09 | QL7 | Degraded condenser vacuum | [45 empty] | North Anna 2 | P | WE | PO | 100 | At 1423 hours on 12/9/09, electrical supply breaker L102 was inadvertently opened, which caused the "C" Reserve Station Service Transformer (RSST) to de-energize. This caused a loss of power to the 1H and 2J Emergency Buses and an automatic start of the 1H and 2J Emergency Diesel Generators (EDGs); both EDGs operated as designed. The Unit 1 "B" and Unit 2 "A" Charging pumps automatically started, as designed, due to the loss of power. The Unit 2 "G" Bus did not automatically transfer from the "C" RSST to the "B" RSST prior to undervoltage relay lockout operation resulting in the loss of the Unit 2 Circulating Water pumps. This resulted in a loss of condenser vacuum and a subsequent Unit 2 turbine and reactor trip. The Unit 2 Auxiliary Feedwater (AFW) pumps automatically started and operated as designed. The Unit 2 "C" Station Service Bus was also de-energized following the trip, as expected with the "C" RSST de-energized. This resulted in the loss of the Unit 2 "C" Reactor Coolant Pump (RCP). The "A" and "B" RCPs operated as designed. This event is reportable per 10 CFR 50.73 (a)(2)(iv)(A) for the automatic actuation of the Reactor Protection System, EDGs, AFW System, and Charging Systems. No significant safety consequences resulted from this event since all Engineered Safety Feature equipment responded as designed. Therefore, the health and safety of the public were not affected by this event.
339 | 3392010001 | 2010-04-27 | QR5 | Turbine Trip | [45 empty] | North Anna 2 | P | WE | PO | 74 | On April 27, 2010 at 1637 hours, with Unit 2 in Mode 1 at 74% power during recovery from a refueling outage, an automatic reactor trip occurred while testing a new digital automatic voltage regulator (AVR). A turbine trip due to a generator lockout caused the automatic reactor trip. The direct cause of the generator lockout protective relay actuation was the incorrect operability curve set points derived from the voltage regulator Minimum Excitation Level (MEL) tuning software. Following the reactor trip, all control rods inserted into the core and decay heat was removed using the normal steam dump system. The Auxiliary Feedwater (AFW) Pumps received an automatic start signal due to low/low level in the steam generators following the reactor trip. Following the automatic start of the Turbine Driven AFW (TDAFW) pump, the Control Room received annunciator alarm (F-D8). This was an AFW Pump Trouble or Lube Oil Trouble alarm. An operator was dispatched and reported that oil was spraying from the pump bearings and reservoir. The TDAFW pump was secured and declared inoperable. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) for the automatic actuation of the Reactor Protection System and AFW System. No significant safety consequences resulted from this event. Steam Generator inventory was restored to the normal operating level. Therefore, the health and safety of the public were not affected by this event.
339 | 3392010002 | 2010-05-28 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | North Anna 2 | P | WE | PO | 100 | On May 28, 2010, at 0004 hours North Anna Unit 2 experienced an automatic Reactor trip from 100 percent power following a lightning strike in the switchyard. A combination of events precluded the transfer of the "B" Station Service (SS) bus to the "B" Reserve Station Service Transformer (RSST), resulting in the "B" SS bus being de-energized and a consequential loss of power to Unit 2 reactor coolant pump 1B (2-RC-P-1 B). Unit 2 tripped on low flow in the "B" RCS loop. All available Engineered Safety Feature equipment responded as designed. A non-emergency 4-hour report was made to the NRC Operations Center at 0323 hours on May 28, 2010, in accordance with 10 CFR 50.72(b)(2)(iv)(B). An 8-hour report was also made in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to actuation of the Auxiliary Feedwater System (AFW). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in automatic actuation of the reactor protection system and the AFW system. This event posed no significant safety implications since the reactor protection system functioned to trip the reactor. Therefore, the health and safety of the public were not affected by this event.
339 | 3392010004 | 2010-06-16 | QR8 | Spurious Reactor Trip | [45 empty] | North Anna 2 | P | WE | PO | 98 | On June 16, 2010, at 1920 hours North Anna Unit 2 experienced an automatic reactor trip from 98 percent power during a severe thunderstorm. A lightning strike within the Protected Area was the direct cause of this event. The lightning strike caused an Overtemperature Delta T (OTAT) reactor trip signal without an actual overtemperature condition. The control room team responded to the reactor trip in accordance with procedure 2-E-0, Reactor Trip or Safety injection. All Engineered Safety Feature equipment responded as designed. A non-emergency 4-hour report was made to the NRC Operations Center at 2108 hours on June 16, 2010, in accordance with 10 CFR 50.72(b)(2)(iv)(B). An 8-hour report was also made, in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to actuation of the Auxiliary Feedwater System (AFW). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in automatic actuation of the Reactor Protection System (RPS) and the AFW system. This event posed no significant safety implications since the reactor protection systems functioned to trip the reactor. Therefore, the health and safety of the public were not affected by this event.
339 | 3382011003 | 2011-08-23 | QR7 | Other Reactor Trip (Valid RPS Trip) |  | X | [13 empty] | X | [29 empty] | North Anna 2 | P | WE | PO | 100 | On August 23, 2011, at 1351 hours, with both units in Mode 1 at 100% power, a magnitude 5.8 earthquake occurred approximately 11 miles WSW of North Anna Power Station. The earthquake caused an automatic reactor trip of both Units, and a loss of offsite power. At 1403 hours, an Alert was declared based on Shift Manager judgment, due to significant seismic activity onsite with the loss of offsite power. All Engineered Safety Feature equipment responded as designed with the exception of the Unit 1 turbine driven auxiliary feedwater pump, which was undergoing surveillance testing when the earthquake occurred. All 4 Emergency Diesel Generators (EDG) started as designed but the 2H EDG was manually tripped 49 minutes later due to a coolant system leak. The alternate AC diesel generator was subsequently aligned to re-energize the 2H emergency bus. Offsite power was fully restored at 2258 hours on August 23. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in system actuations. On August 26, 2011, at 1623, a non-emergency 8-hour report was made to the NRC Operations Center, in accordance with 10CFR50.72(b)(3)(ii)(B) due to the seismic activity potentially exceeding design basis levels. It was later determined that the seismic activity did exceed design levels at some frequencies. The event posed no significant safety implications and the health and safety of the public were not affected by the event.
339 | 3392012001 | 2012-10-24 | QR5 | Turbine Trip | [45 empty] | North Anna 2 | P | WE | PO | 100 | On October 24, 2012, at 0147 hours with Unit 2 in Mode 1, 100 percent power, an automatic reactor trip occurred due to a low-low level in the "C" steam generator (SG) resulting from closure of all four governor valves. The governor valves' closed due to a spurious error signal from Speed Error Amplifier Card "B" (1A08D). The card malfunction was the result of a failed capacitor. All systems responded as expected. All control rods inserted into the core at the time of the trip and decay heat was removed via the main condenser steam dumps. The auxiliary feedwater (AFW) pumps received an automatic start signal due to low-low level in "C" SG at the time of the trip. The SG levels were restored to normal operating level. At 0240 hours, a 1 hour report was made to the NRC as an After-The-Fact Unusual Event due to a pressurizer relief valve opening momentarily exceeding EAL SU6.1, Reactor Coolant System Leakage. The emergency notification was subsequently retracted. At 0318 hours, a 4 hour report was made in accordance with 10CFR50.72(b)(2)(iv)(B) for Reactor Protection System (RPS) actuation and 8 hour report in accordance with 10CFR50.72(b)(3)(iv)(A) for AFW pump automatic start. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in automatic actuation of the RPS and AFW System. The health and safety of the public were not affected by the event.
339 | 3392013001 | 2013-05-10 | QR6 | Manual Reactor Trip | [45 empty] | North Anna 2 | P | WE | PO | 60 | On May 10, 2013, at 0612 hours with Unit 2 in Mode 1, 60 percent power following a refueling outage, a manual reactor trip was initiated as a result of increased vibrations on the number 9 main turbine/generator bearing and a report of a luminous discharge in the main generator exciter enclosure. All systems responded as expected following the manual trip. The auxiliary feedwater (AFW) pumps received an automatic start signal due to the resulting low-low level in "C" Steam Generator (SG). The AFW System operated as designed with no abnormalities noted and was subsequently returned to automatic operation. The SG levels were restored to normal operating level. When resetting AMSAC, a second AFW system automatic start occurred due to a procedure sequence error and was determined to be an invalid signal. At 0820 hours, a 4 hour report was made in accordance with 10CFR50.72(b)(2)(iv)(B) for Reactor Protection System (RPS) actuation and 8 hour report in accordance with 10CFR50.72(b)(3)(iv)(A) for the first AFW pump automatic start. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in automatic actuation of the RPS and AFW System. The health and safety of the public were not affected by the event since the equipment responded as designed.
339 | 3392013002 | 2013-05-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 2 | P | WE | PO | 98 | On May 28, 2013, at 1507 hours with Unit 2 operating at 98 percent power (Mode 1), a manual reactor trip was initiated due to a main feedwater system transient. The main feedwater system transient resulted from the spurious closure of the "C" Main Feedwater Pump Discharge Motor-Operated Valve, 2-FW-MOV-250C, that subsequently resulted in the tripping of "A" Main Feedwater pump on low suction pressure. The cause of the spurious closure of 2-FW-MOV- 250C was a loss of conductivity in the upper cell switch of breaker 2-EP-BRK-25C5 which indicated that one motor on 2-FW-P-1C had tripped. At 1809 hours, a 4 hour report was made to the NRC in accordance with 10CFR50.72(b)(2)(iv)(B) for a Reactor Protection System (RPS) actuation and a 8 hour report in accordance with 10CFR50.72(b)(3)(iv)(A) for a Auxiliary Feedwater system actuation. The event is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) for a condition that resulted in the automatic actuation of the RPS and AFW Systems. The health and safety of the public were not affected by the event.
339 | 3392014001 | 2014-02-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | North Anna 2 | P | WE | PO | 100 | At 0859 on February 2, 2014, with Unit 2 operating at 100% power, the "A" Main Feedwater (MFW) Pump, 2-FW- P-1A, had a motor lead connection that grounded and caused the power supply breakers for 2-FW-P-1A to trip open. The standby MFW pump, 2-FW-P-1C, auto started, as designed. The Reactor Operator (RO) believed the standby pump did not auto start, since one of the Control Room indicating lights did not illuminate as expected. The RO believed that only one MFW pump was running with two required for operation greater than 70% power. Based on this indication and the perceived loss of MFW, the RO initiated a manual reactor trip as directed in 2-AP-31. Although the remaining control room team members were aware that the standby pump had autostarted, they were unable to intervene in time to prevent the manual trip. Following the manual reactor trip, the unit was stabilized in Mode 3 at normal reactor coolant temperature and pressure. This event was reportable per 10CFR50.72(b)(2)(iv)(B) for actuation of the reactor protection system. Following the reactor trip, the Auxiliary Feedwater pumps automatically started as designed and provided makeup flow to the steam generators. This event was reportable per 10CFR50.72(b)(3)(iv)(A) for actuation of an Engineered Safety Feature (ESF) system. The health and safety of the public were not affected by this event.
339 | 3392019001 | 2019-03-02 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | North Anna 2 | P | WE | PO | 12 | On March 2, 2019 North Anna Unit 2 Operations personnel were lowering reactor power in preparation for a scheduled refueling outage. Condenser vacuum began to degrade and personnel entered the Abnormal Operating Procedure for Low Condenser Vacuum. The reactor was manually tripped at approximately 12% power. The Operations crew entered the reactor trip procedure and stabilized the Unit in Mode 3 at normal operating pressure and temperature. The manual reactor trip was not complicated and shift personnel responded appropriately. After the trip, decay heat was removed by the Steam Generator Pressure Operated Relief Valves and Unit 2 was cooled down to support a scheduled refueling outage. <br /><br /> The direct cause of the degrading condenser vacuum was a failed socket weld downstream of a High Pressure Turbine Main Steam Supply Header Drain Valve on the condenser (steam) side.<br /><br /> A 4-hour report per 10CFR50.72(b)(2)(iv)(B) at 0013 hours on March 3, 2019 was made for a manual actuation of the reactor protection system. <br /><br /> The reactor trip is reportable per 10CFR50.73(a)(2)(iv)(A) for a manual actuation of the reactor protection system.
341 | 3411987002 | 1987-02-26 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 29 | POWER LEVEL - 029%. ON FEBRUARY 26, 1987 AT 1336 HOURS A GROUND FAULT CAUSED THE TURBINE TO TRIP. THIS IN TURN INITIATED A REACTOR SCRAM. DURING THIS EVENT, A REACTOR VESSEL LOW WATER LEVEL TRANSIENT OCCURRED, RESULTING IN A REACTOR WATER LEVEL 3 SCRAM SIGNAL. AN ALUMINUM STRIP WHICH HAD BEEN USED AS AN ASSEMBLY AID IN THE ISO-PHASE BUS COOLING DUCT BROKE FREE. WHEN THE ALUMINUM STRIP BROKE FREE IT CONTACTED THE Y-PHASE BUS CAUSING THE GROUND FAULT. TO PREVENT RECURRENCE THE ACCESSIBLE AREAS OF THE ISO-PHASE BUS COOLING DUCTS WERE INSPECTED FOR ITEMS WHICH COULD BREAK FREE.
341 | 3411987008 | 1987-03-01 | L3 | Turbine Bypass Unavailable | [10 empty] | X | [30 empty] | X |  |  |  | Fermi 2 | B | GE | PO | 18 | POWER LEVEL - 018%. AT 0458 HRS ON 3-1-87, FERMI 2 WAS IN OPERATIONAL CONDITION 1 (POWER OPERATION), OPERATING AT 525 F, 921 PSIG, AND 18% REACTOR POWER. WHILE RESETTING AN ELECTRICAL GOVERNOR TROUBLE ALARM, POWER TO PORTIONS OF THE TURBINE CONTROL CIRCUITRY WAS LOST. REACTOR LEVEL AND PRESSURE CONDITIONS WERE SUBSEQUENTLY CREATED WHICH RESULTED IN ESF VALVE ISOLATIONS, A REACTOR PROTECTION SYSTEM ACTUATION, AND A REACTOR SCRAM. THIS EVENT WAS CAUSED BY A PERSONNEL ERROR WHILE ATTEMPTING TO RESET THE GOVERNOR ALARM. THE ERROR INVOLVED INCOMPLETE UNDERSTANDING OF THE CONSEQUENCES OF ACTIONS WHICH WERE TAKEN TO RESET THE ALARM. AN INADEQUATE PROCEDURE CONTRIBUTED TO THE ERROR. THE PROCEDURE DID NOT ADEQUATELY DESCRIBE HOW TO RESET A 'MOD F' INITIATED GOVERNOR ALARM. AS A CORRECTIVE ACTION, THE RESPONSE PROCEDURE FOR THE GOVERNOR ALARM AND THE OPERATING PROCEDURE FOR THE MAIN TURBINE HAVE BEEN REVISED. ADDITIONALLY, THE OPERATOR INVOLVED IN THIS EVENT WAS COUNSELED. THIS EVENT WAS NOT CONTRIBUTED TO BY ANY FAILED SYSTEMS OR COMPONENTS. OR COMPONENTS.
341 | 3411987011 | 1987-04-06 | QR8 | Spurious Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 31 | POWER LEVEL - 031%. AT 2241 HOURS ON APRIL 6, 1987 FERMI 2 WAS IN OPERATIONAL CONDITION 1 (POWER OPERATION), OPERATING AT 520 DEGREES FAHRENHEIT, 940 PSIG AND 31 PERCENT REACTOR THERMAL POWER. WHILE PERFORMING SURVEILLANCE PROCEDURE 44.010.125 'RPS - APRM B CHANNEL FUNCTIONAL TEST', A REACTOR PROTECTION SYSTEM (RPS) ACTUATION AND LEVEL 3 INITIATED ENGINEERED SAFETY FEATURE VALVE ISOLATIONS OCCURRED. THIS EVENT WAS CAUSED BY PERSONNEL ERROR. WHILE A HALF SCRAM SIGNAL WAS PRESENT DURING APRM 'B' FUNCTIONAL TESTING, THE TRIP REFERENCE CARD FOR APRM 'A' WAS INADVERTENTLY REMOVED. THIS RESULTED IN THE RPS ACTUATION. AS A CORRECTIVE ACTION, THE PROCEDURES FOR PERFORMING APRM 'A' AND 'B' FUNCTIONAL TESTING WILL BE REVISED. IN ADDITION, THE INDIVIDUAL INVOLVED IN THIS EVENT WAS COUNSELED.
341 | 3411987017 | 1987-05-13 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Fermi 2 | B | GE | PO | 18 | POWER LEVEL - 018%. ON MAY 13, 1987 AT 1703 HOURS THE SOUTH REACTOR FEED PUMP TURBINE (SRFPT) TRIPPED DUE TO EXCESSIVE VIBRATIONS. REACTOR VESSEL LEVEL DECREASED BELOW THE LEVEL 3 REACTOR PROTECTION SYSTEM TRIP SETPOINT AND A FULL SCRAM OCCURRED AT 1705 HOURS. THE MOST PROBABLE CAUSE OF THIS EVENT WAS THE SRFPT HIGH PRESSURE CASING DRAIN VALVE BEING CLOSED DURING SRFPT STARTUP DUE TO AN INADEQUATE PROCEDURE. THIS RESULTED IN WATER BUILDUP WHICH EXAGGERATED THE VIBRATION NORMALLY EXPERIENCED AT THE TURBINE CRITICAL SPEED. THIS EXCESSIVE VIBRATION COMBINED WITH OPERATION NEAR THE CRITICAL SPEED RESULTED IN FAILURE OF THE SRFPT. AS CORRECTIVE ACTION, THE REACTOR FEEDWATER SYSTEM PROCEDURE HAS BEEN REVISED TO CLARIFY STEPS FOR TURBINE DRAIN OPERATION. IN ADDITION, ALARM RESPONSE PROCEDURES FOR NORTH AND SOUTH REACTOR FEED PUMP TURBINE SHAFT TROUBLE HAVE BEEN REVISED TO CLARIFY INSTRUCTIONS FOR VIBRATION RESPONSE. THE SRFPT WILL BE REPAIRED AND AFTER FINAL REASSEMBLY, THE UNIT WILL BE MONITORED ON STARTUP.
341 | 3411987031 | 1987-07-20 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 48 | POWER LEVEL - 048%. ON JULY 20, 1987 AT 1813 HOURS, A HIGH VIBRATION SIGNAL FOR THE MAIN TURBINE GENERATOR NUMBER ONE BEARING WAS RECEIVED. CLOSURE OCCURRED AND A REACTOR SCRAM RESULTED. DURING THE REACTOR SCRAM, ALL SAFETY SYSTEMS FUNCTIONED NORMALLY. THIS ACTUATION OF THE REACTOR PROTECTION SYSTEM WAS THE RESULT OF AN ERRONEOUS HIGH VIBRATION SIGNAL FROM A FAULTY SHAFT RIDER SENSOR CONNECTION. AS AN INTERIM MEASURE TO PREVENT SPONTANEOUS TRIPS OF THE MAIN TURBINE GENERATOR DUE TO FAULTY VIBRATION DETECTION EQUIPMENT, THE OPERATORS WERE DIRECTED TO TRIP THE MAIN TURBINE GENERATOR MANUALLY ON HIGH VIBRATION INDICATION. THE ALARM RESPONSE PROCEDURE FOR HIGH VIBRATION SIGNALS WAS REVISED TO PROVIDE CLEAR INSTRUCTION TO CONTROL ROOM PERSONNEL. A DESIGN CHANGE HAS BEEN IMPLEMENTED TO REQUIRE TWO HIGH VIBRATION SIGNALS TO TRIP THE UNIT. THIS CHANGE WAS IMPLEMENTED PRIOR TO PLANT RESTART ON OCTOBER 9, 1987.
341 | 3411987035 | 1987-07-31 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Fermi 2 | B | GE | SU | 3 | POWER LEVEL - 003%. ON JULY 31, 1987 AT 0220 HOURS, AN UNUSUAL EVENT WAS DECLARED DUE TO EXCESSIVE PRIMARY CONTAINMENT LEAKAGE THROUGH A CHECK VALVE, AND REACTOR SHUTDOWN WAS INITIATED. AS THE OPERATOR WAS DEPRESSURIZING THE REACTOR WHILE STILL AT POWER, AN INJECTION OF COLD FEEDWATER OCCURRED. THIS COLD FEEDWATER CAUSED AN INCREASE IN POSITIVE REACTIVITY. THE CHANGE IN REACTIVITY CAUSED AN INCREASE IN REACTOR POWER LEVEL WHICH RESULTED IN AN UPSCALE TRIP OF THE INTERMEDIATE RANGE MONITORS (IRMS). AS A RESULT, A REACTOR SCRAM OCCURRED AT 0311 HOURS. EXCESSIVE VALVE LEAKAGE WAS CAUSED BY RANDOM COMPONENT FAILURE. THE SUBSEQUENT SCRAM WAS DUE TO THE REACTOR POWER LEVEL INCREASE IN THE IRM RANGE DUE TO CHANGES IN FEEDWATER FLOW. THE CHECK VALVE WAS REPAIRED AND TESTED. THE OPERATING PROCEDURES WILL BE REVIEWED AND REVISED TO CLARIFY USE OF THE TURBINE BYPASS VALVES. A DISCUSSION OF THE LESSONS LEARNED ABOUT THE REACTOR POWER LEVEL SENSITIVITY TO CHANGES IN FEEDWATER FLOW WILL BE GIVEN TO THE OPERATORS. ADDITIONAL TRAINING ON DEPRESSURIZATION WITH THE BYPASS VALVES WILL BE GIVEN.
341 | 3411987056 | 1987-12-31 | QP5 | Excessive Feedwater Flow | [45 empty] | Fermi 2 | B | GE | PO | 75 | POWER LEVEL - 075%. ON DECEMBER 31, 1987 DURING THE INSTALLATION OF A TEMPORARY MONITOR AND PRINTER, AN INCREASING DEMAND SIGNAL WAS RECEIVED BY THE FEEDWATER CONTROL SYSTEM DUE TO THE ACCIDENTAL GROUNDING OF A CABLE. FEEDWATER FLOW INCREASED UNTIL HIGH REACTOR VESSEL WATER LEVEL CONDITION OCCURRED. A REACTOR SCRAM OCCURRED APPROXIMATELY 30 SECONDS LATER. IN THE PROCESS OF PLANT COOLDOWN, THE REACTOR WATER CLEANUP SYSTEM (RWCU) ISOLATED DUE TO A DIFFERENTIAL FLOW CONDITION. THE PERSONNEL INVOLVED HAD ALTERED A PLANT INPUT TO THE UNIT WITHOUT PROPERLY ASSESSING THE CONSEQUENCES. APPROPRIATE LEVELS OF DISCIPLINE WERE ADMINISTERED. THE TEMPORARY MODIFICATION PROCEDURE IS BEING REVISED TO ADD ADDITIONAL INSTALLATION GUIDANCE. THE POSITION INDICATION AND RELAYS FOR THE VENT VALVE WHICH CONTRIBUTED TO THE RWCU ISOLATION WAS REPLACED. A DESIGN CHANGE WHICH WILL PREVENT RECURRENCE OF THE ISOLATION IS SCHEDULED TO BE IMPLEMENTED DURING THE LOCAL LEAK RATE TESTING OUTAGE THIS SPRING.
341 | 3411988004 | 1988-01-10 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Fermi 2 | B | GE | PO | 49 | On January 10, 1988, the North Reactor Feed Pump speed control power supply failed. The pump responded to the loss of control signal. A low reactor vessel water level resulted which caused a reactor scram. High Pressure Coolant Injection and Reactor Core Isolation Cooling Systems actuated along with the appropriate isolations. <br /><br /> The cause for the Feedwater transient was that the overvoltage trip for the power supply had drifted into the normal operating range. The power supply was replaced and the overvoltage protection was set to the maximum value. <br /><br />During restoration of the RWCU System, a Technical Specification requirement was exceeded. The Technical Specification Action Statement for defeating the high temperature isolation function of the RWCU isolation valves does not allow sufficient time to restart the RWCU System during high operator activity periods. A Technical Specification change will be submitted to delete the requirement for RWCU isolations on high non-regenerative heat exchanger outlet temperature indication.
341 | 3411988019 | 1988-05-07 | QR3 | Reactivity Control Imbalance | [45 empty] | Fermi 2 | B | GE | SU | 3 | On May 7, 1988 at 0138 hours, offsite power to Division 1 was interrupted. Control Rod Drive pump A tripped on loss of power. Since reactor power was less than 900 psig, a manual scram was initiated by placing the mode switch in the shutdown position as required by Technical Specifications. All actuations and isolation occurred as expected. <br /><br /> Investigation determined a raccoon climbing the System Service Transformer #1 had caused a ground fault on the "Z" phase. The transformer was inspected, cleaned and repaired prior to being returned to service. Inspection of the mat around the transformer revealed that the grade had settled below the fence allowing a path for the raccoon to enter. Gravel was brought in to bring the grade above the fence line.
341 | 3411988020 | 1988-05-08 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Fermi 2 | B | GE | SU | 6 | A Technical Specification Surveillance Requirement Procedure 24.202.04 "HPCI System Automatic Actuation/Suction Valve Auto Transfer" was required to be performed as part of the normal required surveillance frequency. During the performance of the surveillance test, feedwater flow was diverted to the condensate storage tank. Operator actions taken to compensate for a low reactor water level alarm resulted in a reactor intermediate range monitor high flux reactor scram. During the reactor scram all plant systems functioned per design. <br /><br /> A technical review of the surveillance test determined that the surveillance procedure was intended to be performed in the cold shutdown or refueling conditions. The procedure did not contain the appropriate precautions to prohibit operations personnel from performing the surveillance test in other plant modes of operation. Procedure 24.202.04 was revised to define when the surveillance test will be performed.
341 | 3411988021 | 1988-05-10 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Fermi 2 | B | GE | PO | 17 | On May 10, 1988 the plant staff was conducting electrical overspeed surveillance testing on the main turbine generator while the unit was in power operation. During the test, both main steam bypass valves closed. At 2251 hours, a reactor protection system high pressure scram occurred. <br /><br />The event was caused by a faulty relay which generated a deviation between the three channel signals acting on the bypass valve control modules. <br /><br />The relay was replaced. A modification will be implemented to alter the comparator trip circuits to actuate at a prescribed level of deviation between input signals. The modification will be completed prior to the end of the first refueling outage.
341 | 3411988030 | 1988-08-13 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 78 | On August 13, 1988 at 0722 hours a Main Turbine Generator (MTG) trip was automatically initiated because of high main turbine bearing vibration. As designed, the turbine trip from high power initiated an automatic reactor scram due to fast closure of the MTG stop and control valves. The scram initiated a reactor water level 3 actuation and a level 8 trip. Control room personnel responded to the turbine trip and reactor scram and secured the plant in a stable condition. During this event all safety systems functioned normally. <br /><br />Subsequent to the plant shutdown the General Service Water flow control valve to the Main Turbine Generator (MTG) lube oil coolers was found to have failed open. The failed open valve provided additional cooling to the lube oil coolers. This additional oil cooling caused oil whirl to initiate which increased the turbine vibration above the bearing trip circuit setpoints. <br /><br />The number 8 bearing vibration circuit was recalibrated. The failed temperature control valve for the MTG lube oil coolers has been repaired. The possibility of increasing the low turbine lube oil temperature alarm setpoint will be investigated.
341 | 3411989006 | 1989-02-26 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 100 | On February 26, 1989, a turbine trip and reactor scram occurred during operation of a reset pushbutton for the main turbine mechanical overspeed test. The operator had not received the expected indication at one point in the test and wanted to verify that the logic was reset. When the reset pushbutton was depressed a second time, a turbine trip occurred followed by a reactor scrams. <br /><br /> The cause of the turbine trip was a poor design of the main turbine overspeed trip linkage, as recognized by the manufacturer. Additionally, the lack of knowledge of the consequences of using this reset pushbutton out of sequence contributed to the event. <br /><br /> The training department has incorporated a discussion of the linkage operation into the turbine controls lecture. The operator has been counselled. Also, a critique of this event is being given in licensed operator training. An evaluation of the necessity for a design change to improve the human factors considerations of this reset will be performed.
341 | 3411989007 | 1989-03-07 | QR6 | Manual Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 100 | On March 7, 1989, the operators observed an increasing trend in the vibration of the number 8 bearing on the main turbine generator. Attempts to reduce the vibration by reducing the turbine load were unsuccessful. Therefore, the reactor was scrammed and the turbine shutdown in accordance with the site procedure. All systems responded per their design during the scram.<br /><br /> The turbine was balanced during the subsequent outage. During the first refueling outage, parts of the turbine will be disassembled and/or inspected.
341 | 3411989036 | 1989-12-18 | QL5 | Partial Closure of MSIVs | [45 empty] | Fermi 2 | B | GE | PO | 20 | On December 18, 1989, Instrument & Controls (I&C) personnel signed on surveillance 44.020.151, "NSSSS - Reactor Water Cleanup Differential Flow Functional Test". An I&C technician stationed in the Control Room requested the Control Room Operator to reset Nuclear Steam Supply Shutoff System (NSSSS) Division I and II Main Steam Isolation Valve (MSIV) logic, as directed by the procedure.<br /><br /> At 2230 hours, the Control Room Operator inadvertently depressed the closed push buttons on the A, B and C inboard MSIV's and a reactor scram resulted. The immediate actions of the Reactor Scram Abnormal Operating Procedure (20.000.21) were performed and the plant was in a stable condition at 2240 hours. <br /><br /> The cause of this event was Operator error. Nuclear Training is reviewing resetting the Nuclear Steam Supply System isolation logic with control room personnel. The Operator involved was removed from licensed duties and participated in an accelerated requalification training program. A critique of this event will be issued as required reading.
341 | 3411989038 | 1989-12-23 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Fermi 2 | B | GE | PO | 42 | On December 23, 1989, smoke was discovered in the vicinity of the high pressure turbine. The fire brigade was dispatched, and reactor was manually scrammed. The brigade discovered the lagging insulation pads were burning and extinguished the fire. <br /><br /> Investigation has determined that the insulation pads were soaked with oil and the turbine casing had heated up to the oil's flash point. An oil spill had occurred several weeks earlier during a flush of the turbine lube oil system during turbine reassembly. Apparently, the spill was not adequately cleaned up.<br /><br /> The damaged insulation pads were replaced and an inspection for other damage performed. No other damage was noted. An accountability meeting was held between management and the personnel involved in the maintenance on the turbine. Procedures have been revised to assure that oil leaks are detected/cleaned up and to prescribe appropriate inspections. This incident coupled with other incidents which occurred during startup from the First Refueling Outage led to Fermi 2 developing an Accountability Action Plan. The Accountability Action Plan was implemented by site organizations and evaluated by Quality Assurance as committed to in Detroit Edison Letter NRC-89-0300, dated December 26, 1989.
341 | 3411990003 | 1990-04-10 | QC4 | Loss of ac Instrumentation and Control Bus. |  |  |  | X | [6 empty] | X | [8 empty] | X | [19 empty] | X | [5 empty] | Fermi 2 | B | GE | PO | 100 | On April 10, 1990 at 0156 hours, the Reactor Protection System (RPS) motor-generator (MG) set "A" tripped due to a coil failure in the K1 relay. The appropriate isolations and actuations occurred as a result of the MG set trip. While the operators were verifying plant response and preparing to restore power, the inboard Main Steam Isolation Valves (MSIVs) closed. This resulted in a reactor scram and subsequent turbine trip. <br /><br /> The RPS MG set relay failed when its coil termination failed. Closure of the MSIVs is attributed to loss of pneumatic pressure due to pneumatic supply isolations. Leakage within the isolated system was traced to two sources: (1) leakage through the Traversing In-core Probe (TIP) indexer boxes and (2) additional leakage through the TIP purge system which had been added to the drywell pneumatic system loads during the first refueling outage. <br /><br /> As corrective action, the failed relay and the identical relay on MG set "B" were replaced. The failed relay was further analyzed to confirm its failure mechanism. Five of the six relief valves on the TIP purge system were gagged. Also the pressure regulator of the purge system was set lower to allow more than fifteen minutes for operators to restore the pneumatic supply following its isolation.
341 | 3411990011 | 1990-10-06 | QR8 | Spurious Reactor Trip | [45 empty] | Fermi 2 | B | GE | SU | 1 | On October 6, 1990, Fermi 2 was in startup and holding while plant personnel were investigating Reactor Water Level indication discrepancies. The discrepancy was noted during a channel check prior to heat-up. Instrumentation & Controls Technicians conducting troubleshooting on the level difference noticed at the remote location that the "B" reference leg instruments indicated approximately 20 inches lower than the equivalent RPS instrumentation associated with "A" reference leg at approximately 1750 hours. The I&C technicians were in the process of notifying the Control Room when at 1754 hours, a reactor scram on Low Reactor Water Level occurred. <br /><br /> The cause of this event was attributed to air voids in the "A" reference leg. <br /><br /> Initial troubleshooting was performed as close to pre-scram conditions as possible and, based on the results, the plant was placed in cold shutdown and the Drywell was deinerted for further investigation following the reactor scram. The sources of level indication difference were investigated and corrective actions were formulated. The corrective actions, the root cause evaluation, and the startup plan were reviewed by the On-Site Safety Review Organization prior to startup.
341 | 3411991004 | 1991-03-12 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Fermi 2 | B | GE | PO | 65 | On March 12, 1991, at 0509 hours, the Off-Gas system sand filter differential pressure high alarm annunciated. At 0615 hours, operations personnel found a broken Moisture Separator Reheater (MSR) relief valve manifold drain line to the condenser, common to both the east and west MSR relief valve manifolds. The drain line was failed at the heat affected zone of a weld. There is no isolation valve between the location of the break and the condenser. At 0623 hours, the reactor was manually scrammed due to an impending loss of condenser vacuum. At 0636 hours, reactor pressure and level stabilized and the scram was reset. <br /><br /> The piping system failure occurred at a socket-welded elbow and initiated at the toe of the weld in the heat affected zone. Two pipe supports, one on each side of the failure location, had broken U-bolts. Failure of the pipe support U-bolts allowed unacceptable cyclic pipe displacements which led to the pipe failure. The piping system and supports were repaired and additional temporary supports were added to the piping system to reduce line movement.
341 | 3411991015 | 1991-06-27 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Fermi 2 | B | GE | PO | 100 | At 2115 hours on June 27, 1991, a pipe was discovered glowing red on one of two main unit transformers. The glowing pipe was located at the point of contact between the low voltage side isophase bus housing and an oil line which is connected to a pipe header from the conservator tanks (oil reservoirs). A controlled plant shutdown was ordered. Self-extinguishing flames were subsequently observed and an immediate plant shutdown was ordered. The main generator breakers were manually opened resulting in a reactor scram due to a turbine control valve fast closure. <br /><br /> An investigation determined the overheating was due to a vent pipe cap in direct contact with the low voltage side isophase bus housing. The root cause has several contributing factors. The primary one is the arrangement of the vent cap port relative to the isophase bus housing and another is the use of a larger size vent cap than needed which reduced the clearance between the vent cap and the housing. <br /><br /> A small part of the isophase bus housing was ground away to re-establish the physical separation between the vent pipe cap and the housing. An inspection of other pipe caps was conducted. The Preventive Maintenance events for both transformers will be revised to include a check of the physical separation between the pipe caps and the isophase bus housing. Required reading will be conducted for the off-site utility personnel and all involved supervision.
341 | 3411992002 | 1992-03-16 | QR6 | Manual Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 100 | At 1709 hours on March 16, 1992, during the performance of a Technical Specification Channel Functional Surveillance Test on Division 2 Reactor Water Levels 1, 2 and 8, an inadvertent actuation of the Low Pressure Coolant Injection (LPCI) system Loop Select Logic (LSL) occurred. The LSL signal caused the Reactor Recirculation Pump (RRP) "B" discharge valve to close. The resulting core flow decrease led to entry into Region A of the power/flow map. No Thermal Hydraulic instability occurred. By procedure and the Technical Specification Action Statement, the reactor operator then manually tripped the reactor by placing the Mode Switch in the "Shutdown" position. The plant responded as expected to the resultant manual scram. <br /><br /> The LSL signal actuation occurred due to a short circuit condition across the K79 relay contacts for the LPCI LSL. This occurred when a Digital Multimeter (DMM) was connected to take the voltage readings required of the surveillance test. The input impedance on the meter will go to a relatively low value with the function switch slightly clockwise of the "Volts DC" position. The DMM in question, and all DMMs of the same model number and series have been taken out of service at the site.
341 | 3411992012 | 1992-11-18 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Fermi 2 | B | GE | PO | 98 | On November 18, 1992, in accordance with System Operating Procedure 23-103, 'Condensate Polishing Demineralizer System', a Nuclear Power Plant Operator (NPPO) backwashed condensate polishing demineralizer 'H' and then as directed by procedure flushed the demineralizer influent line. The procedure required that the NPPO open valve N20-F409H, 'Demin H Influent Bypass Valve', a one inch valve, instead the NPPO inadvertently opened valve N20-F004H, 'Demin H Influent Isolation Valve', a ten inch valve. The Heater Feed Pumps tripped on low suction pressure and subsequently the two Reactor Feed Pumps tripped. The Reactor Pressure Vessel water level decreased on the loss of feedwater. At 2029 hours, the Nuclear Supervising Operator initiated a manual scram by placing the Mode Switch to Shutdown. <br /><br /> The root cause of this event was determined to be personnel error by the NPPO. The NPPO inadvertently opened valve N20-F004H due to inattention to detail. The NPPO did not use proper Self Checking before opening the valve. An Accountability Meeting was held with the individual involved and plant management. A Human Performance Enhancement System report was completed. This event will be discussed in Operations Requalification training.
341 | 3411993004 | 1993-02-19 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | Fermi 2 | B | GE | PO | 98 | On February 19, 1993, Circulating Water Pump number 3 was removed from service for performance of Preventive Maintenance PM!. Electrical Maintenance personnel were to perform procedure 35.318.017, "Inspection and Testing of Multi-Contact Auxiliary Relays". An electrician located and connected his test equipment to the incorrect relay which resulted in the loss of 4160 VAC bus 69J. Circulating Water Pumps number 1 tripped and 2 de-energized, and their discharge valves de-energized in the open position. Circulating Water Pumps 4 and 5 continued to operate. However, their discharge was partially re-directed through Circulating Water Pumps 1 and 2 in the opposite direction. Because of inadequate cooling water, Condenser pressure began to increase. The Main Turbine tripped on high Condenser pressure. At 2102 hours, an automatic Reactor Protection System shutdown was initiated by the Main Turbine control valve fast closure trip signal. The Reactor shutdown and all safety systems responded properly. <br /><br /> The root cause of this event was determined to be personnel error. The electrician did not verify that he was on the proper relay before connecting and energizing his test equipment. The General Supervisor of electrical maintenance discussed the importance of self checking and verification with electrical maintenance personnel. An accountability meeting was held. Training for electricians on self checking and trip relays will be reviewed.
341 | 3411993007 | 1993-04-20 | QP5 | Excessive Feedwater Flow | [45 empty] | Fermi 2 | B | GE | SU | 3 | April 20, 1993, with the reactor at 510 psig during startup, a control room operator noticed that the main steam manifold pressure control system was unexpectedly switching between the "A" and "B" regulators when the Electric Governor Trouble Alarm actuated and the turbine bypass valves opened approximately 40 percent. Reactor pressure began to decrease and reactor water level increased due to increased void fraction resulting from the increased steam flow. The increased void fraction also led to a decrease in reactor power. When control room operators began to gradually close the bypass valves, reactor water level decreased. As water level decreased through the normal operating band, feedwater flow automatically increased. The addition of cold feedwater caused reactor power to increase until the reactor automatically tripped on Intermediate Range Monitor upscale. All safety systems responded properly. <br /><br /> This event occurred because leakage past a threaded adapter allowed steam and water to leak into an instrument cabinet which contained the pressure transmitters used to control main steam manifold pressure, causing failure of these transmitters. The cause of the event was personnel error in that a threaded adapter used to install temporary test equipment for startup monitoring did not match the fitting into which it was threaded. Training will be conducted on this event to reinforce the need for control of contractor activities.
341 | 3411993010 | 1993-08-13 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 93 | On August 13, 1993, while performing routine reactor building rounds, a Nuclear Power Plant Operator (NPPO) removed some tape from the valve handle on a manifold to instrument B21-R004B "Reactor Vessel Division 2 Pressure Indicator". While removing the tape residue, the NPPO noticed a pressure spike on instrument B21-R004B and heard the scram pilot valves vent. He called the main control room and was informed that an automatic reactor shutdown had occurred. <br /><br /> An investigation determined the cause of the event to be personnel error. The NPPO inadvertently unseated an instrument calibration/vent isolation valve while removing the tape residue from the valve handle. This induced a pressure transient into an instrument header shared by other instruments. A false high reactor water level signal caused the main turbine generator to trip off. Closure of the main turbine generator control valves initiated a reactor scram. <br /><br /> A lessons learned meeting was conducted. Signs have been posted on instrument racks H21-P004/P005 warning of the sensitivity of these instruments. Lessons learned will be incorporated into the licensed and non-licensed operator training program.
341 | 3411993013 | 1993-09-17 | QK4 | Steam or Feed Leakage | [45 empty] | Fermi 2 | B | GE | PO | 17 | On September 17, 1993 an inadvertent breach of the Reactor Feedwater System occurred during a planned reactor shutdown with the reactor at 17% power. Maintenance personnel had begun work on the No. 5 North Feedwater Heater Level Control valve, N22-F415A, located on the discharge side of the heater drain pump prior to the establishment of the proper plant conditions. As a result, control room operators manually scrammed the reactor in order to shut down the feedwater system and isolate the system leak. All plant systems performed as expected and all leakage was contained within the plant. <br /><br /> The cause of the event was personnel error in failing to follow established work control practices. Poor communications, weaknesses in the implementation of the Work Control Process, and modification to the planned schedule of work contributed to this event. Corrective actions will include discipline administered in accordance with plant policy, counseling of those involved and training of appropriate plant personnel.
341 | 3411993014 | 1993-12-25 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Fermi 2 | B | GE | PO | 93 | On December 25, 1993 at 1315 hours an automatic reactor shutdown occurred when the main turbine tripped off line. The turbine generator tripped when the mechanical overspeed device was activated. This was due to high vibration levels and was not due to an actual overspeed condition. The turbine generator unit and associated support systems sustained significant damage. All safety systems and isolations performed as designed during the event. An Unusual Event was declared at 1352 hours. This was upgraded to an Alert at 1357 hours. A fire at the main generator brush rig area was extinguished by the plant fire brigade using hand held extinguishers. <br /><br /> The cause of the high turbine vibration was due to the failure of the number 9 blade, on the 8th stage, turbine end of the low pressure section number 3. The root cause of this failure continues to be under investigation. <br /><br /> Turbine/generator repairs will be determined based on the results of the investigation. Other corrective actions needed to return the plant to power operation are being formulated and implemented.
341 | 3411995005 | 1995-04-25 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Fermi 2 | B | GE | PO | 87 | On April 25, 1995, at 1159 EDT, with the reactor at 87 percent power, the reactor automatically tripped on average power range monitor (APRM) upscale condition. All safety systems responded properly. The main generator did not automatically trip off-line. Manual trip actuation of the generator output breakers was required. <br /><br /> Based on post-transient recorder data, it was determined that a reactor pressure regulator failure caused the turbine control valves (TCVs) and turbine bypass valves (TBVs) to open, decreasing reactor pressure and increasing moderator void formation. Approximately four seconds later, the pressure regulator returned to normal control, the TBVs closed, and the TCVs returned to normal operation. in high neutron flux due to moderator void collapse. <br /><br /> Replacement of circuit boards, replacement of the pressure regulator potentiometers, the additional testing to locate potential sources of voltage signal introduction or current loading, and removal of the pressure regulator monitoring system interconnection to the pressure regulator control circuitry provide a high level of confidence that the cause of the event has been corrected.<br /><br /> Additional investigation will be performed to attempt to determine the root cause at the component level. The scram response abnormal operating procedure has been revised to relocate verification of the output breakers being tripped from the subsequent scram section to the immediate actions section.
341 | 3411995006 | 1995-06-02 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 95 | During the performance of test procedure 27.112.03, 'Turbine Generator Mechanical Overspeed On Load Test' on June 9, 1995 the main turbine tripped, causing a reactor scram at 1636 hours. During testing of the number 1 trip ring, the number 2 trip mechanism unexpectedly actuated. This caused a turbine trip causing a reactor scram on turbine control valve fast closure. All control rods fully inserted. The subsequent reactor water level 3 actuated isolation logic for selected primary containment isolation valves as expected. All safety related equipment performed its intended safety function. At 1648 hours, reactor water level was restored above level 3, and the plant was stabilized. <br /><br /> The main turbine tripped because the test on the number 1 trip ring sufficiently vibrated the number 2 trip lever when the 'On Load Overspeed Test' pushbutton was depressed causing the number 2 trip mechanism to actuate. This occurred because the number 2 trip lever had not fully latched into its reset state during the performance of the actual overspeed test 27.112.01 on May 4, 1995. Procedure 27.112.01 was revised to incorporate holding the reset overspeed pushbutton depressed for at least 15 seconds.
341 | 3411996024 | 1996-12-28 | QR8 | Spurious Reactor Trip | [13 empty] | X | [30 empty] | X | Fermi 2 | B | GE | SU | 18 | On December 28, 1996, at 1314 hours, the Division 1 reference leg backfill system was being placed in service. As the isolation valve from the backfill system to the reference leg was opened, a rapid pressure spike occurred in the reactor pressure vessel (RPV) water level instrument reference leg which induced several actuations from the false water level signals. A High Level 8 actuation on Division 1 level instrumentation occurred that tripped the operating reactor feed pump. This was immediately followed by a RPV water Low Level 2 and Low Level 3 actuations. The reactor scrammed properly on the false Level 3 signal and all rods fully inserted. Due to the short duration of the Division 1 reference leg level spike, not all Level 2 trip channels actuated. These are expected responses due to the short signal duration. <br /><br /> The causes of this event are design deficiencies and procedural inadequacies. The design of the backfill system did not facilitate complete venting of entrained air in a two foot section of Division 1 tubing. The procedure used to place the backfill system in service did not adequately address the potential for a pressure spike when placing the system back in service after filling and venting. If the backfill system is not adequately repressurized following venting, a transient may occur in the common reference leg while placing the system in service.<br /><br /> Corrective actions included revising the procedure for placing the backfill system in service to ensure the system is completely filled and vented and that the differential pressure between the backfill system and the reference leg is minimized prior to placing it in service. On Division 1, a design modification was developed and implemented to relocate a test valve used for system venting closer to the backfill isolation valve. The test valves for both divisions were elevated to facilitate proper venting of the lines.
341 | 3411998001 | 1998-02-01 | QR8 | Spurious Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 96 | On February 1, 1998, the plant experienced a Reactor Protection System (RPS) actuation due to a Turbine Control Valve Fast Closure and the reactor scrammed at 0918 hours. The Turbine Control Valve Fast Closure was initiated when generator output breakers CM and CF opened resulting in a turbine load reject. The turbine load reject was initiated when the outside rounds Nuclear Power Plant Operator (NPPO) actuated the test reset switch for the Brownstown 3 "B" relaying panel in the 345 kV relay house. In addition to circuit breakers CM and CF, circuit breaker CT opened and Brownstown - Fermi 3 Line de-energized. The 345 kV buses remained energized through the DM and DF breakers, the redundant off-site power source. All control rods fully inserted into the core. Reactor Pressure Vessel (RPV) level decreased below the Level 3 setpoint resulting in a Nuclear Steam Supply Shutoff System (NSSSS) Group 4, 13, and 15 isolation signals. Two degraded conditions existed on the Brownstown 3 "B" relay scheme. A circuit card was installed in the 50BF relay for the CM breaker in January 1997. The card that was installed in the relay had a latching resistor that should have been removed prior to installation. Secondly, an internal failure of the 95 (SRU) relay created and passed a voltage spike of sufficient amplitude and duration to pick up the breaker failure relay. Corrective actions included replacement of the 50BF (SBFU) relay to eliminate the undesirable latching circuit and replacement of the 95 (SRU) relay to eliminate the stray high output signal.
341 | 3411998004 | 1998-07-19 | QR6 | Manual Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 62 | On July 19, 1998 at approximately 1000 hours, a reactor power reduction was commenced in preparation for a control rod pattern adjustment. Power was reduced to approximately 64% using the reactor recirculation pumps and the control rods. With the reactor at approximately 64% power, the operator noted that reactor power began fluctuating between 50% and 75%. Main Steam flow, flow to both Main Steam Reheaters, and reactor pressure, were also fluctuating. The control room operator immediately placed the reactor mode switch in the Shutdown position. All control rods were fully inserted and no Safety Relief Valves lifted. The Emergency Operating Procedures (EOPs) were entered based on reactor water level decreasing to a level 3 condition, an expected condition following the scram. All safety equipment functioned properly in response to the scram. Plant conditions were such that no Emergency Core Cooling Systems were required to initiate. Reactor vessel water level was restored and the EOPs were then exited. Power level at the time of the scram was approximately 62%. The most probable cause of the reactor power fluctuations was determined to be unstable flow through the No. 4 High Pressure Turbine Control Valve (HPTCV). Operation for the remainder of the cycle with the No. 4 HPTCV closed was evaluated and it was determined that the plant could be operated safely in this condition with the resultant reduction in power required to accommodate it.
341 | 3411998005 | 1998-09-04 | QR6 | Manual Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 70 | On September 4, 1998 at approximately 1700 hours, a reactor power reduction was commenced in preparation for the Sixth Refueling Outage (RFO6). Power was reduced to approximately 70% using the reactor recirculation pumps. With the reactor at approximately 70% power, operators observed that reactor power began fluctuating between 61% and 79%. Concurrent fluctuations in reactor water level, main steam line flows, Moisture Separator Reheater (MSR) steam flows, and turbine valve position were also noted. The reactor mode switch was immediately placed in the Shutdown position, thereby initiating a manual reactor scram. AR control rods fully inserted and no Safety Relief Valves lifted. The Emergency Operating Procedures (EOPs) were entered based on reactor water level decreasing to a Level 3 condition, an expected response following the scram. All safety equipment functioned properly in response to the scram. Plant conditions were such that no Emergency Core Cooling Systems (ECCS) were required to initiate. Reactor vessel water level was restored and the EOPs were then exited. The cause of the reactor power fluctuations was determined to be spindle/tongue degradation of the No. 3 High Pressure Turbine Control Valve (HPTCV). A complete inspection of the No. 3 HPTCV and No. 4 HPTCV was completed during RFO6. In addition, the spindle/tongue inspections of the No. 1 HPTCV and No. 2HPTCV, Turbine Stop Valves (TSVs), and the Turbine Bypass Valves (TBPVs) were completed in RFO6.
341 | 3411999002 | 1999-05-18 | QR6 | Manual Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 97 | On May 18, 1999, plant personnel were performing routine field brush maintenance for the Reactor Recirculation Pump (RRP) "A" Motor Generator (MG) Set. The RRP tripped when personnel were changing the MG set exciter brush. The brush had shorted on the opposite polarity bus bar. Core flow decreased which placed the plant in the "Scram Region" of the Power to Flow Map. Operators inserted a manual Scram at 1709 hours. Plant systems responded as designed. All Control Rods fully inserted. Reactor Water Level 3 Primary Containment Isolation Valves [ISV] for Groups 4 (Shutdown Cooling/Head Spray), 13 (Drywell Sumps), and 15 (Traversing In-Core Probe) isolated as designed. Reactor water level was restored to its normal band, and Emergency Core Cooling Systems did not actuate. The brush change out was completed while the plant was shutdown. Previous actions taken to minimize risk for a RRP trip during MG set brush replacement were not effective. An action was included in the corrective action program to evaluate options for improving the ability for successful changing of MG set brushes online.
341 | 3412000004 | 2000-04-01 | QR3 | Reactivity Control Imbalance | [45 empty] | Fermi 2 | B | GE | PO | 24 | On April 1, 2000 at 1200 hours, a planned shutdown began for the seventh refueling outage. At 1815 hours, operators lowered the Reactor Recirculation Pump (RRP) speed to 30 percent. At that time, the "A" RRP speed oscillated between approximately 24 and 30 percent speed. This type of RRP speed oscillation is due to the hydraulic characteristics of RRP Motor Generator [MG] set fluid coupling and is expected near the 24 to 28 percent RRP speed range. The "A" MG fluid coupler scoop tube was locked in an attempt to maintain "A" RRP speed constant. The scoop tube apparently did not lock and the "A" RRP speed increased rapidly. The "A" RRP was immediately tripped as required by plant procedures. In single loop operation, procedures require the remaining ("B") RRP speed be maintained at greater than 50 percent. This could not be achieved because at the low power condition that existed at the time, RRP speed is limited to 31.5 percent speed. Lacking specific procedural guidance for the conditions that existed, reactor operators decided to manually trip the reactor. At 1915 hours, with reactor power at approximately 24 percent the mode switch was placed in shutdown, initiating a manual scram. Troubleshooting of the scoop tube and its controls could not duplicate or determine the cause for the scoop tube not locking. Additional post maintenance testing is planned during restart from the refueling outage. Corrective actions include development of appropriate procedural guidance for single loop operation at low power conditions.
341 | 3412001004 | 2001-12-06 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 100 | On December 6, 2001, at 0350 hours operators inserted a manual scram from 100 percent power due to a leak on the Stator Water Cooling system upper heat exchanger. The leak occurred when a vent line separated from the heat exchanger during removal of the pipe cap from the vent line. All systems responded as expected and all control rods fully inserted. Reactor level was recovered with the Feedwater/Condensate System. No Emergency Core Cooling Systems initiated and no Safety Relief Valves lifted. The cause of the vent line failure was inadequate problem documentation and resolution that dates back to 1996. The original vent line design was a contributing factor. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in manual or automatic actuation of any systems listed in paragraph (a)(2)(iv)(B), (i.e., actuation of the Reactor Protection System including reactor scram or reactor trip). The original vendor supplied heat exchanger vent lines were strengthened and an unsupported length was reduced. Schedule 80 steel was used to replace the schedule 40 steel and the connection to the heat exchangers was welded vice threaded.
341 | 3412002004 | 2002-10-02 | QL7 | Degraded condenser vacuum | [45 empty] | Fermi 2 | B | GE | PO | 100 | On October 2, 2002, at 1453 hours, the reactor scrammed from 100 percent power. Condenser pressure increased when Circulating Water Pump (CWP) 2, one of four running CWPs, failed. Condenser pressure exceeded the main turbine trip setpoint. The main turbine tripped, resulting in a reactor scram. Prior to the scram at 1452 hours the Circulating Water Header Low Pressure annunciator was received. The Condenser Pressure High annunciator was received and control room operators (licensed, utility) entered the Abnormal Operating Procedure for Loss of Condenser Vacuum. The main turbine automatically tripped causing a reactor scram on main turbine control valve fast closure. All safety systems responded as expected. All rods fully inserted into the core. Reactor level decreased below Level 3, resulting in expected isolation signals. After the reactor scram, condenser vacuum recovered. Reactor level was recovered with the Feedwater/Condensate System. No Emergency Core Cooling Systems initiated and no Safety Relief Valves lifted. The cause of the event was a failure of CWP 2. This event is being reported in accordance with 10 CFR 50.73 (a)(2)(iv)(A), as an event that resulted in manual or automatic actuation of any systems listed in paragraph (a)(2)(iv)(B), i.e., actuation of the Reactor Protection System including reactor scram or reactor trip. The cause of the CWP failure was fatigue failure of the diffuser casing to column bolts due to insufficient or loss of pre-load.
341 | 3412002006 | 2002-12-29 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Fermi 2 | B | GE | PO | 100 | On December 28, 2002, at 0440 hours, a low voltage condition was discovered on Modular Power Unit. Investigation into this condition concluded that the 120 VAC voltage (MPU) 3, Distribution Cabinet 2. Investigation into this condition concluded that the 120 VAC voltage regulator associated with MPU 3 had degraded such that the output voltage was93 VAC. MPU 3 is a non-Class 1E 120 VAC Instrumentation and Control Power (ICP) System that provides related Balance of Plant (BOP) instrumentation and control loads including several control circuits, indicators and. It was concluded that a loss of the feedwater pumps and the circulating recorders in the control roomwater pumps could occur if operation were allowed to continue, or if on line repair was attempted. Reactor power was reduced to approximately 73 percent using recirculation flow. Further power reduction using control rods was then attempted when it was found that control rods could not be moved using the Reactor Manual Control System (RMCS). The inability to manually move rods during the power reduction was attributed to the degraded voltage on MPU 3. The normal power reduction was stopped and the reactor was manually scrammed on December 29, 2002, at 0010 hours. All other systems responded as expected. Following shutdown, the voltage regulator in MPU 3 was bypassed under a temporary modification to allow an upstream voltage regulator associated with its normal power supply, Bus 72 F, to control the MPU 3 voltage.
341 | 3412003002 | 2003-08-14 | QR5 | Turbine Trip |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | Fermi 2 | B | GE | PO | 100 | On August 14, 2003, at approximately 1610 hours, the Reactor Protection System initiated an automatic reactor scram from 100% power as a result of a Turbine Control Valve (TCV) fast closure. The TCV closure was caused by a turbine trip signal initiated by the main turbine-generator protective control system upon sensing electrical grid voltage fluctuations. A Loss of Offsite Power occurred as a result of the regional electric grid disturbance that affected several eastern and central states and portions of Canada and that led to blackout conditions in a large portion of the United States. All safety related systems operated as expected in response to this event. All control rods fully inserted into the reactor core. Reactor Pressure Vessel (RPV) water level decreased and the Reactor Core Isolation Cooling system was manually started to restore RPV level; however, the High Pressure Coolant Injection system automatically started when RPV water level reached the setpoint for Level 2. Primary containment penetration isolations associated with RPV Level 3 and 2 setpoints occurred as expected. All Main Steam Isolation Valves closed and all four Emergency Diesel Generators started and energized their pertinent emergency loads. Nine Safety Relief Valves lifted and reseated. Combustion Turbine Generator (CTG) 11-1 did not initially start in response to this event. Offsite power was restored on August 15, 2003, and the plant was restarted on August 18, 2003.
341 | 3412004002 | 2004-09-03 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 100 | On September 3, 2004, at 2345 hours EDT, the reactor scrammed from 100% power as a result of the actuation of an Automatic Voltage Regulator (AVR) trip relay. The AVR experienced an interruption of the communications link between the digital AVR and the power converter thyristors of the generator exciter. The AVR trip resulted in a main generator trip with subsequent main turbine trip and reactor scram. The reactor protection system (RPS) performed as expected, and all rods were fully inserted into the core. Reactor water level reached a low of 137 inches above top of active fuel and recovered to normal automatically without operator intervention. Subsequent to the event, the main steam isolation valves (MSIVs) remained open and reactor water level was maintained in the normal band of 173 to 214 inches. Reactor water was supplied by the condensate and reactor feedwater systems, and the resultant reactor steam was sent to the condenser via the turbine bypass lines. Pressure control was maintained by the turbine bypass valves. Reactor dome pressure peaked at about 1090 psig. With reactor pressure maintained below the Safety Relief Valve (SRV) setpoints, none of the SRVs lifted. Reactor water Level 3 isolations occurred as expected. These included isolation Group 4 (Residual Heat Removal Shutdown Cooling and Head Spray), Group 13 (Drywell Sumps), and Group 15 (Traversing In-core Probe System) isolations. Failed AVR components were repaired or replaced, and the plant was restarted on September 5, 2004.
341 | 3412004004 | 2004-12-04 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 60 | On December 4, 2004, at 0417 hours EST, during startup from the tenth refueling outage, the reactor scrammed from 60% power as a result of the actuation of an Automatic Voltage Regulator (AVR) trip relay. The AVR experienced an interruption of the communications link between the digital AVR and the power converter thyristors of the generator exciter. The AVR trip resulted in a main generator trip with subsequent main turbine trip and reactor scram. The reactor protection system (RPS) performed as expected, and all rods were fully inserted into the core. Reactor water level reached a low of 136 inches above top of active fuel and recovered to normal automatically without operator intervention. Subsequent to the event, the main steam isolation valves (MSIVs) remained open and reactor water level was maintained in the normal band of 173 to 214 inches. Reactor water was supplied by the condensate and reactor feed water systems, and the resultant reactor steam was sent to the condenser via the turbine bypass lines. Pressure control was maintained by the turbine bypass valves. Reactor dome pressure peaked at about 1010 psig. With reactor pressure maintained below the Safety Relief Valve (SRV) setpoints, none of the SRVs lifted. Reactor water Level 3 isolations occurred as expected. These included isolation Group 4 (Residual Heat Removal Shutdown Cooling and Head Spray), Group 13 (Drywell Sumps), and Group 15 (Traversing In-core Probe System) isolations. The plant was restarted on December 5, 2004. Required circuit board replacements, the addition of noise suppression devices, AVR software changes, and associated testing were completed, and the unit was synchronized on December 8, 2004.
341 | 3412005001 | 2005-01-24 | QR6 | Manual Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 100 | On January 24, 2005 at 1619 hours, the Fermi 2 power plant was manually shutdown (tripped) from 100% power due to unidentified drywall leakage that exceeded the technical specification requirements. The reactor protection system (RPS) performed as expected, and all rods were fully inserted into the core. The reactor water level decreased from a normal level of 197 inches to a level of 123 inches above the top of active fuel, and recovered to normal without operator intervention. The main steam isolation valves (MSIVs) remained open and reactor water level was maintained in the normal band. Reactor water was supplied by the condensate and reactor feedwater systems. Pressure control was maintained by the turbine bypass valves. There was no increase in reactor dome pressure as a result of this event, and none of the Safety Relief Valves (SRVs) lifted. Reactor water low level (Level 3) isolations occurred as expected. These included isolation Group 4 (Residual Heat Removal Shutdown Cooling and Head Spray), Group 13 (Drywell Sumps), and Group 15 (Traversing In-core Probe System) isolations. The operation of all of these systems was as expected in response to this event. At 1321 hours on January 25, 2005, the plant entered cold shutdown (Mode 4). The source of the leak was determined to be from a failed end bell gasket on drywell cooler number 4. After appropriate repairs, plant restart commenced at 1710 hours on February 2, 2005.
341 | 3412006002 | 2006-06-15 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 100 | On June 15, 2006, at 1053 hours EDT, a reactor scram occurred from 100% power as a result of a main turbine /generator trip due to an internal fault on main unit transformer 2B. A reactor scram occurred as designed from the turbine control valve fast closure signal. The reactor protection system performed as expected, and all rods were fully inserted into the core. Reactor water level reached a low of approximately 134 inches above top of active fuel and recovered to normal automatically without operator intervention. Subsequent to the event, the main steam isolation valves remained open and reactor water level was maintained in the normal band of 173 to 214 inches. Reactor water was supplied by the condensate and reactor feedwater systems, and the resultant reactor steam was sent to the condenser via the main turbine bypass lines. Pressure control was maintained by the turbine bypass valves. Reactor dome pressure peaked at about 1077 psig, and none of the safety relief valves lifted. Reactor water Level 3 isolations occurred as expected. An internal fault to ground of the Z-phase of the high voltage transformer winding caused the transformer failure. The most probable cause of the internal fault is that two adjacent transformer oil coolers were taken out of service together and washed with cold water which caused the internal fault. Transformer 2B was isolated from the generator and the electrical system, and the plant was restarted at reduced power on June 18, 2006. The plant was subsequently shut down on July 8, 2006 for replacement of failed main unit transformer 2B and returned to 100% power on July 22, 2006.
341 | 3412006003 | 2006-07-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Fermi 2 | B | GE | PO | 100 | On July 29, 2006 at 15:50 hours EDT, a reactor scram and main turbine / generator trip occurred due to a partial loss of feedwater accompanied by a reactor recirculation system scoop tube lock. The loss of the south reactor feedwater pump and scoop tube lock were caused by a loss of Division 1 electrical power which occurred when the transformer 2 differential relay tripped 120 kV bus 101 during an energization of transformer 2. This led to a reactor scram on reactor low water level 3. The lowest reactor vessel water level reached was 110 inches which is below the reactor low water level 2 setpoint. Plant safety system actuations and isolations occurred as expected, and the standby feedwater system was started and used to maintain reactor level in the normal range. Reactor pressure control was maintained using the turbine pressure regulator with the main condenser available as the heat sink. The event occurred during an energization of transformer 2 and was caused by a trip of the transformer 2 differential relay which is designed to preclude such a trip. Inaccurate risk perception by the Fermi organization was identified as the primary organizational cause of the event since work was allowed to be performed without adequate consideration of risk to generation that resulted in a loss of bus 101 and reactor scram. The transformer and associated relaying were removed from service, and a plant stand down (training session) was held with site personnel on the scheduling issues involved. Risk sensitive and safety related work was postponed until adequate risk reviews were performed. The plant was restarted, and the main generator was synchronized to the electrical grid on August 1, 2006.
341 | 3412007002 | 2007-11-15 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Fermi 2 | B | GE | PO | 9 | At 03:13 EST November 15, 2007, during restart of the reactor, an initiation of the alternate rod insertion/recirculation pump trip (ARI/RPT) system occurred due to an invalid reactor water level 2 (Level 2) signal from the Division 1 reactor water level instrumentation. In response, control room operators placed the reactor mode switch to shutdown inserting a manual scram. When performing a safety tag-out of the Division 1 reactor water level reference leg, an operator first cracked the isolation valve open and then immediately closed the valve. This action caused a short pressure perturbation on the level instrumentation reference leg that initiated a false Level 2 Division 1 ARI/RPT system initiation, half-scram, and a reduction in feedwater flow. Due to the short duration of the false water level signal, the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems operated properly and did not automatically initiate, nor was an automatic reactor scram initiated. The lowest reactor vessel water level reached was 183 inches above top of active fuel, and the standby feedwater pumps were placed in service to maintain reactor water level in the desired range. The cause of the event was attributed to a failure to adhere to procedures and a less than adequate pre-job brief. The Operations Manager met with each of the Operations shifts and set expectations for the use of human performance techniques as a means to reduce human errors. The Plant Manager met with all site personnel to review recent human performance events and to reinforce expectations. There were no safety consequences as a result of this event.
341 | 3412008001 | 2008-01-31 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Fermi 2 | B | GE | PO | 100 | At 15:44 hours EST January 31, 2008, the reactor mode switch was taken to shutdown in response to the trip of both reactor recirculation pumps. This inserted a manual reactor scram within 9 seconds of the trip of the recirculation pumps. The reactor protection system (RPS) performed as expected, and all rods were fully inserted into the core. Reactor water level reached a low of approximately 157 inches above top of active fuel and recovered to normal automatically without operator intervention. Subsequent to the event, the main steam isolation valves (MSIVs) remained open and reactor water level was maintained in the normal band of 173 to 214 inches. Pressure control was maintained by the main turbine bypass valves. Reactor dome pressure peaked at about 1077 psig. Reactor water Level 3 isolations occurred as expected. There was no maintenance or testing in progress that would explain the pump trips. No operator performance issues were identified in response to this event. Safety related plant equipment responded as expected to the manual reactor scram. This event posed no significant safety implications because the reactor protection and safety related systems functioned as designed following the manual reactor trip. The cause of both recirculation pump trips was determined to be an intermittent failure of the 65G bus undervoltage trip logic. The undervoltage relay and its cutoff knife switches were replaced. The undervoltage circuit fuses were replaced, fuse clips tightened, connections cleaned, continuity checked, and the circuit was meggered to identify any potential faults prior to restart of the unit.
341 | 3412009001 | 2009-03-28 | QR6 | Manual Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 24 | At 0146 hours EDT March 28, 2009, the reactor mode switch was taken to shutdown in response to high vibration levels on the Main Turbine number 1 bearing. Reactor power had been reduced in preparation for a manual scram from below 25 percent power to enter into a unit refueling outage (RF13). The reactor protection system (RPS) performed as expected, and all rods were fully inserted into the core. Reactor water level reached a low of approximately 162 inches above top of active fuel and recovered to normal automatically without operator intervention. Reactor water level was maintained in the normal band with the Control Rod Drive System Supply. Reactor water Level 3 isolations occurred as expected. There was no maintenance or testing in progress that would affect high turbine vibration levels. Safety related plant equipment responded as expected to the manual reactor scram. The manual scram was inserted when turbine vibration levels on bearing number 1 reached 15 mils during the shutdown for RF13. The high turbine vibration was determined to be due to a High Pressure Turbine rub transversing bearing number 1. Cooling of the Moisture Separator Reheaters (MSRs) occurred early in the shutdown process, and it was determined that the rub was due to the MSR cool down process. The shutdown procedures will be reviewed in conjunction with vendor information and other industry operating experience to determine potential procedure enhancement.
341 | 3412009002 | 2009-09-30 | QR6 | Manual Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 100 | At 11:09 EDT on September 30, 2009, the reactor mode switch was taken to shutdown and the main turbine generator was manually tripped in response to hydrogen gas leakage into the stator water cooling system from the main generator. The reactor protection system performed as expected, and all control rods fully inserted into the core. Reactor water level reached a low of approximately 122 inches above top of active fuel and recovered to normal level automatically without operator intervention. Reactor water level was maintained above Level 2, and as expected, none of the primary containment isolations or safety injection systems initiations associated with Level 2 occurred. The main steam isolation valves remained open, and the reactor feedwater system automatically restored and maintained reactor water level. The main steam bypass valves opened and automatically controlled reactor pressure. There was no transient increase in reactor dome pressure and no safety relief valves (SRVs) actuated. All primary containment isolations and actuations for reactor water Level 3 occurred as expected. The manual scram was inserted due to hydrogen leakage from the generator hydrogen cooling system into the stator water cooling system that exceeded a predetermined maximum allowable operational leakage rate. A leak in the generator stator water cooling system was located and repaired in accordance with the generator manufacturer's recommendations.
341 | 3412010001 | 2010-03-25 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 63 | At 16:27 EDT on March 25, 2010, the reactor mode switch was taken to shutdown following an automatic scram due to a main turbine trip. The Main Turbine Trip relays actuated causing a turbine control valve fast closure which initiated a scram signal. The scram was uncomplicated. The reactor protection system (RPS) performed as expected, and all control rods were fully inserted into the core. Both safety and non-safety related plant equipment responded as expected to the reactor scram. At the time of the event, all Emergency Core Cooling Systems (ECCS) and Emergency Diesel Generators (EDGs) were operable. All reactor parameters were maintained well within analyzed limits. Plant procedures were appropriately utilized to complete scram recovery actions. Investigation determined that the turbine trip relays actuated due to a generator differential current relay trip in the Main Generator Z phase protection circuit. The cause of the Z phase relay actuation was the result of a shorted current transformer wire in the Main Generator Z phase line terminal bushing enclosure. The wire was repaired and other preventive measures were implemented for similar wiring. Additional corrective actions are being considered in accordance with the corrective action program.
341 | 3412010002 | 2010-06-06 | QR5 | Turbine Trip | [45 empty] | Fermi 2 | B | GE | PO | 100 | At 0238 hours, on June 6, 2010, the Reactor Protection System initiated an automatic reactor scram from 100% power as a result of a Turbine Control Valve (TCV) fast closure. The TCV closure was caused by a turbine trip signal initiated by the main turbine-generator protective control system upon sensing the loss of Division II offsite power. The loss of Division II offsite power occurred as a result of the severe weather and tornado in the area. All safety related systems operated as expected in response to this event. All control rods fully inserted into the reactor core. Reactor Pressure Vessel (RPV) water level decreased and the Reactor Core Isolation Cooling system was manually started to restore RPV level. Reactor Water Level 3 Primary containment isolations occurred as expected. Two Division II Emergency Diesel Generators started and energized their emergency loads as designed. At 0417 hours, on June 6, an Alert was declared due to damage to the Auxiliary Building fifth floor siding during the severe weather. At 0220 hours, on June 7, 2010, the Alert was terminated. The Main Generator was synchronized to the grid at 1921 hours, on June 16, 2010, following repairs to offsite power feeds and station structures.
341 | 3412010003 | 2010-10-24 | QL7 | Degraded condenser vacuum | [45 empty] | Fermi 2 | B | GE | PO | 97 | On October 24, 2010 shortly after 16:00 EDT with the reactor operating at approximately 97% power, condenser pressure began an upward trend. High condenser pressure alarmed at 16:38 EDT, plant operators responded to the conditions using plant procedures, and at approximately 16:42 EDT on October 24, 2010, a second condenser high pressure relay actuated resulting in a turbine trip. Turbine control valve fast closure then initiated a reactor scram. All control rods fully inserted except control rod 10-35 which initially stopped moving at position 42. Control rod 10-35 was manually inserted from position 38 to the full in position three minutes later. Extensive troubleshooting was performed on control rod 10-35 and it has been demonstrated to be capable to perform its scram function. Other safety related systems performed as expected. Reactor water level decreased to below Level 3 to a minimum of approximately 133 inches above the top of active fuel. Reactor water level was returned to normal and controlled in the normal band using the Control Rod Drive and Reactor Feedwater systems. Reactor pressure was controlled and decay heat removed through the main turbine bypass valves to the main condenser. The event was caused by a degraded condenser vacuum which was caused by the erosion of the No. 3 Steam Jet Air Ejector steam supply first stage nozzle which resulted in a loss of ejector capacity. Inspections were performed of all four Steam Jet Air Ejectors, and repairs were made to restore expected performance before resuming operation.
341 | 3412012003 | 2012-06-25 | QL7 | Degraded condenser vacuum | [45 empty] | Fermi 2 | B | GE | PO | 26 | On 6/25/2012 after completing repairs to the main unit transformer, reactor power was raised to approximately 22% and the unit was synchronized to the power grid at 1203 EDT. At 1234 EDT Operations began a power increase. At 1322 to 1325 EDT multiple vibration related alarms were received for the south reactor feed pump, and the pump tripped at 1325 EDT. Manual operation of the north reactor feed pump was used initially to recover reactor level. At 1330 hours a manual scram was performed by placing the reactor mode switch in shutdown in response to degrading condenser vacuum. All rods fully inserted and operators used the standby feedwater system to restore water level. Reactor water level reduced to below Level 3 as a result of the scram, and all isolations and actuations associated with that level occurred as expected. The south reactor feed pump turbine was damaged which resulted in main condenser vacuum leaks that were isolated following the event. Decay heat was removed using the main condenser via the turbine bypass valves.
341 | 3412012005 | 2012-09-14 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Fermi 2 | B | GE | PO | 68 | At approximately 1603 EDT, a fault occurred on the 13.2 kV side of 120 kV Transformer 1. The fault caused the isolation of Bus 101, and a loss of power to Transformer 64, Division I emergency safety system busses 64B and 64C, balance of plant bus 64A, the center condenser pump, center heater feed pump and both north and center heater drains pumps. The loss of the pumps resulted in a trip of the operating north reactor feed pump. Reactor water level lowered as a result of the loss of feedwater, and the unit automatically scrammed on low reactor water level 3 as designed. All control rods fully inserted, and the lowest reactor water level reached was approximately 96 inches above top of active fuel. Division I Emergency Diesel Generators, EDG-11 and EDG-12, automatically started and loaded Division I buses. The High Pressure Coolant Injection and Reactor Core Isolation Cooling systems automatically started as designed on low reactor water level 2 and restored reactor water level which was then maintained using the Condensate/Feed and Control Rod Drive systems. All isolations and actuations occurred as expected. The cause of the trip was determined to be animal intrusion that initiated a phase to ground fault at the Z-phase surge arrestor on the secondary side of Transformer 1. The potentially affected equipment was inspected and tested and the surge arrestor and associated jumpers were replaced prior to restart.
341 | 3412012006 | 2012-11-07 | QR6 | Manual Reactor Trip | [45 empty] | Fermi 2 | B | GE | PO | 68 | At 09:21 EST 11/7/12, the reactor mode switch was taken to shutdown and the main turbine generator was manually tripped in response to excessive hydrogen gas leakage into the stator water cooling system from the main turbine generator. Two control rods did not respond as expected; however, both rods exhibited normal scram times up to position 02, and the scram was uncomplicated. The lowest reactor vessel water level reached was 125 inches above top of active fuel which is below reactor water Level 3 and above Level 2. As expected, the High Pressure Coolant Injection and Reactor Core Isolation Cooling did not actuate. Reactor pressure did not increase above normal operating pressure during the transient. No safety relief valves actuated, and all isolations and actuations associated with reactor water Level 3 occurred as expected. Water level was restored during the transient and maintained at 196 inches by the post scram feedwater logic and the North Reactor Feed Pump. Decay heat was removed via steam to the main condenser using the turbine bypass valves. Two control rod drive mechanisms have been replaced for the control rods that did not respond as expected. A leak in the generator stator water cooling system was located and repaired.
341 | 3412015003 | 2015-03-19 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Fermi 2 | B | GE | PO | 74 | On March 19, 2015 at 0702 EST the reactor protection system at Fermi 2 initiated an automatic reactor scram on Oscillation Power Range Monitor (OPRM) Upscale following the manual trip of the north reactor recirculation pump due to a cooling water leak. The reactor protection system performed as expected and all control rods were fully inserted into the core. Reactor water level reached a low of approximately 126 inches above top of active fuel and was restored and maintained in the normal operating band by the feedwater and control rod drive systems. No safety relief valves actuated and reactor pressure was controlled by the main turbine bypass valves. Plant systems responded to the scram as designed and all reactor parameters were maintained within design limits following the event.<br /><br /> The cause of the automatic reactor protection system scram on OPRM Upscale was the neutron flux oscillations following the large core flow reduction and lowering feedwater temperature after the trip of a reactor recirculation pump. This event was documented and evaluated in the Fermi 2 Corrective Action Program. The associated root cause evaluation is in progress and may identify additional corrective actions which will be tracked and implemented by the corrective action program.<br /><br /> This event is reportable in accordance with 10 CFR.50.73(a)(2)(iv)(A) as a critical reactor scram.
341 | 3412015006 | 2015-09-13 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [28 empty] | X | [5 empty] | Fermi 2 | B | GE | PO | 100 | At 2305 EDT on September 13, 2015, a manual reactor scram was initiated in response to a loss of Turbine Building Closed Cooling Water (TBCCW). Reactor Water Level went below the Level 3 setpoint automatically actuating the Reactor Protection System and Primary Containment Isolation Systems (PCIS). A tube leak in the East TBCCW heat exchanger tripped the running TBCCW pumps which resulted in loss of TBCCW. As a result, the Reactor Feed Pumps lost cooling and had to be secured. At 2310 EDT, the Standby Feedwater system was initiated. The loss of TBCCW cooling tripped all Station Air Compressors, which caused Instrument Air header pressure to degrade and the Secondary Containment (SC) isolation dampers to drift closed. This resulted in a positive SC differential pressure. Operators started the Standby Gas Treatment system and manually inserted a SC isolation signal. SC vacuum was promptly restored to within Technical Specification limits. The degradation of Instrument Air header pressure also caused Main Steam Isolation Valves to drift and be manually closed, which led to an expected loss of Condenser vacuum and resulted in isolation of PCIS Group 1. The East TBCCW heat exchanger was repaired. The Root Cause Evaluation determined that important internal equipment operating history and industry Operating Experience (OE) were not identified and implemented. The following corrective actions to prevent recurrence were identified: current heat exchanger inspection scope, frequency, and techniques will be compared against previous historical failures and plant procedures will be revised in consideration of industry and site OE.
341 | 3412018002 | 2018-04-14 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Fermi 2 | B | GE | PO | 100 | On April 14, 2018 at approximately 1040 EDT, a reactor scram on low reactor water level occurred due to a partial loss of feedwater accompanied by a reactor recirculation system scoop tube lock. The High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems automatically started in order to restore reactor water level as designed. Reactor water level was subsequently maintained using RCIC. No Safety Relief Valves actuated and the Primary Containment Isolation System responded as expected. The partial loss of feedwater and scoop tube lock were caused by a loss of Division 1 electrical power which occurred following a trip of the normal feed to Transformer 64, the 13.8 kV Bus 11 Position D breaker. Division 1 Emergency Diesel Generators (EDGs), EDG-11 and EDG-12, automatically started and energized Division 1 buses. In addition, both Low Pressure Coolant Injection (LPCI) subsystems were declared inoperable while aligned to their alternate power source following loss of their normal power source. The LPCI subsystems were declared operable following realignment to their normal source after EDG-11 and EDG-12 were started. Investigation has determined the direct cause of this event to be moisture intrusion into the A6 cubicle of the Bus 1-2B enclosure, which caused a ground fault that tripped the Bus 11 Position D breaker. Immediate corrective actions were completed to eliminate moisture intrusion into the Bus 1-2B enclosure. The root cause evaluation determined that the organization failed to recognize the degradation of the Bus 1-2B enclosure as a failure mechanism of the A6 switchgear. Corrective actions to prevent recurrence include developing and implementing a Preventive Maintenance strategy for outdoor metal clad switchgear.
344 | 3441987001 | 1987-01-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Trojan | P | WE | PO | 100 | POWER LEVEL - 100%. ON 1-6-87, THE PLANT WAS OPERATING AT 100% POWER AT NORMAL OPERATING TEMPERATURE AND PRESSURE. AT 1129, THE 'A' MAIN FEEDWATER PUMP TRIPPED WHILE MAINTENANCE WAS BEING PERFORMED ON THE PUMP CONTROL CIRCUITRY. THIS RESULTED IN A REACTOR TRIP BECAUSE THE FEEDWATER FLOW/STEAM FLOW MISMATCH REACTOR TRIP BISTABLES WERE IN A PARTIAL TRIP CONDITION DUE TO ROUTINE INSTRUMENT SURVEILLANCE TESTING. THE CAUSE OF THE EVENT WAS PERSONNEL ERROR. WHILE TROUBLESHOOTING THE 'A' MAIN FEEDWATER PUMP CONTROL OIL PRESSURE INDICATOR, AN I&C TECHNICIAN SHORTED THE PUMP CONTROL POWER SUPPLY. THIS CAUSED THE POWER SUPPLY FUSE TO BLOW WHICH ALSO PROVIDES POWER TO THE PUMP OVERSPEED CONTROL CIRCUIT. THIS RESULTED IN ACTUATION OF THE PUMP OVERSPEED TRIP AND TRIPPING OF THE PUMP. CORRECTIVE ACTION TO PREVENT RECURRENCE IS TO EVALUATE ADDITIONAL MANAGEMENT CONTROLS ON MAINTENANCE WHICH HAS A HIGH POTENTIAL FOR CAUSING PLANT TRIPS AND TO EVALUATE SCHEDULING OF ROUTINE SURVEILLANCE CONCURRENT WITH MAINTENANCE ACTIVITIES. THIS EVENT WAS DISCUSSED WITH I&C TECHNICIANS.
344 | 3441987024 | 1987-08-28 | QP5 | Excessive Feedwater Flow | [45 empty] | Trojan | P | WE | PO | 30 | POWER LEVEL - 030%. ON AUGUST 28, 1987, THE PLANT WAS OPERATING AT 30 PERCENT POWER AT NORMAL OPERATING TEMPERATURE AND PRESSURE. AT 0831, A TURBINE TRIP OCCURRED DUE TO 'C' STEAM GENERATOR HIGH-HIGH LEVEL WHILE BRINGING THE SOUTH MAIN FEED PUMP (MFP) ON LINE. THIS RESULTED IN A REACTOR TRIP. THE CAUSE OF THE EVENT WAS COGNITIVE PERSONNEL ERROR. THE OPERATOR MISREAD THE AUTOMATIC SPEED CONTROLLER INDICATION AND PLACED THE PUMP IN SERVICE AT MAXIMUM SPEED INSTEAD OF MINIMUM SPEED. THE RESULTING TRANSIENT LED TO INADEQUATE FEED FLOW AND STEAM GENERATOR LEVEL CONTROL. SLUGGISH BEHAVIOR OF THE 'C' FEEDWATER REGULATING VALVE WAS A CONTRIBUTING FACTOR. THE EVENT WAS DISCUSSED WITH ALL PLANT OPERATORS. THE SLUGGISH BEHAVIOR OF THE 'C' FEEDWATER REGULATING VALVE IS BEING INVESTIGATED. THIS EVENT HAD NO EFFECT ON PUBLIC HEALTH AND SAFETY.
344 | 3441987037 | 1987-12-06 | QR6 | Manual Reactor Trip | [45 empty] | Trojan | P | WE | PO | 100 | POWER LEVEL - 100%. ON DECEMBER 6, 1987, THE REACTOR WAS MANUALLY TRIPPED FOLLOWING A LOAD REJECTION TRANSIENT. ABOUT TEN MINUTES AFTER THE REACTOR TRIPPED, IT WAS REPORTED TO THE CONTROL ROOM THAT THE TURBINE-DRIVEN AUXILIARY FEEDWATER (AFW) PUMP HAD NOT AUTOMATICALLY STARTED. THE PUMP WAS MANUALLY STARTED. STEAM GENERATOR BLOWDOWN ISOLATION VALVE MO-2808 FAILED TO INDICATE COMPLETELY CLOSED FOLLOWING THE MAIN TURBINE TRIP. THE UPSTREAM ISOLATION VALVE CLOSED AS DESIGNED. THE CAUSE OF THE LOAD REJECTION TRANSIENT WAS A FAILURE OF THE LOAD DECREASE PUSH BUTTON IN THE ELECTRO HYDRAULIC CONTROL (EHC) SYSTEM. THE FAILURE OF THE TURBINE-DRIVEN AFW PUMP TO AUTO-START WAS DUE TO A LOOSE ELECTRICAL CONNECTION IN THE AUTO-START CIRCUITRY. THE FAILURE OF VALVE MO-2808 TO INDICATE FULLY CLOSED WAS DUE TO THE THREADED VALVE SEATING BACKING OUT AND PREVENTING COMPLETE CLOSURE INDICATION FOR THE VALVE. THE PLANT WAS PLACED IN MODE 3 (HOT STANDBY). THE EHC LOAD DECREASE PUSH BUTTON WAS REPLACED. THE LOOSE CONNECTION IN THE TURBINE-DRIVEN AFW PUMP AUTO-START CIRCUITRY WAS TIGHTENED. OTHER ACCESSIBLE TERMINAL CONNECTIONS WERE CHECKED FOR TIGHTNESS, AND NO DISCREPANCIES WERE FOUND. BLOWDOWN VALVE MO-2808 WAS REPAIRED AND TESTED SATISFACTORILY. THIS EVENT HAD NO EFFECT ON PUBLIC HEALTH AND SAFETY.
344 | 3441988001 | 1988-01-08 | QR8 | Spurious Reactor Trip | [45 empty] | Trojan | P | WE | PO | 100 | On January 8, 1988, the plant was operating at 100% power at normal operating temperature and pressure. At 1506, a reactor trip occurred due to a spurious overpower delta temperature (OPDT) trip signal on one channel which occurred while another OPDT channel was in a tripped state while surveillance testing. At 1518, source range neutron detector N-32 was energized, but no indication was received on this channel of nuclear instrumentation. <br /><br />The cause of the OPDT channel's spurious trip signal was found to be a failed transistor in the channel's Lead-Lag Amplifier (TY-412D). The source range channel's failure to indicate was due to a reduction in channel signal strength which apparently resulted from formation of an oxide film on the cable connector to the instrument's pre-amplifier. <br /><br /> The faulty transistor in the OPDT amplifier was replaced. The connector to the source range instrument's pre-amplifier was cleaned. <br /><br />This event had no impact on public health and safety.
344 | 3441988026 | 1988-08-16 | QR8 | Spurious Reactor Trip | [45 empty] | Trojan | P | WE | PO | 100 | On August 16, 1988, the plant was in Mode 1 (power operation). Reactor coolant loop 'B' flow transmitter (FT)-424 was out of service for calibration with its low flow bistable tripped. At 1107 a reactor trip occurred on a Reactor Coolant System loop 'B' low flow signal. Venting of FT-424 caused a transient on a second loop 'B' flow transmitter, FT-425, which shares a common high pressure sensing line. This transient caused FT-425 to momentarily sense pressure below the low flow setpoint and trip its low flow bistable. This satisfied the logic for a reactor trip on loop low flow. <br /><br /> Immediate corrective action was to carry out the emergency instruction recovery actions and to restore flow transmitter FT-424 to service. The root cause of the event was inadequate work instructions on risks associated with venting FT-424. The cause of the reactor trip was a technician's procedural error in re-venting FT-424 with the transmitter valved into service. Plant procedures were revised to provide additional reviews and controls for tasks that could cause a reactor trip or Engineered Safety Features system actuation. <br /><br />This event had no effect on public health and safety. There was no actual plant condition requiring a reactor trip however, the reactor protection system functioned as designed to trip on reactor on receipt of a loss of flow trip signal.
344 | 3441988028 | 1988-09-16 | QR8 | Spurious Reactor Trip | [45 empty] | Trojan | P | WE | PO | 100 | On September 16, 1988, preparations were being made to replace failed pressurizer pressure transmitter PT-458. The bistables associated with this transmitter, including one which provides input to one channel of the overtemperature delta temperature circuit (OTDT), were in the tripped position. While establishing conditions necessary for replacement of the PT-458 transmitter, a technician erroneously tripped the input bistable from another pressurizer pressure transmitter to the OTDT circuit. This satisfied the two out of four OTDT trip logic, causing a reactor trip at 0830. <br /><br /> The causes of this event were deficiencies in the work instructions for the PT-458 transmitter replacement, personnel error (procedural) and inadequate supervision. The work instructions directed that the correct bistable be checked as tripped, but listed the wrong cabinet as its location. The technician then entered this incorrect cabinet and checked position of a bistable other than the one specified in the work instructions. Upon finding this incorrect bistable not tripped, he decided to trip the bistable despite instructions which stated to only check the bistable as tripped. Inadequate supervision was evidenced by lack of an adequate pre-evolution briefing and lack of an adequate verification/validation of the work instructions. <br /><br /> A detailed critique of this event conducted by senior management personnel identified numerous plant practices which are being revised as a result of this event. This event had no effect on public health and safety.
344 | 3441988043 | 1988-11-13 | QP5 | Excessive Feedwater Flow | [45 empty] | Trojan | P | WE | PO | 100 | On November 13, 1988 with the plant in Mode 1 at 100% power, with the Reactor Coolant System at Tavg 585 degrees Fahrenheit, 2235 psig, the 'B' steam generator main feedwater regulating valve controller failed. This resulted in a reactor trip at 1053 due to a turbine trip on Hi-Hi steam generator level. The valve controller failure was due to a power supply failure. Immediate corrective action was to carry out Emergency Instruction (EI)-O Reactor Trip, Safety Injection and Diagnosis and to restore steam generator level. <br /><br />At 1159 an evacuation of a portion of the turbine building was ordered, and main steam isolation manually initiated, due to a report of a steam leak in the turbine building. The source of the leak was found to be a bonnet/body leak of main turbine gland seal steam relief valve (PSV-3589). The leak was due to poor material condition of the valve (loose studs/nuts) and failure of two bonnet/body studs from low cycle, high stress, fatigue. The valve was rebuilt and similiar valves were checked to determine their condition (found acceptable). <br /><br />During post trip work it was discovered that one steam generator blowdown isolation valve had failed to close on a feedwater isolation signal. The cause was determined to be an instantaneous breaker overload setting which was within specification but did not have enough margin to prevent undesirable trips. All steam generator blowdown isolation valves were declared inoperable, closed, and power removed. After an engineering evaluation, the instantaneous trip settings were adjusted from the middle to the high of the setpoint range. This event had no effect on public health and safety.
344 | 3441989006 | 1989-04-06 | QR3 | Reactivity Control Imbalance | [45 empty] | Trojan | P | WE | PO | 6 | At 0024 hours on April 6, 1989, the plant was at 6% power in Mode 1, in the process of a planned shutdown. When the steam dump valves were partially opened as a part of the planned evolution, one of the valves went to the full open position rather than modulating flow. Shortly afterward, the same valve fully shut due to loss of instrument air when the instrument airline leading to the valve ruptured. This sequence of events resulted in an increase in steam generator level in the "C" steam generator due to excessive steam flow. The steam generator reached the High-High alarm setpoint, resulting in feedwater isolation, auxiliary feedwater pump start and steam generator blowdown isolation. The failed valve vas quarantined and plant shutdown recommenced. While continuing the plant shutdown, bank "A" shutdown rods failed to drive in properly. There was no need to withdraw the rods, so the reactor was manually tripped. <br /><br /> The cause of the event was a broken wire that energized the "trip open" solenoid in the valve control circuitry and opened the valve. A high stresslow cycle fatigue failure of the instrument airline shut the valve. The rods failed to move in due to a thermal cycle/age related failure of a fuse. <br /><br /> Corrective actions were to repair the broken wire, overhaul the affected steam dump valves mechanically and electrically, replace applicable airlines with a flexible tubing, replace all similar rod control fuses, and develop a periodic replacement program for this type of rod control fuse. <br /><br /> This event had no effect on public health and safety.
344 | 3441989017 | 1989-08-09 | QR8 | Spurious Reactor Trip | [45 empty] | Trojan | P | WE | PO | 50 | On August 9, 1989 at 1220 hours the Plant was operating at 50 percent power when a reactor trip signal was generated, The reactor tripped when the logic for Over Temperature Delta Temperature (OT Delta T) was satisfied from a spurious signal. The other signal completing the two out of four logic was already being generated in Channel 3 of the OT Delta T logic due to the performance of Periodic Instrumentation and Control Test (PICT) 11-1, "Nuclear Instrumentation, Power Range". The trip was caused by receipt of a spurious signal, apparently from Channel 4 of the OT Delta T circuit. The signal was considered spurious because Reactor Coolant System conditions were acceptable when the trip occurred. A comprehensive investigation was conducted with no exact cause identified. However, the continued investigation did identify conditions which could have caused a spurious signal. These conditions included intermittent failure of a comparator module or an intermittent open in a termination connection which generated a transitory signal large enough to cause the bistable to trip. A potential contributing factor was a lower OT Delta T setpoint than in previous operating cycles. Immediate corrective actions prior to return the power included replacement of three Channel 4 OT Delta T modules (even though no indication of failure existed) and performance of PICTs for inputs into all four of the OT Delta T channels. Corrective action included cleaning instrument cabinets, correcting problems with wiring terminations, implementing periodic cleaning of instrumentation cabinets and training of technicians on terminating connectors, and increasing the OT Delta T safety limit. Because the reactor tripped and all systems responded to the trip signal as designed, this event did not have any effect on public health and safety.
344 | 3441990034 | 1990-08-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Trojan | P | WE | PO | 100 | On August 9, 1990, the Trojan Nuclear Plant was operating in Mode 1 (Power Operation) at 100 percent Rated Thermal Power. The generator load was approximately 1135 MW. At 1648 the "B" Feedwater Pump tripped on indication of high thrust bearing wear. In response to the loss of the Feedwater Pump, the Main Turbine began an automatic runback and the control rods began automatically stepping in to reduce Reactor power. The turbine runback continued for one minute, twenty seconds; then the Reactor automatically tripped on low-low level in the "D" steam generator. Following the Reactor trip, automatic Feedwater Isolation and Auxiliary Feedwater initiation occurred. The "B" Feedwater Pump trip was initiated by protective instrumentation which received indication of excessive thrust bearing wear in the pump's turbine driver. The excessive bearing wear indication was the result of incorrectly set instrumentation, not actual wear. The thrust bearing wear indicating instruments were recalibrated and the pump was reassembled. The plant was returned to power operation on August 11, 1990. This event had no effect upon public health and safety. The Reactor Protective System and Engineered Safety Features Actuation System functioned as required. The plant responded as expected to the trip.
344 | 3441991004 | 1991-02-12 | QR5 | Turbine Trip | [45 empty] | Trojan | P | WE | PO | 100 | On February 12, 1991, the Trojan Nuclear Plant was operating at 100 percent Rated Thermal Power. At 1020, maintenance was in progress to repair a damaged electrical conduit associated with the plant lighting system. During the course of the repairs, a wiring jumper was incorrectly installed within a lighting contactor panel, and resulted in 120 Volt A.C. power being applied to the negative leg of a 125 Volt D.C. bus. The electrical noise on the D.C. bus resulted in actuation of the Electro-Hydraulic Control Master Trip Bus, tripping the turbine. The turbine trip initiated a Reactor trip. Following the Reactor trip, Auxiliary Feedwater was initiated on a low-low steam generator level signal and Main Feedwater was isolated on a Reactor trip combined with low Tave signal. The cause of this event was the lack of adequate drawings which resulted in the preparation of inadequate work instructions. This in turn led to installation of the jumper in an inappropriate location. An Engineering Evaluation and component walkdown were performed and determined that no damage to plant components occurred. Procedures have been revised to require specific instructions for the placement of electrical jumpers.
344 | 3441992014 | 1992-06-05 | QP5 | Excessive Feedwater Flow | [45 empty] | Trojan | P | WE | PO | 30 | On June 5, 1992, the Trojan Nuclear Plant experienced a reactor trip. The plant had been operating at 30 percent power while preparing to shutdown for an unrelated condition. Feedwater to the 'B' steam generator was being controlled manually using its feedwater bypass valve.<br /><br /> Plant personnel were attempting to restore the steam generator water level control to automatic prior to initiating the shutdown. The operator stationed at the Steam Generator Water Level Control Panel in the Control Room began to open the 'B' main Feedwater Regulating Valve (FWRV) manually. The operator was not able to clear the open signal, which caused the steam generator to fill to its high-high level trip setpoint, causing a turbine trip/reactor trip. The cause of the controller failure was determined to be stuck contacts on a manual pushbutton on the controller. The failed controller was replaced with a spare controller. The manual switches were removed from the failed controller and returned to the vendor for additional analysis. The failure of the pushbutton has been determined to be a random component failure caused by a manufacturing defect. In addition, operators were instructed concerning additional methods to terminate future similar controller failures. Plant systems responded as expected to the event. This event had no safety consequences.
344 | 3441992020 | 1992-07-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Trojan | P | WE | PO | 100 | On July 22, 1992, the Trojan Nuclear Plant experienced a reactor trip from 100 percent power. The trip was caused by the loss of flow from the 'B' Main Feedwater Pump (MFP). At the time of the trip, both MFPs were in manual control due to oscillations in automatic flow control. Following the reactor trip, the 'A' Auxiliary Feedwater Pump (AFW Pump) started, but tripped on overspeed shortly after starting. Subsequent attempts to start the 'A' AFW Pump failed. The failure of the 'B' MFP was due to an electronic component failure on its governor's electronic control assembly (Woodward Model 8270). The control problems with the 'A' MFP were caused by a failed electronic component on its flow controller (Westinghouse-Hagan Model 124). The 'A' AFW Pump failure was caused by a failed integrated circuit on the Ramp Generator Signal Converter in the Woodward Governor turbine startup control circuitry. Corrective Actions included repairing and/or replacing the failed components and circuit boards. There were no safety consequences resulting from the component failures. The 'B' AFW Pump functioned as required to provide cooling water to the steam generators. Other plant systems functioned as expected.
344 | 3441992027 | 1992-09-12 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Trojan | P | WE | PO | 100 | On September 12, 1992, at 1625 hours, the 'B' Condensate Pump and the 'B' Circulating Water Pump tripped on an indicated ground fault. The 'B' Main Feedwater Pump tripped due to the Condensate Pump trip. The Main Turbine load setback circuitry actuated, but was unable to prevent Steam Generator level from decreasing to a low level setpoint. A reactor trip signal was generated by Steam Generator low level coincident with a steam flow/feed flow mismatch. The Engineered Safety Features equipment functioned properly and plant response was normal following the trip. <br /><br /> The 'B' Condensate Pump tripped because of a phase to ground fault in the shielded cable connecting the motor coils to the field cable connection point. This fault caused stresses which resulted in two turn-to-turn failures in two different sets of coil end turns. The Pump motor has been rewound. The other 12 kilovolt motors will be reviewed for potential similar problems. The Circulating Water Pump motor was tested shortly after the trip. No abnormalities were found, and the pump was restarted on September 13, with no problems encountered.
344 | 3441992028 | 1992-09-13 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Trojan | P | WE | PO | 60 | On September 13, 1992, at 1934 hours, the reactor was manually tripped after the operating Main Feedwater Pump tripped. The Main Feedwater Pump tripped on low suction pressure which was caused by the Heater Drain Tank pump discharge valves going closed on low Heater Drain Tank level and the inability of the one operating Condensate Pump to provide adequate suction to the Main Feedwater Pump. Because the Heater Drain Tank level sightglass was erroneously providing an indication of high Heater Drain Tank level, the plant operators increased flow from the Heater Drain Tanks to the Main Condenser, which ultimately resulted in low Heater Drain Tank level. Plant response was normal with the exception of a letdown isolation on low pressurizer level. This occurred because of a Reactor Coolant System cooldown. The minimum temperature was approximately 542 degrees Fahrenheit. <br /><br /> Several factors contributed to this event, including a lack of direct, reliable level indicators and alarms; incomplete understanding of the level control system; inadequate verbal communications; and a lack of procedural guidance. Corrective actions include revising procedures to provide additional guidance, conducting training, and evaluating indication adequacy and alarm/control circuitry setpoint changes.
346 | 3461987001 | 1987-01-01 | P1 | Total Loss of Feedwater Flow | [7 empty] | X | [5 empty] | X | [19 empty] | X | X | [9 empty] | X | Davis-Besse | P | BW | PO | 40 | POWER LEVEL - 040%. ON JANUARY 1, 1987 WITH THE REACTOR AT 40 PERCENT POWER, THE UNIT TRIPPED AT 1039 HOURS. THE TRIP WAS THE RESULT OF THE LOSS OF #1 MAIN FEEDWATER PUMP TURBINE (MFPT). THE MFPT 1 TRIPPED AS A RESULT OF HIGH VIBRATION DUE TO BEARING FAILURE. MFP 2 WAS OUT OF SERVICE AT THE TIME. THE LOSS OF FEEDWATER INITIATED AN ANTICIPATORY REACTOR TRIP SYSTEM (ARTS)/REACTOR PROTECTION SYSTEM (RPS) TRIP OF THE UNIT. ALL THE SAFETY SYSTEMS CHALLENGED DURING THIS TRANSIENT AND THE OPERATIONS PERSONNEL PERFORMED THEIR FUNCTIONS SUCCESSFULLY. IN ADDITION OIL VAPORS IN THE AREA OF THE FAILED BEARINGS IGNITED, AND THE FIRE WAS EXTINGUISHED BY OPERATION PERSONNEL SOON AFTER THE REACTOR TRIP. THIS REPORT IS BEING SUBMITTED IN COMPLIANCE WITH 10CFR50.73(A)(2)(IV) AS AN ACTUATION OF THE RPS. THE RPS.
346 | 3461987006 | 1987-03-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Davis-Besse | P | BW | PO | 92 | POWER LEVEL - 092%. THE REACTOR TRIPPED AS A RESULT OF HIGH REACTOR COOLANT SYSTEM (RCS) PRESSURE FOLLOWING A LOSS OF MAIN FEEDWATER FLOW TO STEAM GENERATOR (SG) #2 ON MARCH 13, 1987 WITH POWER AT 92 PERCENT. WHILE WORKING IN THE VICINITY OF SG #2 MAIN FESDWATER STOP VALVE (FW 601). A CONTRACTOR ENGAGED IN MAINTENANCE INADVERTENTLY BUMPED ITS LOCAL CONTROL SWITCH VALVE CLOSURE RESULTED IN ISOLATING FEEDWATER FLOW TO STEAM GENERATOR (SG) #2 CAUSING A RAPID INCREASE IN RCS TEMPERATURE AND PRESSURE. THE REACTOR TRIPPED DUE TO HIGH RCS PRESSURE. SUBSEQUENTLY, STEAM AND FEEDWATER RUPTURE CONTROL SYSTEM ACTUATION OCCURRED DUE TO LOW LEVEL IN SG #2. THE TURBINE-GENERATOR AUTOMATICALLY TRIPPED AS A RESULT OF THE REACTOR TRIP. THIS RESULTED IN AN INCREASE IN SECONDARY PRESSURE WHICH CAUSED THE MAIN STEAM SAFETY VALVES (MSSVS) TO LIFT AS EXPECTED. ONE MSSV FAILED TO FULLY RESEAT, BUT DID NOT ADVERSELY AFFECT SAFE SHUTDOWN OF THE PLANT.
346 | 3461987010 | 1987-08-21 | QR5 | Turbine Trip | [45 empty] | Davis-Besse | P | BW | PO | 100 | POWER LEVEL - 100%. ON 8/21/87 AT 2258 HOURS WITH A SEVERE THUNDERSTORM IN THE AREA, THE UNIT EXPERIENCED A TRIP FROM 100% REACTOR THERMAL POWER. THE POST-TRIP RESPONSE WAS NORMAL WITH THE EXCEPTION OF A FASTER THAN NORMAL REACTOR COOLANT SYSTEM (RCS) AND PRESSURE REDUCTION. THE MAIN CONTRIBUTOR WAS THE EXCESSIVE STEAM LOAD WHEN THE 2ND STAGE REHEAT STEAM SOURCE VALVE TO THE #1 MOISTURE SEPARATOR REHEATER FAILED TO AUTOMATICALLY CLOSE AFTER THE TURBINE TRIP. THE CAUSE OF THIS VALVE FAILURE WAS TRACED PRESSURE SWITCH, PS9806, WHICH FAILED TO ACTUATE. ALSO THE RAPID FEEDWATER REDUCTION CIRCUIT DID NOT RESPOND AS DESIRED AND REQUIRED MANUAL OPERATOR ACTION TO OBTAIN THE DESIRED POST-TRIP STEAM GENERATOR WATER LEVEL. THE CAUSE OF THE UNIT TRIP WAS A PARTIAL LOSS OF THE A AND C PHASES (FOR 3-1/2 CYCLES) IN THE POWER GRID WHICH CAUSED A SUDDEN SHIFT IN THE TURBINE-GENERATOR SHAFT POSITION AND RESULTANT VIBRATION SPIKES AT THE BEARINGS. THE #9 BEARING EXCEEDED ITS VIBRATION TRIP SET POINT. THIS CAUSED A TURBINE GENERATOR TRIP WHICH INITIATED AN ANTICIPATORY REACTOR TRIP SYSTEM (ARTS) TRIP OF THE REACTOR. THE UNIT WAS BACK ON LINE ON AUGUST 23, 1987 AND RETURNED TO FULL POWER OPERATION ON AUGUST 24, 1987. THE PRESSURE SWITCH WAS REPAIRED AND SELECTED TURBINE-GENERATOR BEARING TRIP SETPOINTS WERE INCREASED SUCH THAT ALL TRIPS NOW OCCUR AT 12 MILS.
346 | 3461987011 | 1987-09-06 | QP5 | Excessive Feedwater Flow |  |  |  |  | X | [16 empty] | X | [23 empty] | Davis-Besse | P | BW | PO | 100 | POWER LEVEL - 100%. WITH THE UNIT AT FULL POWER, A FEEDWATER FLOW TRANSMITTER FAILED. THE INTEGRATED CONTROL SYSTEM (ICS) THEN INCREASED FEEDWATER FLOW TO STEAM GENERATOR NO. 2. DUE TO AN ABNORMAL CONTROL ROD GROUP SELECTION, THE CONTROL ROOM OPERATOR INADVERTENTLY DROVE AXIAL POWER SHAPING RODS INSTEAD OF CONTROL RODS CAUSING AN UNDESIRED POWER INCREASE. THE REACTOR PROTECTION SYSTEM (RPS) TRIPPED THE REACTOR ON HIGH FLUX. FOLLOWING THE TRIP SEVERAL OTHER ANOMALIES OCCURRED. BREAKER HX01A FAILED TO AUTOMATICALLY TRANSFER DUE TO A FAILED POSITION SWITCH AND INADEQUATE ADJUSTMENT OF THE FLOOR TRIPPER, ONE MAIN STEAM SAFETY VALVE FAILED TO FULLY RESEAT DUE TO A FAILURE OF A DISC COLLAR; AND A SERVICE WATER PUMP FAILED TO AUTOMATICALLY START WHEN THE EMERGENCY DIESEL GENERATOR STARTED DUE TO A MISSING WIRE IN A CONTROL CIRCUIT. AS CORRECTIVE ACTION, BREAKER HX01A WAS ADJUSTED AND THE POSITION SWITCH REPLACED, THE MAIN STEAM SAFETY VALVE WAS REMOVED AND BLANKED; AND THE MISSING WIRE WAS INSTALLED INTO THE SERVICE WATER PUMP CONTROL CIRCUIT. AFTER THE TRIP, A TURBINE BYPASS VALVE FAILED OPEN DUE TO AN IMPROPER VALVE TRAVEL STOP ADJUSTMENT CAUSING A STEAM AND FEEDWATER RUPTURE CONTROL SYSTEM (SFRCS) ACTUATION. AS CORRECTIVE ACTION, THE TRAVEL STOP ADJUSTMENTS WERE CORRECTED.
346 | 3461987015 | 1987-12-07 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Davis-Besse | P | BW | PO | 81 | POWER LEVEL - 081%. ON 12/7/87 THE UNIT EXPERIENCED A REACTOR TRIP AT 0656 HOURS FROM 81% REACTOR THERMAL POWER. THE INITIATING EVENT WAS A LOSS OF INSTRUMENT AIR PRESSURE WHICH CAUSED SEVERAL SECONDARY SYSTEM VALVES TO GO TO THEIR FAILED POSITION REACTOR POWER INCREASED TO THE INTEGRATED CONTROL SYSTEM (ICS) HIGH DEMAND LIMITER FEEDWATER FLOW INCREASED CAUSING REACTOR COOLANT SYSTEM TAVE TO DECREASE. DUE TO A LARGE MODERATOR TEMPERATURE COEFFICIENT, REACTOR POWER INCREASED TO THE REACTOR PROTECTION SYSTEM HIGH FLUX TRIP SETPOINT. THE POST-TRIP PLANT RESPONSE WAS NORMAL EXCEPT THAT STEAM GENERATOR 1.1 PRESSURE WAS SLIGHTLY LOWER AND STEAM GENERATOR 1.2 LEVEL WAS HIGHER THAN THE EXPECTED POST TRIP RANGES. OPERATOR ACTIONS WERE REQUIRED TO CLOSE THE MOISTURE SEPARATOR REHEATER (MSR) SECOND STAGE REHEAT STEAM SOURCE VALVES AND TO STABILIZE STEAM GENERATOR 1.1 WATER LEVELS. THE LOSS OF INSTRUMENT AIR PRESSURE WAS CAUSED BY DIRECT VENTING OF THE INSTRUMENT AIR HEADER TO ATMOSPHERE WHEN A SOLENOID VALVE FAILED ON INSTRUMENT AIR DRYERS 1-1 AND 1-2. THIS SOLENOID VALVE WAS REPAIRED. THE MSR SECOND STAGE REHEAT STEAM SOURCE VALVES DID NOT CLOSE DUE TO A PRESSURE SWITCH FAILURE. THIS SWITCH WAS REPLACED. THE ICS DID NOT RESPOND FAST ENOUGH TO STEAM GENERATOR 1-1 DECREASING WATER LEVEL. A MODIFICATION TO THE ICS IS SCHEDULED.
346 | 3461988028 | 1988-12-17 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Davis-Besse | P | BW | PO | 28 | On December 17, 1988, the reactor was operating in mode 1 at approximately 28 percent power. The operators were increasing reactor power by increasing feedwater flow and reactor demand to come off of low-level limits. This caused Reactor Average Temperature to decrease. The Integrated Control System responded by withdrawing control rods. This combination of events increased indicated reactor power, resulting in a reactor trip on high flux at 0743 hours. Following the trip, a Turbine bypass valve failed open and increased the cooldown rate. The operators shut Main Steam Isolation Valve number 2 and reduced the cooldown rate. The cooldown was terminated within approximately 17 minutes. <br /><br />The apparent cause of this occurrence was failure to establish high flux trip setpoints appropriate for coming off low level limits and the calibration error between heat balance power and indicated reactor power. Requirements for preevaluation briefings will be incorporated in the conduct of Operations Procedure DB-OP-00000 by March 31, 1989. A modification to the turbine bypass valve is being considered for implementation during a forthcoming planned maintenance outage to minimize water accumulation which contributed to the turbine bypass valve failure.
346 | 3461989003 | 1989-01-18 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Davis-Besse | P | BW | PO | 100 | On January 18, 1989, at 1344 hours, with Control Rod Drive (CRD) trip breaker testing in progress, the reactor tripped from 100 percent Rated Thermal Power (RTP). The trip was initiated by a spurious CRD Trip Confirm Signal which caused the Integrated Control System (ICS) to initiate the Rapid Feedwater Reduction (RFR). This resulted in feedwater flow being reduced to about six percent while the Reactor was still at 100 percent. This caused the Reactor Coolant System (RCS) pressure to increase rapidly until it reached the high pressure trip setpoint of 2300 psig where the Reactor Protection System (RPS) tripped the reactor. The post-trip response of the plant was normal with no major problems. <br /><br /> The cause of the spurious CRD Trip Confirm Signal was narrowed to at least one of three logic boards in the CRD Systems Logic Cabinet No. 1. The boards will be returned to the vendor for troubleshooting. If anything other than a random component failure is determined, a revision to this report will be issued. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(iv) as an automatic actuation of RPS.
346 | 3461989005 | 1989-05-30 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Davis-Besse | P | BW | PO | 100 | On May 30, 1989, Davis-Besse experienced a reactor trip from 100 percent power. The event began as a trip of the main turbine due to loss of condenser vacuum when the Circulating Water (CW) Pumps 2 and 4 tripped on high phase differential current. The post-trip response of the plant was good. The cause of the high differential current was in a failed splice in one phase of a 13.8KV feeder cable which was sensed by the protective relaying for the Cw pumps. The failed splice was removed for determination of cause. The failure of the splice was determined to be caused by improper installation.<br /><br /> With the faulty load cable isolated from the 13.8KV bus, the Plant was restarted and brought back on line by 1530 hours on May 31, 1989.
346 | 3461990002 | 1990-01-26 | QR8 | Spurious Reactor Trip | [45 empty] | Davis-Besse | P | BW | PO | 73 | On January 26, 1990, at 0846 hours, during performance of Surveillance Test DB-MI-03205, RCP Current Monitor Inputs to SFRCS ACH1 and RPS Channel 1, the Station experienced a reactor trip from 73 percent full power. Prior to the trip, the Station had been operating with three of the four RCPs running. Plant response to the trip was normal with key parameters remaining in the normal post-trip band. Steam generator header pressure was intentionally reduced to approximately 970 psig to aid in fully reseating two main steam safety valves solidly. After stabilization of the plant, the Letdown Isolation Valve, MU2B, would not reopen. The inability to restore the letdown flow resulted in slower than normal plant cooldown and Mode 5 was achieved of January 27, 1990, at 0345 hours.<br /><br /> Immediate notification was made per 10CFR50.72(b)(2)(ii) on January 26, 1990, at 1007 hours. The reactor trip is reportable as an LER per 10CFR50.73(a)(2)(iv). <br /><br /> An action plan implemented to determine the cause of the RCP current monitor circuit transient concluded that there were two major factors. They were the inadequacy of the test switches to provide current isolation and the use of a standard isolation plug which results in unintended forces on the knife switch which carries the bypass current. <br /><br /> The cause of MU2B failure was determined to be thermal binding of the disc in the valve seat. The valve was replaced with a fully flexible wedge gate valve under MWO 2-89-0053-00. A similar failure occurred with RC-11, PORV Block Valve, during restart. It was replaced under MWO 1-90-1368-03.
346 | 3461990016 | 1990-12-13 | QR3 | Reactivity Control Imbalance | [45 empty] | Davis-Besse | P | BW | PO | 100 | On December 13, 1990 at 0844 hours, the plant experienced a Reactor Coolant System (RCS) low pressure trip. A functional test of the Reactor Protection System (RPS) Channel 1 Reactor Trip Module Logic and Reactor Trip Breaker B was in progress when the trip occurred. Reactor Trip Breaker B had been previously tripped as part of the RPS functional test. Seven of eight control rods in Rod Group 7 dropped into the core causing reactor power to initially decrease to approximately 48 percent. RCS pressure and temperature decreased due to a resulting mismatch between reactor power and feedwater flow. RPS subsequently tripped the reactor on low RCS pressure. The cause of the Group 7 rod drop was determined to be a failed contact in a motor return Silicon Controlled Rectifier (SCR) gating signal blocking relay for the "A" side power train of the Control Rod Drive (CRD) System. Plant response to the reactor trip was normal with key parameters remaining in the normal post-trip band.<br /><br /> Immediate notification was made per 10CFR50.72(b)(2)(ii) on December 13, 1990, at 0944 hours. The reactor trip is being reported pursuant to the requirements of 10CFR50.73(a)(2)(iv).
346 | 3461992002 | 1992-03-01 | QR8 | Spurious Reactor Trip | [45 empty] | Davis-Besse | P | BW | PO | 40 | On March 1, 1992, at 1500 hours, the plant experienced a reactor trip from approximately 40 percent power. The reactor trip was initiated by an I&C technician troubleshooting the rewiring of the main turbine vacuum trip system. While checking the condition of the main turbine vacuum pressure switches, the technician incorrectly placed a short across the high exhaust hood temperature trip contact. This resulted in an Anticipatory Reactor Trip System trip of the reactor. <br /><br /> Failure of the position feedback arm on Turbine Bypass Valve (TBV) SP13B2 resulted in the valve failing open causing a slight post-trip overcooling of the Reactor Coolant System (RCS). Operator initiated actuation of the Steam and Feedwater Rupture Control System at 1503 hours terminated the RCS overcooling. <br /><br /> I&C Maintenance personnel will review this LER and receive training by June 26, 1992. Maintenance corrective actions associated with the main turbine vacuum trip circuitry were completed prior to plant startup. Repairs to the failed TBV were completed on March 2, 1992. The four remaining TBVs of the style that failed are scheduled for replacement during 8RFO. Corrective actions related to work control issues include procedure changes, required reading, and training of appropriate personnel.
346 | 3461993003 | 1993-05-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Davis-Besse | P | BW | PO | 100 | On May 20, 1993, at 1138 hours, the plant experienced a trip from approximately 102% power. Loss of continuity between a fuse and fuseholder resulted in a loss of power to an auxiliary relay in the Non-Nuclear Instrumentation (NNI) System. This caused a loss of the selected RCS average temperature (Tave) input to the Integrated Control System (ICS). The ICS Tave input failed to zero VDC indicating that the RCS average temperature was approximately 570 degrees F. Normal RCS average temperature is 582 degrees F. To compensate, the ICS Tave integral increased Reactor Demand, withdrawing control rods and increasing reactor power. In an attempt to reduce reactor power, operators took manual control of ICS and decreased the Steam Generator/Reactor Demand signal. The primary reactor operator overreacted and lowered demand too far. Primary to secondary heat flow became unbalanced as feedwater flow followed the lowered demand, but reactor power did not decrease due to the low Tave input. As feedwater flow decreased, RCS pressure increased. The reactor tripped on high RCS pressure. <br /><br /> The faulty fuse cap and fuse were replaced and other NNI fuse holders and fuses were inspected. The plant was returned to service on May 21, 1993 at 1308 hours.
346 | 3461993005 | 1993-10-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Davis-Besse | P | BW | PO | 100 | On October 8, 1993, at 0843 hours, with Control Red Drive (CRD) trip breaker testing in progress, the reactor tripped from 97 percent Rated Thermal Power (RTP). The trip was initiated by a momentary CRD Trip Confirm signal which caused the Integrated Control System (ICS) to initiate the Rapid Feedwater Reduction (RFR) and Main Feedwater Block Valve (MFWBV) closure. This resulted in feedwater flow being reduced by approximately forty percent while the Reactor was still at full power. The feedwater flow upset caused the Reactor Coolant System (RCS) pressure to increase rapidly until it reached the high pressure trip setpoint where the Reactor Protection System (RPS) tripped the reactor. The post-trip response of the plant was normal with no major problems.<br /><br /> The momentary CRD Trip Confirm Signal was caused by a degraded power supply in the CRD System Logic Cabinet No. 1. Excessive Alternating Current (AC) ripple on the Direct Current (DC) power supply output caused a CRD logic protection circuit to change state and actuate the CRD Trip Confirm Signal. The degraded power supply and CRD logic protection circuit were replaced prior to restart.
346 | 3461997010 | 1997-05-04 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Davis-Besse | P | BW | PO | 100 | On May 4, 1997, at 1731 hours, with the plant at 100 percent power, the Main Transformer Deluge System automatically actuated due to a degraded temperature sensor in the transformer fire detection system. At 1735 hours, a flashover occurred when the Main Transformer faulted to ground due to the deluge system actuation. The Main Generator locked out on overall differential current, which initiated a trip of the Main Turbine and a subsequent reactor trip by the Anticipatory Reactor Trip System. The plant was cooled down to replace the Main Transformer that was damaged as a result of the flashover. The temperature sensors that actuate the deluge system have been replaced with a different type of temperature sensor to prevent inadvertent actuation, and four nozzles near the top of the transformer have been realigned to reduce the chances of a transformer flashover upon a deluge system actuation. This event is being reported in accordance with 10CFR50.73(a)(2)(iv).
346 | 3461998002 | 1998-04-10 | QR6 | Manual Reactor Trip | [45 empty] | Davis-Besse | P | BW | PO | 31 | On April 10, 1998, at 2000 hours, with the plant operating at approximately 72 percent power, a scheduled plant shutdown was initiated. At 2124 hours, Makeup and Purification Demineralizer (PD) #3 was placed in service. Makeup Filter (MUF) differential pressure alarms were received in the Control Room shortly thereafter. In response, the MUF in service was swapped with the standby filter. Following additional alarms, the letdown system was isolated, and a rapid plant shutdown was initiated. Due to the letdown flowpath being isolated, Pressurizer (PZ) level increased, and at 2231 hours, the reactor was manually tripped from 31 percent power due to PZ level exceeding the maximum administrative level of 290 inches. The manual trip was required by high PZ level due to filter restrictions and loss of letdown capability. A cause analysis concluded the filter restrictions resulted from corrosion failure of PD #3 internal screens that allowed resin release into downstream piping. The screens were repaired in March 2002, and a resin control program was implemented in June 2003. Initial notification to the NRC was made at 2327 hours on April 10, 1998, in accordance with 10CFR 50.72(b)(2)(ii). This Licensee Event Report is being submitted in accordance with 10CFR 50.73(a)(2)(iv)(A), an event that resulted in manual actuation of the Reactor Protection System.
346 | 3461998006 | 1998-06-24 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Davis-Besse | P | BW | PO | 100 | On June 24, 1998, at approximately 2040 hours, with the unit in Mode 1 at 99 percent power, a storm cell moved through the site area, and, at approximately 2044 hours, a tornado touched down onsite. The Emergency Diesel Generators were both manually started when the Control Room received a report of a tornado on site. The damage from the tornado, accompanying straight-line winds, rain and lightning, resulted in a complete loss of offsite power (LOOP). The LOOP caused the turbine control valves to close in response to a load rejection by the main generator. The Reactor Protection System (RPS) initiated a reactor trip on high Reactor Coolant System (RCS) pressure. At 2118 hours, an Alert was declared in accordance with procedure RA-EP-01500, Emergency Classification, Emergency Action Level (EAL) 8.B.2, Any tornado striking facility. Following restoration of an offsite power source, the Alert was downgraded to an Unusual Event at 0200 hours on June 26, 1998, and at 1405 hours, the Unusual Event was terminated. The tornado resulted in significant damage to the offsite electrical distribution system, telecommunications, power to the sirens and other unfortified structures. Immediate corrective actions involved the testing and repairing of the affected electrical and mechanical equipment necessary to restore two offsite power sources and assessing damage to other plant components and structures and initiating repairs. Plant telecommunications were restored and the siren system was returned to 90 percent availability prior to plant startup. There were no adverse effects to the public health or safety. Davis-Besse Nuclear Power Station Unit 1 startup was initiated, with reactor criticality reached on July 1, 1998, at 2257 hours, but was shutdown due to elevated sulfate levels in the steam generator water chemistry on July 2, 1998. Following steam generator fill, soak and drains, startup was initiated on July 5, 1998, and at 0400 hours on July 7, 1998, the Main Generator was synchronized to the grid.
346 | 3461998010 | 1998-09-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Davis-Besse | P | BW | PO | 100 | On September 24, 1998, at 1401 hours with the plant at 100 percent power, during testing of the Steam Feedwater Rupture Control System (SFRCS), the position indicating light for a Main Feedwater Control Valve to Steam Generator (SG) 1 solenoid valve did not illuminate after the test trip switches were released. Troubleshooting erroneously determined the limit switch internal to the solenoid valve had failed, when in actuality the solenoid valve failed to properly reset. At 2200 hours, testing on the complimentary SFRCS logic channel repositioned the complimentary channel solenoid valve. This combined with the solenoid valve failure resulted in closure of the Main Feedwater Control Valve to SG 1. The reactor was manually tripped by the control room operator after observing closure of the Main Feedwater Control Valve to SG 1. The failed solenoid valve has been replaced, and training has been conducted regarding the misdiagnosis that occurred during troubleshooting of the solenoid valve failure. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in manual actuation of the Reactor Protection System.
346 | 3461998011 | 1998-10-14 | C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) |  |  | X | [13 empty] | X | [28 empty] | Davis-Besse | P | BW | PO | 87 | On October 14, 1998, at 1523 hours, with the Davis-Besse Nuclear Power Station operating in Mode 1, at 87 percent rated thermal power, the plant was manually tripped. Previously on October 14, at 1356 hours, the plant was operating at 100 percent power, when electrical busses D1 and D2 experienced a lockout. As a result of the loss of a condensate pump and several other plant loads powered by these busses, thermal power was reduced to 87 percent. When the lockout occurred, Component Cooling Water (CCW) Pump 1-2 stopped. When CCW Pump 1-1 automatically started, a CCW system leak developed that was determined to be located inside the containment. When CCW pump 1-2 was restarted, the CCW Surge Tank level decreased rapidly. At a surge tank level of 35 inches and decreasing, plant operators tripped the Reactor, and the Reactor Coolant Pumps in accordance with plant procedures. During the trip recovery, a makeup pump failed to start on demand, and a plant overcooling occurred. The cause of the CCW leak was failure of one letdown cooler rupture disk. All of the letdown cooler rupture disks were replaced prior to plant restart. This event was reported to the Nuclear Regulatory Commission (NRC) within four hours via the Emergency Notification System at 1750 hours on October 14, 1998 as an event that resulted in manual actuation of the Reactor Protection System (RPS) in accordance with 10CFR50.72(b)(2)(ii). This report is being submitted in accordance with 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(iv).
346 | 3461998012 | 1998-10-18 | QR8 | Spurious Reactor Trip | [45 empty] | Davis-Besse | P | BW | SU | 4 | At 2152 on October 18, 1998, with the plant in MODE 2, a reactor trip occurred from approximately four (4) percent power due to an Anticipatory Reactor Trip System (ARTS) signal. The ARTS signal was initiated while a control room operator was placing the ARTS channel 1 test trip bypass switch to normal after placing the number 2 Main Feed Pump in-service. This action completed the trip logic for ARTS channels 2, 3, and 4, resulting in a trip signal to three of the four control rod drive trip breakers. The initial investigation of this event determined that the apparent cause of this event was an inadequate design drawing resulting in an inadequate procedure. The procedure was revised to correct the perceived inadequacy. Further investigation revealed that this event resulted from non-installed wires on the spare position of all four ARTS Test Trip Bypass Switches. Initial notification of this reactor trip was made to the NRC at 2358 on October 18, 1998, in accordance with the four-hour reporting requirements of 10CFR50.72(b)(2)(ii). This report is being submitted in accordance with 10CFR50.73(a)(2)(iv).
346 | 3462004002 | 2004-08-04 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Davis-Besse | P | BW | PO | 100 | On August 4, 2004, at 1023 hours with the plant at approximately 100 percent power, surveillance testing was in progress on the Reactor Trip Breakers. When Reactor Trip Breaker "B" was opened in accordance with the test procedure, a reactor trip occurred unexpectedly due to the simultaneous opening of the Reactor Trip Breaker "A." Reactor Trip Breaker "A" opened due to a fuse that had failed prior to the test in a circuit designed to open the breaker when an undervoltage condition is detected. When Reactor Trip Breaker "B" was opened in accordance with the test procedure, both inputs to the Source Interruption Device indicated an undervoltage condition, initiating a trip of Reactor Trip Breaker "A" and a subsequent trip of the reactor. No procedural check existed to check the status of the existing failed fuse indicator lights prior to simulating a trip of the Reactor Trip breakers. The fuse was determined to have failed due to age and fatigue. The failed fuse along with the other three similar fuses in the Reactor Trip Breaker circuitry were replaced, and the four Reactor Trip Breaker Surveillance Tests were revised to require verification of fuse indication prior to performing the test. This event is being reported in accordance with the 10CFR50.73(a)(2)(iv)(A) as an event that resulted in actuation of the Reactor Protection System.
346 | 3462006003 | 2006-09-06 | QL7 | Degraded condenser vacuum | [45 empty] | Davis-Besse | P | BW | PO | 45 | On September 6, 2006, at 0137 hours with the plant at approximately 100 percent power, control room operators noticed rapidly rising condenser pressure. The operators commenced lowering reactor power in accordance with plant abnormal procedures, but could find no obvious cause for the increased pressure. When reactor power was reduced to approximately 45 percent power and condenser pressure remained above permitted values for continued operation, the reactor and main turbine were manually tripped at 0231 hours in accordance with procedures. Subsequent investigation determined the cause of the high condenser pressure to be air in-leakage from a broken low pressure turbine bearing waste water and oil drain pipe that is routed through the condenser. This pipe appeared to have failed as a result of cyclic fatigue that caused a complete shear of the drain pipe inside the condenser. The failed piping was plugged/capped at both ends, and the plant was returned to power operations. This report is being submitted in accordance with the 10CFR50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the Reactor Protection System.
346 | 3462013001 | 2013-06-29 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Davis-Besse | P | BW | PO | 100 | On June 29, 2013, at 2120 hours, with the Davis-Besse Nuclear Power Station'operating at approximately 100 percent power, the Reactor Coolant Pump (RCP) Motor 1-2 tripped due to actuation of a differential trip relay in the motor source breaker. This resulted in a reactor trip at 2122 hours from the Reactor Protection System on Flux/Delta-Flux/Flow. Investigation determined the cause of the RCP motor trip to be a failure in the current transformer (CT) circuit. A screw on the RCP Motor 1-2 CT terminal block had a stress/fatigue related failure which caused the wire to detach in the CT circuitry causing an open circuit and actuation of the differential trip. The investigation also found degraded wiring in the CT circuit because it was touching the high voltage buss bar insulation in the RCP motor termination box and experienced degradation caused by corona discharge. The CT wiring and terminal block including all screws were replaced. The screws were replaced with a different type of material. Procurement documents will be revised to ensure replacement hardware is of appropriate quality to meet ANSI standards. The CT wiring, terminal blocks and screws in all four RCPs will be inspected during the next scheduled outage. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of the Reactor Protection System.
346 | 3462015002 | 2015-05-09 | QR6 | Manual Reactor Trip | [45 empty] | Davis-Besse | P | BW | PO | 100 | On May 9, 2015, with the Davis-Besse Nuclear Power Station (DBNPS) operating in Mode 1 at approximately 100 percent power, a steam leak was identified in the Turbine Building. A rapid shutdown was initiated, and the reactor was manually tripped at 1909 hours from approximately 30 percent power. The Steam Feedwater Rupture Control System was manually initiated to isolate the leak and start the Auxiliary Feedwater System. The cause of the leak was failure of a four-inch pipe in the Moisture Separator Reheater System due to Flow Accelerated Corrosion (FAC). An incorrect data input caused the FAC software model to underestimate the predicted wear rate, so inspections were not performed to identify the piping wall thinning prior to failure. Additionally, a previous event was not evaluated to ensure the proposed corrective actions would encompass a validation of all critical data inputs. Corrective Actions include improvements in the fidelity of the data in the FAC Software model, and improvements in the Corrective Action Program with respect to Root Cause Evaluations.<br /><br /> This issue is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of the Reactor Protection System and the Auxiliary Feedwater System.
346 | 3462016001 | 2016-01-29 | QR8 | Spurious Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Davis-Besse | P | BW | PO | 100 | On January 29, 2016 at 1322 hours, with the Davis-Besse Nuclear Power Station operating at approximately 100 percent power, an automatic reactor trip occurred due to the actuation of the Reactor Protection System (RPS). Nuclear Instrumentation calibration for RPS Channel 2 was in progress. RPS Channel 2 was in bypass and Channel 1 was inoperable/tripped due to an existing Reactor Coolant System (RCS) temperature element (RTD) issue. A fuse failure in an input to RPS Channel 4 caused RPS Channel 4 trip on Flux/Delta-Flux/Flow, resulting in the reactor trip. Post trip, the Steam Feedwater Rupture Control System (SFRCS) actuated due to high Steam Generator (SG) 1 level, initiating the Auxiliary Feedwater (AFW) System. The cause of the SFRCS actuation was an improper response by the Integrated Control System (ICS) after the reactor trip. ICS Rapid Feedwater Reduction (RFR) circuit did not actuate and the ICS SG/Reactor Demand Hand/Auto Station transferred from automatic control to manual. <br /><br /> Corrective actions include: RPS Channel 4 power failed fuse replaced, RCS RTD replacement next refueling outage, ICS RFR switch module replaced, ICS Hand/Auto Station modification. This report is being submitted as an event that resulted in automatic actuation of the RPS, and an automatic actuation of AFW per 10CFR50.73(a)(2)(iv)(A).
346 | 3462016009 | 2016-09-10 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Davis-Besse | P | BW | PO | 100 | On September 10, 2016, with the Davis-Besse Nuclear Power Station (DBNPS) operating at approximately 100 percent power, rainwater intrusion into the Main Generator Automatic Voltage Regulator (AVR) cabinet due to an open roof vent caused a lockout of the Main Generator, resulting in a trip of the Main Turbine and Reactor. Following the Reactor trip, the Steam Feedwater Rupture Control System (SFRCS) actuated due to high Steam Generator 1 level and initiated the Auxiliary Feedwater System. The most probable cause of the SFRCS actuation was a failed operational amplifier in the Integrated Control System (ICS), causing the ICS to not reduce Feedwater flow to Steam Generator 1 following the Reactor trip. <br /><br /> Completed corrective actions include closing the roof vents, sealing the top of the AVR cabinet, improved configuration control of the vents, and replacement of the failed ICS module. Scheduled corrective actions include presenting a case study to improve recognition of elevated risk issues, and review of the ICS by a multi-functional team to address system performance concerns.<br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of the Reactor Protection System, and an automatic actuation of the Auxiliary Feedwater System.
346 | 3462019003 | 2019-09-07 | QR5 | Turbine Trip | [45 empty] | Davis-Besse | P | BW | PO | 95 | On September 7, 2019, with the Davis-Besse Nuclear Power Station operating at approximately 95 percent power, during scheduled Main Turbine Stop Valve 2 (MSV) testing, Main Turbine Stop Valve 4 unexpectedly stroked closed and Anticipatory Reactor Trip System (ARTS) actuated, tripping the reactor. <br /><br /> The most likely cause of the MSV 4 closure was mechanical binding / sticking or foreign material in the internals of the valve operating system (fast acting solenoid valve) causing its inadvertent actuation. <br /><br /> Actions taken include replacing and testing the MSV 4 fast acting solenoid valve and testing ARTS. Scheduled actions include replacing similar components on the other MSVs, and cleaning the EHC fluid sump, replacing the EHC fluid and particulate strainers. <br /><br /> This issue is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A).
346 | 3462020002 | 2020-03-25 | QR6 | Manual Reactor Trip | [45 empty] | Davis-Besse | P | BW | SU | 0 | On March 25, 2020, with the Davis-Besse Nuclear Power Station starting up from a refueling outage in Mode 2 at approximately zero (0) percent power in the Intermediate Range, the control room operators received a plant computer trouble alarm and low voltage indication for the 13.8 kV B Bus. As a result of this indicated power loss on B Bus, the two (2) Reactor Coolant Pumps powered from this bus tripped. The operators subsequently manually tripped the reactor at 1240 hours and performed actions to stabilize Reactor Coolant System temperature and pressure. Plant response to the reactor trip was uncomplicated and decay heat removal through normal feedwater and main condenser remained available and the plant remained in Mode 3.<br /><br /> The most likely cause of the fuse failure (and subsequent manual reactor trip) is that the replacement fuses installed and specified by a 2014 equivalency evaluation were not appropriate for this fuse application. Actions taken include replacing the B Bus fuses. Scheduled actions include determining a more appropriate fuse for this and similar applications and replacing identified fuses. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of the Reactor Protection System.
346 | 3462021003 | 2021-07-08 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Davis-Besse | P | BW | PO | 100 | On July 8, 2021, with the Davis-Besse Nuclear Power Station operating at approximately 100 percent power, an automatic reactor trip occurred due to de-energization of Motor Control Centers caused by a breaker failure during planned testing. The simultaneous failure of an uninterruptible power supply (UPS) caused a loss of power to the Main Generator Automatic Voltage Regulator (AVR), resulting in a Generator lockout and trip of the Main Turbine and Reactor. Following the Reactor trip, overcooling was observed due to loss of power to a Moisture Separator Reheater steam source valve, and operators manually initiated Emergency Core Cooling Systems (ECCS) per procedure. The Steam and Feedwater Rupture Control System (SFRCS) actuated on low Steam Generator (SG) 1 level, starting the Auxiliary Feedwater System. During post-trip response, SG 2 low pressure was experienced while transferring Gland Steam Supply, actuating SFRCS to isolate Main Feedwater and close the Main Steam Isolation Valves. <br /><br />The cause of the reactor trip was inadequate review for impact on the UPS when selecting it as a power source during AVR installation. The cause of the subsequent SFRCS actuation was failure of the Gland Steam Seal feed valve pneumatic actuator. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as automatic actuations of the Reactor Protection and Auxiliary Feedwater Systems, and manual actuation of ECCS.
348 | 3481987002 | 1987-01-08 | QL5 | Partial Closure of MSIVs | [45 empty] | Farley 1 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 0649 ON 1-8-87, THE REACTOR TRIPPED DUE TO THE MANUAL TRIPPING OF THE MAIN TURBINE. AT APPROXIMATELY 0630, THE UNIT OPERATOR HAD OBSERVED A MAIN STEAM LINE ISOLATION VALVE (MSIV) POSITION INDICATOR WITH DUAL INDICATION. AN ATTEMPT TO FULLY OPEN THE MSIV BY MOVING THE MSIV HANDSWITCH TO THE OPEN POSITION WAS UNSUCCESSFUL. THE DECISION WAS MADE TO TRIP THE UNIT. THE UNIT WAS STABILIZED IN MODE 3 (HOT STANDBY). THIS EVENT WAS CAUSED BY AN AIR LEAK FROM A CRACKED AIR SUPPLY LINE TO THE MSIV. THE CRACK DEVELOPED WHEN THE MAIN STEAM LINE THERMAL GROWTH DURING HEAT-UP CAUSED AN INTERFERENCE BETWEEN THE AIR LINE AND A RIGID TUBING SUPPORT. THE ROOT CAUSE FOR THE FAILURE WAS THAT INADEQUATE CLEARANCE FOR THE MAIN STEAM LINE WAS ALLOWED DURING PLACEMENT OF THE TUBE SUPPORT. THE AIR LINE WAS REPLACED, THE TUBING SUPPORT WAS NOTCHED, AND THE UNIT WAS RETURNED TO SERVICE AT 0800 ON 1-9-87.
348 | 3481987003 | 1987-01-09 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Farley 1 | P | WE | PO | 27 | POWER LEVEL - 027%. AT 0936 ON 1-9-87, WITH THE UNIT AT 27% AND RAMPING UP FOLLOWING A UNIT SHUTDOWN, THE REACTOR TRIPPED DUE TO LO-LO STEAM GENERATOR LEVEL FOLLOWING THE MANUAL TRIPPING OF THE MAIN TURBINE. THE MAIN TURBINE WAS TRIPPED IN ACCORDANCE WITH FNP-0-AOP-13 (LOSS OF MAIN FEEDWATER) BECAUSE BOTH STEAM GENERATOR FEED PUMPS (SGFPS) HAD TRIPPED DUE TO LOW SUCTION PRESSURE. THE UNIT WAS STABILIZED IN MODE 3 (HOT STANDBY). THE REACTOR TRIP WAS CAUSED BY PERSONNEL ERROR IN THAT THE OPERATORS AND SHIFT SUPERVISOR FAILED TO ADEQUATELY MONITOR THE SGFP SUCTION PRESSURE AND TAKE APPROPRIATE ACTION TO PREVENT SGFP SUCTION PRESSURE FROM DECREASING BELOW THE TRIP SETPOINT FOR SGFPS. THE APPROPRIATE UNIT OPERATING PROCEDURES HAVE BEEN REVISED TO REMIND THE OPERATORS TO MONITOR SGFP SUCTION PRESSURE. THE UNIT WAS RETURNED TO SERVICE AT 1616 ON 1-9-87.
348 | 3481987004 | 1987-01-22 | QR8 | Spurious Reactor Trip | [45 empty] | Farley 1 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 1218 ON 1-22-87, WITH THE UNIT OPERATING AT 100% POWER, A REACTOR TRIP OCCURRED DUE TO HIGH FLUX RATES INDICATED BY POWER RANGE NUCLEAR INSTRUMENTATION CHANNELS N-41 AND N-42. THE HIGH FLUX RATE ON N-42 WAS DUE TO TESTING WHICH WAS IN PROGRESS AT THE TIME. THE HIGH FLUX RATE ON N-41 WAS CAUSED BY THE FAILURE OF THE 1A INVERTER WHICH SUPPLIES POWER TO N-41. TESTING OF N-42 WAS COMPLETED AND N-42 WAS RETURNED TO SERVICE. THE BACKUP POWER SUPPLY FOR N-41 WAS PLACED INTO SERVICE. THE UNIT RETURNED TO POWER OPERATION ON 1-23-87. SUBSEQUENTLY, THE 1A INVERTER WAS TESTED AND FOUR BLOWN FUSES WERE REPLACED. NO CAUSE FOR THE BLOWN FUSES COULD BE FOUND. THE INVERTER WAS RETURNED TO SERVICE.
348 | 3481987010 | 1987-05-14 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Farley 1 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 1045 ON 5-14-87, WITH THE UNIT OPERATING AT 100% REACTOR POWER, THE REACTOR TRIPPED DUE TO STEAM FLOW GREATER THAN FEEDWATER FLOW COINCIDENT WITH LOW STEAM GENERATOR LEVEL. SURVEILLANCE TESTING WAS IN PROGRESS ON THE 1-2A DIESEL GENERATOR AND THE DIESEL GENERATOR WAS CONNECTED TO THE 1F 4160 VOLT BUS. UPON COMPLETION OF THE SURVEILLANCE, THE OPERATOR INTENDED TO OPEN THE DIESEL GENERATOR OUTPUT BREAKER. HOWEVER, HE INADVERTENTLY OPENED THE BREAKER WHICH SUPPLIES POWER TO THE 1H 4160 VOLT BUS. THIS CAUSED DEENERGIZATION OF THE LOAD CENTER WHICH POWERS THE AC OIL PUMPS FOR BOTH STEAM GENERATOR FEED PUMPS. THE DC OIL PUMPS FOR BOTH STEAM GENERATOR FEED PUMPS STARTED AND PROVIDED OIL TO THE FEED PUMPS' BEARINGS. BY DESIGN, THE DC OIL PUMPS DO NOT SUPPLY CONTROL OIL. THUS, THE STEAM GENERATOR FEED PUMPS TRIPPED. THE LOSS OF FEEDWATER FLOW LED TO THE REACTOR TRIP. THIS EVENT WAS CAUSED BY PERSONNEL ERROR. THE INDIVIDUAL INVOLVED IN THIS EVENT HAS BEEN COUNSELED.
348 | 3481988021 | 1988-10-21 | QR5 | Turbine Trip | [45 empty] | Farley 1 | P | WE | PO | 100 | At 1234 on 10-21-88, with the unit operating at 100% power, the reactor tripped due to a turbine trip. The turbine tripped due to inadvertent injection of a maintenance diagnostic card (QDT) test signal which vas sensed as an overspeed protection system fault condition. This occurred during troubleshooting of the turbine speed input channel 2 of the digital electro-hydraulic control (DEHC) system. While inserting the ODT in the speed channel card chassis, an erroneous data input condition was inadvertently created which was sufficient to cause a data communications failure on both overspeed protection (OPC) processors. The DEHC DC power failure relay subsequently deenergized and the turbine tripped. This event was caused by personnel error. The mode selector switch on the ODT was inadvertently placed in the simulate position while the card was being inserted. With this switch in the simulate position, a test signal was injected which was sensed as an overspeed protection system fault condition and a turbine trip was generated. This event has been discussed with the personnel responsible for maintenance of the DEHC computer system. The simulate mode function of the ODT will be disabled so that inadvertent positioning of the mode selector switch will not cause an input during on-line testing. <br /><br />The unit returned to power operation on 10-22-88 at 1619.
348 | 3481989006 | 1989-11-12 | QR7 | Other Reactor Trip (Valid RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Farley 1 | P | WE | PO | 34 | At 1658 on 11-12-89, with the unit operating at 34% power, a safety injection and reactor trip were initiated due to low steam line pressure. Troubleshooting of an oscillation in the #3 turbinegenerator governor valve was in progress. As part of troubleshooting this problem, a circuit card that controls the #3 governor valve was replaced with an improperly configured card. This caused the digital electro-hydraulic control (DEHC) system to open all three of the other governor valves. This in turn resulted in a decrease in steam line pressure. The rate of decrease caused the rate sensitive feature of the low steam line pressure safety injection to actuate an automatic safety injection and reactor trip. A Notification of Unusual Event was declared at 1658. The Notification of Unusual Event was terminated at 1900. <br /><br /> This event was caused by cognitive personnel error. The circuit card that was installed for the #3 governor valve had been configured for the #4 governor valve. <br /><br /> The person involved has been counseled. As a further enhancement, when troubleshooting the DEHC system during power operation, the governor valve position limiter will be restricted to limit the amount of valve opening. <br /><br /> This LER also provides the Special Report information required by Technical Specification 3.5.2.
348 | 3481990005 | 1990-07-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Farley 1 | P | WE | PO | 100 | At 2218 on 07-20-90, with the unit operating at 100% power, the reactor was tripped manually following the automatic trip of the 1A steam generator feed pump (SGFP). The 1A SGFP turbine tripped on overspeed due to the failure of the speed sensor converter. The reactor was tripped manually in anticipation of an automatic reactor trip. The unit was stabilized in Mode 3 (Hot Standby). <br /><br /> The unit returned to power operation at 0446 on 07-24-90.
348 | 3481991006 | 1991-05-24 | QR8 | Spurious Reactor Trip | [45 empty] | Farley 1 | P | WE | PO | 78 | At 0050 on 05-24-91, with the unit operating at approximately 78 percent power, a reactor trip occurred when the two-out-of-three coincidence was satisfied for over-temperature-delta-temperature (OTDT). Work in progress on pressurizer pressure instrument PT456 required channel II of OTDT to be placed in the tripped condition. During the same time period, a portable instrument was attached to what was believed to be a spare resistance temperature detector (RTD) in channel I to support an unrelated test. However, the RTD was actually the one used by the OTDT channel. Attaching the test instrument to the RTD caused the second channel of OTDT to enter the tripped condition and the coincidence for a reactor trip was satisfied. <br /><br /> This event was caused by failure to request a drawing revision when a spare RTD was placed in service in 1977. Therefore, drawings used by the designer in the development of the 1991 RTD bypass removal design change did not show that a spare RTD had been placed in service. The post-modification test of the new RTD installation was not sufficiently thorough to detect this condition. <br /><br /> All the associated wiring has been verified to be in agreement with the current RTD bypass removal design change. The appropriate Maintenance and Plant Modifications personnel will be trained on this event.
348 | 3481991007 | 1991-06-29 | QR5 | Turbine Trip | [45 empty] | Farley 1 | P | WE | PO | 100 | At 2045 on 6-29-91, a Unit one reactor trip occurred. Two of the neutral overcurrent relays on the 1B unit auxiliary transformer (UAT) actuated resulting in a generator trip. By design, the generator trip caused the turbine to trip and the turbine trip caused the reactor to trip. <br /><br /> The low and high setpoint neutral overcurrent relays on the 1B UAT actuated as a result of an electrical fault. The fault was caused by a broken strand of a multiple stranded conductor coming into contact with the grounded core frame structure of the transformer. The multiple stranded conductor is located in the transformer oil box and connects the transformer winding to the transformer output bushing. <br /><br /> The conductor was repaired by removing the loose strand and reinsulating the conductor. The integrity of the conductor and crimp connection was verified prior to reinstallation of the insulation. <br /><br /> The 1B UAT was returned to service on 3-16-93 at 0227.
348 | 3481991008 | 1991-08-02 | QR8 | Spurious Reactor Trip | [45 empty] | Farley 1 | P | WE | PO | 100 | At 0001 on 8-2-91, with the unit operating at 100 percent power, an automatic reactor trip was initiated due to loss of power to reactor coolant pump (RCP) breaker position indication for 1C RCP breaker. This occurred when a systems operator (SO) reset a breaker which appeared to be tripped. This breaker supplies power to 120 volt regulated panel 1E which in turn provides power to the 1C RCP breaker position contact. Above 35 percent power a reactor trip is generated when an RCP breaker opens. Loss of power to the breaker position contact causes solid state protection to generate an RCP breaker reactor trip. The breaker supplying power to the 1C RCP breaker did not actually open. <br /><br /> This event was caused by cognitive personnel error. The control room plant operator granted permission to reset the breaker which provides power to 1C RCP breaker position indication contact without verifying the function of the breaker or determining the cause of the apparent tripped condition. <br /><br /> The personnel involved have been counseled. Also, this event will be included in the next cycle of licensed and nonlicensed operator retraining. <br /><br /> A caution label which reads "Opening this breaker may cause a reactor trip" has been placed on the four associated breakers in Unit 1 and the four associated breakers in Unit 2.
348 | 3481991009 | 1991-08-19 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Farley 1 | P | WE | PO | 100 | At 1720 on 08-19-91, while operating at approximately 100 percent power, a reactor trip occurred. A lightning induced deenergization of the 1B startup transformer (SUT) caused the loss of 1B and 1C reactor coolant pumps (RCPs). The reactor tripped due to RCP breakers opening while at 100 percent power. <br /><br /> A lightning strike in the 230KV switchyard caused an instantaneous overcurrent trip on phase 2 of the 1B SUT. The deenergization of the 1B SUT caused a loss of power at 4160V buses B and C which deenergized 1B and 1C RCP. The plant responded to the loss of B train offsite power as designed with the automatic start and tie-on of the 1B and 2C Diesel Generators (DG) to the B train Engineered Safety Feature (ESF) 4160V buses G and J. This restored power to the B train ESF equipment. A train offsite power was not lost during this event. <br /><br /> Inspection and testing of 1B SUT, the oil static cables and the associated switchyard breakers revealed a damaged phase 2 lightning arrestor located at the 1B SUT 230KV terminal. The damaged lightning arrestor was replaced, and the 1B SUT returned to service. <br /><br /> An engineering study to investigate possible methods of preventing lightning induced reactor trips has been initiated. <br /><br /> The unit returned to power operation at 0921 on 08-21-91.
348 | 3481991010 | 1991-10-03 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Farley 1 | P | WE | PO | 100 | At 0606 on 10-03-91, while operating at 100 percent power, the operators manually tripped the reactor in accordance with FNP-1-AOP-13, "Loss of Main Feedwater." <br /><br /> The sequence of events resulting in the manual reactor trip began with the main turbine control system's unexpected automatic closure of the main turbine governor valves. The operators responded by placing the main turbine digital electro-hydraulic control system (DEHC) in "Turbine Manual" which stopped the governor valves' closure at 15 percent open. The ensuing plant transient resulted in both steam generator feed pumps (SGFPs) tripping on low suction pressure. <br /><br /> This event was caused by a degraded DC voltage output from the primary Operator Auto Controller (OAC) power supply in the main turbine DEHC system and a failure of the circuitry which should have transferred the power supply. This degraded voltage resulted in a change of several control parameter values within the primary OAC prior to its complete failure. These degraded control parameters were passed to the back-up OAC which resulted in continued governor valve closure until the system was placed in manual by the operators. <br /><br /> The degraded power supply was replaced and the primary OAC programming was reloaded. A DEH Task Force is continuing the investigation of this failure and will evaluate corrective action to prevent recurrence.
348 | 3481992008 | 1992-12-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Farley 1 | P | WE | PO | 100 | On 12-13-92 at 0257, the Unit 1 reactor tripped on feedwater flow less than steam flow coincident with low steam generator water level on the C steam generator (SG). At the time of the trip, a monthly surveillance test procedure (STP) was in progress on C SG feedwater flow protection channel III. The prerequisites for this STP require verification of a two position main control board (MCB) handswitch to ensure the redundant channel (protection channel IV) provides an uninterrupted steam flow control signal input to the SG water level control circuitry during testing. In this case, the selector switch was already in the channel IV position and the operators verified the switch position as part of the STP prerequisites. The SG feedwater flow channel was successfully placed in test. The STP proceeded successfully until a channel III steam flow multiplier-divider (NMD) card was removed per procedure. When this card was removed, the steam flow signal to the C SG water level control circuitry was lost. The loss of the steam flow signal was the result of a control circuit relay in the Westinghouse 7300 control system failing to energize when the MCB selector switch for steam flow input was selected to the redundant channel (IV). The C SG steam flow signal provides input to the water level control circuitry for the C SG main feedwater flow control valve and also to the common feed pump speed control circuitry. With the loss of the steam flow input, feed pump speed control for both main feed pumps and the main feedwater flow control valve associated with the C SG became erratic. This resulted in oscillations in feedwater flow and steam generator level which eventually led to the reactor trip. The failure of the relay to energize was attributed to a cracked fuse on the control system relay card. The card was replaced, and the unit returned to power operations at 1152 on 12-14-92.
348 | 3481995001 | 1995-01-13 | QR5 | Turbine Trip | [45 empty] | Farley 1 | P | WE | PO | 100 | At 0758, on January 13, 1995 with Unit 1 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip in response to a loss of digital electro-hydraulic control (DEHC) overspeed protection. The primary overspeed protection (OPC) controller (DROP 2) failed in a manner which prevented the redundant OPC controller (DROP 52) from assuming control of the turbine DEHC overspeed protection function within the designed time frame. This resulted in a turbine trip due to a loss of both OPC controllers. <br /><br /> An investigation determined this event was most likely caused by the response of the DEHC OPC processors and their associated power supplies to minor voltage transients. An evaluation of the DEHC system design indicated a vulnerability of the DEHC system to minor voltage transients. Modifications have been performed to the DEHC system in order to reduce the vulnerability to minor voltage transients. <br /><br /> The unit was returned to power operation at 2203 on January 17, 1995.
348 | 3481995005 | 1995-06-11 | QL5 | Partial Closure of MSIVs | [45 empty] | Farley 1 | P | WE | PO | 100 | At 2139, on June 11, 1995 with Unit 1 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip in response to a spurious main steam line isolation valve (MSIV)[SB] closure. The main steam line isolation valve closure was attributed to water intrusion into a junction box located in the 1B motor driven auxiliary feedpump room. The water intrusion resulted in a short circuit across normally open relay contacts causing closure of the main steam line isolation valve. The water intrusion was a result of a room cooler which leaked water in the area of the junction box. Water accumulated on the electrical conduit entering the junction box and seeped into the junction box through a conduit connection. An inspection of the O-ring seal associated with the conduit connection indicated that the O-ring appeared to have been damaged during original installation. Similar Unit 1 junction boxes associated with the remaining MSIV's were inspected. <br /><br /> Additional Unit 1 junction boxes which may be potentially susceptible to water intrusion were inspected. Some evidence of previous moisture accumulation was noted. Identified discrepancies have been resolved. Unit 1 was cooled down to mode 5 for an inspection of the MSIV and no damage was evident. The MSIV actuator assembly did not reveal any discrepancies that would have contributed to a spurious closure. In addition, selected portions of the main steam piping and hangers were inspected and no damage was evident. <br /><br /> The unit was returned to power operation at 2315 on June 17, 1995.
348 | 3481998004 | 1998-09-09 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Farley 1 | P | WE | PO | 100 | On September 9, 1998, while operating in Mode 1 at 100% power, the Unit 1 reactor automatically tripped due to a main turbine trip. Additionally, both steam generator feed pumps (SGFPs) automatically tripped and a main feedwater isolation occurred. The cause of the trip was failure of a circuit card in solid state protection system (SSPS) train B. Failure of this card resulted in a spurious hi-hi steam generator water level signal. This condition directly caused a main turbine trip, both SGFP trips, and a main feedwater isolation. The main turbine trip resulted in an automatic reactor trip. The specific failure mechanism for this card is under investigation by the supplier. All other systems functioned as designed and plant response to the transient was as expected. The failed card was replaced. Unit 1 returned to power operation on September 10, 1998.
348 | 3481999002 | 1999-05-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Farley 1 | P | WE | PO | 92 | On May 27, 1999 at 08:55, with turbine load being reduced rapidly as a result of loss of the 1A Steam Generator Feed Pump (SGFP), FNP Unit 1 Reactor tripped on Overtemperature Delta T (OT Delta T). At 08:54:15, while attempting to swap the on service SGFP oil cooler, oil pressure to the SGFP was momentarily lost resulting in a trip of the SGFP. In response to the SGFP trip, the operator performed a rapid manual turbine load reduction. Control rods inserted in automatic; however, due to the magnitude of the power mismatch, Reactor Coolant System (RCS) temperature rose rapidly and resulted in the OT Delta T Reactor Trip setpoint being reached. A pressurizer Power Operated Relief Valve (PORV) lifted prior to the trip and then closed as designed. This event was due to personnel error by the operator performing an excessive load reduction. This was complicated by the failure of the steam dump system to respond as quickly as designed. The loss of main feedwater abnormal operating procedure has been enhanced to provide additional guidance for a loss of a SGFP event. Operations and licensed personnel have been made aware of these changes. These procedure changes will be covered during appropriate simulator training on response to scenarios involving loss of a SGFP.
348 | 3482000006 | 2000-05-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Farley 1 | P | WE | SU | 4 | On May 28, 2000 at 0545, with the reactor at 4% power, Unit 1 experienced an automatic reactor trip due to steam generator (SG) level reaching the low-low (lo-lo) level trip setpoint. At 0259 with the reactor at 14% power, the main turbine was manually tripped as part of planned maintenance to perform balancing. The turbine did not stop rolling as expected, and the decision was made to cycle the main turbine governor valves (GVs) to attempt to stop the turbine. The GVs were opened slightly in Turbine Manual mode, and then manually tripped. Following the turbine trip, low electrohydraulic (EH) control fluid pressure resulted in the only running steam generator feed pump (SGFP) losing speed and providing insufficient flow. The EH system is common to the SGFP turbines and the main turbine. Auxiliary feedwater (AFW) pumps were started and reactor power was rapidly reduced in accordance with plant procedures. SG levels had been stabilized with reactor power at 4% when cooldown caused the steam dumps to close. The resulting SG level shrink caused an automatic reactor trip on to-lo SG level. This event was caused by personnel error in that: 1) the governor valve cycling evolution was performed with inappropriate procedural guidance selection and use of Turbine Manual mode when Operator-Auto mode was the appropriate method; and 2) a prior software change to the turbine control system was prepared with inadequate documentation of its operational impact, leading to an inadequate procedure for operation in Turbine Manual mode. The event will be discussed with all licensed personnel, and all licensed personnel will be retrained on procedure use expectations by July 31, 2000. Personnel responsible for the digital electrohydraulic control (DEHC) system and software will be trained on expectations for software change package documentation by July 31, 2000. Applicable operating procedures have been changed to reflect the changed response of the EH system to a turbine trip when in Turbine Manual mode. Recent changes to DEHC software have been reviewed for additional operational impact and appropriate procedure changes have been made.
348 | 3482002001 | 2002-05-03 | QR8 | Spurious Reactor Trip | [45 empty] | Farley 1 | P | WE | PO | 100 | On May 3, 2002, with the reactor at 100% power, Unit 1 experienced an automatic reactor trip due to an indicated reactor coolant pump bus undervoltage on 2 of 3 busses. Undervoltage relays associated with "A" Reactor Coolant Pump (RCP) bus were in a tripped condition due to surveillance testing in progress. While reconnecting power leads to the neutron flux recorder following recorder repair, the tape on an energized power lead was inadvertently breached and the lead was shorted to ground. The short caused an undervoltage condition on the B vital instrument bus. The B vital instrument bus is the power supply for the recorder as well as the B RCP undervoltage relays. As a result of the "A" RCP bus undervoltage relays tripped for testing and drop out of the "B" RCP bus undervoltage relays due to the shorted power lead, the coincidence necessary to generate a RCP bus undervoltage reactor trip was met. A second trip signal was generated in another 2 milliseconds due to a 1 of 3 RCP breaker position open signal resulting from the "B" vital instrument bus undervoltage condition alone. All safeguards equipment functioned as designed following the trip. All RCPs continued to operate throughout the event. The event was caused by an inadequate work order planning and scheduling process which did not consider potential consequences of energized work. A second cause was inadequate management expectations with respect to taping of electrical leads. Procedural guidance has been developed to require work planning to, specifically identify work activities associated with energized conductors and the affected power source. Procedural guidance has been developed to evaluate work activities involving energized conductors during work scheduling. Procedural guidance has been developed and personnel working on energized conductors have been trained on enhanced taping/insulating techniques for energized leads.
348 | 3482002002 | 2002-10-15 | QR6 | Manual Reactor Trip | [45 empty] | Farley 1 | P | WE | PO | 100 | On October 15, 2002 at 2356, with the reactor at 100% power, Unit 1 was manually tripped due to a partially dropped control rod. Rods had been stepped in from 227 to 222 steps over the past three hours for routine xenon oscillation suppression. Upon inserting Bank D rods from 222 to 221 steps, rod F-06 dropped 24 steps to 198. A rod deviation alarm and a single channel high negative neutron flux rate trip alarm annunciated. Operators manually tripped the reactor in accordance with Abnormal Operating Procedures. All safeguards equipment functioned as designed following the trip. The dropped rod was due to an open failure of the movable gripper coil blocking diode. When the diode failed open and rod motion was attempted, the control rod was in an unlatched condition for up to 300 milliseconds while power was removed from the stationary gripper during the normal rod motion cycle. This resulted in a free fall of rod F-06 until the rod control logic re-energized the stationary gripper. A design change was implemented to remove the blocking diodes from all stationary and movable gripper coil circuits. Testing was performed to verify that this change had no significant effect on the gripper unlatch times and therefore no effect on rod drop times. Testing verified that the rod control system continued to operate per design. The reactor was returned to critical at 0542 on October 17, 2002. The corresponding design change was implemented on Unit 2.
348 | 3482002004 | 2002-12-10 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Farley 1 | P | WE | PO | 100 | On December 10, 2002 at 0824, with the reactor at 100% power, Unit 1 was manually tripped due to loss of both Steam Generator Feed Pumps (SGFP's). Facilities personnel were removing a catch bag near the area of the lA SGFP and the 120/208 Volt Miscellaneous Bus. An individual was applying force to break a tie-wrap which had been used to support the catch bag. When the tie-wrap broke, the individual momentarily lost his balance, reached out to steady himself, and inadvertently depressed a pushbutton on the local control panel for the 120/208 Volt Miscellaneous Bus. This resulted in deenergization of the Miscellaneous Bus and loss of control power to both SGFP's. The SGFP control valves closed resulting in loss of main feedwater to the Steam Generators. Operators manually tripped the reactor in accordance with Abnormal Operating Procedures. All safeguards equipment functioned as designed following the trip. This event was caused by personnel error-a lack of awareness of the sensitivity of surrounding equipment and the consequences of inadvertent contact with such equipment. Contributing causes were failure to consider the consequences of actions prior to the event and failure to use the proper tool to safely remove the tie wrap. A protective barrier has been installed over the Unit 1 Miscellaneous Bus control panel pushbuttons to prevent inadvertent contact. Access to the Unit 2 panel has been barricaded until plant conditions permit barrier installation. The individuals directly and indirectly involved have been coached on specific human performance aspects of this event. A stand down meeting of facilities personnel was held to reinforce station expectations for human performance aspects of this event, including proper tool use, situational awareness of sensitive plant equipment, communications with Operations prior to performing activities near sensitive equipment, and prejob briefings.
348 | 3482004001 | 2004-03-01 | QP5 | Excessive Feedwater Flow | [45 empty] | Farley 1 | P | WE | PO | 100 | On March 1, 2004 at 0522, with the reactor at 100% power, Unit 1 automatically tripped due to Steam Generator 1C level reaching its high level setpoint. At approximately 0521, the lead-lag card in the Steam Generator Feedwater Pump (SGFP) master speed control circuit failed, causing a ramp increase in the speed of both SGFPs. The speed increase caused an increase in feedwater flow to all three steam generators. As a result of the increase in SGFP speed, a low SGFP suction pressure condition occurred. Operators responded to the low suction pressure condition and the increasing feedwater flow by starting a stand-by condensate pump and manually closing the Main Feedwater Regulating Valves (MFRVs). The MFRVs responded to the transient, but the integrated reactor operator and system response was not rapid enough to prevent steam generator level reaching the high level setpoint. Per design, the main turbine, both SGFPs, and the reactor tripped. All safety systems functioned as designed. This event was caused by failure of the Lead-Lag (NLL) card in the master SGFP speed control circuit, resulting in a ramp increase in SGFP speed. The unexpected SGFP low suction pressure alarm delayed the operators' diagnosis of the failure, thus delaying operator action which might have prevented the trip. The failed lead-lag (NLL) card has been replaced. Annunciator response procedures have been revised to provide additional guidance for malfunctions of the feedwater control system.
348 | 3482008004 | 2008-11-19 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Farley 1 | P | WE | PO | 100 | On November 19, 2008 at approximately 04:25, Farley Unit 1 was operating at 100 % power. Due to a gradual drop in 4160 v safety related bus voltage over the last several hours from grid conditions, Farley contacted Alabama Power - Alabama Control Center (ACC) to discuss removing the shunt reactor from service in the Farley High Voltage Switch Yard (HVSY) to raise the 230 kv grid voltage. After receiving the request, the ACC operator used an air-break disconnect switch to isolate the shunt reactor, instead of using the breakers normally used for this purpose. Opening the disconnect switch which is not designed to break load, caused a significant electrical arc and phase to phase fault. The transmission protection system tripped the appropriate devices and cleared the fault in approximately 3 cycles. However, the instantaneous HVSY voltage drop resulted in loss of breaker position indication for the 1B Reactor Coolant Pump (RCP) [AB] which initiated an automatic Solid State Protection System (SSPS) [JC] reactor trip. Flow to the reactor core was never lost. The reactor tripped without complications and all safety systems performed normally. The switching control screens for ACC have been updated to alert the ACC operator of the requirement to isolate the shunt reactor prior to operating the air-break disconnect and the requirement to use switching orders for operations at the Farley HVSY. Farley Operations shift personnel and ACC personnel have been briefed of the event.
348 | 3482013001 | 2013-06-11 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Farley 1 | P | WE | PO | 100 | On June 11, 2013 at 2105, Unit 1 automatically tripped from 100% power due to a Reactor Coolant Pump (RCP) undervoltage condition on the 1B and 1C RCPs and experienced a BTrain loss of off-site power (LOSP). The RCP undervoltage condition and B-Train LOSP were caused by the trip of the 1B Startup Transformer. The B-Train LOSP resulted in the automatic start and load sequencing of the 1B Emergency Diesel Generator. All three Auxiliary Feedwater (AFW) Pumps auto-started during the event. All systems responded as expected to the reactor trip and B-Train LOSP. The reactor trip, diesel generator auto-start, and AFW auto-start are reportable as system actuations per 10 CFR 50.73(a)(2)(iv)(A). The direct cause of the trip of the 1B Startup Transformer was the failure of a lightning arrester on the switchyard supply to the startup transformer. The 1B Startup Transformer was returned to service following replacement of the failed lightning arrester. The root cause of the event was determined to be a compromise of the lightning arrester sealing plate during factory assembly which led to moisture ingress into the arrester. Corrective actions for this event will include replacement of similar vintage lightning arresters.
348 | 3482016002 | 2016-10-01 | QL5 | Partial Closure of MSIVs | [45 empty] | Farley 1 | P | WE | PO | 99 | On 10/1/2016 at 0512 CDT with Unit 1 at 99 percent power the plant experienced a turbine trip and automatic reactor trip as a result of inadvertent closure of the 1A Steam Generator Main Steam Isolation Valve (MSIV). This caused a rapid pressure reduction in the remaining two Steam Generators' steam lines, resulting in a Safety Injection (SI). The 1A MSIV closure was caused by failure of its test solenoid in conjunction with other air system leakage, which vented air pressure from the 1A MSIV actuator. An inadequate technical justification allowed the improper deactivation of the preventive maintenance (PM) task of the test solenoid valve in 2004. Decision making by control room personnel not to strictly adhere to an Annunciator Response Procedure was a contributing cause to the reactor trip being automatic versus manual, and led to the SI. Following the reactor trip and SI the 1A MSIV test solenoid was replaced and check valves on the 1A MSIV steam line were tested and replaced. The technical justifications of a sample of previously extended or deleted PMs strategies will be reviewed and corrected. The PM for the Unit 1 solenoid will be reinstated. Procedure use and adherence standards have been reinforced with Operations personnel, simulator just-in-time training was conducted for all crews, and further causal analysis is planned to investigate operations fundamental performance gaps. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system, Emergency Core Cooling System (ECCS) injection into the Reactor Coolant System, and automatic actuation of the AFW system.
348 | 3482016006 | 2016-11-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Farley 1 | P | WE | PO | 32 | On November 8, 2016, Joseph M. Farley Nuclear Plant Unit 1 was reducing power to remove the main generator from service. The 1A steam generator feed pump did not respond to control steam generator levels as expected when the miniflow valve was opened per procedure. Steam generator levels lowered due to lower feed flow, and at 1331 the reactor was manually tripped from 32 percent power to prevent reaching the low steam generator level automatic reactor trip setpoint. The motor driven auxiliary feed pumps also started automatically, as expected, with the manual reactor trip. The main steam isolation valves were closed to limit the unit cool down, decay heat removal was accomplished with the atmospheric relief valves, and the unit was maintained in mode 3. The controller failure was caused by the speed reference adjust and speed controller (C2) card being out of tolerance due to a failed A2 operational amplifier on the card, which was caused by infant mortality. The C2 card was replaced, and the new card was verified to be within the required tolerance. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) due to manual actuation of the reactor protection system and automatic actuation of the auxiliary feedwater system.
348 | 3482016008 | 2016-11-27 | QR6 | Manual Reactor Trip | [45 empty] | Farley 1 | P | WE | PO | 100 | On 11/26/16 at 2357 while Unit 1 was operating at 100 percent reactor power the main generator began to experience voltage and load swings, which were caused by a problem with the main generator. The unit was manually tripped at 0026 on 11/27/16 to protect the generator from potential damage. All control rods fully inserted and Auxiliary Feedwater (AFW) auto-started as expected. The Turbine Driven AFW (TDAFW) was secured at 0037, with Motor Driven AFW pumps continuing to provide flow to ensure adequate heat sink. The TDAFW auto-started a second time at 0041 on a valid actuation signal when Steam Generator levels decreased to the TDAFW actuation setpoint. The TDAFW system was secured a second time at 0047. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system and an automatic actuation of the AFW system.<br /><br /> The swings were caused by an intermittent failure of the voltage isolation transducer. The voltage isolation transducer was replaced prior to the plant restarting. The transducer module is being sent off for failure analysis to aid in determination of the cause of this failure.
348 | 3482021001 | 2021-04-22 | QR5 | Turbine Trip | [45 empty] | Farley 1 | P | WE | PO | 48 | At 1450 CDT on April 22, 2021, with Farley Nuclear Plant (FNP) Unit 1 in Mode 1 at 48% power an automatic reactor trip occurred due to a main turbine trip. The main turbine / generator trip was due to data input error in the exciter switchgear software during exciter testing. The trip was not complex with all systems responding normally. Operations stabilized the plant in Mode 3. Due to low decay heat load, the Main Steam Isolation valves were closed to minimize cooldown and the Atmospheric Relief Valves were used to remove decay heat. This event was initially reported as event notification 55206. <br /><br /> Corrective Actions included correcting the data entry in the exciter switchgear control software and performing causal analysis on the human performance aspect of this event. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to the automatic actuation of a system listed in 10CFR50.73(a)(2)(iv)(B). <br /><br /> FNP Unit 2 was not affected during this event.
352 | 3521987046 | 1987-09-07 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Limerick 1 | B | GE | PO | 83 | POWER LEVEL - 083%. ON SEPTEMBER 7, 1987 AT 1321 HOURS, THE REACTOR PROTECTION SYSTEM (RPS) INITIATED A FULL REACTOR SCRAM, WHEN THE MAIN TURBINE STOP VALVES CLOSED FOLLOWING A MAIN TURBINE TRIP ON HIGH-HIGH WATER LEVEL IN THE 'C2' MOISTURE SEPARATOR DRAIN TANK. A NUCLEAR STEAM SUPPLY SHUTOFF SYSTEM (NSSSS) GROUP IIB ISOLATION OCCURRED AS REACTOR WATER LEVEL DECREASED TO 12.5'. THE UNIT WAS OPERATING AT 83% POWER FOLLOWING START-UP FROM THE FIRST REFUELING OUTAGE AT THE TIME OF THE EVENT. AN UNUSUAL EVENT WAS DECLARED DUE TO THE UNPLANNED SCRAM. PLANT PERSONNEL DISCOVERED THAT THE INSTRUMENT AIR SUPPLY ROOT VALVES SERVICING THE TWO 'C2' MOISTURE SEPARATOR LEVEL TRANSMITTERS WERE NOT FULLY OPEN. AS A RESULT, THE LEVEL SIGNAL RECEIVED BY THE LEVEL CONTROLLERS FROM THE LEVEL TRANSMITTERS DID NOT INDICATE A TRUE LEVEL. THEREFORE, THE DRAIN VALVE AND DUMP VALVE FAILED TO PROPERLY CONTROL DRAIN TANK LEVEL. THE ROOT VALVES WERE OPENED FULLY AND THE SCRAM WAS RESET AND THE UNUSUAL EVENT TERMINATED AT 1345 HOURS. A NEW SPECIAL PROCEDURE WAS IMPLEMENTED TO VERIFY PROPER OPERATION OF ALL MOISTURE SEPARATOR DRAIN AND DUMP VALVE LEVEL CONTROL SYSTEMS. THE INSTRUMENT AIR SUPPLY PIPING AND INSTRUMENTATION DRAWINGS (P&IDS) WILL BE UPGRADED TO INCLUDE VALVES THAT CAN ISOLATE TWO OR MORE INSTRUMENTS OR DEVICES, AND A CHECK OFF LIST WILL BE DEVELOPED FOR VALVE POSITION VERIFICATION.
352 | 3521987048 | 1987-09-19 | QR5 | Turbine Trip | [45 empty] | Limerick 1 | B | GE | PO | 90 | POWER LEVEL - 090%. ON 9/19/87 AT 0910 HOURS, THE REACTOR SCRAM FROM 90% POWER AND A RECIRCULATION PUMP TRIP, FOLLOWING A MAIN TURBINE TRIP ON LOW ELECTRO-HYDRAULIC CONTROL (EHC) SYSTEM OIL PRESSURE. FOLLOWING THE TURBINE TRIP, OPERATION OF THE TURBINE BYPASS VALVES WAS MAINTAINED UNTIL THEIR EHC ACCUMULATOR PRESSURE BLED DOWN. REACTOR PRESSURE REACHED A PEAK VALUE OF 1093 PSIG AND REACTOR VESSEL WATER LEVEL REACHED A MINIMUM LEVEL OF MINUS 2 INCHES DURING THE EVENT. THERE WERE NO ADVERSE CONSEQUENCES AND THERE WAS NO RELEASE OF RADIOACTIVE MATERIAL RESULTING FROM THIS EVENT. THE CAUSE OF THE EVENT WAS THE FAILURE OF A TUBING SOCKET WELD IN THE EHC FLUID ACTUATING SUPPLY (FAS) LINE TO THE #3 MAIN TURBINE CONTROL VALVE (MTCV). THE SECTION OF EHC PIPE CONTAINING THE FAILED WELD WAS REMOVED FOR INSPECTION AND A NEW SECTION OF PIPE WAS WELDED INTO THE LINE. ANALYSIS OF THE MEASURED PIPING MOVEMENT AND VIBRATION LEVELS INDICATES THAT A PROPERLY BONDED WELD WOULD NOT HAVE FAILED AS A RESULT OF THE VIBRATIONS PRESENT. AS SUCH, THIS EVENT IS CONSIDERED AN ISOLATED INCIDENT. ADJUSTMENTS WERE MADE TO THE STEAM LINE RESONANCE COMPENSATOR (SLRC) AND A SECOND SLRC WAS TEMPORARILY INSTALLED IN SERIES WITH THE FIRST TO REDUCE THE CONTROL SIGNAL OSCILLATIONS. FULL POWER OPERATION WAS ACHIEVED ON NOVEMBER 21, 1987.
352 | 3521988012 | 1988-04-09 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Limerick 1 | B | GE | PO | 27 | On April 9, 1988 at 0415 hours an actuation of the Reactor Protection System, an Engineered Safety Feature occurred. A controlled shutdown was in progress and control rod insertion was stopped at 0400 hours to facilitate a gradual reactor depressurization to minimize offgas releases. Approximately three minutes prior to the scram, power began increasing due to the positive reactivity effect of decreasing moderator temperature. Reactor power, initially 27 on range 2, rose to 108 on range 2 where an intermediate range monitor high neutron flux alarm initiated, and caused the scram at 120 on range 2. Reacting to the alarm, the reactor operator was unable to "uprange" all the intermediate range monitors before the scram occurred six seconds after the alarm. All systems actuated as designed and the scram was reset at 0423 hours. There was no release of radioactive material to the environment as a result of this event. The cause of the event was a cognitive personal error when the utility employed licensed reactor operator did not adequately anticipate and observe the effects of decreasing moderator temperature on core reactivity. To prevent recurrence, the operator was cautioned to be constantly aware of those conditions which affect core reactivity; a caution was added to the general shutdown procedure and additional training of all licensed control room personnel was completed by July 15, 1988.
352 | 3521991009 | 1991-04-12 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Limerick 1 | B | GE | PO | 100 | On April 12, 1991, a Unit 1 reactor SCRAM and a partial Group VIC Primary Containment and Reactor Vessel Isolation Control System actuation occurred following a Main Turbine trip. The Main Turbine trip resulted from a spurious loss of the 125 volt DC electrical power supply to the Electrohydraulic Control (EHC) system. Following the SCRAM, all control rods fully inserted, reactor pressure increased to 1103 psig, and level decreased to approximately -20 inches instrument level. The Reactor Core Isolation Cooling (RCIC) system was manually operated to maintain reactor level when a loss of normal feedwater injection occurred. All systems operated as designed except for the normal feedwater system in which operator interaction occurred. Operations personnel successfully controlled the plant shutdown using the appropriate plant procedures. The cause of the loss of the 125 volt DC electrical power supply to the EHC system was due to a loose copper link inside a switch cabinet. The cause of the loss of normal feedwater injection was due to a personnel error resulting from a misinterpretation of the indications for the Condensate Filter Demineralizer system. The copper links were replaced with hard wire connectors, and an evaluation of other similar switch cabinets with copper links will be performed. Operator training will be implemented to address this specific loss of normal feedwater injection incident.
352 | 3521993011 | 1993-09-07 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Limerick 1 | B | GE | PO | 100 | On September 7, 1993, a loss of one of the two independent station offsite power supplies occurred. The 10 Station Auxiliary Bus Feeder Breaker opened and locked out due to an overcurrent condition when a bus feeder cable was struck during excavation work. All affected electrical buses transferred. The partial loss of power caused several Engineered Safety Feature actuations including fast starts of four Emergency Diesel Generators. The Unit 1 D114-G-D Feeder Breaker failed to reclose. The D114-G-D Feeder Breaker failure caused a Unit 1 Feedwater System anomaly which resulted in a reactor SCRAM on low water level. All safety systems functioned as designed. Unit 2 continued to operate at full power. The root causes of the 10 Station Auxiliary Bus trip are inadequate control of non-routine work processes, unclear supervision and worker expectations, and inadequate control of excavations including inadequate shoring procedural guidance. A primary casual factor of the Unit 1 reactor SCRAM was the Feeder Breaker failure. Corrective actions include the establishment of an excavation coordinator, a revision to the excavation procedure, the communication of management expectations, and a Feeder Breaker Diagnostic Testing Program.
352 | 3521994001 | 1994-01-14 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Limerick 1 | B | GE | PO | 76 | On January 14, 1994, at 1930 hours, a manual reactor scram was initiated by the licensed main control room reactor operator as directed by procedure in response to the loss of both recirculating water pumps. These pumps tripped as designed to reduce reactor power in response to an automatic reduction of main turbine load because of the loss of main generator stator water cooling. This loss of cooling was the combination of the 1A stator water coolant pump being out of service for maintenance work, and a 1B stator water coolant pump trip. The 1B pump trip was due to the unexpected failure of an indicating light bulb during reinstallation into its control panel socket by an operator. The indicating light is an integral part of the motor control circuit for the pump. The broken bulb created a short that energized a trip coil within this circuit. Plant systems functioned as designed. Operations personnel quickly responded by implementing the appropriate transient response procedures. The cause of this event was the lack of expectations concerning the replacement of indicating light bulbs. Expectations regarding the need to exercise care when replacing indicating light bulbs have been communicated to the applicable plant personnel, and will be included in plant staff continuing training.
352 | 3521995002 | 1995-02-21 | QR5 | Turbine Trip | [45 empty] | Limerick 1 | B | GE | PO | 100 | On 02/21/95 at 0305 hours, the Unit 1 and Unit 2 Reactor Protection Systems actuated as a result of main turbine trips that occurred within a fraction of a second of each other. An offsite electrical transmission system ground fault actuated Unit 1 and Unit 2 main transformer ground overcurrent protective relays tripping the generator output breakers and the main turbines. Both units were successfully stabilized with no emergency core cooling system or other engineered safety feature actuations. The onsite 4 kV safeguard power distribution system remained energized throughout the event. All of the Limerick Generating Station (LGS) equipment operated per design in response to the ground fault. The protective relays actuated as a result of a breaker failure, a lightning arrestor failure, and the failure of other protective relays on the transmission system to properly isolate the fault from the LGS equipment. The specific causes and corrective actions of the offsite equipment malfunctions have been investigated. The overcurrent protective relay setpoints are currently being revised to provide better trip coordination between onsite and offsite transmission system equipment.
352 | 3521995006 | 1995-08-28 | QG9 | Primary System Leak | [45 empty] | Limerick 1 | B | GE | SU | 9 | On 08/28/95 at 0652 ours, the reactor was manual shutdown, a Reactor Protection System actuation, due to high leakage into the Primary Containment. An Unusual Event was declared as a result of high leakage into the Primary Containment and complications prior to the shutdown resulting from the normal low power feedwater level control valve (FWLCV) being unavailable. The FWLCV was unavailable due to the 'A' Reactor Feedwater Pump being secured as a result of temperature recorder problems. operations personnel successfully controlled the manual shutdown using the appropriate plant procedures, and all control rods fully inserted. The low power FWLCV was returned to service and reactor pressure vessel level was stabilized. On 08/30/95 at approximately 1400 hours, a flange on an instrument line connected to the reactor head was determined to be misaligned and leaking. The cause of the misalignment resulted from the difficulty of this particular flange to be reassembled, an inadequate Maintenance procedure, and an inadequate task follow- through by a Maintenance Foreman. The corrective actions included an All Hands meeting on this event, a best practice revision to the procedure for reassembly of this flange, and a review of procedure steps for all reactor vessel disassembly/reassembly activities.
352 | 3521995008 | 1995-09-11 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Limerick 1 | B | GE | PO | 100 | On 09/11/95 at 1247 hours, unit 1 was manually shutdown in response to the unexpected opening of the 'M' Main Steam safety relief valve (SRV) when the valve could not be closed within 2 minutes per Technical Specifications (TS) Section 3.4.2. Following the reactor shutdown, the TS maximum reactor coolant system (RCS) cooldown rate, of 100 Degrees F/hour, was temporarily exceeded due to the RCS depressurization through the open SRV. Inspection of the SRV revealed steam erosion attributed to pilot valve seat leakage, resulted in the failure of the pilot valve. This produced a differential pressure across the SRV main disc, thereby opening the SRV. During this transient, the 'A' Residual Heat Removal (RHR) pump was operating in the Suppression Pool Cooling mode, and Operations personnel observed oscillations in motor current and decreasing pump flow, indicating potential suction strainer fouling. Inspection of the suction strainer identified a brown, fibrous material covering approximately 70% of the strainer. Chemical analysis identified the material as polypropylene fibers, and iron oxide and zinc oxide corrosion products. Five SRVs were replaced while the unit was shutdown. The Unit 1 Suppression Pool and its components were cleaned. Enhancements to the Foreign Material Exclusion Program are currently being implemented.
352 | 3521996013 | 1996-05-21 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Limerick 1 | B | GE | PO | 100 | On May 21, 1996, while performing Reactor Protection System (RPS) channel functional testing related to Main Steam Isolation Valve (MSIV) closure, a Unit 1 reactor scram occurred during closure of the 1B inboard MSIV. The Surveillance Test (ST) procedure for this testing directs the operator to partially close the MSIV using the test push button until either a half scram signal is generated or until an unexpected increase in reactor pressure occurs. When the expected half scram signal did not occur and an unexpected increase in reactor pressure was observed, the Reactor Operator immediately released the test push button. The MSIV continued to close due to the differential pressure across the valve caused by the increasing reactor pressure. The reactor scram occurred due to high neutron flux and increased reactor pressure. The plant responded as designed to these scram signals. The cause of the reactor scram was inadequate procedural guidance and an undetermined equipment malfunction. Two relays involved in the testing were replaced with new relays. The ST procedures will be revised to ensure that appropriate barriers are in place to minimize the risk of a reactor scram during RPS-MSIV closure testing.
352 | 3521996016 | 1996-07-25 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Limerick 1 | B | GE | PO | 100 | On 07/25/96, at 0224 hours, Unit 1 experienced a power transient due to a sudden momentary opening of main turbine by-pass valves and partial closure of the control valves. Indicated APRM neutron flux increased to 113.75% over a 10 second period. <br /><br /> Analysis indicates that actual peak heat flux was 107.5%. This event was bounded by the licensing basis of the core. In addition, at 0242 hours, an automatic reactor scram occurred on high neutron flux caused by a loss of feedwater heating due to the isolation of various feedwater heaters following recovery from the power excursion. The plant responded as designed to the high neutron flux signals. The cause of the power excursion was a malfunction of the primary speed frequency/voltage (F/V) converter in the main turbine electrohydraulic control system. The defective primary speed F/V converter was replaced. The cause of the reactor scram was less than adequate procedural guidance regarding power reduction in response to reactivity insertion resulting from the loss of feedwater heating. The emergency operating procedure was revised to provide an appropriate target power level on the loss of a feedwater heater string.
352 | 3521999003 | 1999-04-20 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Limerick 1 | B | GE | PO | 100 | On April 20, 1999, at 1830 hours, Limerick Generating Station (LGS) Unit 1 was operating at 100% power when a loss of feedwater was experienced. The Main Control Room received a condensate filter trouble, a Reactor Low Level, and Loss of Feedwater alarms. All three Reactor Feed Pumps tripped on low suction pressure causing a reactor SCRAM when level decreased to + 12.5 inches. The Reactor Protection System actuation is reportable pursuant to 10CFR50.73(a)(2)(iv). The low reactor water level Reactor Protection System actuation occurred due to a spurious tripping of a breaker that supplies position indication to the inlet valves of the Deep Bed Condensate Demineralizer System (DBCDS). Loss of inlet position indication to the DBCDS programmable logic controller created a signal for the deep bed outlet valves to close. The resultant rapid increase in differential pressure at the DBCDS bypass valves prevented their ability to be opened and maintain flow to the Reactor Feed Pumps and the reactor. This event is bounded by the previously analyzed loss of feedwater flow transient as described in the LGS Updated Final Safety Analysis Report (UFSAR). The plant responded as designed to a loss of feedwater flow. The DBCDS breaker that spuriously tripped was replaced and the DBCDS breakers for the outlet valves were procedurally opened to prevent closure. This event resulted in High Pressure Core Injection, and Reactor Core Isolation Cooling injections into the Reactor Coolant System. SPECIAL REPORT information required pursuant to Technical Specification (TS) 6.9.2 and TS Limiting Conditions for Operation ACTION statements 3.5.1.f and 3.7.3.b is included in this report.
352 | 3521999005 | 1999-06-11 | QR5 | Turbine Trip | [45 empty] | Limerick 1 | B | GE | PO | 100 | On June 11, 1999 at 19:29 hours, Limerick Generating Station (LGS) Unit 1 was operating at 100% power. An equipment operator performing a routine test, "Backup Overspeed And Power/Load Unbalance Test" in the auxiliary equipment room failed to place the backup overspeed trip interlock keylock switch to the "TEST" position before depressing the test push button. Failing to bypass the interlock resulted in a Turbine Stop Valve Fast Closure Scram signal. The weekly test verifies proper function of the Backup Overspeed Trip Circuit and Power/Load Unbalance Trip Circuit for continued reliable operation of the main turbine. The root cause for the turbine trip and subsequent reactor scram was personnel error. The plant was brought to a normal, safe shutdown condition and the appropriate notifications were made. There was no effect on the safe operation of the plant. Reactor Protection System (RPS) and Engineered Safety Feature (ESF) actuations as a result of this event are reportable pursuant to 10CFR50.73(a)(2)(iv).
352 | 3522000002 | 2000-05-01 | QR5 | Turbine Trip | [45 empty] | Limerick 1 | B | GE | PO | 92 | On May 1, 2000 at 03:07 hours, an automatic scram occurred on Unit 1 due to a phase-to-phase fault which caused a generator lockout and resultant turbine trip. This automatic shutdown was the result of a faulty electrical connection at the 220 kV main transformer "C" phase bushing. This was due to inadequate administrative controls for assembly of the connection following maintenance on the main transformer. Standards and procedures will be created to ensure proper assembly, independent verification, and post maintenance testing of the electrical connection.
352 | 3522002003 | 2002-05-19 | QR5 | Turbine Trip | [45 empty] | Limerick 1 | B | GE | PO | 100 | An actuation of the Unit 1 main turbine thrust bearing wear detector (TBWD) occurred during scheduled testing of the main turbine combined intermediate valves (CIV). Excessive clearances within the thrust bearing assembly allowed 31 mils of axial displacement on the main turbine shaft during closure of CIV-2. This was detected by the TBWD and caused an actuation. Detailed inspections of the detector and partial disassembly of the housing were performed. The TBWD trip will be bypassed during CIV testing.
352 | 3522003003 | 2003-04-23 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Limerick 1 | B | GE | PO | 100 | A valid reactor low level condition resulted in an automatic actuation of the reactor protection system. A closure of the deep bed condensate demineralizer inlet header block valve caused the reactor feed pumps to trip on low suction pressure resulting in the reactor low level condition. In addition, the low level condition resulted in actuation of the high pressure injection system, reactor core isolation cooling system and primary containment isolation valves. Operating procedures were revised to maintain the deep bed condensate demineralizer inlet header block valve open and de-energized during operation at power.
352 | 3522005003 | 2005-07-18 | QR5 | Turbine Trip | [45 empty] | Limerick 1 | B | GE | PO | 100 | A valid automatic actuation of the reactor protection system was initiated by a main turbine trip that was caused by an invalid main generator lockout relay actuation. A corroded disconnect position switch and concurrent ground on the balance of plant DC power distribution system adversely affected the main generator output breaker position monitoring circuit and caused the circuity to falsely sense that both main generator output breakers were open. The corroded switch and ground were repaired and the unit was restarted. Monitoring of the generator output breaker position monitoring circuit relays has been added to the operator rounds. Enhancements to the ground elimination processes, training and test equipment are planned.
352 | 3522008002 | 2008-03-22 | QR5 | Turbine Trip | [45 empty] | Limerick 1 | B | GE | PO | 87 | A valid automatic actuation of the reactor protection system occurred as a result of an invalid power/load unbalance actuation. This invalid power/load unbalance actuation caused an actuation of the main generator protection lockout relays, which resulted in a Main Turbine trip. The root cause of this event was the main generator protection relay logic that failed due to a defective relay. The main generator relay testing procedures will be revised to include a circuit loop signal verification test to ensure reliability of newly installed equipment.
352 | 3522010001 | 2010-06-23 | QR6 | Manual Reactor Trip | [45 empty] | Limerick 1 | B | GE | PO | 100 | A valid manual actuation of the reactor protection system was initiated due to an automatic trip of both reactor recirculation pumps. The event was caused by a failure of a 13 kV cable that powered a non-safeguard 480 VAC load center, a failure of a load center control power undervoltage auxiliary relay to automatically provide control power to the adjacent load center and a failure of a reactor recirculation pump M-G set standby lube oil pump relay. The faulted 13 kV cable section has been replaced but has not been energized. The failed undervoltage auxiliary relay has been replaced. The failed reactor recirculation pump M-G set standby lube oil pump relay was replaced. The north stack ventilation exhaust wide range accident monitor also failed due to the initial electrical distribution voltage transient. The radiation monitor has been repaired and returned to service.
352 | 3522011002 | 2011-06-03 | QR5 | Turbine Trip | [45 empty] | Limerick 1 | B | GE | PO | 100 | An automatic actuation of the reactor protection system occurred due to a main turbine trip. The main turbine tripped due to an actuation of the reactor vessel high level trip logic during surveillance testing. The high level trip actuation was due to use of an incompatible volt-ohm meter to verify the state of the opposite high level trip logic channels prior to introducing trip signals during the test. The root cause of the event was the reactor vessel high level trip calibration and functional surveillance test revisions did not fully assess the impacts of the test equipment on the direct current turbine trip circuit. The procedure for the control of portable measurement and test equipment program will be revised to include a requirement to evaluate changes to the type of test equipment used and test methodology. The reactor vessel high level trip calibration and functional surveillance tests will be revised to incorporate test equipment that is compatible with the digital feedwater level control system.
352 | 3522012002 | 2012-04-19 | QC5 | Loss of Non-safety-Related Bus |  |  | X | [14 empty] | X | [27 empty] | Limerick 1 | B | GE | PO | 100 | A transformer failure and subsequent low voltage condition resulted in a loss of the main generator stator cooling water system. The loss of stator cooling water resulted in an automatic trip of both reactor recirculation pumps which required a valid manual actuation of the reactor protection system. The transformer failure was caused by partial current discharge (corona effect). The partial current discharge was caused by a manufacturing defect resulting in improper insulation of the High Voltage line rod where it passes through the polyester support board. The faulted transformer was replaced.
352 | 3522012005 | 2012-07-18 | QR6 | Manual Reactor Trip | [45 empty] | Limerick 1 | B | GE | PO | 100 | A valid manual actuation of the reactor protection system was initiated due to an automatic trip of both reactor recirculation pumps. The reactor recirculation pumps tripped due to a loss of stator cooling water following a failure of a connection in a 13 kV/480 VAC non-safeguard load center air termination cabinet. An Unusual Event was declared due to flash-over damage on the failed transformer air termination cabinet which was classified as an explosion within the protected area boundary. The cause of the failed transformer was a high voltage connection clamp that was larger than the 13 kV cable size and the cable was not installed properly. The cable in use was a solid conductor and the clamp used was designed for stranded cable. This resulted in overheating and subsequent failure of the connection which damaged the cable and the load center transformer. The investigation determined that this connection is not disturbed during routine maintenance. Therefore, this is believed to be a manufacturing issue. The 124A load center transformer supply cable was upgraded to a stranded cable with a crimped lug connection. The faulted 124A load center transformer was replaced and returned to service. Similar load center transformers will be upgraded to stranded cable with crimped lug connections.
352 | 3522014004 | 2014-03-04 | QR6 | Manual Reactor Trip | [45 empty] | Limerick 1 | B | GE | PO | 100 | A valid manual actuation of the reactor protection system (RPS) was initiated due to an unexpected closure of all six main turbine intercept valves (TVs). The cause of the main turbine IVs closure was due to a degraded Electro-hydraulic Control (EHC) 30 VDC house power supply. The Unit 1 EHC system was replaced with a Digital EHC (DEHC) system during the subsequent refueling outage 1R15. The Unit 2 EHC system is scheduled to be replaced with a DEHC system during the next refueling outage 2R13 in April 2015. The Unit 2 EHC house and permanent magnet generator (PMG) power supplies as-found voltages were verified to be within the calibration procedure limits and the as-left voltages were adjusted to the middle of the procedure acceptable band during the planned maintenance outage 2M49.
352 | 3522015001 | 2015-02-23 | QL5 | Partial Closure of MSIVs | [45 empty] | Limerick 1 | B | GE | PO | 100 | A valid automatic actuation of the reactor protection system (RPS) occurred due to a high reactor pressure condition following an unexpected closure of the 1C Inboard main steam isolation valve (MSIV). The cause of the event was that an undersized fitting was installed on the air supply tubing to the 1C Inboard MSIV, which was not capable of withstanding existing cyclic stresses. The fitting failed due to cyclic fatigue. An inspection of Unit 1 inboard (I/B) and Outboard (O/B) MSIV Primary Containment Instrument Gas (PCIG)/Instrument Air tubing was performed to verify that the correct fittings are installed as specified by the design drawings or subsequent evaluation. The inspection of Unit 2 will occur during the in progress refueling outage. The failed fitting connection was replaced with a more robust fitting that is suitable for the application.
352 | 3522020001 | 2020-11-13 | QL5 | Partial Closure of MSIVs | [45 empty] | Limerick 1 | B | GE | PO | 100 | A valid automatic actuation of the reactor protection system (RPS) occurred due to a high reactor pressure condition following an unexpected closure of the 1B Inboard Main Steam Isolation Valve (MSIV). The valve failed closed when a fitting installed on the instrument gas supply tubing sheared at the Primary Containment Instrument Gas (PCIG) MSIV manifold. The reactor scram was the result of a high reactor pressure condition due to the unexpected closure of the 1B Inboard MSIV following the failure of PCIG tubing. The failure was caused by an overstressed tubing and fitting in combination with a vibratory environment capable of driving the fitting to failure. The overstressed condition resulted from an ambiguous procedure, permitting reusing a welded-in tubing connector that had the thread repaired. The tubing was replaced and the welded-in connector will be replaced at the next opportunity. The Maintenance Procedure will be revised to remove ambiguous direction which allowed the use of the repaired fitting. A piping modification will be installed on the Inboard MSIV manifold tubing to reduce the vibration at the connection.
353 | 3531989013 | 1989-11-10 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 98 | On November 10, 1989, a Unit 2 reactor SCRAM occurred following a Main Turbine trip. All control rods fully inserted as designed. The turbine trip resulted from a Unit 2 generator trip caused by actuation of the A-phase overall differential current relay. Following the SCRAM, reactor vessel pressure increased to 1125 psig and level decreased to approximately 0 inches instrument level. Operators restored normal operating vessel level and pressure. The High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems received momentary initiation signals due to spiking of level transmitters. The RCIC system did not initiate and the HPCI system partially initiated due to the short duration of the initiation signals. Both systems were operable and able to respond to a valid initiation signal throughout the event. Both systems were secured and all initiation logics were reset.<br /><br /> An "Unusual Event" emergency classification was declared and all appropriate notifications were made. The cause of the overall differential current relay actuation was a miscalculation of the trip setpoint performed during the original Unit 2 design. The calculation was corrected and the affected relays setpoints were adjusted. The miscalculation was verified to be an isolated event and no further actions to prevent recurrence are planned. Operators restarted Unit 2 on November 14, 1989.
353 | 3531990012 | 1990-07-15 | QL7 | Degraded condenser vacuum | [45 empty] | Limerick 2 | B | GE | PO | 65 | On July 15, 1990, a Unit 2 Reactor SCRAM occurred following a Main Turbine Stop Valve (TSV) closure, a Reactor Protection System (RPS) actuation. The TSV closure resulted from a loss of Main Condenser vacuum due to a failed low pressure turbine bearing cavity waste oil drain pipe. <br /><br /> Reactor Pressure Vessel (RPV) pressure increased to 1005 psig and level decreased from a normal operating level of +35 inches to +6 inches instrument level. Primary Containment and Reactor Vessel Isolation Control System (PCRVICS), an Engineered Safety Feature (ESF), actuation signals were received and no valve motion occurred, as expected, due to plant conditions. Operators restored RPV pressure and level to normal post SCRAM operating levels. An "Unusual Event" emergency classification was declared and all appropriate notifications were made in accordance with 10CFR50.72(a)(3) and 10CFR50.72(b)(2)(ii). The pipe failure was determined to be caused by insufficient pipe support resulting in vibration induced metal fatigue. The failed pipe was replaced and the remaining five similar pipes were inspected. Pipe supports were added to all six low pressure turbine bearing cavity waste oil drain pipes. Nuclear Engineering and Services Department personnel are evaluating the need for further corrective actions on Unit 2 and any similar actions on Unit 1. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an automatic actuation of the RPS and an ESF actuation.
353 | 3531990015 | 1990-09-10 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Limerick 2 | B | GE | PO | 100 | On September 10, 1990, a Unit 2 Reactor Protection System (RPS) actuation occurred resulting from an actuation of the Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) Engineered Safety Feature (ESF) actuations. A PCRVICS Group I Main Steam Isolation Valve (MSIV) isolation signal occurred due to a spurious trip signal on the 'D' channel of the Steam Leak Detection System (SLDS) when a temperature switch momentarily spiked when an operator repositioned the switch while Instrumentation and Control technicians were simultaneously testing the 'A' channel of the SLDS. Reactor Pressure Vessel (RPV) pressure increased to 1120 psig and RPV level decreased from a normal operating level of +35 inches to -48 inches instrument level. Additional PCRVICS actuation signals were received and appropriate valve and damper motion occurred. The Reactor Core Isolation Cooling (RCIC) system received an initiation signal on low low RPV level and injected into the RPV. <br /><br /> Operators restored RPV pressure and level to normal post SCRAM operating levels by 0941 hours. The cause of the event was a spurious trip signal from a Steam Leak Detection System temperature switch. The isolation signals were reset by 0948 hours. The temperature switch was replaced and the failure mechanism of the temperature switch is under investigation. A Shift Training Memorandum was issued and will be incorporated into the Operating Manual to formalize control of testing of both channels of any PCRVICS logic while daily operator readings are being taken.
353 | 3531992012 | 1992-12-04 | QR6 | Manual Reactor Trip | [45 empty] | Limerick 2 | B | GE | PO | 77 | On December 4, 1992, at 1001 hours both Reactor Recirculation pumps tripped when their respective End-of-Cycle Recirculation Pump Trip (EOC-RPT) breakers inadvertently tripped open during the performance of a Surveillance Test (ST) procedure. Main Control Room (MCR) Operations personnel then placed the reactor mode switch in the 'SHUTDOWN' position in accordance with the Operational Transient (OT) procedure OT-112, "Recirculation Pump Trip," in order to initiate a reactor shutdown (i.e., SCRAM). The reactor shutdown was accomplished with no abnormalities and all Control rods fully inserted. Following recovery from the SCRAM and a review of the event, Unit 2 entered Operational Condition 2 (Startup) on December 9, 1992. The manual reactor SCRAM was due to MCR Reactor Operators complying with procedure OT-112 following the trip of both Recirculation pumps. The trip of the Recirculation pumps was the result of the 'A' logic subsystem for the 'A' and 'B' EOC-RPT trip breakers being momentarily energized. The root cause of the trip of the Recirculation pumps is indeterminate, however, we have concluded that corrective actions associated with this event will be made with the assumption that the resistance readings were taken in a panel prematurely. To prevent the occurrence of a similar event, appropriate ST procedures and upcoming Continuing Training Programs will be enhanced to require the practice of taking voltage readings prior to resistance readings to ensure the circuit is not energized.
353 | 3531993001 | 1993-01-03 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 69 | On January 3, 1993, the Unit 2 reactor shut down automatically on high pressure after a transient in the Electrohydraulic Control (EHC) system occurred coincident with a Balance of Plant (BOP) battery ground alarm. Following the reactor SCRAM, reactor water level momentarily decreased to -37.9 inches causing the Reactor Core Isolation Cooling (RCIC) system to initiate, various Primary Containment and Reactor Vessel Isolation-Control System (PCRVICS) isolations to occur, and a Reactor Enclosure Secondary Containment isolation. These are Engineered Safety Feature (ESF) actuations. The reactor shut down on high pressure as designed, and all control rods fully inserted. The RCIC system initiated but did not inject since the signal was not present long enough to have other injection valve 'open' permissives satisfied. The ESF actuations functioned as designed and the affected systems were expeditiously restored, thereby preventing any adverse impact on other plant systems. Following recovery from the SCRAM, Unit 2 entered Operational Condition 2 (Startup) on January 6, 1993, at 2307 hours. The cause of the EHC system transient and coincident BOP battery ground could not be established. While the unit was in operation, monitoring equipment was installed on the EHC system to provide information if a similar transient occurred. Tests on the EHC and BOP battery systems are currently being performed during the Unit 2 Refueling Outage, which began on January 23, 1993, and any related problems identified will be corrected during this outage.
353 | 3531993005 | 1993-03-26 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 100 | On March 26, 1993, during performance of a Surveillance Test procedure, a Unit 2 reactor SCRAM occurred in response to an inadvertent closure of the Main Turbine Main Stop Valves (MSVs). The reactor SCRAM was followed by a Main Turbine trip. Reactor water level decreased to +12.5 inches as expected, and various Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuations occurred, however, no PCRVICS valve movements occurred. The Reactor Core Isolation Cooling system and the High Pressure Coolant Injection system received spurious initiation signals, but neither system injected into the reactor vessel. The reactor shutdown automatically and all control rods fully inserted as designed. Operations personnel successfully controlled the plant shutdown using the appropriate plant procedures. Unit 2 was returned to power operation on March 28, 1993. An investigation included that the MSV closures resulted from air entrapment in the Main Turbine Emergency Trip System (ETS) which is supplied by the Electro Hydraulic Control (EHC) system. The primary cause of the air entrapment was a procedure deficiency which did not adequately identify when to vent air from the ETS/EHC systems. A contributing factor to the cause was that orifices required to mitigate the effects of air in the ETS/EHC systems had not been installed. As a result of this event, a procedure revision was made, the required orifices were installed, and additional evaluations of this event are planned.
353 | 3531994010 | 1994-10-19 | C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) |  |  | X | [13 empty] | X | [28 empty] | Limerick 2 | B | GE | PO | 93 | On 10/19/94, a licensed operator (LO) performing a surveillance test inadvertently de-energized the D24 4KV Safeguard Bus. Immediately following the de-energization, the Reactor Feedwater Pump (RFP) minimum flow control valves fully opened. A reactor SCRAM occurred on low reactor water level, as designed. During the transient, reactor water level reached the low-low level setpoint, and the Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection systems received initiation signals. The RCIC system injected to recover reactor water level. Actuation of the Primary Containment and Reactor Vessel Isolation Control System also occurred, as designed, as a result of the vessel low-low water level signal. The reactor shutdown was accomplished with no abnormalities. The reactor SCRAM was caused by the failure of the N-relay coil in the RFP minimum flow control valve control power supply transfer logic. The cause of the N-relay coil failure was insulation breakdown, and is considered isolated. De-energization of the D24 Safeguard Bus occurred due to an inappropriate action by a LO when securing the D24 Emergency Diesel Generator following testing. Corrective actions included a failure analysis of the relay coil, an evaluation of the normal to alternate power supply transfer circuits, and discipline of the involved LO.
353 | 3521995002 | 1995-02-21 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 94 | On 02/21/95 at 0305 hours, the Unit 1 and Unit 2 Reactor Protection Systems actuated as a result of main turbine trips that occurred within a fraction of a second of each other. An offsite electrical transmission system ground fault actuated Unit 1 and Unit 2 main transformer ground overcurrent protective relays tripping the generator output breakers and the main turbines. Both units were successfully stabilized with no emergency core cooling system or other engineered safety feature actuations. The onsite 4 kV safeguard power distribution system remained energized throughout the event. All of the Limerick Generating Station (LGS) equipment operated per design in response to the ground fault. The protective relays actuated as a result of a breaker failure, a lightning arrestor failure, and the failure of other protective relays on the transmission system to properly isolate the fault from the LGS equipment. The specific causes and corrective actions of the offsite equipment malfunctions have been investigated. The overcurrent protective relay setpoints are currently being revised to provide better trip coordination between onsite and offsite transmission system equipment.
353 | 3531995008 | 1995-08-08 | QP5 | Excessive Feedwater Flow | [45 empty] | Limerick 2 | B | GE | PO | 100 | On August 8, 1995, at approximately 1337 hours, Unit 2 was operating at 100% power when an automatic reactor scram occurred. The scram resulted when the main turbine tripped on high reactor pressure vessel water level of +54 inches instrument level. Prior to the main turbine trip, a 2A reactor feed pump lockout, 2A & 2B reactor recirculation pump runback to the low speed limit, and a swap of the feedwater level control system (FWLCS) master level controller and 2A/2B/2C RFP motor gear units from Auto to Manual control occurred. The reactor operator attempted to take manual control of the FWLCS, but was unable to prevent the level transient. Detailed troubleshooting identified that the 'A' FWLCS power supply experienced a momentary loss of output power for approximately 250 milliseconds which caused the aforementioned equipment responses. All plant systems responded properly to the transient. The cause is believed to be a loose connection in the DC output of the FWLCS power supply. A detailed check of all terminal connections was performed.
353 | 3531995010 | 1995-08-20 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 100 | On 08/20/95, an automatic Unit 2 reactor SCRAM occurred, a Reactor Protection System actuation, from a high reactor vessel pressure signal resulting from main turbine control valve closures. Subsequent to the reactor SCRAM the main turbine tripped on high reactor pressure vessel (RPV) water level. Following the main turbine trip, the rapid pressure change from the turbine stop valve closure resulted in a pressure wave traveling through the RPV causing a 'ringing' in the wide range RPV water level instrumentation. This caused various Engineered Safety Feature actuations to occur. The RPS functioned as designed by automatically shutting down the reactor on high RPV pressure. The RPV water level 'ringing' and the resultant instrumentation spike were consistent with the results of previous events. The cause of the turbine valve oscillations was concluded to be high impedance across the normally closed (NC) contacts of relay KT106 (Agastat TDPU, Model 2112-D-H116YE), causing an energized relay coil downstream of the KT106 relay to drop out momentarily. The KT106 relay boards for the Units 1 and 2 Electrohydraulic Control systems were replaced, modifications were made to wire the spare sets of NC contacts in parallel with the original contacts, and preventative maintenance for the KT106 relay boards will be evaluated.
353 | 3531996004 | 1996-05-14 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 100 | At 1033 hours on 05/14/96, Unit 2 experienced a Main Generator lockout due to the inappropriate actuation of the volts/hertz relay 359/381A. The Main Generator lockout relay 386B caused a Main Turbine trip and subsequent automatic reactor SCRAM due to a Main Turbine control valve fast closure Reactor Protection System actuation signal. Also, various Engineered Safety Feature actuations occurred as a result of this event. All control rods fully inserted as designed, and Operations personnel successfully controlled plant shutdown using appropriate station procedures. No Emergency Core Cooling Systems initiated following the unit SCRAM. Following recovery from the SCRAM the unit was taken critical on 05/15/96, at 0932 hours. The cause was attributed to an inadequate Design Change Package (DCP) implemented in 1988, which failed to update a specific relay drawing. The volts/hertz relay 359/381A should have been set to trip at 24,240 volts at 60 hertz, but was incorrectly set to trip at 22,680 volts at 60 hertz. Relay 359/381A was recalibrated to the correct setpoint. Other similar relays were inspected and determined to be unaffected by the DCP. Further investigation is in progress, and any significant findings will be reported in a supplement to this report.
353 | 3531996007 | 1996-12-06 | QR6 | Manual Reactor Trip | [45 empty] | Limerick 2 | B | GE | PO | 90 | On 12/6/96, operators manually scrammed the Unit 2 reactor as a result of a degrading Electro-Hydraulic Control (EHC) system. Alarms and EHC system operating parameters indicated an EHC system leak. The operators conservatively initiated a manual shut down of the unit in advance of a probable automatic main turbine trip and reactor scram. An EHC system pressure switch support bracket developed a crack and failed due to main turbine control valve vibration. The pressure switch tubing then cracked creating the EHC system fluid leak. The failed bracket was replaced with a modified bracket design, and the associated tubing was replaced. The remaining turbine control valve pressure switch brackets were also upgraded with the modified design. A comprehensive walkdown of the main steam system piping was performed to identify other piping supports and attachments that may have been degraded by vibration. An analysis of the turbine control valve and piping vibration will be performed through the next Unit 2 operating cycle to determine causes of the system vibration and corrective actions, as appropriate.
353 | 3531996009 | 1996-12-24 | QR3 | Reactivity Control Imbalance | [45 empty] | Limerick 2 | B | GE | PO | 37 | At 0608 hours on 12/24/96, an overspeed condition occurred on the 'B' reactor recirculation pump (RRP) ad the RRP was manually tripped. At 0613 hours Operations identified that the reactor was operating in the exclusion region of the power/flow map and a manual scram was performed, a Reactor Protection System actuation. All control rods inserted as designed. The cause of the overspeed condition was a failed ball joint which connects the 'B' Motor Generator (MG) set scoop tube to the scoop tube positioner. The ball joint failed from high stress reverse bending fatigue from low amplitude low frequency vibration induced by the fluid coupler. Additional causes were an inadequate diagnosis of a 10/23/94 event, and an inadequate follow-up to GE SIL 355. Corrective actions include installation of vibration monitoring equipment, Unit 1/2 MG set inspections, revisions to appropriate preventive maintenance tasks, the assessment of a design change, and Engineering re-reviews of previous responses to industry experience. A parallel evaluation identified that the manual scram may have been unnecessary since the procedure for determining actual core flow after a RRP trip was conservative, and jet pump instrumentation logic assumes reverse flow in an inactive loop with 1 RRP in service. As a result, the affected procedure will be assessed for revision.
353 | 3531999006 | 1999-12-31 | QR5 | Turbine Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Limerick 2 | B | GE | PO | 100 | On December 31, 1999 at 01:11 hours Unit 2 reactor scrammed from 100% power on a main generator lockout/turbine trip when the generator protective relays detected a B phase-to-ground fault. The fault was initiated when a 500kV surge arrester located at the main step-up transformer failed. The fault was isolated from the 500 KV system through the automatic operation of the switchyard circuit breakers. Following the scram, it was discovered that one of the two grading capacitors located on the B-phase pole of the 355 circuit breaker had also failed when removing the 500 KV capacitor bank from service resulting in two successive restrikes of the 355 circuit breaker. No emergency core cooling systems (ECCS) were actuated. The surge arresters on all three (3) phases of the main transformer were replaced as were 5 grading capacitors. The unit was returned to service on January 2, 2000.
353 | 3532000001 | 2000-01-08 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 100 | At approximately 16:30 hours on January 8, 2000 Unit 2 scrammed on a main generator lockout/turbine trip from a positive ground on the Balance of Plant (BOP) 222 plant services transformer alarm circuit. The shutdown was normal with all rods in and the reactor was stabilized. The trip was determined to be caused by a voltage transient as a result of ground on the non-safeguard DC distribution system resulting from closure of a knife switch while investigating a ground on the BOP DC System. The ground was caused by an exposed spare wire on the transformer low liquid level switch. The voltage transient caused the failure of two main generator differential relays. Additionally, a controlled process was not used in the search for the ground which has been addressed by management directives. The unit was returned to service on January 10, 2000.
353 | 3532001001 | 2001-02-23 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Limerick 2 | B | GE | PO | 85 | On February 23, 2001, operators were performing a planned Unit 2 shutdown to repair the 2N Main Steam Relief Valve (MSRV) due to first stage pilot valve seat leakage. During power reduction the 2N MSRV inadvertently lifted and remained open. The cause was a sudden loss of material from the first stage pilot valve due to erosion and oxidation of the Stellite disc material in the area of the seating surface. A manual scram was initiated as required by Technical Specifications (TS). Suppression Pool Cooling was placed in service. The Main Steam Isolation Valves (MSIVS) were manually closed in response to the reactor depressurization but the cooldown rate exceeded the TS limit of 100 Fahrenheit degrees per hour due to the open MSRV. The reactor level response to the scram resulted in a valid low-level signal to the Reactor Protection System (RPS) and Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) systems. Group 2A and 2B isolation valves were in the closed position but received a valid isolation signal from the reactor low-level condition. The 2N and 2M MSRVS were subsequently replaced and Unit 2 was returned to power operation. The SRV Leakage Determination Monitoring Process was revised to provide added margin and improved direction on actions associated with pilot valve leakage.
353 | 3532002001 | 2002-07-23 | QL7 | Degraded condenser vacuum | [45 empty] | Limerick 2 | B | GE | PO | 100 | Limerick Unit 2 was manually scrammed due to degraded main condenser vacuum. The condenser air removal system failed due to temperature in the steam jet air ejector (SJAE) condenser exceeding the design limit. The design limitations of the steam jet air ejector system were not properly addressed during the turbine retrofit project resulting in plant operating procedures allowing these limitations to be exceeded. Operating procedures for both units were revised to require a power reduction prior to condensate temperature or condenser backpressure exceeding established limits that maintain sufficient margin to ensure proper operation of the air removal system.
353 | 3532003001 | 2003-03-03 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 26 | An unplanned automatic scram occurred as a result of a manual main turbine trip. The main turbine developed a high vibration condition during a planned power reduction to enter a refueling outage. The main turbine developed a light radial rub due to an inadequate specification for clearance between the oil deflectors and the main shaft as a result of main turbine retrofit. The oil deflector clearance specification has been restored to the pre-retrofit value. In addition, the affected gland seal clearances were restored to design values. Also, the operating procedures were revised to ensure main condenser backpressure remains greater than 1.5 inches Hg when less than 50% power.
353 | 3532004001 | 2004-06-22 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 100 | A valid automatic actuation of the reactor protection system occurred when the reactor was critical. This actuation was caused by a main turbine trip due to a power/load unbalance condition. An internal fault occurred on a 500 kV circuit breaker during opening resulting in actuation of the#1 bus differential relay. A concurrent failure on the secondary wiring of the current transformer associated with a different 500 kV circuit breaker combined with the ground fault current from the initial fault to cause an actuation of #3 bus differential relay. Both main generator output circuit breakers tripped due to the actuations of the associated bus differential relays. The 500 kV circuit breaker was repaired and returned to service. The current transformer was replaced and returned to service.
353 | 3532005004 | 2005-10-12 | QR5 | Turbine Trip | [13 empty] | X | [30 empty] | X | Limerick 2 | B | GE | PO | 100 | A valid automatic actuation of the reactor protection system was initiated by a malfunction of the Electro-Hydraulic Control (EHC) system that closed the main turbine control valves at power. The most likely cause was a transient malfunction of a circuit card. The four circuit cards that most likely caused the malfunction were replaced and tested.
353 | 3532007003 | 2007-04-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Limerick 2 | B | GE | PO | 100 | An invalid feedwater runback demand was initiated due to a failure of a redundant reactivity control system (RRCS) circuit card coincident with surveillance testing on the system. The feedwater runback resulted in an automatic actuation of the reactor protection system due to a valid reactor low-level condition. The high pressure coolant injection (HPCI) and reactor core isolation cooling (RCIC) systems initiated and injected on the low level condition and successfully restored reactor level. HPCI and RCIC were placed in manual flow control mode during the level recovery due to flow oscillations caused by incorrect flow controller gain and reset settings. The failed RRCS circuit card was replaced and tested successfully. The HPCI and RCIC flow controller gain and reset settings were adjusted to the required settings to ensure stable automatic flow control.
353 | 3532008002 | 2008-02-01 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 100 | A valid automatic actuation of the reactor protection system occurred as a result of a phase-to-ground fault at the 2A Main Transformer low voltage (22 kV) bushing connection to the Iso-Phase bus. The Main Generator neutral overvoltage relay actuated and tripped the generator protection lockout relays, which resulted in a Main Turbine trip. The cause of the ground fault was overheating of the bolted connection between the Main Transformer bushing and the flexible links that connect the bushing to the Iso-Phase Bus. The degraded bushings and flexible links were replaced. The transformer maintenance procedure was revised to provide enhanced direction for assembly of the bolted connection.
353 | 3532011002 | 2011-02-25 | QR6 | Manual Reactor Trip | [45 empty] | Limerick 2 | B | GE | PO | 100 | A manual actuation of the reactor protection system was initiated following an automatic trip of both reactor recirculation pumps. The pumps tripped due to a main generator stator cooling water high temperature actuation which also resulted in an automatic main turbine electro-hydraulic control load set runback. The root cause of the event was a failure to properly control a degraded stator cooling water temperature control valve that required manual operator action in lieu of an automatic control function. The automatic temperature control valve was repaired. The "Adverse Condition Monitoring and Contingency Planning" and "Operational and Technical Decision Making Process " procedures will be revised regarding actions required to substitute a manual operator action for an automatic control function.
353 | 3532011004 | 2011-05-29 | QR5 | Turbine Trip | [45 empty] | Limerick 2 | B | GE | PO | 100 | An automatic actuation of the Unit 2 reactor protection system occurred due to an actuation of the turbine control valve fast closure logic. The actuation occurred during restoration from maintenance on a main turbine control valve. The "A1" channel of turbine control valve fast closure logic was placed in the trip condition during the maintenance. The "B1" channel tripped when the electrohydraulic control relayed emergency trip supply oil supply was restored to the control valve. The root cause of the event was a void in the electrohydraulic control relayed emergency trip supply oil supply line that resulted in a perturbation of the oil supply pressure at the adjacent control valve. A procedure will be developed and implemented to provide specific restoration steps for turbine control, stop, and combined intermediate valves.
353 | 3532015008 | 2015-12-19 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Limerick 2 | B | GE | SU | 6 | An unplanned valid automatic actuation of the reactor protection system (RPS) when critical occurred during a reactor restart from a planned maintenance outage. The actuation occurred due to a deficient procedure when using digital electro-hydraulic control (DEHC) main steam bypass valve (BPV) jack adjustments to increase reactor pressure. Following a demand for a pressure increase all nine BPVs opened causing a reactor high level trip of the reactor feed pump followed by a reactor low level RPS actuation. The root cause of the event was a failure to identify the risk associated with procedure changes for the DEHC installation modification and the DEHC modification team failed to adequately evaluate DEHC software changes. The corrective actions will revise the procedure change process to validate modification related procedure revisions with risk impact.
353 | 3532016001 | 2016-06-01 | QR6 | Manual Reactor Trip | [45 empty] | Limerick 2 | B | GE | PO | 100 | A manual actuation of the reactor protection system (RPS) when the reactor was critical was initiated during Plant Process Computer (PPC) modification testing at power. A modification wiring design error caused an actuation of both reactor recirculation pump (RRP) trip relays when a circuit isolation switch was closed. The direct cause of the event was a circuit wiring design error implemented in the field that caused energization of the RRP adjustable speed drive (ASD) trip coils. The root cause of the event was a failure of station personnel to appropriately apply Technical Human Performance (THU) error prevention techniques to identify the design error and prevent its installation and testing as part of the modification. The isolation switch for the mis-wired circuit was opened to enable reset of the ASD trip coils. The 2A and 2B ASDs were returned to service. The corrective actions are to change the circuit design to correct the design error. The human performance aspects of the event will be addressed through several management actions that include reinforcement of proper standards and behaviors related to THU error techniques with station personnel.
353 | 3532019001 | 2019-06-04 | QL7 | Degraded condenser vacuum | [45 empty] | Limerick 2 | B | GE | PO | 100 | On June 3, 2019, with Limerick Unit 2 at approximately 100% power, the D214-24 Load Center tripped due to an invalid undervoltage signal; resulting in de-energization of a 480 VAC Divisional Motor Control Center (MCC) D214-G-D. The power failure impacted several components in the Offgas System resulting in water building up in the system and causing stalling of the Steam Jet Air Ejectors and a resultant degradation of Main Condenser vacuum. At 01:45 June 4, Operators inserted a manual SCRAM due to Main Condenser vacuum approaching the Main Turbine trip setpoint. The cause of the event is the procedure used to stabilize the plant did not fully address the loss of power to the Offgas System. The corrective action is to revise the procedures used to stabilize the plant to address the loss of power to the Offgas System.
354 | 3541987014 | 1987-02-11 | QG9 | Primary System Leak | [45 empty] | Hope Creek | B | GE | PO | 100 | POWER LEVEL - 100%. TECHNICAL SPECIFICATION ACTION STATEMENT 3.4.3.2.B WAS ENTERED BECAUSE OF UNIDENTIFIED REACTOR COOLANT LEAKAGE IN THE DRYWELL IN EXCESS OF 5 GPM. AFTER VARIOUS ATTEMPTS TO REDUCE THE LEAKAGE RATE FAILED, AT 0405 AN ORDERLY MANUAL PLANT SHUTDOWN WAS COMMENCED AT A RATE OF 100 MWE/HR. AT 0635, AN UNUSUAL EVENT WAS DECLARED AND APPROPRIATE NOTIFICATIONS WERE MADE. A DRYWELL ENTRY WAS MADE WHEN REACTOR POWER HAD BEEN REDUCED TO 20%, AND THE SOURCE OF LEAKAGE WAS IDENTIFIED AS A WELD FAILURE ON A DRAIN LINE OFF OF THE 'A' REACTOR RECIRCULATION PUMP DISCHARGE VALVE BODY. BECAUSE THE ROD SEQUENCE CONTROL SYSTEM (RSCS) HAD INHIBITED FURTHER ROD MOVEMENT EARLIER IN THE INCIDENT, AND CONTINUED SHUTDOWN WAS REQUIRED BY TECHNICAL SPECIFICATION, A MANAGEMENT DECISION WAS MADE TO MANUALLY SCRAM THE REACTOR. THE REACTOR WAS MANUALLY SCRAMMED AT 1630 AND THE UNUSUAL EVENT WAS TERMINATED AT THIS TIME. IMMEDIATE CORRECTIVE ACTIONS FOR PLANT RESTART CONSISTED OF REPAIRING THE SUBJECT DRAIN LINE, INSPECTING SIMILAR CONNECTIONS ON ALL RECIRC PUMP SUCTION AND DISCHARGE VALVE DRAIN LINES, AND OBTAINING A SAFETY EVALUATION OF THE INCIDENT FROM NUCLEAR ENGINEERING DEPARTMENT.
354 | 3541987017 | 1987-02-24 | QR8 | Spurious Reactor Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | POWER LEVEL - 100%. A REACTOR SCRAM OCCURRED DURING THE PERFORMANCE OF AN I&C SURVEILLANCE PROCEDURE ON REACTOR VESSEL LEVEL CHANNEL C32-K624C (NARROW RANGE, LEVEL 8). THE TECHNICIAN PERFORMING THE PROCEDURE WAS IN THE PROCESS OF CHECKING TRIP CONTACT CLOSURES ON LEVEL 8 TRIP RELAY K7C, AND PLACED OHM METER LEADS ACROSS THE WRONG CONTACTS. THIS ACTION CREATED A +125VDC CIRCUIT TO THE MAIN TURBINE LEVEL TRIP RELAY, TRIPPED THE TURBINE, AND SCRAMMED THE REACTOR. SEVERAL WORK ENVIRONMENT FACTORS CONTRIBUTED SIGNIFICANTLY TO THE TECHNICIANS ERROR, AND AS SUCH, THIS INCIDENT HAS BEEN CLASSIFIED AS AN INHERENT TESTABILITY PROBLEM INSIDE THE ASSOCIATED RELAY PANEL. DURING THE COURSE OF THE SCRAM, WITH MINOR EXCEPTIONS, ALL SYSTEMS AND COMPONENTS RESPONDED AS EXPECTED. CORRECTIVE ACTIONS TAKEN TO PREVENT REOCCURRENCE INCLUDED INSTALLATION OF COLOR CODED TEST JACKS ON THE CONTACTS FOR RELAYS K7A, K7B, AND K7C AND ADMINISTRATIVELY IDENTIFYING SURVEILLANCE PROCEDURES WHICH HAVE A HIGH POTENTIAL FOR INITIATING A FULL SCRAM.
354 | 3541987034 | 1987-07-30 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Hope Creek | B | GE | PO | 100 | POWER LEVEL - 100%. A REACTOR SCRAM OCCURRED WHEN A 120 VAC UNINTERRUPTABLE POWER SUPPLY (UPS) INVERTER WHICH POWERS THE FEEDWATER CONTROL CABINET BECAME DE-ENERGIZED DURING THE COURSE OF ROUTINE MAINTENANCE. THE RESULTANT LOSS OF FEEDWATER CONTROL CAUSED THE REACTOR TO SCRAM ON LOW LEVEL AT +12.5' DECREASING. SUBSEQUENT INVESTIGATION DETERMINED THAT THE INVERTER BECAME DE-ENERGIZED WHEN IT WAS BEING RETURNED TO A NORMAL CONFIGURATION. A SWITCHING ERROR CAUSED THE INVERTER MAIN POWER SUPPLY FUSE TO BLOW. SEVERAL FACTORS CONTRIBUTED TO A LACK OF AWARENESS ON THE PART OF THE OPERATOR INVOLVED THAT THE INVERTER MAIN FUSE HAD BLOWN. IN AN ATTEMPT TO CORRECT THE SWITCHING ERROR, THE BACKUP INFEED SOURCE TO THE INVERTER WAS ALSO DE-ENERGIZED. THESE ACTIONS COMBINED TO REMOVE THE ENTIRE INVERTER FROM SERVICE. CORRECTIVE ACTIONS INCLUDED VERIFYING FAULT INDICATING LAMPS ON ALL INVERTERS WERE INSTALLED, REVISING THE INVERTER OPERATING PROCEDURE, COUNSELLING THE OPERATOR INVOLVED, AND ENHANCING OPERATOR TRAINING ON INVERTER OPERATIONS.
354 | 3541987037 | 1987-08-16 | L2 | Loss of Condenser Vacuum | [10 empty] | X |  |  | X | [26 empty] | X |  |  |  | X | Hope Creek | B | GE | PO | 85 | POWER LEVEL - 085%. ON AUGUST 16, 1987 AT 0207 HOURS THE PLANT WAS IN OPERATIONAL CONDITION 1 (POWER OPERATION) AT 85% POWER GENERATING 905 MWE. FEED PUMP (RFP) TO SERVICE FOLLOWING MAINTENANCE, ALL FEEDWATER PUMPS TRIPPED DUE TO A LOSS OF CONDENSER VACUUM, AND A LOW VESSEL WATER LEVEL SCRAM LEVEL 3, +12.5' DECREASING AND SUBSEQUENT HIGH PRESSURE COOLANT INJECTION (HPCI) INJECTION OCCURRED. THE LOSS OF CONDENSER VACUUM WAS CAUSED BY OPENING THE 'C' REACTOR FEED PUMP TURBINE (RFPT) EXHAUST VALVE WITH A BLOWN RUPTURE DISK IN THE RFPT EXHAUST LINE. INVESTIGATION SUBSEQUENT TO THE SCRAM DETERMINED THAT THE PRIMARY CAUSE OF THE EVENT WAS A DEFICIENT FEEDWATER SYSTEM OPERATING PROCEDURE. THE PROCEDURE DID NOT CONTAIN ADEQUATE GUIDANCE FOR REMOVING AND RETURNING AN RFP TO SERVICE DURING POWER OPERATION. IMMEDIATE CORRECTIVE ACTIONS CONSISTED OF REVISING THE AFFECTED PROCEDURE. LONGER TERM CORRECTIVE ACTIONS INCLUDE EVALUATING CONDENSER VACUUM SETPOINTS AND PERFORMING A DYNAMIC RESPONSE TEST OF THE RFP AND MAIN TURBINE TO ENSURE PROPER RESPONSE OF THE RFP'S AND MAIN TURBINE TO A LOSS OF CONDENSER VACUUM.
354 | 3541987039 | 1987-08-29 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | POWER LEVEL - 100%. A REACTOR SCRAM OCCURRED WHILE PERFORMING A TURBINE OVERSPEED PROTECTION OPERABILITY TEST. COMBINED INTERMEDIATE VALVE (CIV) #5 WAS BEING STROKED CLOSED, AND A TRANSIENT OF UNDETERMINED ORIGIN IN THE EMERGENCY TRIP SYSTEM (ETS) CAUSED THE TURBINE CONTROL VALVES TO FASTCLOSE, RESULTING IN THE SCRAM. THE SUBJECT TEST WAS REPEATED A NUMBER OF TIMES SUBSEQUENT TO THE EVENT IN AN ATTEMPT TO DETERMINE THE FAILURE MECHANISM THAT CAUSED THE TRANSIENT IN THE ETS HEADER. BECAUSE THE TRANSIENT WAS NOT REPEATABLE, CORRECTIVE ACTIONS WERE DEVELOPED BASED ON INDUSTRY EXPERIENCE WITH THE TURBINE EHC SYSTEM/ETS HEADER. THESE ACTIONS INCLUDED INITIATING A DESIGN CHANGE TO INSTALL RESTRICTING ORIFICES IN THE FAST-ACTING SOLENOIDS FOR ALL 20 TURBINE VALVES, AND, AS AN INTERIM MEASURE PRIOR TO DCP IMPLEMENTATION, REDUCING REACTOR POWER TO LESS THAT 30% POWER WHEN PERFORMING THE TURBINE OVERSPEED PROTECTION OPERABILITY TEST.
354 | 3541987047 | 1987-10-10 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Hope Creek | B | GE | PO | 10 | POWER LEVEL - 010%. ON OCTOBER 10, 1987 AT 1950 HOURS, THE PLANT WAS IN OPERATIONAL CONDITION 2 (STARTUP/HOT STANDBY) AT 10% POWER GENERATING 0 MWE WHEN THE 'J' SRV FAILED TO CLOSE ON SIGNAL. THE SRV HAD BEEN OPENED DURING A TEST WHICH WAS BEING PERFORMED TO COLLECT BASELINE DATA FOR THE ACOUSTIC MONITORS. THE REACTOR WAS SCRAMMED MANUALLY AT 1952 HOURS IN ACCORDANCE WITH THE HCGS ABNORMAL OPERATING PROCEDURES. PROCEDURES TO PLACE THE UNIT IN COLD SHUTDOWN WERE EXECUTED. THE ROOT CAUSE OF THIS OCCURRENCE WAS DETERMINED TO BE SAND BLASTING GRIT IN THE SOLENOID VALVE. CORRECTIVE ACTIONS INCLUDED REPLACEMENT OF THE MALFUNCTIONING TARGET ROCK VALVE AND INSPECTION OF A SAMPLING OF THE SOLENOIDS OF OTHER SRVS.
354 | 3541987051 | 1987-12-08 | QR8 | Spurious Reactor Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | POWER LEVEL - 100%. ON DECEMBER 8, 1987 AT 1405 HOURS, THE PLANT WAS IN OPERATIONAL CONDITION 1 (POWER OPERATION) AT 100% POWER GENERATING 1106 MWE WHEN AN AUTOMATIC REACTOR SCRAM OCCURRED. VESSEL LEVEL DECREASED TO -18 IN. FOLLOWING THE SCRAM AND INCREASED RAPIDLY UNTIL ALL REACTOR FEED PUMPS TRIPPED AT +54 IN. THE REACTOR SCRAM WAS RESET AT 1409 HOURS AT WHICH TIME THE REACTOR WAS STABLE. THE ROOT CAUSE OF THIS EVENT WAS THE COMMON GROUNDING OF THE 'C' AND 'D' CABINETS WHICH PROVIDED A PATH FOR THE SPURIOUS SIGNAL WHICH RESULTED IN THE SCRAM. CONTRIBUTING CAUSES WERE THE FAULTY CABLE ATTACHMENT AT THE 'D'MSL RAD MONITOR DRAWER CONNECTOR WHICH CREATED THE SHORT TO GROUND AND THE DEGRADED PHYSICAL CONDITION OF THE CABLE AND DRAWER. CORRECTIVE ACTIONS INCLUDE AN ANALYSIS OF THE MSL RAD MONITOR GROUNDING CONFIGURATION FOR POSSIBLE IMPROVEMENT AND INSTRUCTION OF PERSONNEL IN THE IMPORTANCE OF RESTORING INSTRUMENT DRAWERS TO THEIR ORIGINAL CONFIGURATION.
354 | 3541988012 | 1988-04-30 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Hope Creek | B | GE | PO | 55 | On April 30, 1988 at 0550 hours, the Plant was in OPERATIONAL CONDITION 1 (Power Operation) at 100% power generating 1085 MWe when the Circulating Water System began to experience spurious pump discharge valve closures and pump trips. At approximately 0850 hours both 4.16 KVA unit substation Circulating Water System infeeds tripped, placing all Circulating Water System pumps in emergency trip condition. The reactor was manually scrammed at 0852 hours. The Main Steam Isolation Valves (MSIV) were closed at 0938 hours. All Reactor Feed Pump Turbines were tripped. With the Main Condenser isolated, High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) were placed in service. While both HPCI and RCIC were running, a high reactor water level trip occurred, reactor pressure increased and a Safety/Relief Valve (SRV) lifted. On the subsequent SRV closure, reactor water level shrank to level 3 and generated an automatic scram signal. HPCI and RCIC were then manually returned to service to control pressure and water level during shutdown. The root cause of this occurrence was failure in the Circulating Water System Multiplex (MUX) system which caused multiple spurious signals to the Circulating Water System components - an equipment failure. Corrective actions include the development of enhanced maintenance and troubleshooting practices and the planned replacement of the Circulating Water MUX system with a hard wired system.
354 | 3541988013 | 1988-05-05 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Hope Creek | B | GE | PO | 100 | On May 5, 1988 at 0917 hours, the Plant was in OPERATIONAL CONDITION 1 (Power Operation) at 100% power generating 1090 MWe, when the performance of preventive maintenance on the "A" Secondary Condensate Pump Auxiliary Oil Pump Circuit Breaker was approved. Reactor level was being maintained by the "B" and "C" Reactor Feedwater Pumps (RFP) only since the "A" Reactor Feedwater Pump Turbine (RFPT) was out of service. When the breaker was opened, the "A" Secondary Condensate Pump tripped. The reactor water level began to decrease when the suction pressure to the remaining Feedwater pumps decreased. As a result, the "B" and "C" RFPT increased in speed to compensate for the reduction in flow. Reactor level was stabilizing when the "B" turbine tripped on overspeed, resulting in a reactor water level decrease to level 3, initiating an automatic scram. The cause of this occurrence was determined to be a personnel error due to a failure to recognize the consequences of the design interface between the Secondary Condensate Pump and its Auxiliary Oil Pump. A contributing factor was the premature trip of the "B" RFPT. Corrective actions include operator training, outage requirement justifications in work orders, evaluation of need for design change, verification of the RFPT overspeed trip setpoints and departmental reviews of this event with their personnel.
354 | 3541988022 | 1988-08-26 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On August 26, 1988 at 1825 hours, the Plant was in OPERATIONAL CONDITION 1 (Power Operation) at 100% power generating 1100 MWe and the weekly Main Turbine Functional Test was in progress on August 26, 1988 at 1825 hours. The Thrust Bearing Wear Detector (TBWD) was being tested when a turbine trip occurred which caused a reactor trip. All control rods inserted without incident and all safety systems performed their design functions when called upon to do so. A level 8 (+54 in.) trip signal was generated and all Reactor Feedwater pumps tripped. The High Pressure Coolant Injection (HPCI) System initiated at level 2 (-38 in.) and injected for approximately 90 seconds before being secured. The "C" Feedwater pump was restarted to maintain level and the reactor was stabilized. An Unusual Event was declared and the NRC was notified. The root cause of this occurrence was a loose TBWD, drive motor switch actuating arm which prevented the drive motor runback and actuation of the trip function lockout switches, resulting in a main turbine trip. Corrective actions include the restoration of the TBWD and the "P" SRV to service, declaring the "M" SRV inoperable and planning for the restoration to service of all other equipment which was determined to have malfunctioned during this event.
354 | 3541988027 | 1988-10-15 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Hope Creek | B | GE | PO | 100 | On October 15, 1988 at 1625 hours, the Plant was in OPERATIONAL CONDITION 1 (Power Operation) at 100% power generating 1085 MWe when all Reactor Feedwater Pumps (RFP) tripped on a high discharge pressure signal. The resultant loss of feedwater flow caused a scram when the reactor level reached +12.5" (level 3). Reactor water level continued to decrease to -38" (level 2) at which point High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) auto initiated and injected to the vessel. Reactor water level continued to drop to -75" inches before beginning to recover. When reactor water level reached +54" (level 8) HPCI and RCIC tripped. The "B" and "C" RFPs were reset and restored to service to control vessel inventory. An Unusual Event was declared at 1640 hours when HPCI initiated and terminated at 1643 hours when reactor water level was stabilized. The sequence of events following the RFP trips was normal and expected with the exception of the failure of the drywell equipment drain inboard isolation valve to close on isolation signal. The root cause of this occurrence was a spurious RFP high discharge pressure trip signal to all three RFPs. Troubleshooting reduced the possible sources of the signal to a Bailey logic card which is common to all three RFP high discharge pressure trip circuits. Corrective actions include the replacement of all four of the Bailey logic cards in the feedwater system and further testing of the suspect Bailey card.
354 | 3541988029 | 1988-11-01 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On November 1, 1988 at 1048 hours, the Plant was in OPERATIONAL CONDITION 1 (Power Operation) at 100% power generating 1086 MWe when a main generator lockout occurred followed by fast closure of the turbine control valves, main turbine trip and reactor scram. The "A" and "B" recirculation pumps tripped as expected on an end-of-cycle recirculation pump trip logic signal. Reactor pressure increased and the "H" safety/relief valve (SRV) lifted. The "A", "B" and "C" reactor feedwater pumps (RFP) tripped on a level 8 (+54") signal. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) initiated on a level 2 (-38") signal and injected for approximately ten (10) minutes. The "C" RFP was restarted to maintain reactor water level and HPCI and RCIC were removed from service. All reactor protection system isolations occurred as expected, however the "P" SRV failed to lift due to a faulty Rosemount pressure transmitter. The loss of main generator excitation was caused by the failure of the exciter brush- collector ring assembly. The root cause of this failure could not be determined because of the extreme damage to the failed exciter brushes. Corrective actions include replacement of the exciter brushes, the development of a new procedure to replace the existing weekly brush inspection and the addition of channel checks of the Rosemount pressure transmitters associated with the low-low set SRVs to provide earlier detection of transmitter failures.
354 | 3541989017 | 1989-08-30 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Hope Creek | B | GE | PO | 82 | On August 30, 1989 at 0112, a reactor scram occurred as a result of a low reactor pressure vessel (RPV) water level (+12.5") signal. The transient was initiated by the failure of a 1/2" soldered connection where the scram pilot air line from Control Rod Drive (CRD) hydraulic control unit (HCU) 34-59 joined a 1-1/2" air header interconnecting a bank of HCU's on the south side of the Reactor Building. This failure resulted in the rapid depressurization of the scram air header, and in response, control rods began to insert. The ensuing void collapse resulted in an unrecoverable low level transient and the subsequent scram. Failure analysis following the scram determined the root cause of the initial air line failure to be deficiencies in initial installation of the air line during plant construction. Immediate corrective actions included radiography of similar joints prior to restarting th plant, leak checking all soldered connections at all 185 scram pilot air header risers, and pull testing all 185 tee joints to demonstrate the ability of the joints to withstand normal operating stresses. Long term corrective actions include completion of an ongoing testing program for instrument air piping prior to the end of the current refueling outage.
354 | 3541989025 | 1989-12-30 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On 12/30/89 at 1947, during the performance of the TBWD section of the Main Turbine Monthly Functional Test procedure, a turbine trip occurred. This trip was followed immediately by a reactor scram via the Reactor Protection System on a turbine control valve fast closure signal. All control rods inserted, and plant systems responded as expected, with minor exceptions as noted in the text of this report. Investigation subsequent to the event determined that a TBWD limit switch had malfunctioned during the test, resulting in the turbine trip circuitry sensing that the turbine end thrust bearing had actually failed. While the initiating cause of this event was the TBWD limit switch failure, the root cause of this event was the inadequate prioritization of a design change which had been pending since 1988. This design change would have modified the TBWD circuitry to prevent a turbine trip signal while testing the TBWD. Corrective actions included implementing this design change, repairing the TBWD limit switch, reviewing all other "scram reduction" design changes for adequate prioritization, reviewing other turbine trip test procedures for administrative adequacy, and incorporating this event into appropriate training programs.
354 | 3541990001 | 1990-01-06 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 97 | On 1/6/90 at 0120, during performance of a surveillance procedure which tests the Main Turbine Combined Intermediate Valves (CIV), the "A" Moisture Separator experienced a high level condition. In response to this high level condition, the associated dump valve opened, but not in time to prevent a turbine trip on moisture separator high level. Immediately following the turbine trip, the reactor scrammed on a Turbine Control Valve Closure signal from the Reactor Protection System. All control rods were verified to be inserted, and plant systems responded as expected, with minor exceptions as noted in the text of this report. Investigation subsequent to the scram determined that multiple causes combined to result in the scram - moisture separator level controllers which were not optimally tuned and the cycling of a CIV prior to stabilization of moisture separator level after cycling a previous CIV. Corrective actions included tuning of the moisture separator drain control instrumentation loops, procedurally increasing the time between cycling of CIV's during the subject surveillance, counselling the Nuclear Control Operator (NCO, RO licensed) who performed the surveillance, and including a review of the event during the next licensed operator requalification cycle.
354 | 3541990003 | 1990-03-19 | H1 | Fire | [7 empty] | X | [5 empty] | X | [19 empty] | X | [10 empty] | X | Hope Creek | B | GE | PO | 98 | On March 19, 1990 at 1850, a reactor scram occurred on low reactor vessel level (+12.5") when all feedwater pumps tripped in response to a loss of the primary and secondary condensate pumps. Following the scram, reactor vessel level decreased to below the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems initiation setpoint (vessel level 2, -38"). The HPCI and RCIC systems automatically initiated and were utilized to restore vessel inventory to normal level. <br /><br /> Investigation subsequent to the event determined that the primary and secondary condensate pumps tripped in response to a perturbation in the station electrical distribution system caused by an electrical fault in an offsite 500KV transmission line. This electrical fault was caused by flashover between two phases of the transmission line as a result of combustion particles generated during an offsite marsh fire. Switchyard relay protection cleared the fault, and during this process, a voltage reduction was propagated through all station electrical distribution systems. Investigation and testing by PSE&G Nuclear Electrical Engineering Department concluded that the voltage reduction sensed at the 120VAC (control power) level was of sufficient magnitude and duration to cause the tripping of the condensate system, which ultimately resulted in the tripping of the operating feedwater pumps. Corrective actions include continuing discussions with the local municipality on control of marsh fires, reviewing all system responses to the scram, and reviewing possible electrical system enhancements to improve electrical system stability during transients.
354 | 3541990024 | 1990-11-04 | QL5 | Partial Closure of MSIVs | [45 empty] | Hope Creek | B | GE | PO | 100 | On 11/4/90 at 0042, a Reactor Scram occurred due to Average Power Range Monitor (APRM) Fixed Neutron Flux Upscale (118% Power), which was initiated by closure of the B Inboard Main Steam Isolation Valve (MSIV). The B MSIV closure resulted from failed fitting on a Primary Containment Instrument Gas (PCIG) Supply Line to the MSIV, causing it to close. The Reactor Protection System functioned normally to shut down the Reactor. A second Scram signal occurred on low level (12.5") in the Reactor Vessel when a Nuclear Control Operator (NCO, RO licensed) placed the C Feedpump in the positioner mode, and did not adequately monitor Reactor vessel water level. Also, during the course of recovery from the scram, the Condenser Mechanical Vacuum Pumps were started to maintain vacuum in the Main Condenser due to unavailability of the Steam Seal System. This system alignment resulted in Condenser gas being released via the South Plant Vent (SPV) without the normal offgas treatment (no holdup time), and initiated an SPV Radiation Alarm. <br /><br /> Corrective Actions include performing design enhancements on the Inboard MSIV piping, evaluating further potential design changes for this piping configuration, repairing defective equipment, procedural enhancements, additional administrative guidance, licensed operator training on this event, and counselling for the NCO involved in the second Scram.
354 | 3541990028 | 1990-11-17 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On 11/17/90 at 0352, during performance of a surveillance procedure which tests the Main Turbine Combined Intermediate Valves (CIV), the "A" Moisture Separator experienced a high level condition. In response to this high level condition, the associated dump valve began to open, but level continued to rise, and the main turbine tripped on moisture separator high level. Immediately following the turbine trip, the reactor scrammed on a Turbine control Valve Closure signal from the Reactor Protection System. All controls rods were verified to be inserted, and plant systems responded as expected. Investigation subsequent to the scram determined that the initiating cause of this event to be a malfunction of the level control system for the "A" Moisture Separator. During the stations third refueling outage, inspection and testing of "A" Moisture Separator valves, controls, and internal piping was conducted. The results of these tests and inspections concluded that a primary contributor to this scram was a broken bushing on the hinge pin for the "A" Moisture Separator normal drain line check valve. The as-found condition of the check valve was evaluated as having caused the check valve to stick open. With the check valve stuck open, a backflow of condensate from the #5 feedwater heater would occur as pressure in the moisture separator decreased during CIV cycling, resulting in an increase in moisture separator level. The subject check valve was repaired prior to return from the stations third refueling outage.
354 | 3541991005 | 1991-02-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hope Creek | B | GE | PO | 24 | On 2/19/91 at 1010, while in the process of power ascension during restart following the stations third refueling outage, a reactor scram on low reactor pressure vessel (RPV) level occurred. Prior to the scram, the Nuclear Control Operator (NCO, RO licensed) controlling the reactor feedwater (RFW) system was in the process of swapping RFW control from startup level control (single element) to master level control (three element). When RFW was placed in master level control, the NCO experienced difficulty in maintaining normal vessel level (+35"), and swapped back to startup level control. A relay failure in the control circuit associated with one of the two startup level control valves (the RFW system utilizes one 3" and one 12" valve for system startup) resulted in the 12" startup level control valve driving closed during the swap. Feedwater flow through the 3" valve was not sufficient to compensate for the loss of flow through the 12" valve, and the reactor scrammed on low RPV level (+12.5"). Subsequent investigation determined that the primary cause of this event was a relay failure in the circuit controlling the 12" startup level control valve. Immediate corrective actions included relay replacement and reviewing feedwater system startup procedures for possible enhancements with respect to the RPV level transient normally experienced during the transition from single element to three element RFW control. Longer term corrective actions include reviewing operating characteristics of the feedwater system during startup evolutions to determine if hardware enhancements are necessary and reviewing the preventive maintenance program for non-safety related solid state relays.
354 | 3541991008 | 1991-05-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hope Creek | B | GE | PO | 100 | On 5/7/91, at 2102, a Reactor Scram occurred due to a low Reactor Vessel water level. Conditions leading to the Scram were the 'A' Channel Feedwater Level Control indication alarming with a high level, causing the feedpumps to back down. This was followed by the 'C' Channel alarming at 30" and a subsequent Reactor Scram. All control rods were verified to be inserted and plant systems responded as expected, with minor exceptions as noted in the text of this report. Follow-up investigation determined that the most probable cause of the event was personnel error when a Controls Technician inadvertently connected a current source to the wrong transmitter while performing a surveillance test. Although the most probable root cause was personnel error, a less than adequate cabinet design also contributed to the event. Immediate corrective actions included counseling the Controls Technician with respect to self-verification and attention to detail and implementing a design change to install test switches with input jacks and to label the input jacks with a channel designator. The surveillance procedure was revised in accordance with the design change and is being reviewed for additional enhancements.
354 | 3541992013 | 1992-12-03 | QR6 | Manual Reactor Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On 12/3/92, at approximately 0936 hrs, Control Room Operators (NCO -RO licensed) received indications of a loss of the reactor recirculation motor generator set (MG set) cooling fans. Loss of both cooling fans resulted in a trip of both reactor recirc MG sets and reactor recirculation pumps. Station Operating procedures require operators to place the Mode switch to the Shutdown position when in Operational Condition 1 with no reactor recirculation pumps in operation. Control room operators placed the Mode Switch to Shutdown position at 0937 hrs, verifying all control rods were fully inserted and all plant safety systems functioned as required. Initial investigation determined that a 480VAC motor control center (MCC) power supply had tripped resulting in the loss of the MG set cooling fans. Additional non safety related equipment such as turbine generator lift pumps, chillers and motor operated valves associated with the steam jets and feedwater heating system had lost power. The MCC feeder breaker was checked for abnormal conditions and none were noted. The MCC was re-energized and all non safety related components were restored to operation. The 'A' Reactor Recirculation pump was restarted at 1305, and was secured again at 1651 when shutdown cooling was initiated. Subsequent investigation revealed the control handle for the MCC feeder breaker was inadvertently bumped by decon techs working in the area of a 480VAC substation. Access to the breaker control area has been restricted and decon techs have been given additional training on the sensitivity of equipment in the work location.
354 | 3541993004 | 1993-05-16 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 61 | On 5/16/93 a component failure in the Electrohydraulic Control (EHC) System resulted in a Generator/Turbine Trip and Reactor SCRAM on Reactor High Pressure. The transient occurred while testing the No.2 Turbine Stop Valve during the Weekly Turbine overspeed Protection Surveillance. Operating pressure exceeded 1037 psig and reactor water level reached -5 inches. Lo Lo Set pressure was reached and "P"&"H" safety relief valves (SRV) cycled open once. Plant systems and components responded as expected. The root cause was attributed to a failed Agastat relay on an EHC control card. corrective actions included troubleshooting and replacement of specific components. The EHC System was monitored and valve testing was repeated successfully during plant startup prior to exceeding 30% power.
354 | 3541993012 | 1993-12-01 | QR6 | Manual Reactor Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On Tuesday, November 30, 1993, at 2100 hours, the equipment operator (NEO -nonlicensed) performing routine equipment inspections noticed sparking on the main generator exciter brushes. The nuclear shift supervisor (NSS - SRO licensed) and shift electrician were notified and inspected the exciter brushes both confirming that the sparking was excessive and immediate corrective actions were required. Additional off-duty personnel from system engineering and maintenance were called in to determine the cause of the sparking and whether the brush change should be attempted. After verifying normal current readings on the collector ring, it was determined that the brush was worn and replacement should be attempted. When the electrician pulled the brush assembly the remaining brushes on that ring began to spark violently. An immediate recommendation was made by system engineering to take the generator off line. Control room personnel were notified who reduced reactor recirculation flow to minimum and inserted a manual scram. All immediate operator actions following the scram were appropriate and all plant systems functioned normally. The root causes of this event were attributed to inadequate inspection guidelines and different style brushes being supplied by the vendor under the same part number. Corrective actions include revising the monthly inspection procedure, performance of additional weekly inspections and removing the incorrect style brushes from stores.
354 | 3541994007 | 1994-05-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hope Creek | B | GE | PO | 96 | On Sunday May 15, 1994 at 1207 hours Nuclear Control Operators (NCO - RO licensed) commenced a reactor power reduction from 100% to 95% to remove the 'A' Reactor Feed Pump (RFP) from service for planned maintenance to repair a bearing temperature problem. At 1300 hours the 'A' RFP was secured from feeding the reactor vessel and at 1315 operators began a power increase to 100% of rated using the reactor recirc pumps. At 1317, and 1318 respectively, the new Digital Feedwater Control System (DFCS) automatically transferred the remaining 'B' & 'C' RFP's speed control from auto to manual. Reactor water level began to decrease due to the feedpumps being in manual and the increase in power from recirc pump speed increases. At 1322 the NCO received a Level 4 alarm (+30 inches) and an invalid intermediate runback occurred on the 'A' reactor recirculation pump. The control operator attempted to restore reactor level by manual operation of the 'B' and 'C' feedpumps. Due to the non linear response of the newly installed DFCS, operators could not mitigate the level transient resulting in a low reactor level scram at 1325. The root causes of this event were attributed to design deficiencies associated with enhancements made to the DFCS and inadequate training for manual operation of the new control system. Corrective actions included design changes to correct problems noted in the DFCS and additional simulator training with the feedwater controls.
354 | 3541994011 | 1994-08-01 | QR8 | Spurious Reactor Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On 8/1/94, Instrument and Controls technicians (I&C techs non-licensed) were in the process of installing measuring and test equipment (M&TE) in order to perform an intermediate range neutron monitor (IRM) surveillance. As the final connection was being made, a spark occurred at the connector shocking the technician and causing two average power range monitors (APRM's) (one each in channel A and B) to invalidly indicate upscale high initiating a reactor scram. The plant response was per design and the operator response was appropriate and effective. The root cause was a damaged isolation transformer that placed a 120VAC signal on the IRM C cable shield. The voltage on the IRM C cable shield induced currents in the adjacent LPRM signal cables resulting in a sensed false high neutron flux input to APRM's C and D. Additionally, failure to inspect the test equipment prior to use, failure to perform routine activities which the technicians are trained to perform and inadequate procedural guidance to enable the testing to be performed in a safe manner, collectively contributed to this event. corrective actions for this event include a program to provide periodic maintenance and inspection of non-calibrated test equipment and a review of the event with appropriate personnel for lessons learned in regard to the hazards to personnel and the plant when working with intentionally ungrounded equipment. Personnel have been instructed that any equipment which has been inadvertently bumped or dropped must be checked and repaired prior to use. Additionally, all procedures which utilize 'floated' test equipment will be revised, as necessary, to provide clear instructions within the body of the procedure on how test equipment is to be 'floated' and checked for personnel safety.
354 | 3541994012 | 1994-08-30 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Hope Creek | B | GE | PO | 100 | On Tuesday, August 30, 1994, with the plant operating at 100% power, Maintenance department personnel were performing 24 month environmental qualification preventive maintenance on a fuel pool heat exchanger motor operated valve. During the course of the inspection, at the valve operator, a short circuit occurred which caused a trip of the logic system for the associated channel. The loss of the logic power resulted in a partial isolation of the 'A' Safety Auxiliaries Cooling System (SACS) which was supplying the Turbine Auxiliaries Cooling System (TACS) at the time of the event. This resulted in a loss of cooling water to the turbine-generator coolers as well as other nonessential loads. The 'B' SACS loop auto initiated per design to supply TACS, but due to the incomplete isolation of the 'All SACS loop, the 'B' SACS loop isolated on low head tank level as water transferred from the 'Bit to 'All head tanks. A turbine-generator load runback resulted from the loss of cooling followed by a reactor scram on high pressure (1037 PSIG). Following the scram operators were able to restore the 'A' SACS loop to supply TACS. The root causes of this event were an incorrectly sized fuse in a logic module and failure of the standby SACS loop to supply TACS loads. Corrective actions included installing the proper size fuse, a check of the components downstream of the oversized fuse, work practice changes regarding both fuse replacement and energized work. Additionally a design review of the SACS transfer scheme will be conducted, as well as a review of this event during continuing training with all departments involved in this event.
354 | 3541994014 | 1994-10-02 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On Sunday evening, October 2, at 2036, with the unit operating at 100% of rated power, a reactor scram occurred due to a sudden trip of the main turbine generator. The main turbine trip and trip of the 'B' reactor feed pump were not preceded by any alarms or indications of a problem with either component. Control room personnel took appropriate actions to verify the scram and that all automatic actions were complete. A review of the alarm chronolog did not indicate the source of the turbine trip. A review of the turbine first hit panel (local EHC cabinet) indicated the customer trip (Reactor Level 8 @ +54'), caused the main turbine trip. The main turbine control valve closure input to RPS provided the scram signal. The turbine trip resulted in a high reactor pressure above the LO-LO SRV setpoint for H and P valves and opening of 'K' on its safety valve function. In addition a dual recirc pump trip and alternate rod insertion signals were provided when pressure increased above the ARI and RRCS initiation setpoints. The reactor water cleanup isolation valve 1BG-HV-F001 also closed due to level instrument ringing. The cause of the main turbine trip and subsequent scram, was due to a design deficiency in the Digital Feedwater Control System (DFCS). The design was to require two redundant high level signals to cause a main turbine trip. The system was actually configured such that either of two signals would trip the turbine. Corrective actions included a design change to correct the deficiency, as well as, testing of the bailey logic card which is suspected of failing and initiating this event. The Engineering department has also completed a review of the DFCS and is confident that critical portions of the system have been designed, installed, modified and tested appropriately to assure proper operation.
354 | 3541994015 | 1994-10-07 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 16 | On Friday, October 7, 1994, with a reactor startup in progress, operators were preparing to roll the main turbine generator. The reactor was operating at approximately 15% of rated with 6 turbine bypass valves open. The Nuclear Control Operator (NCO - RO licensed) had selected the 100 RPM speed demand at the Electro Hydraulic Control System (EHC) panel which should have brought the turbine to the selected speed. The NCO monitoring the turbine roll initially observed normal responses from the Turbine Stop Valves (TSV's) position indicators, the 'all valves closed' light extinguishing and the 'speed increasing' light illuminating. The operator then observed that all turbine bypass valves had closed. This unexpected response was immediately recognized and communicated to other control room personnel by both the NCO and Shift Technical Advisor (STA - SRO licensed). Control room personnel concurrently noted turbine speed had exceeded the 100 RPM selected speed and was accelerating rapidly. The Nuclear Shift Supervisor (NSS - SRO licensed) directed the NCO to trip the main turbine. The NCO recommended to shut down the turbine by selecting 'all valves closed'. When the turbine 'all valves closed' was selected and the valves began to close, a reactor scram occurred. The root cause of this event was attributed to failed components in the EHC control circuit. A contributing factor was operators not recognizing the abnormal plant conditions indicated on the EHC panel when the turbine was reset prior to initiating the turbine roll. Corrective actions included replacement of the EHC card, revising the turbine roll procedures and expanding operator training to include actions to be taken when abnormal plant responses are noted.
354 | 3541995005 | 1995-03-20 | QR6 | Manual Reactor Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On Monday, March 20, 1995, at approximately 08:45, two Instrument and Controls technicians were taking voltage readings on an Optical Receiver Module in a Bailey cabinet located in the lower relay room. As the performer inserted his leads in the first channel, he noticed he did not get a valid reading on his hand-held Digital MultiMeter (DMM). As the technician attempted to adjust the test leads a false breaker trip signal was generated that resulted in a trip of both Reactor Recirculation Pump Motor Generator (MG Set) Drive motor breakers. Upon receipt of the annunciators indicating the Recirculation Pumps had tripped, Control Room Operators (NCO-RO Licensed) placed the reactor mode switch to shutdown inputing a manual scram. Corrective actions include: a design change to eliminate the MG set motor breaker trip which initiated this event, Maintenance Department is reviewing all events associated with misuse of M&TE to ensure lessons learned have been adequately addressed, Maintenance Department is currently reviewing the type of M&TE that is utilized in regard to human factors and checking to ensure that only authorized test equipment is being utilized. Maintenance Supervisors will review their roles and responsibilities regarding pre job briefings, visiting the job site, work standards and use of M&TE.
354 | 3541997022 | 1997-09-10 | QR6 | Manual Reactor Trip | [45 empty] | Hope Creek | B | GE | PO | 76 | On 9/10/97, at 1033, a Main Transformer Trouble alarm was received in the Control Room. Equipment operators were dispatched to investigate and to determine the source of the alarm. The operators discovered the cooling fans and oil pumps on the "A" Phase Main Generator Step-Up Transformer were not operating, heard "popping" noises, and noticed a smell coming from the transformer. This information was relayed to the Control Room. Operations initiated a reactor recirculation pump runback that lowered reactor power level to 38%. At 1040, a manual scram was initiated using the mode switch. At 1041, the main generator was manually tripped. All control rods were verified to be inserted and all systems responded as expected. The loss of cooling was due to a failed relay in the transformer's control panel, which caused the oil pumps and cooling fans to trip. The apparent cause of the failed relay was internal coil heating that caused the coil temperature to exceed the capacity of the insulation. Corrective actions include replacing the relay in the "A", "B", and "C" transformers and considering preventive maintenance. on 9/10/97, at 1344, a four hour notification was made to the NRC in accordance with 10CFR50.72(b)(2)(ii). This event is being reported pursuant to 10CFR50.73(a)(2)(iv) as an Engineered Safety Feature actuation due to the unplanned manual reactor scram.
354 | 3541998008 | 1998-11-15 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 95 | On November 15, 1998, at approximately 0922, the main turbine tripped due to "A" moisture separator high level and the reactor scrammed automatically in response to the closure of the turbine control valves. All control rods inserted properly and all safety related equipment performed as designed, with the exception of safety relief valve "D" which opened prematurely, and the Reactor Protection System channel "B1" reactor pressure vessel steam dome pressure - high signal which was received 1.3 seconds after the redundant signals. This event was initiated by the inadvertent isolation of instrument air from the "A" and "B" moisture separator drain tank (MSDT) normal level control valves and the failure of the "A" MSDT dump valve to open. After the automatic scram, Surveillance Requirements for suppression chamber-drywell vacuum breakers and for the Average Power Range Monitor neutron flux-upscale setdown function were not performed as required by Technical Specifications. There were no safety consequences associated with this event. Corrective actions include testing the MSDT dump valves and developing an event driven Surveillance Requirements matrix.
354 | 3542002004 | 2002-06-22 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Hope Creek | B | GE | PO | 100 | On June 22, 2002 at approximately 1417, Hope Creek Generating Station experienced an automatic reactor scram as a result of a turbine trip due to high moisture separator (MS) level. The high MS level resulted from failure of the level controls to adequately respond to the transient, due in part to two phase flow in the drain path. The initiating event that ultimately resulted in the scram was failure of a logic card that caused a secondary condensate pump (SCP) to trip. The automatic reactor scram was successful, but anomalous control rod position indications immediately after the scram prompted operators to initiate alternate rod insertion in accordance with procedures. Condensate flow to feedwater heaters 1 and 2 isolated due to high heater feedwater level; operators manually established bypass flow. Cooldown was in accordance with Technical Specification limits and there were no safety consequences as a result of this event. Corrective actions include replacement of the SCP logic card, corrective maintenance of the normal MS drain control loop and adjustments to the MS dump valve controls to improve response time. This event is reportable under 10 CFR 50.73 (a)(2)(iv)(A) as an actuation of the reactor protection system.
354 | 3542003007 | 2003-09-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hope Creek | B | GE | PO | 100 | On September 19, 2003 at 2041 hours, Hope Creek reactor scrammed on low reactor water level following a reduction in feed water flow when two of the three reactor feed pumps tripped. The 'A' reactor feed pump turbine (RFPT) tripped when power was lost to the main and auxiliary lube oil pumps. The 'C' RFPT tripped when power was lost to the main lube oil pump and the auxiliary pump did not recover oil pressure prior to the protection logic sensing low oil pressure. The initiating event that led to loss of power was an electrical transient in the station switchyard. The electrical transient was due to an accumulation of salt on switchyard components following Hurricane Isabel. As a result of the electrical transient, the 'A' and 'C' emergency diesel generators successfully started and loaded to their 4160 volt Class 1E busses. The cause of the reactor scram was low reactor water level which resulted from an electrical transient and the loss of two reactor feed pumps due to the failure of the RFPT lube system to maintain proper oil pressure. There were no safety consequences associated with this event. Corrective actions included removing salt from switchyard components and modifying the procedural alignment of the RFPT lube oil pumps to improve reliability. This event is being reported in accordance with 10CFR50.73 (a) (2) (iv) (A).
354 | 3542003008 | 2003-10-04 | QR6 | Manual Reactor Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On October 4, 2003, at 1646 hours, with the plant at 100% power, Control Room Operators received an alarm for low level in the Electro-Hydraulic Control (EHC) system reservoir. Operators entered the appropriate abnormal operating procedure. Field investigation indicated that level in EHC oil reservoir was at approximately -3.5 inches and continuing to lower. At 1713 hours the reactor recirculation pumps were reduced to minimum speed and the reactor was manually scrammed at a reduced power level. The No. 1 and 2 feedwater heater strings automatically isolated following the scram and the feedwater heater bypass valve was opened in accordance with abnormal operating procedures. While reducing Reactor pressure to 500 - 600 psig, the two Reactor Water Cleanup (RWCU) pumps tripped. Two Reactor Water Level 3 Reactor Protection Signal (RPS) scram signals (+12.5 inches) were generated following the manual scram. Following the reactor scram, the EHC leak was identified and isolated allowing the Turbine Bypass Valves (BPV) to be used to control pressure during the plant shutdown. Reactor water level was maintained with the secondary condensate pumps. The cause of the manual scram was attributed to the EHC leak at the No. 4 Combined Intermediate Control Valve (CIV). The cause of the EHC leak is attributed to the failure to properly assemble the No. 4 CIV following cleaning. Corrective actions include procedure changes, lessons learned training and reinforcement of maintenance standards. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A).
354 | 3542004001 | 2004-01-12 | QL5 | Partial Closure of MSIVs | [45 empty] | Hope Creek | B | GE | PO | 67 | On January 12, 2004, at 1015 hours during the performance of 18-month Technical Specification calibration of the 'C' channel Reactor Building Exhaust (RBE) radiation monitor, the 'A' channel RBE radiation monitor actuated resulting in an actuation of the Primary Containment Isolation System (PCIS). The actuation of PCIS caused the isolation of the Primary Containment Instrument Gas (PCIG) supply to the in board Main Steam Isolation Valves (MSIVs). Prior to restoration of the PCIG system, the 'D' and 'B' inboard MSIVs began to drift closed. Anticipating the receipt of an automatic scram, the Reactor Operator (RO) manually scrammed the reactor by placing the mode switch to the shutdown position at 1048 hours. Shortly after the scram, the 'A' and 'C' MSIVs began to drift closed. At 1051, PCIG was restored and the inboard MSIVs returned to the open position. The inboard MSIVs never went fully closed which ensured that the main condenser remained available throughout the event for reactor heat removal. Following the manual scram, a low reactor water level scram signal was received (Level 3, +12.5 inches) as expected. At 2123 hours, a second invalid actuation of the PCIS occurred due to equipment related problems. The cause of the PCIS actuation that led to the manual scram is attributed to a loose LEMO connector on the 'A' channel RBE radiation monitor that allowed intermittent contact when a nearby conduit was used as a hand hold to gain access to the 'C' channel RBE radiation monitor for surveillance testing. The apparent cause of the second invalid PCIS actuation is attributed to faulty Bailey cards associated with the RBE high radiation input to PCIS. The corrective actions associated with this event consist of procedure enhancements, emphasizing standards with maintenance personnel, re-evaluation of the scheduling of surveillance testing, and the repair/replacement of equipment. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A).
354 | 3542004010 | 2004-10-10 | K1 | Steam Line Break Outside Containment | [9 empty] | X | X | [25 empty] | X |  |  | X | X |  |  |  |  | Hope Creek | B | GE | PO | 69 | On October 10, 2004, at 1814 hours, the reactor recirculation pumps were taken to minimum speed and the reactor was scramed due to a steam leak (pipe failure) in the turbine building. Immediately following the scram, a reactor water Level 3 (+12.5") scram signal was received as expected due to water level shrink in the reactor vessel. As a result of the pipe failure, condenser vacuum degraded. Operators began to depressurize the reactor to transition water level control to the condensate system. Prior to establishing condensate feed control, a Level 2 (-38") reactor water level actuation was reached on the A and B channels. High Pressure Coolant Injection (HPCI) automatically started and Channel A and B isolations and actuations occurred. The main steam isolation valves (MSIVs) were manually closed by the operators prior to automatic closure due to degrading condenser vacuum. Another Level 3 scram signal occurred during plant stabilization while HPCI and Reactor Core Isolation Cooling (RCIC) were being used to control reactor pressure and level. During the cooldown of the plant using the safety relief valves (SRV), an additional Level 3 scram signal occurred due to level shrink when the SRV was closed. Hope Creek achieved cold shutdown on October 12 at 0509 hours. The cause of the manual reactor scram was the failure of a moisture separator dump line to the condenser. Corrective actions, in part, include repair of the failed piping, procedure changes, development of an Operational and Technical Decision Making process, and Licensed Operator training concerning this event. The above events are being reported in accordance with 10CFR50.73(a)(2)(iv)(A).
354 | 3542005003 | 2005-06-07 | G1 | Very Small LOCA or Leak | [6 empty] | X | [18 empty] | X | [19 empty] | Hope Creek | B | GE | PO | 100 | On June 7, 2005, at 1413 hours, the reactor recirculation pumps were taken to minimum speed and the reactor mode switch was locked in shutdown to scram the reactor due to increasing drywell pressure and drywell floor drain leakage. An Unusual Event (UE) was declared at 1437 hours due to drywell floor drain leakage exceeding 10 gpm.The operating crew took action to bring the plant to a cold shutdown condition and a drywell entry was performed. At 0240 hours on June 8, 2005, the source of the leak was determined to be from the F050A residual heat removal (RHR) check valve position indicator. On June 8, 2005, at 0336 hours, the B RHR loop was placed in shutdown cooling and Operational Condition 4 was entered at 0456 hours. The UE was terminated at 0515 hours on June 8,2005. The cause of the reactor coolant system leak was the result of an approximately 280 degree circumferential crack in the position indicating tube for the F050A RHR check valve. The through wall leak was caused by the vibration of the attraction sleeve (which is on the end of actuator rod) in the presence of the switch magnetic force resulting in the attraction sleeve fretting/wearing through the position indicating tube. Corrective actions consist of modification of the F050A and F050B RHR check valves, ultrasonic testing of the six other check valves with the same position indicating tubes, development of preventative maintenance activities and an engineering review of components and sub-components communicating with the pressure boundary of the loop 'A' and 'B' reactor recirculation piping. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(A), "the completion of any nuclear plant shutdown required by the plant's Technical Specifications," 10CFR50.73(a)(2)(iv)(A), 'any event or condition that resulted in manual or automatic actuation of ...reactor protection system (RPS) including: reactor scram or reactor trip," and 10CFR50.73(a)(2)(ii)(A), "any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded."
354 | 3542007001 | 2007-01-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hope Creek | B | GE | PO | 21 | On January 29, 2007 during a plant startup from a planned outage with the reactor at 21% power and the main generator synchronized to the grid, an automatic reactor scram occurred due to low reactor water level. The root cause of the scram was a failure of the instrument tap weld at the flow nozzle for the C Reactor Feed Pump (RFP) Minimum Flow Line. This failure caused reduced indicated flow to the "C"RFP minimum flow control system logic and an increased minimum flow valve opening demand signal. As a result of these conditions reactor level could not be maintained and fell below the reactor low-level set point. Corrective actions include repair of the affected weld and an extent of condition review to identify other potential weld deficiencies.
354 | 3542007002 | 2007-05-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hope Creek | B | GE | PO | 100 | On May 29, 2007 while operating with the reactor at 100% power and the main generator synchronized to the grid, a manual scram was initiated in anticipation of low reactor water level condition. An unexpected slow (dead bus) transfer of a 4 KV Class 1-E bus from the normal to alternate source occurred during monthly relay testing. The slow (dead bus) transfer and subsequent loss of a non-safety related motor control center (MCC) resulted in a loss of feed water followed by a reactor scram. A personnel error initiated the slow bus transfer and a low margin condition asscciated with the reactor feed pump oil system design caused a loss of 2 reactor feed pumps. As a result of these conditions reactor level could not be maintained and operators took the action to manually scram the reactor. After the scram, reactor water level lowered to Level 2 and a valid ECCS initiation signal caused HPCI and RCIC to start and inject to the core. The ECCS injection required a 4-hour report that was transmitted to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(A). Corrective actions included revising the surveillance procedure to require testing only be performed on an open breaker and to verify that the relay contacts are in the correct state upon completion of the surveillance. Operating procedures were revised to maintain both Reactor Feedwater Pump (RFP) Lube Oil pumps operating for each RFP.
354 | 3542009001 | 2009-01-17 | QR6 | Manual Reactor Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On January 17, 2009 at 0432, a manual reactor scram was initiated by the operator at the controls by locking the mode switch in the SHUTDOWN position in response to a runback of the turbine generator caused by the current/flow comparator circuit of the stator water cooling (SWC) system. The runback was in response to a loss of the Turbine Auxiliary Cooling System (TAGS) loads due to (1) a solenoid valve failure of one of the TACS supply isolation valves (EG-HV-2522C) which caused the isolation valve to close and the system to transfer to the alternate TAGS supply; and (2) automatic isolation of the alternate TACS water supply due to a LO-LO-LO expansion tank level during the automatic transfer. The loss of cooling to the TAGS loads caused the SWC temperatures to increase, activating the runback circuitry for the turbine generator and the recirculation motor generators. The manually-initiated scram was In anticipation of a turbine generator trip and subsequent load reject that would have been caused by the high SWC temperatures after a time delay. The reactor was at 100% power at the beginning of the event and was approximately 73% power when the manual scram was initiated. Two control rods near the periphery of the core inserted past position "00" ("Full ln"} and did not settle to position "00". The control rods were subsequently tested for channel distortion and were determined to be operable. An ENS notification was made (event number 44784) at 0725 on January 17, 2009, in accordance with 10 CFR 50.72(b)(2)(iv)(6). All other safety systems functioned as required.
354 | 3542009004 | 2009-05-17 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Hope Creek | B | GE | PO | 100 | On May 17, 2009, at approximately 0335, an automatic scram signal was received due to a low RPV water level condition when multiple control rod drives (CRDs) inserted into the reactor core causing lower reactor power and the collapse of voids in the core. The multiple CRD motion was caused by an air leak on the scram air header at hydraulic control unit (HCU) 22-11 (corrective action program (CAP) number: 20415621). The leak was from the separation of a copper solder connection which had been previously identified as having an air leak, but which was not entered into the corrective action process for resolution due to an oversight while reviewing diagnostic test data. The root cause investigation (RCE) determined that there were inconsistent expectations for the supplemental personnel's reporting of test or inspection results that led to the degraded condition not being correctly identified in the CAP to initiate timely repair. An ENS notification (number 45074) was made in accordance with 10CFR50.72(b)(2)(iv)(B) -- an event or condition that results in actuation of the reactor protection system when the reactor is critical. This event is also reportable under 50.73(a)(2)(iv)(A) for actuation of a system listed in 50.73(a)(2)(iv)(B)(1) -- reactor protection system (RPS).
354 | 3542013002 | 2013-06-12 | QL7 | Degraded condenser vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Hope Creek | B | GE | PO | 100 | On June 12, 2013, at 13:33, Hope Creek Unit 1 was manually scrammed from approximately 100 percent rated thermal power due to degrading main condenser vacuum. This condition occurred due to the trip of the 'B' circulating water (CW) pump with the 'B' CW discharge valve stuck in the full-open position. Operators initiated a manual scram when condenser vacuum reached 6.5 inches of mercury absolute (HgA). During the scram response, the operating reactor feed pump tripped due to degrading vacuum and the operators manually placed the reactor core isolation cooling (RCIC) system in service for reactor inventory control. Operators completed the scram response procedures and placed the plant in a stabilized hot shutdown condition. <br /><br /> Immediate corrective actions included replacing the 'B' CW discharge valve and replacing the auxiliary relay card for the 'B' CW pump trip during the forced outage. Additional corrective actions include establishing a program for performing failure analysis, "metallic whisker" evaluations, and trending of circuit card failures in accordance with IN PO and EPRI recommendations, and establishing a preventative maintenance program for replacement of the Bailey auxiliary relay cards. <br /><br /> The cause of the 'B' CW pump trip was due to conductive filament growth that bridged across two solder traces on the auxiliary relay card, creating a short circuit, and generating a CW pump trip signal. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a valid manual actuation of the reactor protection system and manual initiation of the RCIC system.
354 | 3542013008 | 2013-12-01 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 100 | On December 1, 2013, at 06:13 EST, Hope Creek Unit 1 automatically scrammed from 100 percent rated thermal power due to a main turbine trip. The main turbine trip was due to high level in the 'A' moisture separator (MS). As a result of the scram, both reactor recirculation pumps tripped and three safety relief valves opened. The plant was stabilized in hot shutdown Operational Condition 3.<br /><br /> The MS normal level controller failed due to a ruptured bellows causing the MS drain valves to close. The MS dump valve controller attempted to maintain MS level and cycled the dump valve as required. After multiple cycles, the dump valve failed in the closed position. This caused the MS level to increase above the main turbine trip setpoint, resulting in the main turbine trip and the subsequent automatic reactor scram.<br /><br /> A root cause evaluation determined the cause of the MS dump valve failure was thermal binding.<br /><br /> The MS drain and dump valve controllers were replaced, calibrated, and functionally tested. The root cause evaluation performed after a second scram on high MS level on December 5, 2013, determined that the MS dump valve clearances need to be modified to prevent thermal binding.<br /><br /> This is an event reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in actuation of the reactor protection system.
354 | 3542013009 | 2013-12-05 | QR5 | Turbine Trip | [45 empty] | Hope Creek | B | GE | PO | 75 | On December 5, 2013, at 03:25 EST, Hope Creek Unit 1 automatically scrammed from approximately 75 percent rated thermal power due to a main turbine trip that was caused by a high level in the 'A' moisture separator (MS). The MS high level control loop was in the process of being tuned when the dump valve cycled repeatedly and subsequently failed closed. The main turbine trip automatic reactor scram resulted in a trip of both reactor recirculation pumps. The plant was stabilized in hot shutdown Operational Condition 3. During the recovery of the recirculation pumps, the digital electro-hydraulic control system was mis-operated which caused the turbine bypass valves to cycle. This caused reactor level to swell above Level 8 then shrink below Level 3 resulting in a second actuation of the reactor protection system.<br /><br /> A root cause evaluation determined the cause of the MS dump valve failure was thermal binding.<br /><br /> MS dump valve control has been modified from a modulating function to a full open function on high level to prevent valve cycling. The root cause determined that the MS dump valve clearances need to be modified to prevent thermal binding.<br /><br /> This is an event reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the reactor protection system.
354 | 3542015005 | 2015-09-28 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Hope Creek | B | GE | PO | 100 | On September 28, 2015, at 20:46, with the Hope Creek reactor operating at 100% power, a human error during surveillance testing resulted in the actuation of the Redundant Reactivity Control System (RRCS), and subsequently, an automatic reactor scram on a valid low water level signal. At the time of the transient, a surveillance test of division 1 of the RRCS system was in progress. The test simulates a high reactor pressure signal. Plant data show the signal was entered in both channels of division 1 of the RRCS system. The resulting system actuation caused a trip of both Reactor Recirculation Pumps, and the actuation of the Alternate Rod Insertion (ARI) function of the RRCS system. As a result of these two actuations, reactor power lowered, causing reactor water level to lower to the Reactor Protection System (RPS) trip set point of +12.5 inches. The RPS initiated an automatic reactor scram. Reactor operators recovered water level to within the desired band using the feedwater system. Reactor pressure was maintained using turbine bypass valves discharging to the main condenser. <br /><br /> This report is being submitted under 10 CFR 50.73(a)(2)(iv)(A), as an event or condition that resulted in the actuation of the Reactor Protection System.
354 | 3542019001 | 2019-08-03 | QL7 | Degraded condenser vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Hope Creek | B | GE | PO | 37 | At 1906 EDT on August 3 2019, while in OPCON 1 at 93.8 percent power, operators identified degrading main condenser vacuum and commenced reducing power. Degrading vacuum was due to the circulating water cooling tower bypass valve failing open At 1947, the reactor was manually scrammed from 37 percent due to loss of condenser vacuum. Reactor feedwater pumps (RFP) tripped when reactor pressure vessel (RPV) water level rose to level 8 (+54 inches) because the reactor feedwater startup level control valve (SULCV) failed open Operators initiated the reactor core isolation cooling (RCIC) system, recovered a RFP and secured RCIC after establishing control of RPV water level The failed equipment was replaced. <br /><br /> This event is reportable per 10 CFR 50 73(a)(2)(iv)(A).
361 | 3611987001 | 1987-02-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | San Onofre 2 | P | CE | PO | 100 | POWER LEVEL - 100%. ON 2/5/87 AT 0800, WITH UNIT 2 AT 100% POWER, THE REACTOR WAS MANUALLY TRIPPED BY OPERATIONS PERSONNEL OBSERVING THE CLOSURE OF MAIN FEEDWATER BLOCK VALVE 2HV-4051. THE RESULTING LOW STEAM GENERATOR LEVELS INITIATED AN EMERGENCY FEEDWATER ACTUATION GNAL (EFAS). ALL SYSTEMS FUNCTIONED AS DESIGNED, AND THE TRIP RECOVERY PROCEEDED NORMALLY. THIS EVENT HAD NO EFFECT ON THE HEALTH AND SAFETY OF PLANT PERSONNEL OR THE PUBLIC. AT APPROXIMATELY 0755, THE CONTROL OPERATOR (CO) OBSERVED THAT THE RED (OPEN) POSITION INDICATING LIGHT FOR 2HV-4051 WAS EXTINGUISHED, AND INITIATED AN INVESTIGATION. AT 0800, THE '2HV-4051 TROUBLE' ALARM WAS RECEIVED AND THE FLOW TO THE ASSOCIATED STEAM GENERATOR SUDDENLY FELL BELOW 50%. THE CO RECOGNIZED AN AUTOMATIC TRIP WAS IMMINENT, AND MANUALLY TRIPPED THE REACTOR. THE VALVE CLOSURE WAS APPARENTLY THE RESULT OF A CONSTRUCTION CONTRACT ELECTRICAL TEST TECHNICIAN ERRONEOUSLY PERFORMING WORK IN THE UNIT 2 VALVE CONTROL CABINET. WORK HAD BEEN AUTHORIZED IN THE UNIT 3 VALVE CONTROL CABINET LOCATED IN THE SAME ROOM. BOTH CABINETS WERE CLEARLY LABELED. ELECTRICAL TEST TECHNICIANS TESTED THE CIRCUITRY AND DEMONSTRATED THAT THE IMPLEMENTATION OF THE WORK PLAN IN THE UNIT 2 VALVE CONTROL CABINET PRODUCED RESULTS IDENTICAL TO THE INDICATIONS OBSERVED.
361 | 3611987004 | 1987-03-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | San Onofre 2 | P | CE | PO | 85 | POWER LEVEL - 085%. AT 0010 ON 3/28/87, WHILE REDUCING UNIT 2 REACTOR POWER FROM 100% TO 85% TO PERMIT CLEANING OF A CONDENSER WATER BOX, THE REACTOR TRIPPED ON A LOW LEVEL IN STEAM GENERATOR E-089 AFTER MAIN FEEDWATER CONTROL VALVE 2FV-1111 UNCOUPLED FROM THE ACTUATOR, CAUSING A REDUCTION IN FLOW. THE EMERGENCY FEEDWATER ACTUATION SYSTEM (EFAS) ACTUATED AS DESIGNED TO PROVIDE AUXILIARY FEEDWATER AND RESTORE STEAM GENERATOR LEVELS TO NORMAL. INSPECTION OF 2FV-1111 FOUND THE LOCKNUT THAT SECURES THE VALVE STEM TO THE ACTUATOR HAD LOOSENED. INSPECTION OF THE REMAINING FEEDWATER CONTROL VALVES IN BOTH UNITS 2 AND 3 WAS PERFORMED AND ALL VALVE STEMS WERE FOUND TIGHTLY SECURED TO THE COUPLING BLOCK. SUBSEQUENT INVESTIGATION DETERMINED THAT THE LOCKNUT MAY NOT HAVE BEEN ADEQUATELY TORQUED DURING CALIBRATION OF THE VALVE ON 3/17/87 SINCE TORQUING REQUIREMENTS FOR THE LOCKNUT WERE NOT SPECIFIED IN THE CALIBRATION PROCEDURE. APPROPRIATE PROCEDURES HAVE BEEN REVISED. ANTI-ROTATIONAL LOCKING WASHERS HAVE BEEN INSTALLED ON THE UNIT 2 MAIN FEEDWATER CONTROL VALVES. RELATIVE POSITION INDICATION OF MAIN FEEDWATER FLOW CONTROL VALVES WILL BE REVIEWED DAILY TO IDENTIFY CHANGES INDICATIVE OF IMPENDING UNCOUPLING UNTIL THE ANTI-ROTATIONAL LOCKING WASHERS ARE INSTALLED ON THE UNIT 3 MAIN FEEDWATER FLOW CONTROL VALVES AT THE NEXT REFUELING OUTAGE.
361 | 3611987031 | 1987-12-17 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | San Onofre 2 | P | CE | PO | 75 | POWER LEVEL - 075%. AT 0831 ON 12/17/87, WITH UNIT 2 AT 75% POWER, ONE OF TWO MAIN FEEDWATER ISOLATION VALVES (MFIV) FAILED CLOSED, CAUSING BOTH MAIN FEEDWATER PUMPS TO TRIP ON DISCHARGE PRESSURE. UNIT 2 WAS MANUALLY TRIPPED IN ACCORDANCE WITH OPERATING PRACTICE TO MINIMIZE THE EFFECTS OF THE LOSS OF FEEDWATER. CONCURRENT WITH THE AUTOMATIC INITIATION OF THE EMERGENCY FEEDWATER ACTUATION SYSTEM FOR STEAM GENERATOR #2 (EFAS 2) AS A RESULT OF LOW LEVEL IN STEAM GENERATOR #2, EFAS 1 (FOR SG #1) AND EFAS 2 WERE MANUALLY ACTUATED. PLANT CONDITIONS WERE STABILIZED, AND RECOVERY PROCEEDED NORMALLY. THIS EVENT HAD NO EFFECT ON THE HEALTH AND SAFETY OF PLANT PERSONNEL OR THE PUBLIC SINCE ALL SAFETY SYSTEMS OPERATED AS DESIGNED. THE THREADED CONDUIT CONNECTION TO THE AFFECTED MFIV SOLENOID WAS FOUND LOOSE, AND THE CABLE PENETRATION AREA INTO THE CONDUIT CONNECTOR WAS NOT SEALED. BY ONE OR BOTH OF THESE PATHS, WATER AND FOREIGN MATERIAL ENTERED THE SOLENOID HOUSING AND CAUSED CORROSION OF THE POWER LEADS AND TERMINAL BLOCK. THIS RESULTED IN FAILURE OF THE POWER LEAD TO THE MFIV SOLENOID AND CLOSURE OF THE MFIV. THE MAINTENANCE PROCEDURE FOR REASSEMBLY OF THE SOLENOID DID NOT PROVIDE SUFFICIENT GUIDANCE REGARDING THE REINSTALLATION OF THE CONDUIT AND SEALING OF THE CABLE PENETRATION TO ENSURE THEIR WATER TIGHTNESS.
361 | 3611989019 | 1989-09-02 | QR6 | Manual Reactor Trip | [45 empty] | San Onofre 2 | P | CE | PO | 27 | At 0543 on September 2, 1989, during a planned shutdown of Unit 2 at the end of Cycle 4, a manual reactor trip was initiated due to the approach of axial shape index (ASI) to the Core Protection Calculator (CPC) auxiliary trip setpoint. ASI describes the axial power distribution of the reactor core. There is no safety significance to this event since the reactor protection system functioned in accordance with design. <br /><br /> At the end of a fuel cycle, the effect of a decrease in plant power on ASI is greater than at any other time in the cycle. As a result, strict controls must be employed to maintain ASI within limits and prevent a trip. Although action was taken to control ASI, it was not sufficient to maintain ASI within its limits. The guidance in the operating procedure governing plant shutdown was not sufficiently specific to provide assurance that the operators could successfully control ASI during a plant shutdown at end-of-cycle. <br /><br /> An evaluation of this event was performed by the Core Analysis Engineering group. As a result of this evaluation, the above causes were determined and a proper strategy for end-of-cycle plant shutdowns was developed, which will be incorporated into the Plant Shutdown procedure. This event will be discussed with appropriate Operations personnel, and additional operator training on end- of-cycle ASI control will be included in the initial and requalification licensed training programs.
361 | 3611990016 | 1990-12-06 | QR5 | Turbine Trip | [45 empty] | San Onofre 2 | P | CE | PO | 100 | At 2200 on December 6, 1990, Unit 2 automatically tripped from 100% power on a reactor protection system loss of load (LOL) signal. The LOL signal was caused by a turbine trip, which occurred as a result of a momentary loss of power from the non-1E uninterruptible power system (UPS), momentarily de-energizing non-1E instrument bus Q-069. Emergency Feedwater Actuation System (EFAS) 1 and EFAS 2 actuations properly occurred. One 6.9 KV bus did not automatically transfer to offsite power following the trip, de-energizing 2 reactor coolant pumps (RCPs); two other RCPs continued to provide forced circulation. Approximately 1 to 2 minutes following the trip, a complete loss of power on Q-069 occurred. Appropriate actions were initiated in accordance with procedures to compensate for the operation of control systems which were affected by the loss of power on Q-069. One main steam safety valve for each steam generator may have lifted for a short time and properly reseated. Bus Q-069 power was restored at 2220 via the manual bypass switch. Recovery of the plant otherwise proceeded normally. <br /><br /> It was determined that failure of a capacitor in the non-1E UPS inverter output caused the loss of power on bus Q-069. The manufacturer of the non-1E UPS determined that the design of the capacitor which failed was defective; therefore, all such capacitors in the Unit 2 and 3 non-1E UPSs have been replaced with an upgraded model. The Unit 2 and 3 instrument busses powered by the non-1E UPS have also been modified to prevent a total power loss to critical systems (i.e., feedwater, turbine governor, and control element drive mechanism systems) in the event of similar failures, thus reducing the likelihood of plant trips.
361 | 3611991003 | 1991-03-10 | QR8 | Spurious Reactor Trip | [45 empty] | San Onofre 2 | P | CE | PO | 77 | At 1206 on March 10, 1991, with Unit 2 at 77% power and CEDMCS #1 MG set out of service for maintenance, the output contactor for the redundant MG set opened, causing de-energization of the CEDMCS bus and an automatic reactor trip. During recovery from the trip, both main feedwater bypass valves (MFBVs) opened unexpectedly. Control room operators attempted to throttle closed both MFBVs, but MFBV 2HV-1105 failed to respond to demand. As a result, steam generator (SG) E-089 level increased above that anticipated. Control room operators closed the associated main feedwater isolation valve to stop main feedwater flow to E-089. The plant was stabilized in Mode 3 at approximately 1230. During the post trip review, it was noted that SG level Channel C responded more slowly than the other three channels. <br /><br /> Failure of the CEDMCS #2 MG set ammeter (AMR) relay underexcitation contact caused the #2 MG set output contactor to open. The AMR relay was sent to an offsite laboratory for failure analysis. A low proportional band setting of the Feedwater Control System controller caused the MFBVs to open unexpectedly during recovery following the trip, causing the excursion in SG level. The investigation is continuing into the cause for 2HV-1105 anomalous operation. The slow response of the SG level Channel C was attributed to sediment in the transmitter sensing lines; evaluation of the SG level channel sluggish response is continuing. <br /><br /> The AMR relay for the CEDMCS #2 MG set was replaced. The proportional band of the FWCS controller was increased, and a minimum value determined. MFBV 2HV-1105 was stroke tested satisfactorily, demonstrating its proper operation. SG E-089 level Channel C sensing lines were blown down, and the instrument returned to within tolerance of the other three channels. Corrective actions will be implemented as necessary based on the results of the continuing cause investigations into the AMR relay failure, 2HV-1105 response failure, and the SG level Channel C sluggish response.
361 | 3611991007 | 1991-04-10 | QR6 | Manual Reactor Trip | [45 empty] | San Onofre 2 | P | CE | PO | 100 | This revision provides an amended cause assessment and corrective action section based on completion of our root cause evaluation. <br /><br /> At 1606 on April 10, 1991, the Unit 2 reactor was manually tripped on indication of a complete loss of controlled bleedoff (CBO) flow from reactor coolant pump (RCP) P004. P004 was stopped following the trip, and the plant was stabilized in Mode 3 at 1621. Emergency feedwater actuation system (EFAS) signals were generated for both steam generators (SGs) due to the expected SG level "shrink" following the trip.<br /><br /> CBO flow ensures long term integrity of the RCP seals during RCP operation. The loss of CBO flow was due to a shift in position of the P004 rotating baffle, whose fastening bolts were found to have fractured. The root cause of the failure of the baffle bolts was loss of preload due to thread embedment. Embedment is the plastic deformation of local high spots on the mating portions of threads. When this deformation takes place, the fasteners lose preload and are subject to cyclic stresses that can lead to fatigue failure. The P004 baffle was inspected, repaired, and re-installed with new bolts. <br /><br /> The P004 seal assembly was replaced with an in-kind part. The other three RCP baffles were inspected for similar deficiencies. Three (of six) baffle bolts on RCP P001 were found to have slightly loosened; no loose bolts were identified on the other two RCPs. The baffle bolts for these three RCPs were also replaced with new bolts.
361 | 3611992008 | 1992-04-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | San Onofre 2 | P | CE | PO | 79 | At 0924 on 4/24/92, with Unit 2 at 79% power, an automatic turbine trip/reactor trip occurred as a result of an increase of level in the Moisture Separator Reheater (MSR) drain tank to the turbine trip setpoint. The transient was precipitated by the failure of transformer 2B13X at 0919, which in turn caused the trip of one of the two Main Feedwater Pumps. In response to the reduction of feedwater flow to the Steam Generators (SG) and resultant decrease in level, reactor power was reduced and Emergency Feedwater was manually actuated, as required by procedure and training, to recover SG level and avoid a reactor trip on low SG level. The MSR drain tank level control system response was not sufficient to properly respond to the plant transient and avoid a level increase to the turbine trip setpoint. <br /><br /> The failure of transformer 2B13X also de-energized the hydraulic actuator units for the turbine throttle and stop valves. Without power these valves would have closed due to hydraulic pressure decay, resulting in a plant trip even without the rise in level of the MSR drain tank to the turbine trip setpoint. <br /><br /> Transformer 2B13X was replaced. A root cause analysis of the failed transformer will be performed, The MSR drain tank level control system has been verified to be properly calibrated, but testing has indicated additional tuning may be necessary to optimize the response to plant transients such as occurred in this event. Appropriate corrective actions will be implemented based upon additional testing. <br /><br /> There is no safety significance to this event since all safety systems operated as designed.
361 | 3611992012 | 1992-07-31 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | San Onofre 2 | P | CE | PO | 100 | At 0838 on 7/31/92, with Unit 2 in Mode 1 at approximately 100% power, an automatic reactor trip occurred when a potential transformer (PT) drawer located at the 6.9 kV switchgear 2A02 was opened for thermographic inspections. This resulted in tripping two of four reactor coolant pumps (RCP) on a sensed undervoltage condition. As the RCPs began to slow down, the low RCP speed setpoint was reached, causing the core protection calculators to generate a reactor trip signal on low departure from nucleate boiling ratio (DNBR). Emergency feedwater actuation system (EFAS) signals were generated for both steam generators (SG) due to the expected decrease in SG level following the trip. All reactor protection system and auxiliary feedwater system components actuated as designed. Reactor trip recovery was initiated and Unit 2 was stabilized in Mode 3 at approximately 0903. <br /><br /> The root cause was attributed to inadequate positive controls in the work package and an inadequate warning sign on the switchgear which had failed to prevent an electrician from opening the PT drawer while the PT was energized. <br /><br /> Corrective actions include: 1) the development of additional positive controls to prevent inadvertent PT drawer opening, and 2) the installation of improved signage.
361 | 3612002003 | 2002-06-30 | L3 | Turbine Bypass Unavailable | [10 empty] | X | [28 empty] | X |  | X |  |  |  | San Onofre 2 | P | CE | PO | 18 | On June 30, 2002, plant operators were performing startup testing at the end of the Unit 2 Cycle 12 Refueling Outage. At that time, the reactor was at about 18 percent thermal power. In response to a small steam imbalance, the Steam Bypass Control System (SBCS) "quick opened" all four SBCS valves. This caused steam pressure to decrease to the low steam generator pressure trip setpoint, which in turn caused reactor protection system (RPS) and main steam isolation system (MSIS) actuations. The Unit 2 RPS and MSIS actuations occurred because the SBCS Dynamic Response Module (DRM) had been improperly adjusted during the Unit 2 Cycle 12 refueling outage. This adjustment error was caused by an inadequate procedure. On July 5, 2002, the Unit 2 SBCS DRM was adjusted to its correct values; On August 10, 2002, the Unit 3 SBCS DRM was adjusted to its correct values. SCE concludes that this event was of very low to no safety significance. The SBCS is not credited in the accident analysis and safety systems functioned correctly.
361 | 3612002006 | 2002-11-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | San Onofre 2 | P | CE | PO | 100 | On 11/2/2002 at 0316 PST, with the Unit 2 reactor at 100% power, the Reactor Protection System (RPS) tripped the Unit A main Feedwater (FW) controller failed; the FW regulating valve (2FV1111) began to close; and the water level in steam generator 89 decreased to the low-level trip set point. SCE made a 4 hour telephone notification to the NRC in accordance with 10CFR50.72(b) and is providing this follow-up report in accordance with 10CFR50.73(a)(2)(iv)(A). SCE's cause evaluation is ongoing. However, preliminary investigations Indicate that the 2FC1111 main FW controller card had a shorted low limit operational amplifier (Motorola, MLM301AG, date code 7432). This may be an age-related failure. This LER will be supplemented if this conclusion changes significantly. SCE replaced both Unit 2 main FW controller cards (2FC1111 and 2FC1121) with new cards (even though 2FC1121 tested satisfactorily). As a precautionary measure, the corresponding cards in Unit 3 have been scheduled for replacement. UFSAR Section 15 2.2 5 and 15.10.2 2.5 evaluate the Loss of Normal Feedwater Flow with the plant at full power. The UFSAR analysis shows that all of the event acceptance criteria (DNBR, offsite doses, peak linear heat rate, peak RCS pressure, and peak secondary pressure) are met. Therefore, there was little to no safety significance to this event.
361 | 3612002007 | 2002-11-04 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | San Onofre 2 | P | CE | PO | 18 | On November 4, 2002, at about 1625 PST, one of the two-pressurizer spray valves began operating erratically, and ultimately stopped moving at 47 percent open and caused pressurizer pressure to decrease. Attempts to close the spray valve were unsuccessful. At 1638 PST, plant operators manually tripped the reactor. At 2215 PST, SCE made a 4-hour telephone notification to the NRC in accordance with 10 CFR 50 72(b)(2)(iv)(B). SCE is providing this follow-up report in accordance with 10 CFR 50.73(a)(2)(iv)(A). The cause of pressurizer spray valve's behavior has not yet been determined. Testing and observation suggest internal binding. This valve will be disassembled during the next refueling outage. On November 4, 2002, spray valve PV-0100A was isolated when the inlet and outlet manual block valves were closed. The second pressurizer spray valve will be used for the remainder of the operating cycle. A causal evaluation and applicable corrective actions will be performed following the valve disassembly as part of the corrective actions program. The pressurizer spray valves are not safety related, are not included within the Technical Specifications and are not required for accident mitigation purposes. SCE concludes that this event was of low to no safety significance.
361 | 3612003001 | 2003-02-01 | QR5 | Turbine Trip | [45 empty] | San Onofre 2 | P | CE | PO | 100 | On 02/01/03, while Unit 3 was defueled for Cycle 12 refueling and Unit 2 was in Mode 1 at 100 percent power, a Technician (utility, non-licensed) was conducting planned outage work on the Unit 3 relay protection cabinet (RPC), 3L070. While establishing a reference test connection within the Unit 2 RPC, 2L070, the Technician misidentified the reference terminal and made an incorrect connection to the Field Suppression Relay for the Unit 2 Main Generator. Upon initiating the test, at 0310 PST, the error resulted in the following automatic and sequential events at Unit 2: (1) actuation of generator loss of field relay, (2) generated/turbine trip, (3) reactor trip, and (4) initiation of emergency feedwater. Systems responding to the event performed as designed. Additionally, Operator responses were correct and timely. This event was caused by a combination of personnel error and inadequate procedural guidance. SCE will take appropriate personnel actions and improve written work instructions. SCE concludes that this event was of low to no safety significance. There were no consequences to public health and safety.
361 | 3612004002 | 2004-04-10 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | San Onofre 2 | P | CE | PO | 67 | On April 10, 2004, at 1147 PDT, Unit 2 was operating at about 97 percent power when both feedwater pump turbines tripped on high discharge pressure. Plant operators manually tripped the reactor and the auxiliary feedwater system automatically started. SCE reported this event to the NRC in accordance with 10CFR50.72(b)(2)(iv) and 10CFR50.72(b)(3)(iv). This follow-up report is provided in accordance with 10CFR50.73 (a) (2) (iv). The main feedwater pump turbines automatically tripped on high discharge pressure caused by a main feedwater regulating valve and its associated bypass valve closing. SCE concluded the valves began closing due to two concurrent electrical grounds in the feedwater control system (FWCS). The first ground (Ground 1) was caused by a pinched interconnect wire on one of the two feedwater regulating control systems (FWCS); SCE replaced this wire. SCE was unable to locate the second ground but concluded it was an intermittent ground located in the DC power supply of the FWCS. SCE verified that the valves would begin closing (absent a close signal) when two grounds were present. SCE determined that the conditional core damage probability (CCDP) and the conditional large early release probability (CLERP) for this event were 2.8E-6 and 1E-7, respectively.
361 | 3612004004 | 2004-11-19 | QR5 | Turbine Trip | [45 empty] | San Onofre 2 | P | CE | PO | 100 | On 11/19/2004 at about 800 PST, Unit 2 was at about 100 percent power when the main generator [EL] and turbine [TA] tripped, and the reactor [R] automatically tripped. The Auxiliary Feedwater System [BA] actuated as designed. SCE reported this event to the NRC (Log No. 41209) at 0925 PST as required by 10CFR50.72(b)(2)(iv)(B). This follow-up report satisfies 10CFR50.73(a)(2)(iv)(A). The main generator isophase bus includes two de-ionizing filters [FLT], between phases, to reduce the likelihood of a phase-to-phase short circuit. This event resulted when several vanes of the filters failed (metal fatigue) and shorted the “A” phase to ground; protective circuits tripped the generator. During the 4/2004 refueling outage, SCE replaced the generator terminal box, and replaced these filters during that work. SCE determined the replacement filters failed due to use of a lower strength aluminum alloy and a vane/frame connection that caused stress risers. Prior to restarting the Unit, SCE installed new de-ionizing filters that have thicker vanes, use a stronger aluminum alloy, and eliminate vane/frame connection stress risers. Plant protective equipment functioned as designed. There was no safety significance to this event because it is bounded by the existing plant safety analysis (UFSAR 15). In the past 3 years SCE has not reported any events caused by failed de-ionizing filters.
361 | 3612005001 | 2005-02-03 | QR5 | Turbine Trip | [45 empty] | San Onofre 2 | P | CE | PO | 99 | On February 3, 2005, at 1223 PST, Unit 2 was operating at about 99 percent power when a phase C differential current protection relay for Unit Auxiliary Transformer (UAT) 2XU1 tripped the Main Generator. An automatic Turbine Trip and automatic Reactor Trip followed as designed. The Auxiliary Feedwater System automatically started as expected on a Reactor Trip from full power. There were no complications experienced during the event and no other safety systems were actuated or required. The Unit trip was initiated by the UAT 2XU1 phase C differential relay. Subsequent comprehensive testing and inspections of the UAT 2XU1, phase C protection circuit, and Digital Fault Recorder (DFR) components have not revealed any defects or degraded conditions. The most likely cause of the trip has been determined to be an invalid signal introduced during DFR testing, which was in progress at the time of the trip. As corrective action, SCE has placed administrative restrictions on DFR testing. The phase C differential relay and DFR isolation circuit boards for Unit 2 were replaced as precautionary actions. SCE will assure that associated electrical protection circuits are not in service or that the DFR is completely isolated from electrical protection circuits prior to DFR testing. This event was of very low to no safety significance because all safety systems responded as designed.
361 | 3612007001 | 2007-06-20 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | San Onofre 2 | P | CE | PO | 96 | On June 20, 2007, at about 2240 PDT, Unit 2 was operating in Mode 1 at about 96 percent power when a line in the instrument air system separated at a soldered connection. The resulting loss of Instrument Air (IA) pressure caused the loss of control of the Steam Generator Feedwater Regulating valves. One steam generator level rose uncontrolled necessitating the control room Operators to trip the reactor manually at about 2250 PDT, June 20, 2007. Operators subsequently manually tripped the Main Feedwater pumps to stop excess feedwater to the steam generators and actuated the Auxiliary Feedwater System. As designed, loss of IA system pressure isolates cooling water to the normal containment coolers and Operators manually started the Containment Emergency Cooling Units as a conservative measure. Southern California Edison (SCE) reported this occurrence to the NRC Operations Center at 0024 PDT on June 21, 2007 (NRC Event Log Number 43435). SCE is providing this follow-up written report in accordance with 10CFR50.73(a)(2)(iv)(A). The soldered connection failed due to improper fit and slow acting corrosion. SCE inspected the IA system piping and installed pipe clamps to strengthen piping joints where needed to add additional margin.
361 | 3612008004 | 2008-06-05 | QR5 | Turbine Trip | [45 empty] | San Onofre 2 | P | CE | PO | 97 | On June 5, 2008 (Event Date), with Unit 2 at approximately 97 percent power, plant personnel began a monthly test of the stator water cooling system. In accordance with the test procedure, Operators swapped the stator water pumps by starting the pump that was in standby and then stopping the operating pump. Three alarms were received in quick succession indicating a reduction in stator water flow. Approximately two minutes later, the Main Generator [TA] tripped from a "Rectifier Low Flow." At approximately 2256 PDT, Unit 2 reactor automatically tripped on a "Loss of Load" signal. SCE's cause evaluation concluded that a pump discharge check valve momentarily remained open following the stator water pump swap and then slammed shut. The resulting pressure spike was sufficient to lift one or both of the relief valves on the stator water heat exchangers. The discharge from the relief valve(s) reduced stator cooling water flow and resulted in a main generator trip and a reactor trip. SCE repaired the malfunctioning check valve and has suspended monthly stator water cooling flow testing at both Units pending further evaluation. This event remained bounded by the Updated Final Safety Analysis evaluation of a loss of load event. Therefore, the significance of this event was minimal.
361 | 3612009001 | 2009-09-13 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | San Onofre 2 | P | CE | PO | 94 | On 9/13/09 (Event Date) at approximately 12:42 PDT, Unit 2 automatically tripped from 94 percent power on low condenser vacuum [JC] caused when a Circulating Water [NN] intake structure recirculation gate stopped in mid-position. Heat treatment of the intake water tunnels is periodically performed to control marine growth. Intake structure recirculation gates allow reversal of the normal flow path, directing heated water from the condenser discharge through the inlet tunnel, and seawater through the outlet tunnel to the condenser inlet. Operators performing the heat treatment were in the process of reversing the circulating water tunnel flow when the gate stopped 45% open, allowing heated water to enter the condenser inlet. Although actions were taken to reduce power and restore the gate alignment, the continued loss of condenser vacuum caused an automatic turbine trip and reactor trip. All post-trip equipment functioned as required and the event has a low safety significance. The gate misaligned when it operated on 9/5/09; a loose stem stop nut was found. The gate was operated on 9/9/09 after maintenance; the misalignment was not corrected and the gate failed to move into position on 9/13/09. Unit 2 was restarted on 9/16/09. Corrective action was taken to improve the procedural guidance for gate maintenance and to implement a rapid response recovery for gate operations.
361 | 3612011002 | 2011-09-08 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | San Onofre 2 | P | CE | PO | 100 | On 09/08/2011 at 1538 PDT, San Onofre Nuclear Generating Station (SONGS) Units 2 and 3 were in Mode 1 operating at 100 percent power, when actuation of the Reactor Protection System occurred resulting in automatic reactor trips of both units. This event was caused by the loss of a 500 kV transmission line from Arizona to San Diego Gas and Electric (SDG&E) resulting in a cascading grid disturbance, automatic separation of the SDG&E and Southern California Edison (SCE) electrical systems, and collapse of the SDG&E grid voltage. The partial loss of external load caused increasing turbine speed, governor valve fast closure, a momentary reduction of heat removal from the reactor coolant system, and increasing pressure. Both reactors tripped on high pressurizer pressure followed by a turbine trip. All control rods inserted to shut down the reactors. Offsite power remained available from the SCE grid and emergency diesel generators were not required. Safety systems responded as designed. Both units were placed in a stable condition in Mode 3. Loss of qualified offsite circuits required entry into Condition A of Technical Specification Limiting Condition for Operation (LCO) 3.8.1, with Required Action to verify remaining offsite circuits within one hour. This verification was performed approximately 1.5 hours late, which is a condition prohibited by TS.
362 | 3621987011 | 1987-06-21 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | San Onofre 3 | P | CE | PO | 100 | POWER LEVEL - 100%. ON JUNE 21, 1987 AT 0258, WITH UNIT 3 IN MODE 1 AT 100% POWER, THE REACTOR AUTOMATICALLY TRIPPED ON LOW STEAM GENERATOR (SG) WATER LEVEL. THE LOW SG WATER LEVEL WAS CAUSED BY AN INTERMITTENT LOSS OF POWER IN ONE PHASE OF A 120 VAC NON-1E INSTRUMENT BUS WHICH RESULTED IN THE INABILITY TO CONTROL MAIN FEEDWATER AND THE CONSEQUENT REDUCTION IN SG WATER LEVEL. LEVEL CONTINUED TO DECREASE TO THE LOW LEVEL REACTOR TRIP AND EMERGENCY FEEDWATER ACTUATION SET POINT. FOLLOWING THE REACTOR TRIP, 120 VAC NON-1E POWER RETURNED AND MAIN FEEDWATER FLOW RESUMED. THE WATER LEVEL IN SG E088 INCREASED FROM THE LOW LEVEL TRIP SET POINT TO ABOVE THE HIGH LEVEL ALARM SET POINT AS OPERATORS WERE IMPLEMENTING THEIR IMMEDIATE POST-TRIP ACTIONS IN ACCORDANCE WITH EMERGENCY OPERATING INSTRUCTIONS (EOIS). THIS RESULTED IN COOLING DOWN OF THE REACTOR COOLANT SYSTEM (RCS) TO BELOW THE SAFETY INJECTION ACTUATION SIGNAL (SIAS) SET POINT. THE 120 VAC POWER MALFUNCTION WAS DETERMINED TO BE DUE TO A LOOSE BOLT CONNECTING THE 'B' PHASE OF INSTRUMENT BUS #1 TO THE MAIN BUS BARS OF THE NON-1E UNINTERRUPTABLE POWER SUPPLY (UPS) MAIN DISTRIBUTION SWITCHBOARD, WHICH RESULTED IN INTERMITTENT LOSS OF CIRCUIT CONTINUITY. THIS WAS EVIDENCED BY ARCING AND PITTING AT THE CONNECTION, AND CONFIRMED BY SUBSEQUENT DUPLICATION OF POWER INTERRUPTIONS WHEN THE ASSEMBLY WAS MANUALLY MOVED.
362 | 3621987017 | 1987-10-11 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X | [29 empty] | X |  |  |  |  | San Onofre 3 | P | CE | PO | 77 | POWER LEVEL - 077%. ON 10/11/87 AT 1010, WITH REACTOR POWER AT 77%, FLOW DIRECTION THROUGH THE CIRCULATING WATER INTAKE AND OUTFALL TUNNELS WAS REVERSED TO PERFORM A HEAT TREATMENT OF THE CIRCULATING WATER SYSTEM. AT APPROXIMATELY 1500, A HEAVY INFLUX OF SEAWEED OCCURRED WHICH LED TO THE STOPPAGE OF ONE CIRCULATING WATER PUMP AND A DEGRADATION OF CONDENSER VACUUM. THE OPERATORS BEGAN TO NORMALIZE (RETURN TO NORMAL ALIGNMENT) THE CIRCULATING WATER TUNNELS AT 1646 IN AN ATTEMPT TO REDUCE THE EFFECTS OF THE SEAWEED INFLUX. AT 1702, THE TURBINE TRIPPED ON LOW VACUUM, CAUSING THE REACTOR TO TRIP ON LOSS OF LOAD. THE EMERGENCY FEEDWATER ACTUATION SYSTEM FOR STEAM GENERATOR #2 (EFAS 2) ACTUATED ON LOW STEAM GENERATOR LEVEL. ALL COMPONENTS ASSOCIATED WITH EFAS 2 WERE VERIFIED TO HAVE OPERATED IN ACCORDANCE WITH DESIGN. THE TURBINE TRIP ON LOW VACUUM RESULTED FROM NORMALIZING THE CIRCULATING WATER TUNNELS WITH ONE CIRCULATING WATER PUMP STOPPED DURING AN INGRESS OF LARGE AMOUNTS OF SEAWEED. OPERATING INSTRUCTIONS FOR REALIGNING THE CIRCULATING WATER TUNNELS DID NOT INCLUDE ADEQUATE PREREQUISITES THAT WOULD HAVE PREVENTED NORMALIZING THE CIRCULATING WATER TUNNELS UNDER THESE CONDITIONS. THE CONDENSER WATER BOXES WERE CLEANED AS NECESSARY, AND THE UNIT WAS RETURNED TO POWER OPERATION AT 1530 ON 10/12/87.
362 | 3621988002 | 1988-02-19 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | San Onofre 3 | P | CE | PO | 100 | On February 19, 1988 at 1300, with Unit 3 in Mode 1 at 100% power, Trains "A" and "B" of both the Safety Injection Actuation System (SIAS) and Containment Cooling Actuation System (CCAS) were actuated during performance of 31-day Engineered Safety Features Actuation System (ESFAS) matrix logic relay testing. All components actuated as designed. There was no High Pressure Safety Injection System (HPSI) flow into the Reactor Coolant System (RCS) since RCS pressure remained above the shutoff head of the HPSI pumps. <br /><br />At 1304, the reactor was manually tripped in accordance with procedures. As the result of steam generator water level "shrink" following the reactor trip, the Emergency Feedwater Actuation Systems (EFAS) 1 and 2 initiated feed water flow to the steam generators. All safety systems performed as required and operators satisfactorily completed standard post-trip action and stabilized the unit in Mode 3. <br /><br /> Investigation has determined that the spurious ESFAS actuations were caused by improperly assembled push button switch contacts. Due to apparent unreliable electrical operation of these contacts as the push button was being depressed or held in, the trip matrix being tested was prematurely de-energized initiating the above described SIAS and ESFAS actuations. All similar push button switches in Units 2 and 3 have been replaced with switches of a different contact design. Further, the wiring to the switch contacts has been redesigned to reduce the possibility of recurrence of such spurious actuations during testing.
362 | 3621989001 | 1989-01-06 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | San Onofre 3 | P | CE | PO | 100 | At 2335 on 1/6/89, with Unit 3 at 98% power, the reactor tripped on low steam generator (SG) level after a partial loss of non-1E Uninterruptible Power Supply (UPS) power occurred which caused feedwater regulating valves to reduce flow to SG E089. This also resulted in actuation of emergency feedwater to SG E089. Emergency feedwater to SG E088 also actuated due to the resulting level "shrink" in SG E088, which is expected following a trip from high power. Since the Steam Bypass Control System was in manual to perform turbine valve testing, heat removal from the SGs was greater than normal. At 2336, as a result of the lower SG temperature, reactor coolant system (RCS) pressure decreased below the Safety Injection Actuation Signal (SIAS) setpoint (1806 psia), resulting in an SIAS actuation. There was no safety injection flow into the RCS since RCS pressure remained above the shutoff head of the injection pumps. All safety systems operated in accordance with design. At 0025 on 1/7/89, the plant was stabilized and all Engineered Safety Features were reset and lineups returned to normal. <br /><br /> Two of three non-1E UPS phases were lost because of a common fault in the associated inverter's constant voltage transformer (CVT) output windings. A temporary jumper, which had not been properly removed during previous maintenance, was found between UPS ungrounded neutral and ground. There were two prior failures of a CVT in the same inverter after the installation of the temporary jumper, but neither resulted in a safety system actuation. The cause of the transformer failure was the breakdown of insulation between the energized windings and the grounded iron core. Extensive analysis of the failed transformer was unable to determine a root cause for the transformer insulation breakdown. However, with the jumper installed, it is believed that the development of a fault or ground in the transformer created a current path which bypassed the installed ground detection system and caused severe damage to the transformer.<br /><br /> As corrective actions, the jumper was removed, the CVTs were replaced, and the non-1E UPS was satisfactorily tested. The cause of the event was reviewed with applicable personnel and appropriate disciplinary action was taken.
362 | 3621989006 | 1989-04-07 | QR5 | Turbine Trip | [45 empty] | San Onofre 3 | P | CE | PO | 100 | At 0555 on 4/7/89, with Unit 3 at 100% power, an automatic reactor trip on Loss of Load (LOL) occurred in response to a turbine trip caused by spurious deenergization of the Control Element Drive Mechanism Control System (CEDMCS) bus undervoltage (UV) relays. Plant conditions were stabilized, and recovery proceeded normally. The Emergency Feedwater Actuation System (EFAS) for both steam generators (SGs) actuated as a result of the expected decrease in SG level below the actuation setpoint. At 0630, levels of both steam generators were verified to be above the reset setpoint, and EFAS was reset. There is no safety significance to this event since the Reactor Protection System (RPS) operated in accordance with design, and all EFAS components were verified to have actuated as required.<br /><br /> Following the trip, the CEDMCS motor-generator (MG) set #1 load contactor was found to be open, contrary to its normal, expected position. The CEDMCS bus is powered by two parallel and fully redundant MG sets, via output circuit breakers and load contactors. Subsequent testing demonstrated that under certain conditions, the opening of one MG set load contactor could result in a drop in CEDMCS bus voltage of sufficient magnitude to cause the CEDMCS bus undervoltage (UV) relays to deenergize. <br /><br /> Monitoring equipment was installed on the MG sets to establish possible cause and corrective actions for the spurious opening of the MG set load contactor. To minimize the potential of a reactor trip from the opening of an MG set load contactor or output breaker: 1) the UV relay trip setpoint, which was determined to be excessively conservative, was decreased; 2) the procedure governing MG set operation has been amended; and 3) MG set load control circuitry will be modified.
362 | 3621990002 | 1990-02-23 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | San Onofre 3 | P | CE | PO | 100 | At 2257 on February 23, 1990, with Unit 3 at 100% power, during the performance of Main Steam Isolation System (MSIS) subgroup relay testing, a spurious MSIS actuation occurred. This MSIS actuation initiated closure of the main steam isolation valves (MSIVs) and resulted in a reactor trip on high pressurizer pressure. The plant transient included: 1) Lifting of the Main Steam Safety Valves (MSSVs); 2) initiation of the Emergency Feedwater Actuation System (EFAS); and 3) the brief opening of a pressurizer safety valve (PSV). However, during the transient, RCS pressure never exceeded the minimum PSV set point value allowed by Technical Specification (TS) 3.4.2. Operators stabilized the plant in Mode 3. Following this event, it was determined that the lift set points for the Units 2 and 3 PSVs were outside the TS requirements. There is no safety significance to this event since: 1) all reactor protection system, MSIS, and EFAS components were verified to actuate in accordance with design; and 2) the plant response with the as-found PSV lift set points was determined to be acceptable. <br /><br /> Contacts on the MSIS manual actuation pushbutton (PB) were found to be degraded such that one trip leg of MSIS did not reset during the subgroup relay testing. MSIS actuation occurred upon initiation of testing of the other trip leg. The PSV temperature profiles present during power operation were different than the profiles specified for setting the PSV lift set points at Wyle Labs. The cause of set point deviation is attributed to the use of a temperature profile during the calibration process which was different than that which exists during power operation. <br /><br /> Corrective actions included: 1) Replacement of the MSIS actuation PB; 2) examination/replacement of all Unit 3 MSIS actuation PBs; 3) enhancement of the MSIS subgroup relay testing procedure; 4) resetting of the Units 2 and 3 PSVs to within the TS required band; and, 5) performance of a Human Performance Enhancement System (HPES) evaluation. Similar PBs in Units 2 and 3 will be replaced by the end of the next refueling outage for each unit. Additionally, a design change to eliminate the need for the MSIS cycling subgroup relay is under consideration.
362 | 3621991001 | 1991-03-15 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | San Onofre 3 | P | CE | PO | 100 | At 0938 on March 15, 1991, Unit 3 automatically tripped from 100% power on a reactor protection system loss of load (LOL) signal. The LOL signal was caused by a turbine trip, which occurred as the result of a momentary interruption in power from the non-1E uninterruptible power system (UPS), de-energizing bus 3Q069. Emergency Feedwater Actuation System (EFAS) 1 and EFAS 2 actuations properly occurred. One non-1E 4.16 kV (3A03) bus did not automatically transfer from its normal power source to its alternate power source, resulting in the loss of the alternate power supply (3B012) to the non-1E bus 3Q069. One main steam safety valve lifted for a short time and properly reseated. At 1000, when 3A03 was manually reenergized, power was restored to 3Q069. Appropriate actions were taken in accordance with procedures to compensate for the operation of control systems which were affected by the loss of power to the non-1E UPS. Post-trip plant recovery otherwise proceeded normally. <br /><br /> An output capacitor in the constant voltage transformer (CVT) section of the non-1E UPS inverter failed causing the momentary interruption in power from the non-1E UPS. <br /><br /> All capacitors in the Units 2 and 3 non-1E UPS were replaced with an upgraded model. The Unit 3 instrument busses powered by the non-1E UPS were modified such that power will be maintained to critical component systems (i.e., feedwater, turbine governor, and control element drive mechanism control systems) in the event of similar failures.
362 | 3621992003 | 1992-05-15 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | San Onofre 3 | P | CE | PO | 100 | At 1006 on May 15, 1992, with Unit 3 at 100% power, reactor coolant pump (RCP) 3P003 tripped, causing an automatic reactor trip on a low departure from nucleate boiling ratio (DNBR) signal. The plant was stabilized in Mode 3 at approximately 1020. Emergency feedwater actuation signals (EFAS) were generated for both steam generators (SGs) due to the expected decrease in SG level following the trip. There is no safety significance to this event since all reactor protection system and EFAS components actuated as designed.<br /><br /> A short circuit failure of the RCP 3P003 motor phase "C" surge protection capacitor occurred due to long term, vibration-induced abrasion damage to the mylar plastic insulation within the capacitor assembly. <br /><br /> The RCP motor preventive maintenance program will be modified to include periodic replacement of the capacitors. The surge capacitors for the Unit 2 RCPs will be replaced during the next outage of sufficient duration.
362 | 3621993001 | 1993-01-16 | QR5 | Turbine Trip | [45 empty] | San Onofre 3 | P | CE | PO | 75 | On January 16, 1993, Unit 3 was operating at 75% power with a heavy rain storm occurring. At 1641, the Main Generator tripped on a stator ground protection signal, causing a turbine/reactor trip. The plant was stabilized in Mode 3 at normal temperature and pressure at approximately 1715. <br /><br /> Rain water leaked down from the turbine deck into the main generator terminal enclosure, which contains the transition from the main generator conductors to the isophase bus. The water accumulated on some insulating material and provided a low resistance path from the exposed B phase conductor to ground, actuating a Main Generator/Main Turbine trip signal. <br /><br /> Additional sealing was provided for the Main Generator terminal enclosure to minimize the possibility of rain water intrusion, and the insulating material was replaced. SCE will evaluate whether additional measures can be taken to minimize the possibility of rain water intrusion into the Main Generator components. <br /><br /> There is no safety significance to this event since all Reactor Protection System components operated as designed.
362 | 3621993004 | 1993-07-05 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | San Onofre 3 | P | CE | PO | 100 | On July 5, 1993, at 1943, Unit 3 tripped from 100% power, when the instrument air tubing supplying air to the Main Turbine Gland Seal Steam Spillover Valve Actuator failed. In accordance with the design of the valve, the loss of instrument air pressure to the valve caused the valve to fail open. The resulting loss of turbine gland steam pressure caused a Loss of Vacuum Turbine Trip and Reactor Trip. Emergency Feedwater Actuation occurred as expected due to Low Steam Generator Levels following the Reactor Trip from full power and the Auxiliary Feedwater System operated as designed. <br /><br /> The root cause of the instrument air supply tubing failure was a fatigue induced material failure. Corrective Actions include: 1) replacing the failed Instrument Air tubing, and 2) inspecting the tubing for Unit 2 and 3 Turbine Gland Steam supply and spillover valves.
362 | 3621999003 | 1999-05-13 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | San Onofre 3 | P | CE | PO | 100 | On 5/13/1999, at 2144 PDT, with the unit at 97 percent power, technicians were investigating feedwater system oscillations, when a main feedwater control valve closed. Operators manually tripped the reactor,, and started the Auxiliary Feedwater System. All control rods fully inserted. The Emergency Core Cooling System was not required and was not actuated, either manually or automatically. Plant responses were as expected. This event was reported to the NRC pursuant to 10CFR50.72(b)(2)(ii). This Licensee Event Report is provided pursuant to 10CFR50.73(a)(2)(iv). The cause was an "open" relay contact in the output of the Feedwater Regulation Control System which is normally closed during power operation. When this contact opens, the main feedwater regulator valve closes. The contact failed when fine debris from the relay's plastic case migrated to the contact surfaces. causing high contact resistance. The faulty relay was replaced. As a result of this event, and that in LER 3-1999-004, SCE is evaluating its preventative maintenance program. This event is categorized as GREEN. SCE has not reported any related events in the past 3 years.
362 | 3621999004 | 1999-05-15 | QP5 | Excessive Feedwater Flow | [45 empty] | San Onofre 3 | P | CE | PO | 24 | On 5/15/1999, at 2358 PDT, a main feedwater regulator valve moved to full open. The reactor was manually tripped when steam generator level reached the high level pre-trip alarm setpoint. All control rods fully inserted. No other ESF functions were required and none actuated, either manually or automatically. All systems and plant responses were as expected. This event was reported to the NRC pursuant to 10CFR50.72(b)(2)(ii). This Licensee Event Report (LER) is provided pursuant to 10CFR50.73(a)(2)(iv). The cause of this event was a faulty valve positioner. The positioner's failure was a combination by loose fasteners and the air supply nozzle restriction being plugged with dirt and dust. Plugging the supply air nozzle restriction has the same effect as the stuck pilot valve discussed above. With the restriction plugged, the pilot valve did not close and, as a result, caused 3FV1111 to open. The faulty positioner was replaced. As a result of this event, and that in LER 3-1999-003, SCE is evaluating its preventative maintenance program. This event is categorized as GREEN. SCE has reported no related events in the past 3 years.
362 | 3622001001 | 2001-02-03 | QC5 | Loss of Non-safety-Related Bus | [7 empty] | X | [25 empty] | X | [11 empty] | San Onofre 3 | P | CE | PO | 39 | On 2/3/01, plant operators were increasing Unit 3's power following completion of its Cycle 11 refueling outage. At about 1513 PST, when switching offsite power sources for Unit 3, a feeder breaker (3A0712) faulted and started a fire. This resulted in a loss of power to non-1 E systems at Unit 3, a turbine/generator trip, a reactor trip, and a start of both Unit 3 Emergency Diesel Generators. Containment emergency coolers were also started. Anticipating the fire would last more than 15 minutes, an Unusual Event was declared at 1527 PST. The failure of a DC breaker to function properly resulted in the unavailability of the turbine/generator lubricating oil system, causing damage to the turbine/generator. The event was caused when breaker 3A0712 faulted, and started a fire within the breaker cubicle. Ionized gases and smoke diffused through cable passages between adjacent cubicles and entered the Reserve Aux Transformer (RAT) feeder breaker 3A0714 cubicle and caused a ground fault with the 3A0714 cubicle, which resulted in the RAT trip and loss of non-safety-related offsite AC power to Unit 3. The fire consumed much of breaker 3A0712's non-metallic parts and caused substantial melting of current carrying components. Consequently, the exact cause of the breaker fault could not be conclusively determined. SCE will implement modifications to appropriate preventive maintenance procedures to address the apparent failure causes. SCE has replaced/rebuilt 5 electrical cabinets in bus 3A07. This includes replacement of electrical equipment and cables that were either burned directly or damaged by the fire. Damage to the turbine/generator is being repaired.
362 | 3622002001 | 2002-02-27 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | San Onofre 3 | P | CE | PO | 100 | On 2/27/02 at 1043 PST, a technician was performing maintenance and testing in the San Diego Gas & Electric (SDG&E) portion of the San Onofre switchyard. As planned for the work, the South West bus was de-energized. All the transmission lines from SDG&E territory, Unit 3 reserve auxiliary transformer (RAT), and Unit 3 main transformer (main generator) were aligned to "South East" bus. The technician's approved work scope was to test the Breaker Failure Local Backup (BFLBU) scheme on the South West bus breakers. The technician exceeded the authorized work scope and chose also to test the cross bus BFLBU trip from a breaker on the South East bus. While doing so, the technician also failed to isolate a trip signal between the South West bus and the South East bus and the resulting signal tripped all the breakers connected to the South East bus, including the Unit 3 main transformer breaker and Unit 3 RAT breakers. Consequently, the Unit 3 main turbine/generator tripped, the reactor tripped, both emergency diesel generators started and Auxiliary Feedwater started. Operators manually started the Emergency Containment Coolers. The loss of offsite power and associated Reactor Protection System and Engineered Safety Features actuations were reported to the NRC in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A). This written report is provided in accordance with 10CFR50.73(a)(2)(iv)(A). Offsite power was restored in about 32 minutes. Future switchyard detailed work plans will be reviewed and approved by SONGS Operations prior to the commencement of work. The event had minimal safety significance.
362 | 3622004001 | 2004-06-04 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | San Onofre 3 | P | CE | PO | 100 | On June 4, 2004, at 0445 PDT, plant operators manually tripped the Unit 3 reactor due to degraded circulating water pump suction caused by heavy influx of sea grass across the traveling screens during very low tide conditions. At the time of the reactor trip, Unit 3 was at approximately 80 percent power. Safety systems responded as expected. Southern California Edison (SCE) reported this event to the NRC Operations Center (Log No. 40791) at 0821 EDT in accordance with 10 CFR 50.72(b)(2)(iv)(B) for actuation of the Reactor Protection System (RPS) [JC]. This follow-up Licensee Event Report is provided in accordance with 10 CFR50.73(a)(2)(iv)(A). A traveling screen panel was repaired and broken shear pins replaced. The traveling screen system was tested and returned to service. Circulating water pumps are not essential for safe shutdown of the plant and do not provide a safety function. The SONGS 2/3 UFSAR Sections 15.2.1.3 and 15.10.2.1.3 credit the Auxiliary Feedwater System and ADVs for maintaining an adequate heatsink during a transient in which an instantaneous and complete loss of condenser vacuum occurs. Therefore the event reported here in is bounded by the UFSAR safety analysis identified above.
362 | 3612011002 | 2011-09-08 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | San Onofre 3 | P | CE | PO | 100 | On 09/08/2011 at 1538 PDT, San Onofre Nuclear Generating Station (SONGS) Units 2 and 3 were in Mode 1 operating at 100 percent power, when actuation of the Reactor Protection System occurred resulting in automatic reactor trips of both units. This event was caused by the loss of a 500 kV transmission line from Arizona to San Diego Gas and Electric (SDG&E) resulting in a cascading grid disturbance, automatic separation of the SDG&E and Southern California Edison (SCE) electrical systems, and collapse of the SDG&E grid voltage. The partial loss of external load caused increasing turbine speed, governor valve fast closure, a momentary reduction of heat removal from the reactor coolant system, and increasing pressure. Both reactors tripped on high pressurizer pressure followed by a turbine trip. All control rods inserted to shut down the reactors. Offsite power remained available from the SCE grid and emergency diesel generators were not required. Safety systems responded as designed. Both units were placed in a stable condition in Mode 3. Loss of qualified offsite circuits required entry into Condition A of Technical Specification Limiting Condition for Operation (LCO) 3.8.1, with Required Action to verify remaining offsite circuits within one hour. This verification was performed approximately 1.5 hours late, which is a condition prohibited by TS.
362 | 3622012001 | 2012-01-31 | QG9 | Primary System Leak | [45 empty] | San Onofre 3 | P | CE | PO | 100 | On 01/31/2012 at 1505 PST, SONGS Unit 3 was in Mode 1 operating at 100 percent power, when a high radiation alarm from the condenser air ejector monitor indicated a tube leak in one of the two steam generators (SGs). A rapid power reduction was commenced in accordance with plant procedures when the primary to secondary leak rate was determined to be greater than 75 gallons per day (gpd) with an increasing rate of leakage exceeding 30 gpd per hour. At 1731 PST, the operators manually tripped the reactor at 35 percent power as directed by procedure, resulting in actuation of the Reactor Protection System which is reportable. All control rods inserted to shutdown the reactor. Safety systems responded as designed. SG level was maintained using the main feedwater system. Decay heat was removed through the main steam bypass valves to the condenser; no atmospheric relief valves lifted during the trip. The affected SG was isolated. The reactor was placed in a stable cold shutdown condition in Mode 5. Small, monitored radioactive releases to the environment occurred, well below allowable limits. Inspection, testing, and analysis of SG tube integrity in both Unit 3 SGs is ongoing. Defective tubes will be removed from service prior to plant startup. Any subsequent required reporting associated with tube degradation will be addressed in a separate report.
364 | 3641987001 | 1987-02-28 | QR8 | Spurious Reactor Trip | [45 empty] | Farley 2 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 1526 ON 2-28-87, WITH THE UNIT OPERATING IN STEADY STATE AT 100% REACTOR POWER, THE REACTOR TRIPPED DUE TO OVER-TEMPERATURE-DELTA-T (OT- DELTA-T). CHANNEL THREE OF OT-DELTA-T WAS IN TEST FOR SURVEILLANCE TESTING WITH THE BISTABLE TRIPPED. AT 1526, THE INDICATED TAVG IN CHANNEL ONE INCREASED (DUE TO AN APPARENT INTERMITTENT FAILURE IN A LEAD-LAG CARD) CAUSING THE VARIABLE OT-DELTA-T SETPOINT TO DECREASE TO THE ACTUAL DELTA-T VALUE. THIS RESULTED IN THE REQUIRED TWO-OUT-OF-THREE COINCIDENCE ON OT-DELTA-T AND INITIATED THE REACTOR TRIP. THE CHANNEL THREE OT-DELTA-T WAS RETURNED TO SERVICE, THE CHANNEL ONE TAVG WAS VERIFIED TO BE OPERATING PROPERLY, AND THE UNIT WAS RETURNED TO POWER OPERATION ON 3-1-87. THE LEAD-LAG CARD WAS SUBSEQUENTLY REPLACED.
364 | 3641987009 | 1987-12-03 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Farley 2 | P | WE | SU | 2 | POWER LEVEL - 002%. AT 2348 ON 12-3-87, WITH THE UNIT IN MODE 2 OPERATING AT 1.5% REACTOR POWER, THE REACTOR TRIPPED DUE TO LOW WATER LEVEL IN THE 2A STEAM GENERATOR COINCIDENT WITH FEEDWATER FLOW BEING LESS THAN STEAM FLOW. THE REACTOR TRIP WAS CAUSED BY PERSONNEL ERROR IN THAT THE OPERATOR ALLOWED THE STEAM GENERATOR LEVEL TO DECREASE TO THE TRIP SETPOINT. FOLLOWING THE REACTOR TRIP, THE UNIT WAS MAINTAINED IN A STABLE CONDITION. IN ORDER TO PREVENT RECURRENCE, THE OPERATOR INVOLVED HAS BEEN COUNSELED.
364 | 3641989007 | 1989-05-22 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Farley 2 | P | WE | PO | 35 | At 1019 on 5-22-89, with the unit operating at approximately 35% power, the reactor tripped due to lo-lo steam generator level. The lo-lo steam generator level occurred because the 2A steam generator feed pump (SGFP), which was providing feedwater flow to the steam generators, tripped. The unit was stabilized in Mode 3 (Hot Standby).<br /><br /> The SGFP trip vas caused by a loose electrical connector on the 2A SGFP thrust bearing wear device. Although the exact cause could not be determined, it is believed that the connector was not fully tightened following maintenance performed during the recent refueling outage. During pump cleaning activities, the cable attached to the loose connector was inadvertently contacted. This caused a thrust bearing wear trip signal to be generated. Thus, the 2A SGFP tripped which caused the lo-lo steam generator level and an automatic reactor trip resulted. <br /><br /> To prevent recurrence of this problem, a preventive maintenance task will be developed to inspect SGFP instrumentation connections for tightness following major unit or SGFP outages. <br /><br /> The unit returned to power operation on 5-22-89 at 2234.
364 | 3641989008 | 1989-05-27 | QR5 | Turbine Trip | [45 empty] | Farley 2 | P | WE | PO | 88 | At 0906 on 5-27-89, with the unit operating at 88% power and a three percent per hour power increase in progress, the reactor tripped due to a turbine trip. The turbine trip resulted from a generator trip caused by loss of excitation. The loss of excitation was caused by the failure of the #9 exciter bearing which resulted in the failure of the shaft driven permanent magnet generator (PMG). The #9 bearing failed when contract personnel failed to install an insulating washer on one of the four bolts on a bearing oil line flange. <br /><br /> This event vas caused by an inadequate procedure. Although a procedure did exist for the reassembly of the bearing oil piping, there was no method for verifying proper insulation capability following reassembly. Because the bearing oil line flange bolt insulating washer was not installed as required, the #9 exciter bearing eventually failed. A new bearing and PMG stator have been installed, A procedure (FNP-0-EMP-1171.02, Generator Shaft/Pedestal Insulation Verification) has been developed to verify proper insulation of the #9 bearing.<br /><br /> The unit returned to power operation on 5-31-89 at 2021.
364 | 3641989010 | 1989-09-20 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Farley 2 | P | WE | PO | 61 | At 0722 on 9-20-89, with the unit operating at approximately 61% power, the reactor was tripped manually following the loss of the operating steam generator feed pump (SGFP). The 2A SGFP turbine tripped due to a low auto-stop oil pressure signal. The Shift Supervisor directed a manual reactor trip in order to prevent an unnecessary challenge to the reactor protection system. The unit was stabilized in Mode 3 (Hot Standby). <br /><br /> The low auto-stop oil signal was caused by the inadvertent opening of the overspeed trip test valve. Opening this valve lowered auto-stop oil pressure by diverting auto-stop oil to the overspeed test device. Auto-stop oil pressure dropped below the as-found trip set point of the low auto-stop oil pressure switch causing a SGFP trip. The trip setpoint was found to be higher than it should have been. <br /><br /> The unit returned to power operation at 2003 on 9-26-89.
364 | 3641989012 | 1989-10-18 | QR5 | Turbine Trip | [45 empty] | Farley 2 | P | WE | PO | 100 | At 1407 on 10-18-89, with the unit operating at 100% power, the reactor tripped due to lo-lo steam generator level. The lo-lo steam generator level occurred when the turbine generator governor valves closed. This closure resulted from a digital electro-hydraulic control (DEHC) system design feature enhancement which causes the governor valve position limiter to lower to zero as a backup to closing the governor valves when both overspeed protection channel (OPC) power supplies fail. <br /><br /> This event vas caused by a design error in the DEHC system. This error allowed a momentary data loss to be created when the operator requested the "Re-enable Highway" function at the DEHC Operators/Alarms Console. This resulted in the same system control action that is taken when both OPC power supplies fail. <br /><br /> The valve position limiter feature which lovers to zero as a backup to closing the governor valves when the OPC power supplies fail has been removed from the Unit 1 and Unit 2 DEHC systems. Westinghouse has been directed to determine if there are other DEHC features available to the operator which may cause a turbine trip or turbine valve closure.
364 | 3641989013 | 1989-10-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Farley 2 | P | WE | SU | 2 | At 1823 on 10-19-89, with the unit operating at approximately two percent power, the reactor tripped due to lo-lo level in the 2C steam generator. The Unit Operator improperly transferred from auxiliary feedwater (AFW) to main feedwater (MFW) during a plant startup. <br /><br /> This event was caused by personnel error in that the Unit Operator incorrectly transferred steam generator level control from AFW to MFW. A contributing cause was that the personnel involved failed to properly restore air to the 2C MFW bypass valve. <br /><br /> The personnel involved have been counseled concerning improper feedwater transfer and restoration of air to feedwater valves. A training change notice describing this event will be issued to all licensed personnel.
364 | 3641989015 | 1989-11-18 | QR5 | Turbine Trip | [45 empty] | Farley 2 | P | WE | PO | 100 | At 0433 on 11-18-89, with the unit operating at 100% power, the reactor tripped due to a turbine trip. The turbine trip is attributed to a voltage transient in the power circuit to the DEHC system. A voltage transient in this circuit is suspected to have caused the DEHC system to erroneously sense a loss of DC power. The voltage transient is attributed to the failure of the DEHC inverter. <br /><br /> The unit returned to power operation at 0455 on 11-19-89 using the alternate power supply. <br /><br /> The inverter was repaired and returned to service.
364 | 3641990001 | 1990-05-12 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Farley 2 | P | WE | PO | 8 | At 0615 on 5-12-90, during a unit startup, the reactor tripped due to low-low water level in the 2A steam generator. The low-low water level occurred when the steam supply valves for the on-service steam generator feedwater pump (SGFP) closed. Testing being performed in accordance with FNP-2-STP-151.4 (Main Turbine Protective Device Test) resulted in low electro-hydraulic (EH) fluid pressure which caused the SGFP valves to close. <br /><br /> This event was caused by procedural inadequacy. FNP-2-STP-151.4 did not provide adequate guidance concerning the initial conditions required to perform the procedure. Testing performed subsequent to the reactor trip showed that it is not appropriate to perform this procedure while feedwater is being provided by a SGFP.<br /><br /> FNP-2-STP-151.4 has been revised to provide additional initial conditions to prevent performing the procedure when an SGFP is in service.
364 | 3641991001 | 1991-04-01 | QR3 | Reactivity Control Imbalance | [45 empty] | Farley 2 | P | WE | PO | 100 | At 1055 on 4-1-91, while operating at approximately 100 percent power, a reactor trip occurred when rod H-10 dropped into the core. The reactor trip occurred due to a high negative flux rate as detected by the power range nuclear detectors. The operator was performing FNP-2-STP-5.0 (Full Length Control Rod Operability Test). When control rod group C was tested, rod H-10 dropped into the core. <br /><br /> This event was caused by defective circuit card(s) in the rod control system. The suspect cards were replaced and the unit returned to power operation at 1208 on 4-09-91.
364 | 3641991002 | 1991-04-09 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Farley 2 | P | WE | PO | 34 | At 2040 on 4-9-91, the Unit 2 reactor was manually tripped following the loss of the operating (2A) steam generator feedwater pump (SGFP). The loss of the SGFP was caused by a failed electro-hydraulic (EH) fluid supply line coupling and subsequent loss of EH fluid. The failure was in the heat affected zone of a tubing-to-fitting socket weld on the EH supply to the high pressure governor valve to the 2A SGFP. Examination of the failed tubing revealed that the failure resulted from cyclic fatigue. <br /><br /> The EH tubing was repaired and all accessible welds on the EH systems on Units 1 and 2 SGFPs were inspected. Vibration readings were taken on the EH tubing connections in the vicinity of the Unit 2 SGFP turbines. Vibration was found on the EH tubing in the vicinity of the failure. The highest vibration occurred during low power plant operation. An investigation is continuing to determine if additional corrective action is necessary. <br /><br /> The unit returned to power operation at 1648 on 4-10-91.
364 | 3641991004 | 1991-04-20 | QL7 | Degraded condenser vacuum | [45 empty] | Farley 2 | P | WE | PO | 68 | At 1617 on 4-20-91, the reactor tripped due to a turbine trip. The turbine trip was caused by a reduction of condenser vacuum. The valve which supplies instrument air to the air operated steam admission valve for the 2A steam jet air ejector (SJAE) was inadvertently closed by personnel working in the area. This caused the steam supply valve to close and resulted in the loss of condenser vacuum. <br /><br /> The turbine building system operator immediately restored air to the steam admission valve upon finding the air supply isolated. Vacuum recovered shortly after the trip occurred and no further problems were identified. The unit returned to power operation at 0426 on 4-21-91.
364 | 3641991005 | 1991-08-06 | QR3 | Reactivity Control Imbalance | [45 empty] | Farley 2 | P | WE | PO | 100 | At 1704 on 8-6-91, while operating at approximately 100 percent power, a reactor trip occurred. Apparently, a lightning induced transient in the rod control system caused some of the control rods to drop which resulted in a negative flux rate reactor trip. <br /><br /> Testing and inspection of the rod control system revealed no damage. It is postulated that a lightning strike induced voltage on the control rod drive mechanism cables which momentarily de-energized the power supply to one or more rod control cabinets and caused the rods associated with that cabinet or cabinets to drop. <br /><br /> An engineering study has been initiated to determine how to prevent further lightning induced reactor trips. <br /><br /> The unit returned to power operation at 2049 on 8-7-91.
364 | 3641992001 | 1992-01-22 | QR6 | Manual Reactor Trip | [45 empty] | Farley 2 | P | WE | PO | 65 | At 0731 on 1-22-92 a manual reactor trip was initiated due to a service water (SW) leak on a main generator exciter cooling water line. Because of the leak, the unit was being ramped down at a rate of 25MW/min and was at 65 percent power when the trip was initiated. The leak was attributed to a gasket that was damaged during installation when the exciter cooling water lines were reassembled as part of the Fall 1990 refueling outage.<br /><br /> This event was caused by improper gasket installation due to lack of detailed information on reassembly of Victaulic couplings in the exciter cooler inspection procedure. The procedure is in the process of being revised to include specific instructions to facilitate proper mating and assembly of Victaulic couplings. <br /><br /> All accessible gaskets in the north (upper and lower) exciter coolers were inspected and replaced and verified to be leak free. All gaskets in the north and south coolers will be replaced during the March 1992 Unit 2 outage. Also, during each 54 month exciter inspection, the associated gaskets will be replaced.
364 | 3641992002 | 1992-03-06 | QR8 | Spurious Reactor Trip | [45 empty] | Farley 2 | P | WE | PO | 8 | At 2307 on 3-6-92, during a rampdown for the 8th refueling outage, the reactor tripped on an intermediate range (IR) high flux level trip signal. The high flux level reactor trip signal from IR nuclear instrument NI-35 did not reset when power was reduced below the expected power level for trip reset. This resulted in a reactor trip from NI-35 when reactor power went below 10% power (P-10) causing the IR high flux trip to automatically reinstate. <br /><br /> The plant was stabilized in Mode 3 following the trip and the appropriate notifications were made. <br /><br /> The cause for the reactor trip was procedural inadequacy and personnel error. The unit operating procedure did not require the operators to verify the IR high flux trip reset prior to reducing power below 10 percent. Furthermore, the operating crew failed to recognize that the IR high flux trip had not reset. The unit operating procedure has been revised to require operators to check the bistables reset for the IR high flux trip before going below 10 percent reactor power. Appropriate procedures have been revised to increase the IR high flux trip reset setpoint to increase the likelihood of resetting the trip prior to reaching 10 percent reactor power. This incident will also be incorporated into the next cycle of licensed operator retraining scheduled to begin in September 1992. Farley Nuclear Plant experienced a similar event in October of 1990. The corrective action taken at that time was inadequate. The personnel responsible for corrective action with respect to the 1990 event have been counseled.
364 | 3641992005 | 1992-05-12 | QR5 | Turbine Trip | [45 empty] | Farley 2 | P | WE | PO | 12 | At 1331 on 5-12-92, with the unit in Mode 1 operating at 12 percent reactor power, following a refueling outage, the reactor tripped due to low water level in the 2C steam generator (SG) coincident with a steam flow greater than feed flow signal. The low level in the SG occurred as a result of a transient initiated from a main generator trip that occurred at 1243 on 5-12-92. The main generator tripped due to a generator neutral overcurrent. <br /><br /> Various combinations of rod control, steam dump control, and manual and auto feed regulator bypass valve control were utilized over the 48 minutes following the turbine generator trip in an effort to stabilize SG levels. Despite the attempts to regain automatic SG level control, SG 2C level dropped to 25 percent at 1331 on 5-12-92, resulting in a reactor trip.<br /><br /> The reactor trip was caused by personnel error in that the control room crew did not dampen the SG level oscillations with a more restrictive 2C SG low level trip setpoint (25 percent versus 17 percent) imposed by a feedwater flow transmitter being in test. <br /><br /> To prevent recurrence, a critique was conducted with the Shift Supervisor and the plant operators on duty at the time of the trip. Data from the transient were evaluated and the control room crew and the oncoming crews were reinstructed, prior to assuming control room responsibilities, on options available when SG level control cannot be maintained in automatic. <br /><br /> The unit returned to power operation on 5-14-92 at 0822.
364 | 3641992006 | 1992-05-15 | QR8 | Spurious Reactor Trip | [45 empty] | Farley 2 | P | WE | PO | 35 | At 2004 on 5-15-92, while operating at approximately 35 percent power, a reactor trip occurred when the control power fuses for power range NI-41 and NI-43 blew. During the performance of FNP-2-STP-121, "Power Range Axial Offset Calibration," DVMs with unshielded leads were connected to the precision input resistors for each top and bottom detector in the four power range NI drawers. The use of unshielded leads on the DVMs allowed a 60 hertz signal to be superimposed on the normal DC signal from the power range detectors in the NIS. Because the plant power level (approximately 35 percent) was at a power permissive setpoint, the superimposed signal caused the bistable SCRs to rapidly turn on and off. This cycling action caused increased current through the control power fuses of the power range NIs. The high current caused the control power fuses to heat up and subsequently blow for NI-41 and NI-43. The NI-43 fuse blew approximately 9 seconds before the NI-41 fuse blew. The loss of control power to the two power range NIs caused the reactor trip. <br /><br /> This event was caused by procedural inadequacy. STP-121 for both units has been revised to allow instrumentation in only one power range drawer at a time during the performance of the surveillance. Furthermore, the procedure was revised to require the use of shielded cables for connecting test instrumentation to prevent induced voltages from affecting NIS performance. <br /><br /> Following the trip, the operators maintained the unit in a stable condition.
364 | 3641992007 | 1992-05-25 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Farley 2 | P | WE | PO | 100 | At 0545 on 5-25-92, while operating at 100 percent power, the Unit 2 reactor was manually tripped following the loss of the 2A steam generator feedwater pump (SGFP). The 2A SGFP tripped due to low auto stop oil pressure. Investigation revealed that the low auto stop oil pressure was caused by degradation of the lube oil pumps and excessive water in the lube oil system for the 2A SGFP. The lube oil pump degradation was due to the degraded material condition of the impeller coupling and keyway and inadequate technical manual guidance on assembling the pump impellers. One source of water intrusion has been identified as water inleakage past the shaft seals while the SGFP was not rotating. The major source of water intrusion has been identified as condensation from a small gland sealing steam leak that had become trapped by the turbine insulation and drawn into the oil. <br /><br /> The 2A SGFP bearing oil seals were replaced to reduce shaft leakage into the oil system through the bearing housing. All lube oil pumps for the 2A SGFP were disassembled, cleaned, inspected, repaired and reassembled. The oil sump was cleaned and filled with new oil. The bearing oil pressure, auto stop oil pressure, oil pump discharge pressure and the oil pump control circuit voltage were instrumented with recorders for monitoring.<br /><br /> Following return of the 2A SGFP, the water intrusion from the gland seal system was identified and corrected by rearrangement of the turbine insulation. The unit was returned to power operation at 0549 on 05-26-92.
364 | 3641992008 | 1992-05-26 | QR3 | Reactivity Control Imbalance | [45 empty] | Farley 2 | P | WE | PO | 45 | At 1817 on 5-26-92, while operating at 45 percent power, the Unit 2 reactor tripped due to a power range high negative flux rate. This occurred when the stationary gripper coils for the twelve rods powered by the 1 BD rod control power cabinet were mistakenly de-energized. Maintenance personnel intended to replace power supply fuses to the movable grippers to clear a rod control urgent failure condition; however, due to inadequate work planning and inappropriate actions, the stationary grippers were de-energized. <br /><br /> This event was caused by personnel error in that the maintenance work request (MWR) planning was inadequate and the journeyman took inappropriate action when he encountered an unexpected situation. <br /><br /> The individuals involved have been coached. This event will be discussed in licensed, non-licensed and maintenance annual retraining. Electrical Maintenance personnel will receive specialized training on the rod control system. Daily Planning personnel will also receive training on this event. Labels have been placed on the rod control power cabinet disconnects for both units indicating the coils affected and warning that the reactor will trip if the stationary coil disconnect is opened. <br /><br /> The unit returned to power operation at 0132 on 05-28-92.
364 | 3641992010 | 1992-10-20 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Farley 2 | P | WE | PO | 65 | At 0023 on 10-20-92, while operating at 65 percent power, the Unit 2 reactor was manually tripped due to reduced feedwater flow causing low levels in all steam generators (SG). The reduced feedwater flow was caused by a loss of condensate pump net positive suction head, The loss of condensate pump net positive suction head was caused by the inadvertent isolation of one section of condenser cooling water in conjunction with the intentional isolation of one section of condenser cooling water. The loss of cooling caused hotwell temperature to increase resulting in saturation and loss of level. This caused the condensate pumps to lose suction, resulting in a loss of steam generator feedwater pump (SGFP) suction pressure which, in turn, led to reduced feedwater flow to all SGs. <br /><br /> An FNP investigation has concluded that the cause of this event is personnel error in that Operations personnel inadvertently operated the local control switch and closed the AB waterbox outlet cooling water motor operated valve (MOV) during waterbox venting and seating of the outlet cooling water MOV for the AA waterbox. Troubleshooting was performed on the AB waterbox isolation MOV to determine if the valve had closed spuriously. No problems were identified that would support that conclusion. <br /><br /> To prevent recurrence, condenser inlet and outlet cooling water MOVs will normally be deenergized during power operations. As a further enhancement condenser waterbox push button control station labeling will be upgraded and procedure FNP-1/2-SOP-26.0 will be revised to verify flow to all waterboxes prior to isolating one waterbox for testing/maintenance.
364 | 3641993004 | 1993-12-02 | QP5 | Excessive Feedwater Flow | [45 empty] | Farley 2 | P | WE | PO | 5 | At 2233 on December 02, 1993, with the Unit in Mode 1 operating at approximately 5 percent reactor power, the reactor tripped due to a low-low water level in the 2C steam generator (S/G) following a turbine trip and feedwater isolation. <br /><br /> The turbine/generator had been ramped down to between 60 and 70 megawatts in preparation for a turbine overspeed test. At this time reactor power was being maintained at approximately 20 percent power with load being maintained by the main generator in combination with the steam dumps. After the main generator output breakers were opened, S/G level and feedwater flow oscillations occurred. The operators were unable to maintain S/G levels due to the steam generator feed pump speed control maintaining an excessive/erratic pressure differential across the feed regulating bypass valves as a result of a speed controller card failure. <br /><br /> The level in the 2B S/G rose to the point that turbine trip and feedwater isolation signals were generated. With feedwater isolated, the S/G levels decreased. The operators began simultaneously feeding the S/G with auxiliary feedwater at the maximum attainable rate to maintain levels, and began inserting the control rods to reduce reactor power and return the Reactor Coolant System average temperature to the program value. Within approximately 1.5 minutes of the turbine trip/feedwater isolation, the reactor tripped on low-low level in the 2C S/G.
364 | 3641994001 | 1994-08-05 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Farley 2 | P | WE | PO | 100 | At 1459 on August 5, 1994, with the Unit in Mode 1 and operating at approximately 100 percent reactor power, the main turbine was manually tripped due to degrading condenser vacuum. This manual trip of the main turbine from 100 percent power initiated a reactor trip as designed.<br /><br /> Previous to the trip, work had been performed on a low pressure turbine gland seal regulator to repair a steam leak. Upon valving the regulator in after the repair, it was noted that the gland seal steam pressure was being maintained slightly above the normal band as indicated on the local pressure indicator. The regulator was adjusted to lower the gland seal pressure to the proper range as indicated on the local pressure gauge. This adjustment was made by an Instrument and Controls technician who was assisted by an Operations systems operator. The local pressure indicator was subsequently determined to be inaccurate and actual gland seal pressure was too low to prevent air in-leakage into the main condenser. Shortly after completion of the above adjustments, condenser vacuum degraded rapidly, and upon reaching the administrative main turbine manual trip criteria of 2.7 psia, the control room operators tripped the main turbine. This initiated an automatic reactor trip per design. The Operations crew responded to the reactor trip as directed by plant procedures. The faulty gauge was replaced and the Unit was returned to service.
364 | 3641994003 | 1994-12-18 | QR5 | Turbine Trip | [45 empty] | Farley 2 | P | WE | PO | 100 | At 03:52 on December 18, 1994, with Unit 2 in Mode 1 operating at 100 percent reactor power, the reactor tripped due to low-low level in the 2C steam generator (SG). The low-low SG level occurred as a result of a load transient initiated by the digital electro-hydraulic control (DEHC) system closing all four governor valves. The rapid load reduction resulted in SG level shrink sufficient enough to generate a reactor trip signal. <br /><br /> A root cause investigation which included a review of the DEHC system and plant computer data attributed the event to an intermittent failure in the 63AST-2 auto stop oil pressure switch circuit that provides an electrical input to the DEHC governor control auto stop latch circuitry. <br /><br /> The suspect pressure switch was replaced. Additionally, a temporary recorder was installed to monitor auto stop oil pressure. The unit was returned to power operation on 12/19/94 at 1806. <br /><br /> Subsequently, on December 25, 1994, with Unit 2 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip caused by an intermittent failure of the DEHC overspeed protection circuitry. A root cause investigation of this subsequent event indicated that although the sequence of events of the referenced reactor trips were different, both reactor trips were most likely caused by an intermittent DEHC system processor failure. Subsequently, six cards associated with the DEHC system have been replaced and forwarded to the vendor for evaluation.
364 | 3641994004 | 1994-12-25 | QR5 | Turbine Trip | [45 empty] | Farley 2 | P | WE | PO | 100 | At 1534, on December 25, 1994, with Unit 2 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip in response to a loss of digital electro-hydraulic control (DEHC) overspeed protection. Investigations indicated the primary overspeed protection (OPC) controller (DROP 2) failed in a manner which prevented the redundant OPC controller (DROP 52) from assuming control of the turbine DEHC overspeed protection function within the required time frame. This resulted in a turbine trip due to a loss of both OPC controllers. Six cards associated with the DEHC system (three associated with the DROP 2 processor) have been replaced and forwarded to the vendor for evaluation. <br /><br /> The unit was returned to power operation at 2123 on December 26, 1994. Subsequently, on January 13, 1995, with Unit 1 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip in response to a loss of DEHC overspeed protection. An evaluation of this Unit 1 event indicated that both reactor trips could have been caused by the vulnerability of the DEHC OPC processors and their associated power supplies to minor voltage transients. Modifications have been performed to the Unit 1 DEHC in order to reduce the vulnerability to minor voltage transients. Preparations to perform DEHC modifications on Unit 2 are currently in progress.
364 | 3641995005 | 1995-06-01 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Farley 2 | P | WE | PO | 30 | At 0058 on June 1, 1995 with the Unit 2 reactor in mode 1 operating at 30 percent power, the reactor was manually tripped following the loss of the operating (2A) steam generator feed pump (SGFP)[SJ]. The loss of the SGFP was caused by a failed electro-hydraulic (EH) fluid supply line and subsequent loss of EH fluid. tubing-to-fitting socket weld on the EH supply to the high pressure governor valve to the 2A SGFP. Initially, the June 1, 1995 event was attributed to cyclic fatigue (pending the results of metallurgical analysis) caused by a loose support clamp, and higher than normal vibrations which are associated with feed pump operations at low power. and the failed tubing was sent off site for detailed failure analysis. The unit was returned to power operation at 1912 on June 2, 1995 using 2B SGFP as the operating feedpump. Subsequently, at 0948 on June 3, 1995, with the reactor operating at 33 percent power, the reactor was manually tripped following the loss of the operating (2A) SGFP caused by a failed EH fluid supply line on the 2A SGFP and subsequent loss of EH fluid.<br /><br /> Examination of the failed tubing revealed that the failures experienced on June 1, 1995 and June 3, 1995 were sudden impact failures caused by servovalve failures which resulted in mechanical and hydraulic oscillations in the EH system. Portions of the EH tubing were replaced, clamps and supports were inspected and repaired, and servovalves were replaced (June 3, 1995 trip only). The unit was returned to power operation at 1515 on June 5, 1995.
364 | 3641995005 | 1995-06-03 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Farley 2 | P | WE | PO | 33 | At 0058 on June 1, 1995 with the Unit 2 reactor in mode 1 operating at 30 percent power, the reactor was manually tripped following the loss of the operating (2A) steam generator feed pump (SGFP)[SJ]. The loss of the SGFP was caused by a failed electro-hydraulic (EH) fluid supply line and subsequent loss of EH fluid. tubing-to-fitting socket weld on the EH supply to the high pressure governor valve to the 2A SGFP. Initially, the June 1, 1995 event was attributed to cyclic fatigue (pending the results of metallurgical analysis) caused by a loose support clamp, and higher than normal vibrations which are associated with feed pump operations at low power. and the failed tubing was sent off site for detailed failure analysis. The unit was returned to power operation at 1912 on June 2, 1995 using 2B SGFP as the operating feedpump. Subsequently, at 0948 on June 3, 1995, with the reactor operating at 33 percent power, the reactor was manually tripped following the loss of the operating (2A) SGFP caused by a failed EH fluid supply line on the 2A SGFP and subsequent loss of EH fluid.<br /><br /> Examination of the failed tubing revealed that the failures experienced on June 1, 1995 and June 3, 1995 were sudden impact failures caused by servovalve failures which resulted in mechanical and hydraulic oscillations in the EH system. Portions of the EH tubing were replaced, clamps and supports were inspected and repaired, and servovalves were replaced (June 3, 1995 trip only). The unit was returned to power operation at 1515 on June 5, 1995.
364 | 3641995007 | 1995-06-25 | QP5 | Excessive Feedwater Flow | [45 empty] | Farley 2 | P | WE | PO | 63 | At 1640 on June 25, 1995 with the Unit 2 reactor in mode 1 operating at approximately 63 percent power, the reactor tripped due to a turbine trip caused by 2C steam generator water level reaching the Hi-Hi setpoint of 79 percent. This occurred during the evolution of transferring feedwater flow from the 2A operating steam generator feed pump (SGFP)[SJ] to the 2B SGFP. As the speed of the operating 2A SGFP was lowered, the speed of the 2B SGFP automatically increased providing the necessary feedwater flow needed to maintain normal steam generator (SG) levels. However, as the 2A SGFP discharge flow approached minimum flow, the 2A SGFP miniflow valve opened per design. The operating crew failed to anticipate the opening of the miniflow valve which resulted in a decrease of feedwater flow to the SGs. In addition, the 2B SGFP failed to respond as expected. In order to raise SG levels the control room crew manually increased the speed of the 2A SGFP and began taking manual control of the main feedwater regulation valves (MFRVs). 2A and 2B MFRVs were manually adjusted; however, prior to placing the 2C MFRV in manual, the 2C SG level reached the Hi-Hi setpoint of 79 percent. This resulted in an automatic turbine trip which initiated an automatic reactor trip. This event was caused by cognitive personnel error resulting in the overfilling of 2C SG to the Hi-Hi setpoint. The individuals involved have been coached concerning this incident. The unit was returned to power operation 0525 on June 29, 1995.
364 | 3641995008 | 1995-11-28 | QR5 | Turbine Trip | [45 empty] | Farley 2 | P | WE | PO | 100 | At 1233, on November 28, 1995, with Unit 2 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip in response to a loss of digital electro-hydraulic control (DEHC) overspeed protection circuitry. Investigations indicated the turbine trip was caused by the loss of the primary overspeed protection controller (OPC) (DROP 52) while the backup OPC (DROP 2) was momentarily shutdown for card replacement. An electronic card was being inserted in the I/O (Input/Output) chassis to repair DROP 2. A design defect, associated with card replacement in the control circuitry, allowed a momentary interrupt condition to exist on the 110 bus at the time of the replacement card insertion. This interrupt condition caused the operating digital processing unit (DROP 52) to stop processing I/O data. DROP 52 attempted to transfer OPC control to DROP 2 which was momentarily shutdown for card replacement. This resulted in a turbine trip due to a momentary loss of both OPCs. <br /><br /> This event was caused by the presence of a latent design defect in the DEHC circuitry which did not provide for the bumpless transfer during card change out. Three cards, with the latest hardware revision correcting the design defect, were replaced on Unit 2. An additional two cards in the Input/Output (I/O) chassis shared by DROP 52 and DROP 2, associated with the original fault conditions on DROP 2, have been replaced. Applicable Unit 1 DEHC cards will be replaced when plant conditions permit. A review of the DEHC card upgrade history for all DEHC cards is in process to determine if other hardware revisions are required.
364 | 3641999001 | 1999-06-12 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Farley 2 | P | WE | PO | 100 | Unit 2 was manually tripped on June 12, 1999 at 2147 due to decreasing vacuum in the condenser. A steam dump drain line was found broken. Metallurgical analysis of the drain line determined that it had failed due to fatigue. Thermal growth of the main steam line relative to the drain line that was at ambient temperature created high stress points at several points on the drain line due to the supports not adequately allowing for this growth. These high stress points included the location of the break. During construction, installation of the steam dump drain lines was craft routed as allowed for by the applicable piping specification and quality control procedures. The piping specification did not require a stress analysis on small bore piping in the turbine building. Later in plant life, a binding problem was identified. In 1990 a design change was issued to correct the binding problem with the steam dump drain header that, due to personnel error, did not consider the most extreme service condition in the stress analysis. Therefore, the design change was inadequate in that it did not eliminate the overstress condition of the drain line which contributed to a fatigue failure of the pipe. The broken section of line was replaced. Several supports were modified to relieve the stress in the drain header. Engineering review of the new configuration by design personnel has determined it to be acceptable to operate until the next refueling outage. An additional design change, to further reduce the stress on the drain operate until header and the steam dump drain lines, will be implemented during the next refueling outage. The corresponding piping on Unit 1, which is configured differently than Unit 2, has been visually examined, and no indication of excessive stress due to binding was detected.
364 | 3642000004 | 2000-11-16 | QP5 | Excessive Feedwater Flow | [45 empty] | Farley 2 | P | WE | PO | 100 | On November 16, 2000, at 0323, Unit 2 experienced an automatic reactor trip resulting from a turbine trip from high steam generator (SG) water level in the 2A SG. At 0318, approximately 5 minutes prior to the event, both Steam Generator Feedwater Pumps (SGFP) had decreased to minimum speed due to a failure in the master speed control circuit. The operator manually recovered speed control, but due to sluggish response of the 2A SG main feedwater regulating valve (MFRV), too much water was supplied to the 2A SG and the high level turbine trip was actuated. The turbine trip provides a direct reactor trip signal at power greater than 35%. All safety systems functioned as designed following the trip. The transient leading to the trip was initiated by a failed card (failed soldier joint) in the feedwater pump speed control circuit. Nevertheless, had the 2A MFRV responded normally, a trip should not have occurred. The sluggish response of the 2A MRFV was due to the air bleed path filter within the positioner being clogged as a result of inadequate preventive maintenance on the positioner. Feedwater isolation, the safety function of this valve, was unaffected by this condition. The 2A MFRV positioner was replaced. The 2B and 2C MFRV positioner air bleed paths were verified clear, and the positioners were setup to preclude the valves from going into saturation. The failed feed pump speed control circuit card was replaced. To prevent recurrence, preventive maintenance practices for the MFRV will be revised to provide adequate guidance by February 24, 2001. The Unit 1 MFRVs were verified to have a positioner type not susceptible to this type failure.
364 | 3642001001 | 2001-06-23 | QR5 | Turbine Trip | [45 empty] | Farley 2 | P | WE | PO | 100 | On June 23, 2001, with the reactor at 100% power, Unit 2 experienced an automatic reactor trip due to a main generator neutral overcurrent trip, which resulted in a turbine trip/reactor trip. The generator neutral transformer electrical connection bolt had been overtorqued during previous refueling outages and subsequently failed, resulting in a main generator trip. The failure of the bolted electrical connection on the generator neutral overcurrent transformer was due to a combination of personnel error and inadequate procedure in that on three occasions workers misidentified the silicon bronze bolt as steel and consequently overtorqued it. The main generator tagging and backfeed procedure did not provide guidance for distinguishing between coated bronze and steel bolt materials which are visually similar but have different torque requirements. This overtorquing was further aggravated on two of three occasions by failure to follow procedure in the use of metric values with a wrench calibrated in English units. A contributing cause was inadequate procedure in that no guidance on evaluating an overtorquing was established. The main generator tagging and backfeed procedures will be revised by September 1, 2001 to specify the exclusive use of silicon bronze bolts in this application, to specify only a single torque value, and to require replacement of the generator neutral transformer connecting bolts every refueling outage. Appropriate personnel will be made aware of this event and of the above procedure changes by October 1, 2001. Appropriate training and procedure changes will be provided by October 1, 2001 to create a standard requiring that, if a bolt is ever overtorqued, it will be evaluated for suitability for continued service.
364 | 3642001002 | 2001-06-26 | QR5 | Turbine Trip | [45 empty] | Farley 2 | P | WE | PO | 100 | On June 26, 2001, at 0646, with the reactor at 100% power, Unit 2 experienced an automatic reactor trip due to turbine trip. At 0646, the reactor operator reinstalled the turbine latch pushbutton in the turbine control panel on the main control board after changing the light bulbs in the pushbutton. This action requires the pushbutton to be depressed in order to lock it in place. Depressing the turbine latch pushbutton actuates the turbine latch mechanism at the turbine (even if the turbine is already latched). When the latch pushbutton was released, the latch mechanism overtraveled from the latch position through the neutral position to the trip position, resulting in a direct turbine trip and consequently a reactor trip. This event was caused by an equipment deficiency in that the latch mechanism overtraveled to the trip position when released from the latch position. A contributing cause was that operators incorrectly concluded that depressing the pushbutton would not initiate additional actions since the turbine was latched, and therefore did not constitute a risk to continued operation. Administrative controls have been placed on the latch pushbutton on both units to preclude actuation when the turbine is already latched. The latch mechanism will be repaired or modified, or the remote latching feature disabled, at the next outage of sufficient duration. Training material has been revised and will be covered in licensed personnel requalification training by December 14, 2001.
364 | 3642003001 | 2003-11-10 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Farley 2 | P | WE | PO | 100 | On November 10, 2003 at 1036, with the reactor at 100% power, Unit 2 automatically tripped due to loss of power to the 2A Reactor Coolant Pump (RCP) breaker position input to the Reactor Protection System. By design, loss of this single breaker position input results in a direct reactor trip above 30% power. The power to the breaker position input circuit was lost due to a momentary loss of voltage on the 2A 120 VAC Vital Instrument Bus, which is normally powered by the 2A Inverter. The inverter automatically transferred to bypass during the electrical transient as it is designed to do on a fault. All safeguards equipment functioned as designed following the trip. The 2A Reactor Coolant Pump (RCP) breaker did not change position and the pump remained in operation throughout this event. Extensive troubleshooting on both the inverter and the instrument bus failed to determine any reason for the momentary loss of voltage or the transfer of the inverter output to bypass. Possible causes considered included an inverter failure, an electrical fault on the 2A 120 VAC Vital Instrument Bus or its connected loads, and maintenance activities possibly causing a short which would impact the 2A 120VAC Vital Instrument Bus. None of these could be confirmed. The RCP breaker position indication power supplies have been realigned from the inverters to independent dedicated regulated AC sources.
364 | 3642007001 | 2007-10-03 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Farley 2 | P | WE | PO | 100 | On October 3, 2007 at 1410, with the reactor at 100% power, Unit 2 automatically tripped due to a loss of power to the Unit 2 8-train electrical distribution system [EA]. This occurred during a Unit 1 refueling outage while performing testing on Unit 1 Main Generator Differential Lockout relay. As a result, the supply breaker to 2B Startup Transformer was inadvertently tripped. The loss of Unit 2 B-train 4160V power ultimately led to a loss of power to Reactor Coolant Pump (RCP) Breaker Indication (1 out of 3 coincidence). The reactor tripped per design. All safety systems functioned as designed. This event was caused by a testing procedure that lacked a step to block the High Voltage Switchyard (HVSY) breaker failure sequence relays. The failure to block resulted in the breaker failure sequence relays actuating. The breaker failure sequence relays tripped the associated HVSY breakers, which then deenergized the 2B Startup Transformer. Loss of the 2B Startup Transformer ultimately led to loss of RCP Breaker Indication relay, resulting in Unit 2 reactor trip. The subject procedure has been revised.
364 | 3642010002 | 2010-05-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Farley 2 | P | WE | PO | 100 | On May 22, 2010 at 16:34, with Unit 2 at 100% power, the reactor was manually tripped due to 2C Steam Generator (SG) Feedwater Regulating Valve (FRV) failing closed. At approximately 16:34, the control room crew received multiple alarms associated with 2C SG level and a process cabinet failure. The crew noted no feedwater flow and decreasing level in 2C SG. Manual control of the 2C SG FRV was attempted but there was no power or control capability of the main feedwater regulating valve. At approximately 40% narrow range level in the 2C SG, the crew manually tripped Unit 2 prior to the automatic trip setpoint of 28% narrow range level. All safety systems functioned as designed without complications. Investigation revealed that the controller driver (NCD) card in the 2C SG FRV controller circuitry failed causing the 2C SG FRV to close. The failed NCD card was replaced. Unit 2 was restarted and returned to Mode 1 on May 23, 2010 at 17:12.
364 | 3642014002 | 2014-10-14 | QR6 | Manual Reactor Trip | [45 empty] | Farley 2 | P | WE | PO | 82 | On 10/14/14 at 0341 CDT, Unit 2 reactor was manually tripped after a lightning strike In the High Voltage Switchyard (HVSY) led to a phase 3 to ground fault on a 500kV transmission line resulting in a B train Loss of Site Power (LOSP). The fault caused the 2B Startup Auxiliary Transformer (SAT) Instantaneous overcurrent relay to actuate and resulted in deenergizing the 2B SAT. A missing nut in the Power Circuit Breaker (PCB) protection circuitry caused a high resistance on one side of the current transformer circuit resulting in an imbalance in current flows and an actuation in the primary differential instantaneous overcurrent relaying. The B train LOSP in conjunction with the 2B Emergency Diesel Generator (EDG) being out of service for a planned maintenance outage caused a loss of Component Cooling Water (CCW) to the Reactor Coolant Pumps (RCP). The Unit 2 Abnormal Operating Procedures for loss of CCW and loss of A or B Train Electrical Power were entered and the reactor was manually tripped and the RCPs were secured. The reactor trip is reportable per 10 CFR 50.73(a)(2)(iv)(A) for manual actuation of the reactor protection system. Additionally, the reactor trip resulted in a valid actuation of the Auxiliary Feedwater system which is reportable per 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> Corrective actions include: installed the missing PCB current transformer (CT) nut; satisfactorily tested primary and secondary protective relaying for 2B SAT; and strengthening of switchyard standards of the utility performing the maintenance. Extent of Condition walkdowns were performed for other circuits in the HVSY and repaired as necessary
364 | 3642016001 | 2016-05-11 | QP5 | Excessive Feedwater Flow | [45 empty] | Farley 2 | P | WE | PO | 29 | On 5/11/2016 at 0653 CDT, with Unit 2 (U2) at 29 percent power, the Hi-Hi Steam Generator (SG) setpoint was reached. This caused the main feedwater valves to isolate, the running main feedwater pumps to trip, automatic start of the Motor Driven Auxiliary Feed Pumps, and the main turbine to trip automatically. The reactor was manually tripped per procedure. This event is reportable as required by 10 CFR 50.73(a)(2)(iv)(A) due to a manual actuation of the Reactor Protection System and the automatic actuation of the Auxiliary Feedwater system. <br /><br /> The cause of the manual reactor trip was determined to be inadequate control of the feedwater system, leading to an overfilling of the Steam Generators. Corrective actions included additional training provided to the startup control room team on manipulations that affect the feedwater system. Also, more specific guidance on feedwater system operation and control during Startup from Hot Standby to Power Operations will also be incorporated into operating procedures.
364 | 3642019003 | 2019-09-21 | QR6 | Manual Reactor Trip | [45 empty] | Farley 2 | P | WE | PO | 100 | On September 21, 2019, at 0744 CDT, while operating at 100% power, Farley Nuclear Plant (FNP) Unit 2 received a vibration alarm on the 2C Reactor Coolant Pump (RCP). Operators entered the applicable Annunciator Response Procedure (ARP). At 0800 CDT, the Control Room Operators manually tripped Unit 2 due to indicated vibrations on the 2C RCP exceeding procedural limits. The post-trip response was normal. All trains of Auxiliary Feed Water pumps actuated normally due to low Steam Generator (SG) levels post trip. Operators took appropriate action to stabilize the unit in Mode 3.<br /><br /> The investigation determined the most likely cause for the RCP vibration indication was the temporary in-phasing of the various contributing frequencies. The ARP contained insufficient information to allow the Control Room Operators to determine if the indications represented an actual vibration condition that threatened RCP operation. The Control Room Operators tripped the reactor based on available indications per the guidance of the ARP. Corrective Actions included revising the ARP to enhance the guidance for vibration conditions that require action to protect the RCP.<br /><br /> This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual actuation of systems listed in 10CFR50.73(a)(2)(iv)(B). FNP Unit 1 was not affected during this event.
366 | 3661987003 | 1987-01-26 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Hatch 2 | B | GE | PO | 100 | POWER LEVEL - 100%. ON 01/26/87 AT APPROXIMATELY 1308 CST, UNIT 2 WAS IN STEADY STATE OPERATION AT AN APPROXIMATE POWER LEVEL OF 2436 MWT (100 PERCENT OF RATED THERMAL POWER). THE REACTOR MODE SWITCH WAS IN THE RUN MODE. AT THAT TIME, PLANT PERSONNEL WERE PERFORMING A MAIN STEAM LINE RADIATION MONITOR FUNCTIONAL TEST AND A PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) (JM) GROUP 1 ISOLATION OCCURRED. AS PART OF THIS ISOLATION, THE MAIN STEAM LINE ISOLATION VALVES (MSIVS) (JM) CLOSED, WHICH INPUT A REACTOR SCRAM SIGNAL TO THE REACTOR PROTECTION SYSTEM (RPS)(JC). THE ROOT CAUSE OF THIS EVENT WAS EQUIPMENT FAILURE (A TEMPERATURE SWITCH MONITOR). WHEN THE EVENT OCCURRED, A TEST PROCEDURE STEP WAS IN PROGRESS THAT, IN CONJUNCTION WITH THE EQUIPMENT FAILURE, CAUSED THE CLOSURE OF THE MSIVS AND THE RESULTING REACTOR SCRAM. CORRECTIVE ACTIONS INLCUDE: 1) REPLACEMENT OF THE TEMPERATURE SENSOR, AND 2) REVISION TO PLANT PROCEDURE.
366 | 3661987008 | 1987-04-22 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Hatch 2 | B | GE | PO | 97 | POWER LEVEL - 097%. ON 4/22/87 AT APPROXIMATELY 1718 CDT, UNIT 2 WAS IN THE RUN MODE AT AN APPROXIMATE POWER OF 2358 MWT (97 PERCENT OF RATED THERMAL POWER). AT THAT TIME, THE '2C' CONDENSATE PUMP (EIIS CODE SD) TRIPPED. THIS CAUSED THE '2B' AND '2C' CONDENSATE BOOSTER PUMPS (EIIS CODE SD) AND THE REACTOR FEED PUMPS (EIIS CODE SJ) TO TRIP ON LOW SUCTION PRESSURE. REACTOR WATER LEVEL DECREASED TO THE SCRAM SETPOINT AND A SCRAM OCCURRED. THE CONDENSATE PUMP TRIPPED BECAUSE OF A HARD ELECTRICAL GROUND CONDITION IN THE PUMP MOTOR. THIS OCCURRED WHEN ONE OF THE STATOR COILS SHORTED. AN INVESTIGATION IS UNDERWAY TO DETERMINE THE CAUSE FOR THE COIL FAILURE. CORRECTIVE ACTIONS FOR THIS EVENT INCLUDED: 1) SENDING THE '2C' CONDENSATE PUMP MOTOR TO A REPAIR FACILITY FOR INVESTIGATION AND REPAIR; 2) REPLACING THE MOTOR AND PERFORMING PRE-OPERATION MAINTENANCE CHECK-OUTS ON THE NEW MOTOR; 3) REVIEWING MAINTENANCE HISTORY ON THE FAILED MOTOR; AND 4) INVESTIGATING AND SCHEDULING MAINTENANCE FOR THE MAIN FEED PUMP TURBINE TRIP CIRCUITRY.
366 | 3661987006 | 1987-07-26 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Hatch 2 | B | GE | PO | 89 | POWER LEVEL - 089%. ON 7/26/87, AT APPROXIMATELY 1405 CDT, UNIT 2 WAS IN THE RUN MODE AT AN APPROXIMATE POWER LEVEL OF 2170 MWT (APPROXIMATELY 89 PERCENT OF RATED THERMAL POWER). AT THAT TIME, VITAL AC (EIIS CODE EE) POWER WAS LOST. THIS RESULTED IN A DECREASE IN THE REACTOR FEEDWATER PUMPS FLOW AND A DECREASE IN REACTOR WATER LEVEL. THE REACTOR WATER LEVEL DECREASED TO THE REACTOR PROTECTION SYSTEM (RPS EIIS CODE JC) ACTUATION SETPOINT AND A REACTOR SCRAM OCCURRED. THE ROOT CAUSE OF THIS EVENT IS ATTRIBUTED TO EQUIPMENT FAILURE DUE TO INADEQUATE HEATING VENTILATION AND AIR CONDITIONING (HVAC) DESIGN TO ENSURE THE VITAL AC EQUIPMENT (I.E., ELECTRICAL INVERTER) IS PROPERLY COOLED. THE ELECTRONIC EQUIPMENT FAILURE IN THE INVERTER IS ATTRIBUTED TO THE HIGH ROOM TEMPERATURES. CORRECTIVE ACTIONS FOR THIS EVENT INCLUDE: 1) REFURBISHING THE INVERTER, 2) ADDING TEMPORARY COOLING TO THE INVERTER ROOMS, 3) INSTALLING A NEW HVAC SYSTEM FOR COOLING INVERTER ROOMS, 4) DEVELOPING A UNIT COMMON PREVENTIVE MAINTENANCE PROCEDURE FOR BOTH INVERTERS AND, 5) INSTALLING NEW VITAL AC INVERTERS FOR BOTH UNITS 1 AND 2.
366 | 3661987009 | 1987-08-03 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Hatch 2 | B | GE | PO | 90 | POWER LEVEL - 090%. ON 8/3/87 AT APPROXIMATELY 1152 CDT, UNIT 2 WAS IN THE RUN MODE AT AN APPROXIMATE POWER LEVEL OF 2193 MWT (APPROXIMATELY 90 PERCENT OF RATED THERMAL POWER). AT THAT TIME, VITAL AC (EIIS CODE EE) POWER WAS LOST. THIS RESULTED IN A DECREASE IN THE REACTOR FEEDWATER PUMPS FLOW AND A DECREASE IN REACTOR WATER LEVEL. THE REACTOR WATER LEVEL DECREASED TO THE REACTOR PROTECTION SYSTEM (RPS EIIS CODE JC) ACTUATION SETPOINT AND A REACTOR SCRAM OCCURRED. THE ROOT CAUSE OF THIS EVENT IS ELECTRICAL EQUIPMENT FAILURE. SPECIFICALLY, CIRCUIT BREAKER CB-4 WOULD OPEN UNDER UNDULY LOW FORCE CONDITIONS. IT WAS CONCLUDED AFTER FIELD TESTING AND CONSULTATION WITH THE MANUFACTURER THAT THE TRIPPING MECHANISM WAS WEAK. CORRECTIVE ACTIONS FOR THIS EVENT INCLUDED: 1) INSTALLING JUMPERS AND REMOVING EQUIPMENT FROM SERVICE, 2) DESIGNING AND INSTALLING BARRIER BOXES, 3) VERIFYING TRIP INSTRUMENTATION AND LEVEL TRANSMITTERS IN CALIBRATION, 4) VENTING INSTRUMENT LINES AND TRANSMITTERS, 5) PERFORMING EVALUATIONS OF AIR ENTRAINMENT AND SPIKING IN INSTRUMENT LINES, 6) INITIATING PROCEDURE REVISIONS, AND 7) VERIFYING CERTAIN OTHER SYSTEMS DO NOT HAVE LOW SUCTION TRIPS.
366 | 3661988006 | 1988-03-18 | QR8 | Spurious Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Hatch 2 | B | GE | SU | 5 | On 03/18/88 at approximately 0920 CST, Unit 2 was in the startup mode of operation at an approximate power level of 172 MWt (approximately 5 percent of rated thermal power). The main turbine was in the tripped condition. Plant personnel were performing a functional test of the turbine control valve fast closure scram instrumentation. The removal of electrical links, to remove the less than 30% power scram bypass feature, resulted in an unplanned scram. Later, one main steam line drain isolation valve (EIIS SB) failed to close on the expected Group 1 signal due to loss of condenser vacuum. The valve did not receive the isolation signal. <br /><br />The scram was caused by a deficiency in the procedure, which failed to provide proper instructions for performing the functional test. Removing the bypass for both channels at the same time, when the control valve closure signal was present, resulted in the scram. The cause for the valve not receiving the isolation signal could not be determined. <br /><br />Corrective actions for this event included issuing a procedure revision, investigating the lack of isolation signal to the Group 1 valve, and demonstrating the valve would isolate in response to the Group 1 signal.
366 | 3661988008 | 1988-03-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hatch 2 | B | GE | PO | 18 | On 3/21/88 at approximately 1644 CST, Unit 2 was in the run mode of operation at an approximate power level of 440 MWt (approximately 18% of rated thermal power). In the process of transferring the Feedwater Control System (FCS EIIS Code SJ) from startup control to single element control, fluctuations in reactor vessel water level were experienced. Operations personnel manually scrammed the reactor due to decreasing level and also received a Primary Containment Isolation System (PCIS EIIS Code JM) valve Group 2 isolation. Level was restored using the reactor feed pumps and manually initiating Reactor Core Isolation Cooling (RCIC EIIS Code BN). <br /><br />The immediate cause for the FCS instability was improper settings on the master control loop controller (2C32-K636). The root cause for these improper settings was determined to be a deficient calibration procedure. <br /><br />Corrective actions for this event included correcting the settings on the controller and scheduling development of a more comprehensive calibration procedure. As an enhancement, a comparable procedure will also be developed for Unit 1.
366 | 3661988011 | 1988-04-17 | QR8 | Spurious Reactor Trip | [45 empty] | Hatch 2 | B | GE | PO | 80 | On 04/17/88 at approximately 0140 CDT, Unit 2 was in the run mode at an approximate power level of 1949 MWt (approximately 80 percent of rated thermal power). Operations personnel were performing a Turbine Control Valve (TCV EIIS Code JJ) Fast Closure Instrument Functional Test. With the Reactor Protection System (RPS EIIS Code JC) channel A in the tripped condition due to the TCV testing, the RPS channel B unexpectedly tripped, resulting in a scram. <br /><br /> The root cause of this event appears to be equipment failure. Specifically, the probable cause of the RPS channel B trip was a failed 15 volt regulator card in the Average Power Range Monitor (APRM EIIS Code IG) channel B. However, since it was determined that the alarm printer would not have recorded a high pressure scram signal due to a failed process computer board, the RPS channel B trip could also have been caused by a spurious high pressure trip. <br /><br /> Corrective actions for this event included thoroughly investigating trip system B1 (the portion of RPS channel B logic which actually tripped) for the cause of the trip and replacing the failed equipment.
366 | 3661988017 | 1988-05-27 | QP3 | Loss of Condensate Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Hatch 2 | B | GE | PO | 98 | On 05/27/88 at approximately 0407 CDT, Unit 2 was in the run mode at an approximate power level of 2384 MWt (approximately 98% of rated thermal power). In the process of filling and venting condensate pump 2N21-C001B (EIIS Code SJ) an air bubble was released into the condensate system tripping the condensate booster pumps (EIIS Code SJ) and reactor feed pumps (EIIS Code SJ) on low suction pressure. Reactor water level dropped and the reactor scrammed on low water level. In the event the Reactor Core Isolation Cooling (RCIC EIIS Code BN) system did not function as anticipated. <br /><br /> The root cause of this event was a deficient condensate and feedwater system operating procedure. The procedure did not give instructions for filling and venting a condensate pump while the unit was on line. <br /><br />Corrective actions for this event are: 1) replacing the limit switch on a RCIC valve, 2) verbally making involved personnel aware of cause and j consequences of this event, and 3) scheduling revision to the condensate and feedwater system operating procedures for both units. The procedures will be revised to include instructions on filling and venting the condensate pumps.
366 | 3661988018 | 1988-05-29 | QR8 | Spurious Reactor Trip | [45 empty] | Hatch 2 | B | GE | PO | 47 | On 5/29/88 at approximately 1002 CDT, Unit 2 was in the run mode at an approximate power level of 1140 MWt (approximately 47 percent of rated thermal power). At that time, plant operations personnel were performing a normally scheduled main Turbine Control Valve (TCV EIIS Code JJ) surveillance. During procedure performance, a full reactor scram occurred. This was an unanticipated actuation of the Reactor Protection System (RPS EIIS Code JC). <br /><br />The root cause of this event is thought to be a failure of the disc dump valve associated with TCV 2 to seat properly following actuation of the TCV during testing. The failure of the disc dump valve to seat properly is believed to be the result of normal wear. <br /><br />Corrective action for this event included: 1) installing orifices to reduce pressure transients in the Electro Hydraulic Control (EHC EIIS Code TQ) oil manifold and 2) scheduling repair or replacement of disc dump valves during the next refueling outage.
366 | 3661988020 | 1988-08-05 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Hatch 2 | B | GE | PO | 100 | On 08/05/88, at approximately 1546 CDT, Unit 2 was in the run mode at an approximate power level of 2424 MWt (approximately 100 percent of rated thermal power). When reinstalling a repaired Feedwater Minimum Flow Controller, a fuse blew, causing minimum flow valves on the Condensate, Condensate Booster and Reactor Feed Pumps to fail open. This resulted in a loss of suction and subsequent tripping of the Condensate Booster Pumps and Reactor Feed Pumps. <br /><br />The rapid decrease in reactor water level resulted in a reactor scram, a Primary Containment Isolation system valve Group 2 and partial Group 5 isolation. Reactor water level was restored using the 'A' Reactor Feed Pump, the High Pressure Coolant Injection System and the Reactor Core Isolation Cooling System. <br /><br /> The event was caused by a design deficiency. An electrical circuit containing twelve instruments, including four Condensate and Feedwater system controllers, had only one in-line fuse. As a result, an in-line fuse (2N21-F7) failed which resulted in a loss of suction for and the tripping of the Condensate Booster Pumps and the Reactor Feed Pumps. The fuse was replaced and a design review of the Feedwater Control System was initiated to identify and change any similar deficient conditions.
366 | 3661988024 | 1988-12-25 | QR6 | Manual Reactor Trip | [45 empty] | Hatch 2 | B | GE | PO | 90 | On 12/25/88, at approximately 0510 CST, Unit 2 was in the run mode at an approximate power level of 2202 MWT (approximately 90% of rated thermal power). At that time, both Reactor Recirculation Pumps tripped while performing the weekly surveillance on Turbine Stop Valves (TSVs). The unit was manually scrammed immediately as required by Unit 2 Technical Specification Section 3.4.1.1, Action a. Following the manual scram, reactor vessel water level decreased to the Primary Containment Isolation System valve Group 2 isolation setpoint and all Group 2 valves isolated as designed. <br /><br />The root cause of this event is component failure. The roll pin in the actuating arm of the limit switch for TSV Number 4 was broken. This prevented the TSV from picking up the actuating arm when the valve was open fully. As a result, the Recirculation Pump Trip logic sensed TSV Number 4 less than 90% open. When TSV Number 2 was closed for testing, the logic was satisfied and both Recirculation Pumps tripped per design. <br /><br />The corrective actions for this event included repairing the failed limit switch and revising TSV and Turbine Control Valve testing procedures.
366 | 3661989005 | 1989-09-03 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Hatch 2 | B | GE | PO | 70 | On 9/3/89 at approximately 2239 CDT, Unit 2 was in the Run mode at an approximate power level of 1695 CMWT (approximately 70% of rated thermal power). At that time, licensed operations personnel were changing reactor vessel water level control from single element to three element control following completion of procedure 57SV-SUV-004-2S, "Excess Flow Check Valve Operability," for the main steam line flow instruments' excess flow check valves. When the master controller was placed in Automatic following the change from single element to three element control, the controller's output signal suddenly went to zero. Both Reactor Feed Pumps decreased feedwater flow to the reactor vessel in response to the controller's zero output signal. Reactor vessel water level decreased and the reactor scrammed on low water level.<br /><br /> The root cause of this event is component failure. The Self Synchronized Control Unit, the main operating unit of the master controller, failed when the master controller was placed in Automatic. The failure of the Self Synchronized Control Unit caused the master controller's output signal to go to zero. <br /><br /> Corrective actions for this event included replacing the Self Synchronized Control Unit.
366 | 3661990001 | 1990-01-12 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Hatch 2 | B | GE | PO | 100 | On 1/12/90 at approximately 1610 CST, Unit 2 was in the Run mode at an approximate power of 2436 CMWT (approximately 100% of rated thermal power). At that time, the reactor scrammed because the Main Steamline Isolation Valves (MSIVs) were less than 90% open. The MSIVs had isolated on a Group 1 Primary Containment Isolation System (PCIS) signal which resulted from a false low condenser vacuum signal. The High Pressure Coolant Injection (HPCI) system automatically initiated and injected on low reactor water level as required. Following water level recovery, HPCI injection valve 2E41-F006 closed automatically on high water level; however, it could not be re-opened when Operations personnel subsequently attempted to start HPCI manually. The Reactor Core Isolation Cooling system and two Control Rod Drive system pumps were used to control water level following the failure of valve 2E41-F006 to open. <br /><br /> The root causes of the scram are component failure and the configuration of the condenser vacuum sensing lines and instruments. The disc of root isolation valve 2N61-F588D separated from its stem isolating the common sensing line for vacuum switches 2B21-N056C and D. Consequently, these switches then sensed a low condenser vacuum and, because they input to the A and B trip systems respectively of the isolation logic, the MSIVs isolated. The cause of valve 2E41-F006 failing to open is component failure. The heater strip of a thermal overload relay in the valve motor's local starter failed causing an open circuit to the motor. The failure of the heater strip appears to be an isolated event. <br /><br /> Corrective actions for this event included replacing the root isolation valves with a new type of valve, replacing the thermal overload relays in the local starter, and reconfiguring the tubing for the vacuum switches
366 | 3661990003 | 1990-03-28 | QR8 | Spurious Reactor Trip | [45 empty] | Hatch 2 | B | GE | PO | 100 | On 3/28/90 at approximately 0815 CST, Unit 2 was in the Run mode at an approximate power level of 2436 CMWT (approximately 100% of rated thermal power). At that time, a plant Instrument and Controls (I&C) technician was valving-in pressure transmitter 2E32-NO50 following a routine calibration per procedure 57CP-CAL-103-2S, "ITT Barton Model 764 Differential Pressure Transmitter." Valving-in the pressure transmitter, which shares a common sensing line with Reactor Protection System (RPS) and Primary Containment Isolation System (PCIS) water level transmitters 2B21-N080C and D, caused a pressure perturbation in the sensing line which caused water level transmitters 2B21-N080C and D to spike downscale. This resulted in a false low water level signal being sent to the A2 and B2 trip channels in the RPS and the PCIS. Full scram and partial Group II PCIS isolation signals were generated per design; the unit scrammed and the outboard Group II Primary Containment Isolation Valves (PCIVs) closed. <br /><br /> The cause of this event is an inadequate procedure. Procedure 57CP-CAL-103-2S did not provide adequate instructions to prevent the pressure perturbation that resulted when pressure transmitter 2E32-N050 was valved-in. Furthermore, the procedure did not provide adequate return to service instructions (e.g., open links, install jumpers, lift leads) necessary to prevent a scram and PCIS actuation in the event of a perturbation in the common sensing line. <br /><br /> Corrective actions for this event include changing procedure 57CP-CAL-103-2S to correct these and similar errors, and reviewing and changing, as necessary, comparable Unit 1 and Unit 2 procedures.
366 | 3661991004 | 1991-02-14 | QR5 | Turbine Trip | [45 empty] | Hatch 2 | B | GE | PO | 98 | On 2/14/91, at approximately 1854 CST, Unit 2 was in the Run mode at an approximate power level of 2388 CMWT (approximately 97.5% rated thermal power). At that time, a voltage regulator card in the exciter system for the main generator failed, resulting in main generator and main turbine trips. The unit scrammed on turbine stop valve closure. Reactor water level decreased to approximately 2 inches below instrument zero and was restored to normal by the Reactor Feedwater Pumps and the Reactor Core Isolation Cooling system. Reactor vessel steam dome pressure briefly peaked at approximately 1116 psig and the Bypass valves successfully controlled pressure. No Safety Relief Valves opened. The pressure experienced in the main steam lines was transitory and apparently less than reactor vessel steam dome pressure. However, using steam dome pressure, the SRVs were possibly not in compliance with their +/-1% Technical Specifications tolerance requirement. The valves were removed and tested in accordance with code requirements. The actual drift experienced was within the bounds of a previous analysis demonstrating adequate overpressure protection. <br /><br /> The root cause of the scram was component failure. The cause of the SRV setpoint drift was corrosion-induced bonding of the surface between the pilot valve disc and seat.<br /><br /> Corrective actions for this event included replacing the failed component in the generator exciter system and removing and refurbishing the SRVs. Georgia Power Company (GPC) will continue to participate in the BWR Owners' Group action plan to resolve setpoint drift.
366 | 3661991005 | 1991-02-24 | QP5 | Excessive Feedwater Flow | [45 empty] | Hatch 2 | B | GE | SU | 1 | On 2/24/91 at approximately 2013 CST, Unit 2 was in the Startup mode with the reactor critical at less than 1% rated thermal power. Reactor pressure was approximately 280 psig, and reactor coolant temperature was approximately 416 degrees F. A nuclear heatup to rated pressure and temperature (approximately 1000 psig and 545 degrees F, respectively) was in progress per procedure 34GO-OPS-001-2S, "Plant Startup." At that time, the reactor scrammed on Average Power Range Monitor (APRM, EIIS Code IG) high flux. Neutron flux increased to the scram setpoint of about 12% rated thermal power when feedwater was rapidly injected into the reactor vessel in response to decreasing reactor water level. Water level had begun to decrease when a Bypass Valve (BPV, EIIS Code SO) opened to control reactor pressure. The BPV opened during heatup, because licensed Operations personnel failed to maintain the BPV's pressure control setpoint above reactor pressure as required by procedure 34GO-OPS-001-2S. <br /><br /> The cause of this event was personnel error. Licensed Operations personnel failed to maintain the BPV's pressure control setpoint above reactor pressure as required by procedure, As a result, the BPV opened at its pressure setpoint of approximately 280 psig, allowing reactor vessel water inventory in the form of saturated steam to flow to the Condenser (EIIS Code SQ) and thereby causing reactor water level to decrease. Operations personnel failed to recognize the BPV was open. To control water level with the BPV open, feedwater was injected into the vessel, resulting in a power increase and scram on APRM high flux. <br /><br /> Corrective action for this event consisted of counseling the involved personnel.
366 | 3661992009 | 1992-06-25 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Hatch 2 | B | GE | PO | 100 | On 6/25/92, at 0100 CDT, Unit 2 was in the Run mode at 2436 CMWT (100 percent rated thermal power). At that time, a licensed plant operator was in the process of transferring bus 2R24-S018A from its alternate to its normal power supply in accordance with plant procedures when he inadvertently manipulated the wrong breaker control switch resulting in a loss of power to essential 600 V bus 2C. The loss of power resulted in loss of feedwater to the vessel, a half scram, automatic closure of various Primary Containment Isolation system (PCIS) valves, and automatic initiation of the Main Control Room Environmental Control system pressurization mode. The loss of feedwater caused a rapid decrease in reactor water level resulting in a low level scram, automatic closure of Group 2 and 5 PCIS valves, a trip of the Recirculation pumps, automatic initiation of the High Pressure Coolant Injection and the Reactor Core Isolation Cooling systems, and initiation of both units' Standby Gas Treatment systems. The lowest level reached was 113.4 inches above top of the active fuel. The reactor pressure during the event did not exceed the pre-event pressure. By 0103 CDT, reactor water level and pressure were stable and at 0105 CDT, the scram was reset. Following scram recovery, at 0945 CDT, a full Reactor Protection System (RPS) actuation was received when Intermediate Range Monitor 'A' (IRM) spiked upscale. The control rods were fully inserted at this time. The scram was reset at 0947 CDT. <br /><br /> The cause of the loss of the 600 V bus was personnel error; the licensed operator inadvertently manipulated the wrong breaker control switch. The cause of the IRM spiking is unknown. The corrective actions for this event include counseling personnel and testing the IRMs during the next refueling outage.
366 | 3661992015 | 1992-09-16 | QR6 | Manual Reactor Trip | [45 empty] | Hatch 2 | B | GE | PO | 20 | On 9/16/92, at 0242 CDT, Unit 2 was in the Run mode at 487 CMWT (20 percent of rated thermal power), and in the process of shutting down for the tenth refueling outage. Reactor vessel pressure was being controlled by the Main Turbine Bypass valves (BPVs). At that time, a manual scram was initiated as a conservative action due to a leak discovered in the Electro-Hydraulic system control fluid piping that could have affected operation of the BPVs. Earlier, at 0220 CDT, a leak in the EHC piping between the BPVs and a system hydraulic fluid actuator was found during a walkdown of the Condenser Bay area. The EHC reservoir was then checked and found to be 4.5 inches below normal. Due to a concern that the BPVs could drift closed on low EHC system pressure and cause a pressure transient in the reactor vessel, a decision was made to initiate a manual scram. Consequently, at 0242 CDT, a manual scram was initiated. All control rods fully inserted as designed. Reactor water level decreased to a minimum of 27.5 inches above instrument zero (186 inches above the top of the active fuel) subsequent to the scram. At this level, no Engineered Safety Feature systems were required to actuate. Reactor water level was restored by the 2B Reactor Feedwater pump within one minute of the scram. Prior to the event, reactor pressure was approximately 920 psig and remained constant throughout the event, as pressure was controlled by the BPVs. <br /><br /> The cause of the event was through-wall cracking in a high pressure EHC system pipe. <br /><br /> Corrective actions include repairing the cracked portion of the pipe prior to restart from the current refueling outage.
366 | 3661992026 | 1992-11-27 | QR5 | Turbine Trip | [45 empty] | Hatch 2 | B | GE | PO | 70 | On 11/27/92 at 0234 CST, Unit 2 was in the Run mode at a power level of 1705 CMWT (70% rated thermal power). At that time, the unit scrammed on Turbine Stop Valve and Turbine Control Valve fast closure due to a Main Turbine trip on high vibration on the #6 bearing. Reactor water level decreased from 37 inches above instrument zero (195 inches above the top of the active fuel) to its minimum of five inches above instrument zero due to void collapse from the rapid reduction in power. This resulted in another scram signal and a Group 2 Primary Containment Isolation System signal on low water level. Level was restored automatically by the Reactor Feedwater Pumps (RFPs). Reactor pressure increased from 968 psig to a peak of about 1030 psig. The Turbine Bypass Valves opened to reduce and maintain pressure below 920 psig. No Safety Relief Valves lifted nor were any required to lift to reduce or control pressure. <br /><br /> The causes of this event were recorder alarm configuration and personnel error. Personnel were not aware of increasing levels of turbine vibration resulting from normal load increases because the vibration annunciator was already lit due to high vibration on an RFP Turbine. Due to the vibration recorder alarm configuration, high RFP Turbine vibration caused the common turbine vibration annunciator to alarm even though each RFP Turbine has its own annunciator. Due to personnel error, compensatory action for the lit annunciator was not taken. <br /><br /> Corrective actions include changing the vibration recorder alarm configuration and counseling personnel.
366 | 3661993005 | 1993-05-21 | QR6 | Manual Reactor Trip | [45 empty] | Hatch 2 | B | GE | PO | 65 | On 5/21/93 at 1939 CDT, Unit 2 was in the Run mode at a power level of 1581 CMWT (approximately 65 percent of rated thermal power). At that time, licensed Operations personnel were performing surveillance procedure 34SV-C71-005-2S, "TURBINE CONTROL VALVE FAST CLOSURE INSTRUMENT FUNCTIONAL TEST." This procedure tests the "RPT" logic which causes a trip of the Reactor Recirculation Pumps in the event of a Main Turbine trip above 30 percent power. The procedure requires opening a test switch to disable the RPT trip while each Main Turbine Control Valve (TCV) is cycled. Per the procedure, the licensed operator should have disabled the "A" logic using the "A" test switch. Instead, he mistakenly moved the "B" test switch, disabling the "B" logic which was not being tested and leaving the "A" logic active. Subsequently, when the TCV in the "A" logic channel was closed per the procedure, the RPT logic was satisfied, and both Reactor Recirculation pumps tripped per design. Licensed operators immediately inserted a manual scram as required. Reactor water level decreased following the scram as expected, producing a second scram signal and closure of the Group 2 Primary Containment Isolation System valves. Water level was restored from a low point of 161 inches above the top of active fuel by the Reactor Feedwater Pumps. No Emergency Core Cooling Systems injected, nor were any required to do so. The cause of this event is a personnel error on the part of a licensed operator. Specifically, he manipulated the wrong test switch while performing a surveillance. Subsequent movement of the TCV being tested completed the logic required to produce a trip of the Recirculation Pumps. Corrective actions for this event included temporarily removing the involved operator from licensed duties and subjecting him to formal discipline under the Company's Positive Discipline Program. <br /> ?
366 | 3661994007 | 1994-08-30 | QR8 | Spurious Reactor Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Hatch 2 | B | GE | PO | 100 | On 8/30/94, at 1007 EDT, Unit 2 was in the Run mode at 2436 CMWT (100 percent rated thermal power). At that time, the power supply for Reactor Protection System (RPS) bus 'A' was being transferred from the alternate to the normal power supply when a full RPS actuation occurred along with a Group 1, 2, and 5 Primary Containment Isolation System (PCIS) actuation. As a result, all control rods fully inserted and various PCIS valves automatically closed. Immediately following the RPS actuation, the reactor water level began decreasing as expected. The lowest level reached during the level transient was approximately 43 inches below instrument zero (approximately 115 inches above the top of the active fuel). As the reactor water level decreased to the appropriate setpoints, the following engineered safety features initiated: High Pressure Coolant Injection System (HPCI), Reactor Core Isolation Cooling System (RCIC), Standby Gas Treatment System (SGT), and the Recirculation Pump Trip System (RPT). All systems functioned as designed. Reactor water level was restored by the Reactor Feedwater Pumps (RFP) and RCIC. The highest reactor pressure reached during the event was 1092 psig. Eight Safety Relief Valves opened to reduce pressure. The SRVs subsequently closed at the appropriate pressures as the pressure decreased. The cause of the event was a slight overtravel of the RPS power select switch. An intolerance for overtravel of the switch positions resulted in a momentary loss of power to both RPS busses and the consequent actuations. Corrective actions include replacing the switch, installing a warning placard, and considering a design change.
366 | 3661995001 | 1995-04-11 | QP5 | Excessive Feedwater Flow | [13 empty] | X | [30 empty] | X | Hatch 2 | B | GE | PO | 100 | On 4/11/95 at 2051 EDT, Unit 2 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the reactor automatically shut down due to an automatic trip of the main turbine on high reactor water level. Both reactor recirculation and feedwater pumps also tripped. Reactor pressure increased resulting in the opening of all safety/relief valves (SRVs) and main turbine bypass valves. As pressure decreased, the SRVs closed and the bypass valves automatically controlled pressure. Water level decreased due to steam discharge from the SRVs and the bypass valves and loss of the feedwater pumps. A Group 2 primary containment isolation system (PCIS) signal was received and the Group 2 valves closed. Level decreased to 37 inches below instrument zero causing initiation of the high pressure coolant injection (HPCI) and reactor core isolation cooling (RCIC) systems, receipt of a partial Group 5 PCIS isolation signal, start of the Unit 1 and 2 standby gas treatment systems, and isolation of the Unit 1 and 2 secondary containments. Level was recovered with the HPCI and RCIC systems. The cause of this event was personnel error. An operator placed a jumper in the wrong location, shorting the power supply for reactor water level transmitter 2C32-N004B and causing the signal from the transmitter to decrease to zero. The reactor water level control system responded by increasing the flow rates from the feedwater pumps, causing water level to increase. Corrective actions include disciplining the operator, temporarily relieving him of licensed duties, providing him remedial training, and requiring double verification of jumper locations.
366 | 3661995003 | 1995-09-02 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Hatch 2 | B | GE | PO | 28 | On 9/2/95, at 1512 EDT, Unit 2 was in the Run mode at 682 CMWT (28 percent of rated thermal power). At that time, the Reactor Protection System (RPS) was manually actuated in anticipation of an automatic actuation of a Main Turbine trip due to Main Condenser low vacuum. Prior to the reactor shutdown, on 9/1/95, at approximately 2008 EDT, one cell of a cooling tower collapsed, blocking the flow of Circulating Water System (CWS) water from the cooling tower to the flume. Flume level subsequently decreased to the point that the CWS pumps experienced vortexing and pumped air along with water into the system. The air collected in the 'D' waterbox of the Main Condenser. Licensed personnel proceeded to reduce reactor power due to decreasing Main Condenser vacuum. By approximately 2230 EDT, vacuum had stabilized and the flume level had been restored. On the following day, 9/2/95, at 1220 EDT, licensed personnel noticed that the Main Condenser vacuum was decreasing and began reducing reactor power in an attempt to restore vacuum. An apparently unsuccessful attempt was made to vent the 'D' waterbox and, since vacuum could not be restored, at 1512 EDT, conservative actions were taken to manually shut down the reactor. The lowest reactor water level reached during the ensuing transient was 166 inches above the top of the active fuel. The 'B' Reactor Feedwater Pump restored water level to normal. Reactor pressure following the reactor shutdown did not exceed the pre-event level of 975 psig. The cause of the event was air-binding of the 'D' waterbox. Corrective actions include venting the waterbox, returning the cooling tower to service, and briefing Operations shift personnel on the event.
366 | 3661997007 | 1997-04-22 | L2 | Loss of Condenser Vacuum | [10 empty] | X |  |  | X | [26 empty] | X |  |  |  | X | Hatch 2 | B | GE | PO | 55 | On 4/22/97 at 1907 EDT, Unit 2 was in the Run mode at a power level of 1418 CMWT (55 percent rated thermal power). At that time, the reactor shut down automatically on Turbine Stop Valve and Turbine Control Valve fast closure when the turbine tripped on low condenser vacuum. Water level decreased due to void collapse from the rapid reduction in power and the trip of the operating Reactor Feedwater Pump (RFP) on low condenser vacuum. The decrease in water level resulted in receipt of Group 2 and Group 5 Primary Containment Isolation System isolation signals and closure of the Group 2 and Group 5 Primary Containment Isolation Valves per design. Water level reached a minimum of approximately 45 inches below instrument zero (113.44 inches above the top of the active fuel) resulting in automatic initiation of the Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) systems per design. Secondary containment automatically isolated and all four trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low low water level per design. Level was restored to normal within one minute by the RCIC and HPCI systems and the standby RFP. Pressure reached a maximum value of 980 psig; no Safety/Relief Valves lifted nor were any required to lift to reduce or control pressure. This event was caused by reduced heat rejection from the main condenser resulting in a heat buildup in the condenser and a decrease in vacuum. The condenser waterboxes were vented, the circulating pump inlet screens were cleaned, and the redundant steam jet air ejector was placed into service.
366 | 3661997010 | 1997-11-20 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Hatch 2 | B | GE | PO | 71 | On 11/20/97 at 2053 EST, Unit 2 was in the Run mode at a power level of 1816 CMWT (71 percent rated thermal power). At that time, personnel manually scrammed the reactor so the condensate system could be isolated to repair damage. Water level decreased due to void collapse from the rapid reduction in power resulting in Group 2 and 5 primary containment isolation system isolation signals and closure of the Group 2 and 5 primary containment isolation valves. Level reached a minimum of approximately 38 inches below instrument zero (120.44 inches above the top of the active fuel) causing automatic initiation of the reactor core isolation cooling (RCIC) and high pressure coolant injection systems. Level was recovered by the reactor feedwater pumps (RFPs) before either system could inject to the vessel. Secondary containment automatically isolated and the Unit 1 and Unit 2 standby gas treatment systems automatically started per design. Level was restored to normal within one minute by the RFPs and maintained by the RCIC system. Pressure reached a maximum value of 990 psig; no safety/relief valves lifted nor were any required to lift. This event was caused by component failure. The hinge pin in discharge check valve 2N21-F019A broke resulting in the valve failing to close when condensate booster pump 2N21-C002A was removed from service. This caused high pressure water to damage the pump and its low pressure suction piping and bellows. Corrective actions include repairing the damage. The failure of the hinge pin appears to be an isolated case.
366 | 3661999005 | 1999-05-05 | QR5 | Turbine Trip | [45 empty] | Hatch 2 | B | GE | PO | 98 | On 05/05/1999 at 0747 EDT, Unit 2 was in the Run mode at a power level of 2716 CMWT (98.3 percent rated thermal power). At that time, the reactor scrammed and the reactor recirculation pumps tripped automatically on turbine control valve fast closure caused by a turbine trip. The turbine tripped when the main generator tripped on a ground fault. Following the reactor scram, water level decreased due to void collapse from the rapid reduction in power. However, the reactor feedwater pumps maintained water level higher than eight inches above instrument zero. Consequently, no safety system actuations on low level were received nor were any required. Pressure reached a maximum value of 1124 psig; nine of eleven safety/relief valves lifted to reduce reactor pressure. Pressure did not reach the nominal actuation setpoints for the remaining two safety/relief valves. The temperature in the vessel bottom head region decreased by more than the Technical Specification-allowed 100 degrees F in one hour before a recirculation pump could be restarted. This event was caused by a manufacturer error. Some of the turning vanes located in the discharge duct for the "B" isophase bus duct cooling fan broke loose, shorting a generator phase to ground. The manufacturer installed turning vanes that were not the proper thickness for this application thus resulting in some of their connection points failing. Pieces of the broken vanes were retrieved from the isophase bus duct and the remaining turning vanes were removed from the isophase bus duct cooling system.
366 | 3661999006 | 1999-06-15 | L2 | Loss of Condenser Vacuum | [10 empty] | X |  |  | X | [25 empty] | X | X |  |  |  | X | Hatch 2 | B | GE | PO | 41 | On 6/15/99 at 2124 EDT, Unit 2 was in the Run mode at a power level of approximately 1540 CMWT (41 percent rated thermal power) and Unit 1 was in the Run mode at a power level of 2763 CMWT (100 percent rated thermal power). At that time, a manual scram was inserted on Plant Hatch Unit 2 in anticipation of receiving an automatic scram on a turbine trip due to loss of condenser vacuum. When the scram was inserted, an electric power transfer failed which should have automatically re-aligned Unit 2 4160-volt buses "C" and "D." This further resulted in a trip of the Unit 2 reactor recirculation system pumps due to loss of lube oil pressure. When the recirculation system pumps were restarted, the "B" discharge valve began opening and activated an arcing ground fault on a 600-volt bus which is fed from Unit 1. The electrical noise resulted in several Unit 1 600-volt breakers tripping, including the feeder breaker to the reactor protection system power supply. This resulted in various engineered safety features actuating on Unit 1, including automatic closure of Group 2 primary containment isolation system valves. When condenser vacuum was broken on Unit 2 following the scram, bypass switches had not been reset, so the main steamline isolation valves automatically closed. However, one Unit 2 main steam isolation valve did not close as expected. The cause for the loss of condenser vacuum on Unit 2 was a combination of factors that led to the condenser being unable to reject sufficient heat. The cause of the failure of the power transfer was a relay being out of calibration. The cause for the ESF actuations on Unit 1 was a ground in a conductor supplying a Unit 2 load. The cause for the failure of the MSIV to close on demand was the failure of an AC solenoid operated pneumatic valve to shift positions when it was deenergized. Corrective actions for this event included the addition of a level instrument in the circulating water pump pit, promulgation of an operating order on condenser operating parameters, repair of the grounded conductor, and other items.
366 | 3661999007 | 1999-06-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Hatch 2 | B | GE | PO | 98 | On 06/28/1999 at 0300 EDT, Unit 2 was in the Run mode at a power level of approximately 2708 CMWT (98 percent rated thermal power). Personnel were in the process of filling and venting the "B" cold reference leg keepfill system. At that time, the reactor shut down automatically and inboard Group 2 Primary Containment Isolation Valves (PCIVs) closed on low water level. Level decreased when Reactor Feedwater Pump (RFP) flow rate decreased in response to a false high level signal. Following the shutdown, level continued to decrease due to void collapse from the rapid reduction in power resulting in closure of the Group 5 PCIVs. Level reached a minimum of approximately 45 inches below instrument zero causing automatic initiation of the Reactor Core Isolation Cooling and High Pressure Coolant Injection systems. The low level initiation signal cleared before either system could inject makeup water to the vessel. Secondary containment automatically isolated and all four trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low level. The RFPs restored level to normal within one minute. Pressure was at its normal value at the time of the reactor shutdown and decreased thereafter; no Safety/Relief Valves lifted nor were any required to lift. This event was caused by personnel error and inadequate corrective action. Involved personnel were disciplined per the Positive Discipline Program and the calibration of a level instrument has been changed.
366 | 3662001002 | 2001-10-26 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Hatch 2 | B | GE | PO | 100 | On 10/26/2001 at 1917 EDT, Unit 2 was in the Run mode. At that time, the reactor scrammed on Average Power Range Monitor high neutron flux caused by a rapid increase, after an unexpected decrease, in the flow rate of the 2B reactor recirculation pump. Following the scram, water level decreased due to void collapse from the rapid reduction in power resulting in closure of Group 2 and Group 5 primary containment isolation valves and automatic initiation of the Reactor Core Isolation Cooling and High Pressure Coolant Injection systems. The low level initiation signal cleared before either system could inject water to the vessel. The secondary containment dampers automatically isolated and all trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low water level. Level reached a minimum of 40 inches below instrument zero. The Reactor Feedwater Pumps restored level to its pre-event value of approximately 35 inches above instrument zero within 35 seconds of the scram. Reactor vessel pressure did not exceed its normal value of approximately 1035 psig; therefore, no safety/relief valves lifted nor were any required to lift to reduce pressure. The cause of this event is not known conclusively, although the available evidence indicates a problem with the amplifier board in the 2B reactor recirculation pump scoop tube positioner logic circuit is the most likely cause. Corrective actions include replacing the amplifier board; temporarily requiring the 2B recirculation pump scoop tube to be locked when pump speed is not being changed; monitoring selected parameters in the pump speed control system; and performing a failure analysis of the amplifier board.
366 | 3662001003 | 2001-12-25 | QL5 | Partial Closure of MSIVs | [45 empty] | Hatch 2 | B | GE | PO | 100 | On 12/25/2001 at 1819 EST, Unit 2 was in the Run mode. At that time, the reactor scrammed on Average Power Range Monitor high neutron flux caused by a rapid increase in reactor pressure vessel pressure. Pressure increased quickly as a result of the unexpected and sudden closure of main steam line isolation valve 2B21-F028B. The closure of the main steam line isolation valve isolated one of the four main steam lines. Although the flow rates in the remaining three steam lines increased to compensate partially for the isolated line, the sudden isolation of one line was sufficient to cause reactor vessel pressure to increase from a nominal value of 1035 psig to 1041.2 psig within 0.3 seconds. This rapid rate of change in pressure caused reactor power to increase to 120.5 percent rated thermal power and the reactor to scram on high neutron flux level. Following the scram, water level decreased due to void collapse from the rapid reduction in power resulting in closure of Group 2 primary containment isolation valves. Level reached a minimum of 33.5 inches below instrument zero, a level not low enough to initiate other protective actions. Therefore, no systems other than the Group 2 primary containment isolation valves actuated or were required to actuate. The Reactor Feedwater Pumps restored level to its pre-event value of approximately 36 inches above instrument zero within 30 seconds of the scram. Reactor pressure reached its maximum value of 1048.2 psig less than one second after the scram. It decreased thereafter and was maintained below 975 psig by the main turbine bypass valves. No safety/relief valves lifted nor were any required to lift to reduce pressure. This event was the result of component failure caused by high-cycle fatigue. The stem in valve 2B21-F028B failed completely, causing the valve to close and reactor vessel pressure to increase. Corrective actions include replacing the stem and determining the feasibility and cost of options to reduce or eliminate stem vibration.
366 | 3662005003 | 2005-05-23 | QL6 | Condenser Leakage | [45 empty] | Hatch 2 | B | GE | PO | 57 | On 5/23/2005 at 1747 EST, Unit 2 was in the Run mode at an approximate power level of 1598 CMWT (57 percent rated thermal power). At that time, Operations personnel manually scrammed the reactor per procedure 34GO-OPS-014-2, "Fast Reactor Shutdown." This procedure was entered because of a condenser tube leak that resulted in an undesirable reactor water chemistry trend. Following the manual scram, water level decreased due to void collapse from the rapid reduction in power, reaching a minimum of approximately thirteen inches below instrument zero (about 145 inches above the top of the active fuel). The decrease in water level resulted in receipt of a subsequent reactor scram, a Group 2 Primary Containment Isolation System (PCIS) isolation signal and thus closure of the Group 2 Primary Containment Isolation Valves per design. The operating Reactor Feedwater Pumps restored level to its designed set point.Personnel confirmed that all control rods fully inserted and reset the Group 2 isolation signal and restored the isolation valves to normal per procedure 34AB-C71-001-2, "Scram Procedure." The manual scram was initiated as the result of a condenser tube leak. An investigation determined that the condenser tube leak was caused by the loss of a plug that was installed previously in April 2005. The receipt of the Group 2 PCIS isolation and the subsequent reactor scram was the result of a vessel water level decrease due to void collapse from the rapid reduction in power following the insertion of the manual scram.The leaking condenser tube was re-plugged with a plug of a different design.
366 | 3662006002 | 2006-04-05 | QR5 | Turbine Trip | [45 empty] | Hatch 2 | B | GE | PO | 100 | On 4/5/2006 at 00:16 EDT, Unit 2 was in the Run mode at a power level of 2804 CMWT (100 percent rated thermal power). At that time a power-load unbalance was sensed resulting in a turbine control valve fast closure. The sensed power-load unbalance was a false indication introduced by performance of a calibration procedure. Reactor pressure spiked to approximately 1125 psig, which resulted in an additional trip signal due to high reactor pressure. All control rods fully inserted. Eight of the eleven Safety Relief Valves opened as designed to mitigate the pressure transient. Pressure did not reach the nominal actuation set points for the remaining three Safety Relief Valves. Reactor water level initially decreased due to void collapse and then increased to a maximum value of approximately 60 inches due to swell after both Recirculation Pumps tripped automatically on End of Cycle-Recirculation Pump Trip per design and eight SRVs opened. Reactor water level subsequently decreased when the reactor feed pumps automatically tripped on high reactor water level per design. The minimum reactor water level decreased to approximately seven inches and was recovered with manual initiation of the Reactor Core Isolation Cooling and High Pressure Coolant Injection systems. This event was caused by a power-load unbalance created during the calibration of the KVR Generator and Main Transformer Protection Recorder. The calibration procedure was found to be inadequate in that it allowed this calibration to be performed with the main turbine on-line and at greater than 40 percent rated thermal power. The calibration procedure was revised.
366 | 3662007008 | 2007-08-07 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Hatch 2 | B | GE | PO | 100 | On August 7, 2007 at 15:06 EDT, Unit 2 was at 100 percent power in Mode 1 at 2804 CMWT. At this time a partial loss of the Condensate System caused low Feedwater flow resulting in a Reactor Protection System (RPS) actuation on Low Reactor Water Level and a Group 2 Primary Containment Isolation System (PCIS) isolation. The investigation determined that the loss of condensate system was caused by the loss of the 2D 4160V switchgear. The 2D bus provides power to the 2A and 2B Condensate and Condensate Booster Pumps. The loss of the 2D 4160V bus was the result of the inadvertent actuation of the over-current relay protecting one of the three phases of the normal supply breaker. This relay had been removed from services as part of a routine I&C periodic relay calibration. During reinstallation of the relay cover following completion of the calibration, the relay actuated tripping the normal supply breaker for the 2D 4160 switchgear and de-energizing the bus providing power to the pumps. All systems functioned per their design given the water level transient. The root cause of this event was determined to be ineffective execution of a screening procedure written to determine scram/transient potential of I&C activities. The screening procedure was executed for the calibration of the overcurrent relay and errantly determined that there was no reactor trip potential when performing the procedure on-line and did not include a precaution for installation of relay cover. The procedure has been revised to correct these inadequacies and all I&C procedures previously screened will be re-evaluated.
366 | 3662008002 | 2008-03-07 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Hatch 2 | B | GE | PO | 100 | On March 7, 2008 at 14:46 EST, Unit 2 was in Mode 1 at 2804 CMWT, 100 percent power. At that time, the reactor automatically scrammed on low reactor water level following a loss of condensate and subsequent loss of feedwater. Following the scram, level continued to decrease due to void collapse from the rapid reduction in power and the loss of feedwater. This resulted in closure of the Group 2 and Group 5 Primary Containment Isolation Valves as designed. Level reached a minimum of approximately 65 inches below instrument zero causing automatic initiation of the Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) systems. Secondary containment automatically isolated and all four trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low level as designed. The RCIC and HPCI systems recovered level; and RCIC was used to maintain level. Pressure decreased immediately following the automatic scram and was controlled automatically by the Main Turbine Bypass Valves. This event was caused by a software application test that sent data to a server used in the Chemistry Data Acquisition System (CDAS). This CDAS server was connected to the condensate demineralizers’ control PC using a vendor software application. The engineer did not realize that the vendor software application automatically synchronized the data between the connected computers. When the test was executed the data sent to the CDAS server synchronized with the condensate demineralizers’ control computer causing the demineralizer outlet valves to close. The connection between the CDAS server and the condensate demineralizers’ control PC has been disconnected.
366 | 3662009003 | 2009-06-20 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Hatch 2 | B | GE | PO | 100 | On June 20, 2009 at 14:17 EDT, Unit 2 was in mode 1 with an approximate reactor power of 2804 CMWTh. At this time protective circuitry initiated a main generator runback due to a high Stator Water Cooling (SWC) outlet temperature. The electro-hydraulic control (EHC) Mark VI cores processor began reducing turbine load by closing the turbine control valves (TCV) and subsequently opening the turbine bypass valves (TBV). Operations personnel began reducing reactor load in response to the main generator runback by reducing recirculation flow. The reactor power was reduced to approximately 66 percent reactor thermal power and could not be reduced any lower without the insertion of control rods. Due to turbine load reducing faster than the manual actions taken to reduce reactor load, reactor pressure began to increase. Pressure had reached the setpoint to actuate the Reactor Protection System, and a reactor scram was initiated due to high reactor pressure. This event was caused by the improper set-up of the SWC temperature control instrument loop during 2R20 outage. Corrective actions consist of: set-up of SWC valve 2N43F100 was corrected and the control system was calibrated, review of other work during the refueling outage was performed to ensure a similar condition does not exist on other equipment, and review of the Unit 1 SWC system was performed to confirm operation.
366 | 3662009004 | 2009-06-23 | QR5 | Turbine Trip | [45 empty] | Hatch 2 | B | GE | PO | 61 | On June 23, 2009 at 03:51 EDT, Unit 2 was in mode 1 with an approximate reactor power of 1710 CMWTh. At this time an automatic reactor scram occurred as a result of a turbine trip due to high reactor water level. Prior to the event the reactor was increasing in power during startup from a recent outage. An instrument which controls reactor water level failed resulting in an increase in reactor water level. The water level increased to a point where the turbine control valve fast closure trip signal was initiated due to high reactor water level. All control rods fully inserted and Reactor Feed pumps tripped. Reactor water level initially decreased to approximately negative 25 inches, due to void collapse. The Primary Containment isolation Valve Group 2 isolation setpoint was reached, and the Group 2 valves isolated. Both the 'A' and 'B' Reactor Feed Pumps initially tripped, and the 'A' feed pump was restarted and used to restore and maintain reactor water level. Reactor pressure reached an upper value of approximately 964 psig. No Safety Relief Valves opened, nor were they required to open, based on the maximum pressure reached. Reactor water level increased to a maximum value of approximately 60 inches above instrument zero, but was restored to normal range. The cause of this event was the failure of an internal power supply electrolytic capacitor which caused a failure of the DC power supply for the Yokogawa level controller 2C32-K648. The failed power supply card containing the capacitor was replaced following the event and repetitive tasks have been created to replace this and similar power supply cards at a prescribed interval.
366 | 3662019003 | 2019-03-24 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Hatch 2 | B | GE | PO | 25 | On March 24, 2019 at 0026, with Unit 2 in Mode 1 and ascending in power, Control Room Operators noticed the Main Condenser was losing vacuum and initiated a power reduction. Due to vacuum continuing to degrade, Operators lowered reactor power down to 25 percent and initiated a manual reactor SCRAM at 0159. Following the trip of the Main Turbine, the non-safety Station Service 4160V buses failed to fast bus transfer from normal to the alternate power supply resulting in the loss of all non-safety loads. Operators entered an abnormal operating procedure for the Loss of 4160V buses to manually re-energize the Station Service buses. The de-energized Station Service buses resulted in a loss of the Condensate Feedwater system. Reactor water level was then maintained by the Reactor Core Isolation Cooling system while pressure was controlled by High Pressure Coolant Injection. A primary containment isolation signal was received on low reactor water level. The event is reportable pursuant to 10 CFR50.73(a)(2)(iv)(A) for a manual reactor SCRAM and general containment isolation signal.<br /><br /> Corrective actions were taken to properly align the Steam Jet Air Ejector system, which was the cause of the loss of condenser vacuum, and to replace the failed relay, which caused the failure of the Station Service buses to transfer.
368 | 3681987007 | 1987-09-09 | QR5 | Turbine Trip | [45 empty] | Arkansas 2 | P | CE | PO | 100 | POWER LEVEL - 100%. ON 9/9/87 WITH THE UNIT OPERATING AT FULL POWER, A REACTOR TRIP ON HIGH REACTOR COOLANT SYSTEM (RCS) PRESSURE OCCURRED. FAILURE OF AN ALUMINUM SETSCREW TYPE TERMINAL LUG, CONNECTING ONE PHASE OF THE SECONDARY SIDE OF A STEP DOWN TRANSFORMER TO AN INSTRUMENTATION DISTRIBUTION PANEL, CREATED A PARTIAL LOSS OF POWER TO THE MAIN TURBINE ELECTROHYDRAULIC CONTROL SYSTEM RESULTING IN RAPID CLOSURE OF THE TURBINE CONTROL VALVES. THE RESULTING PRIMARY TO SECONDARY POWER MISMATCH CAUSED RCS PRESSURE TO INCREASE RAPIDLY TO THE REACTOR PROTECTION SYSTEM TRIP SETPOINT. EMERGENCY FEEDWATER ACTUATED AS DESIGNED TO RESTORE AND MAINTAIN STEAM GENERATOR WATER LEVELS. TWO TURBINE BYPASS VALVES FAILED TO RESPOND PROPERLY DURING THE TRANSIENT DUE TO FAILURE OF POSITIONERS ASSOCIATED WITH THEIR ACTUATORS. THE CAUSE OF THE TERMINAL LUG FAILURE WAS ELECTRICAL ARCING BETWEEN THE LUG AND CABLE CONDUCTORS AS A RESULT OF POOR ELECTRICAL CONTACT DUE TO LOOSENING OF THE LUG AROUND THE CONDUCTORS. RETURNED TO SERVICE AFTER TESTING TO VERIFY A GOOD CONNECTION IN THE REPAIRED AREA AND AT OTHER LOCATIONS WITH SIMILAR CONNECTIONS. THE TURBINE BYPASS VALVES WERE REPAIRED, TESTED AND RETURNED TO SERVICE. THE ALUMINUM SETSCREW TYPE LUGS ON THE TRANSFORMER WILL BE REPLACED WITH COPPER CRIMP
368 | 3681987008 | 1987-11-14 | QR5 | Turbine Trip | [45 empty] | Arkansas 2 | P | CE | PO | 100 | POWER LEVEL - 100%. ON 11/14/87 WITH THE UNIT OPERATING AT FULL POWER, INDICATED HIGH BEARING VIBRATIONS ON NUMBER NINE MAIN TURBINE GENERATOR JOURNAL BEARING INITIATED AN AUTOMATIC TRIP OF THE MAIN TURBINE. THE RESULTING PRIMARY TO SECONDARY POWER MISMATCH CAUSED AN AUTOMATIC REACTOR TRIP ON HIGH REACTOR COOLANT SYSTEM PRESSURE WITHIN A FEW SECONDS OF THE MAIN TURBINE TRIP. EMERGENCY FEEDWATER AUTOMATICALLY ACTIVATED AS DESIGNED TO RESTORE AND MAINTAIN STEAM GENERATOR WATER LEVELS. SETPOINT FOR NUMBER NINE BEARING HIGH VIBRATION BEING SET AT A VALUE LOWER THAN SPECIFIED IN PLANT PROCEDURES IN COMBINATION WITH INACCURATE INDICATIONS OF NUMBER NINE BEARING VIBRATION PROVIDED TO THE TRIP SYSTEM (HIGH BEARING VIBRATION WAS NOT SHOWN USING LOCAL VIBRATION MONITORING EQUIPMENT). DOCUMENTATION COULD NOT BE FOUND TO SHOW THAT THE VIBRATION MONITORING INSTRUMENTS AND PORTIONS OF THE MAIN TURBINE TRIP SYSTEM UTILIZING THESE INSTRUMENTS HAD BEEN ROUTINELY CALIBRATED. THE NUMBER NINE BEARING HIGH VIBRATION TRIP SETPOINT WAS INCREASED TO THE CORRECT VALUE AND A ROUTINE CALIBRATION PROGRAM FOR THE VIBRATION MONITORING SYSTEM IS BEING DEVELOPED. ON 11/15/87, THE MAIN TURBINE GENERATOR WAS STARTED AND LOADED. VIBRATION INDICATION AT THE NUMBER NINE BEARING HAD RETURNED TO AN ACCEPTABLE LEVEL.
368 | 3681988011 | 1988-08-01 | G1 | Very Small LOCA or Leak | [6 empty] | X | [18 empty] | X | [19 empty] | Arkansas 2 | P | CE | PO | 100 | On 8/1/88, a Notification of Unusual Event was declared and a manual reactor trip and plant cooldown performed following the failure of a reactor coolant pump (RCP) seal cavity pressure sensing instrument line. The sensing line failure, located at the fusion line of a 3/8 inch instrument tubing to 3/4 inch piping reducer socket weld, resulted in a reactor coolant system (RCS) leak of approximately 20 gallons per minute (gpm). The pump shaft seal also degraded following the sensing line failure and contributed to additional RCS leakage. The maximum leak rate during the event was approximately 40 gpm. A high pressure safety injection pump was used in addition to normal charging pump operations to maintain pressurizer level during the rapid, controlled cooldown. The cause of the sensing line failure was low stress, high cycle, fatigue failure of the weld induced by vibration associated with the operating RCP. Corrective actions included RCP seal piping and tubing system configurations reviews which resulted in modifications and weld betterments to reduce susceptability of the systems to vibration induced stress. Long term actions include evaluation of an improved RCP seal design incorporating the use of flexible hoses for process piping connections and other features to minimize the potential for failures of this type and the resulting leaks.
368 | 3681988020 | 1988-12-01 | QR9 | Spurious Engineered Safety Feature Actuation | [45 empty] | Arkansas 2 | P | CE | PO | 100 | On December 1, 1988, at 0854 hours with the plant at 100 percent power, a reactor trip occurred when a spurious Safety Inject on Actuation Signal/Containment Cooling Actuation Signal (SIAS/CCAS) was generated during surveillance testing of the Engineered Safety Feature Actuation system. As designed, the SIAS interrupted power to the two 4160V AC non-vital buses 2A1 and 2A2, which resulted in a momentary loss of power to the Control Element Drive Mechanism cabinets and a subsequent reactor trip on calculated low DNBR (departure from nucleate boiling ratio). All components actuated by the SIAS/CCAS performed as designed. The momentary loss of power to 2A1 and 2A2 resulted in loss of various secondary system components, including the main feedwater pumps and the Steam Dump and Bypass Control System (SDBCS). An Emergency Feedwater Actuation Signal automatically started pump 2P7A on low steam generator water level, and the steam pressure in the steam generators was controlled by the Main Steam Safety Valves (MSSVs) for a short period of time. Primary system post-trip response was normal except for slightly elevated pressure and temperature due to steam generator pressure being controlled by MSSVs instead of SDBCS. The plant was stabilized in Mode 3. A root cause for the inadvertent actuation could not be determined in subsequent investigations. A similar event was reported Licensee Event Report 368/85- 014-00.
368 | 3681989006 | 1989-04-18 | K1 | Steam Line Break Outside Containment | [9 empty] | X | X | [25 empty] | X |  |  | X | X | X |  |  |  | Arkansas 2 | P | CE | PO | 100 | On 4/18/89, a 14 inch, high pressure turbine extraction steam line ruptured resulting in a reactor trip on high Reactor Coolant System (RCS) pressure. During the transient, the steam turbine driven Emergency Feedwater (EFW) pump tripped on overspeed after receiving an automatic start signal. The 'A' train Feedwater Control System (FWCS) malfunctioned causing a slight overfill of 'A' Steam Generator (SG). One of two Atmospheric Steam Dump Valves (ADVs), located downstream of the SG Main Steam Isolation Valves (MSIVs), could not be opened from the control room. Due to the loss of condenser vacuum, the MSIVs were manually closed and upstream ADVs were used for decay heat removal. One of the upstream ADVs apparently failed open, resulting in a minor unexpected RCS cooldown. The plant was stabilized and a cooldown was performed. The failed line was inspected and the root cause was pipe wall thinning due to erosion-corrosion. Additional extraction steam piping was inspected resulting in several areas being replaced. A degraded ramp generator in the governor speed control circuit of the steam turbine driven EFW pump was replaced. The 'A' train FWCS was found to have some wires with degraded insulation which caused the system to malfunction. The defective wiring was replaced and system tested satisfactorily. The downstream ADV was found to have a galled plug; the plug and stem assembly were replaced. The upstream ADV functioned properly during the cooldown; no cause for its response was identified.
368 | 3681989024 | 1989-12-31 | QP5 | Excessive Feedwater Flow | [45 empty] | Arkansas 2 | P | CE | PO | 100 | On December 31, 1989, a reactor trip occurred from 100% of rated thermal power when 'B' Steam Generator (SG) water level reached a high level setpoint and the Reactor Protective System generated a reactor trip signal. During the transient one of the running condensate pumps which was expected to trip did not trip. Otherwise, the plant responded properly when the reactor trip occurred. The Operations staff responded appropriately and in a timely manner to the reactor trip. Of primary concern was the potential for Reactor Coolant system overcooling or a SG overfill event, however, proper system operation prevented either from occurring. No significant safety concerns were identified. The root cause of this event is believed to be a loose terminal on an electrical module in the 'S' Feedwater Control System (FWCS) cabinet. The terminal was not properly reterminated when maintenance activities were performed during 2R7 refueling outage. The loose terminal was on an electrical module in the 'S' Main Feedwater (MFW) flow loop to the 'S' FWCS. To verify that the loose terminal could cause a transient similar to this event, simulated signals for 100 percent power conditions for the inputs to the 'B' FWCS were input and the connection on the terminal loosened. A very similar response to the transient which initiated the reactor trip occurred. The loose terminal was properly reterminated. This event is reportable per 10CFR50.73(a)(2)(iv).
368 | 3681990014 | 1990-06-26 | QR8 | Spurious Reactor Trip | [45 empty] | Arkansas 2 | P | CE | PO | 30 | At about 2348 hours on June 26, 1990, a reactor trip occurred from approximately thirty percent of rated thermal power on low Departure from Nucleate Boiling Ratio. The cause of the reactor trip was attributed to an erroneous indication received by Control Element Assembly Calculator (CEAC) #1 from Reed Switch Position Transmitter (RSPT) #1 on a part length Control Element Assembly (CEA 29). A large penalty factor was calculated by CEAC #1 and resulted in the generation of a reactor trip signal from the Core Protection Calculators (CPCs). The root cause of the high indication has not been determined. A temporary modification was installed for CEA 29, RSPT #1 which provided a fixed signal for the CEA at a full out value. The safety function of the CEA was unaffected with the temporary modification installed. Training was provided to the operations staff responsible for the approach to criticality. <br /><br /> Additionally, appropriate procedure revisions were made and a caution card installed on the control panel to address placing CEAC #1 in an inoperable condition if the part length CEAs were going to be inserted. Placing CEAC #1 in an inoperable condition blocks any CEA position signals sent to the CPCs and thereby, prevents an unnecessary reactor trip. The CEAC/CPC systems functioned as designed, and the reactor trip resulted in all CEAs fully inserting. Therefore, there were no safety concerns.
368 | 3681990019 | 1990-08-21 | QL5 | Partial Closure of MSIVs | [45 empty] | Arkansas 2 | P | CE | PO | 100 | On August 21, 1990 at 0216 hours, while operating at full power the 'B' steam generator (S/G) main steam isolation valve (MSIV) closed fully resulting in an automatic reactor trip generated by the Core Protection Calculators (CPCs). The CPC trip was initiated due to a sensed temperature difference between the reactor coolant system (RCS) cold legs caused by the MSIV closure. The emergency feedwater system actuated automatically and was used to supply S/G feedwater for decay heat removal. The 'B' S/G main steam safety valves opened to limit S/G secondary pressure and reseated properly following the reactor trip. Other plant systems responded properly to the transient. Subsequent investigations revealed the MSIV closure was due to the failure of a normally energized, 125 volt DC solenoid on an air supply valve to the MSIV. The root cause of the solenoid failure could not be determined. The solenoid was replaced and the MSIV was stroke tested for operability. <br /><br /> Approximately one hour after the trip the indication on the 'A' S/G blowdown line radiation monitor was noted to be slightly elevated. Analysis of S/G secondary water confirmed that a very small primary to secondary leak existed. The leak rate stabilized at this value and has not increased. There was no actual safety significance as the result of this event.
368 | 3681990020 | 1990-09-28 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Arkansas 2 | P | CE | PO | 82 | At 2142 hours on September 28, 1990, during a planned power reduction from full power, main condenser circulating water pump 2P-3B was secured. The pump discharge valve failed to automatically close allowing a flowpath for circulating water flow to bypass the main condenser. At 2143 hours an automatic main turbine trip on High Condenser Pressure occurred and control room personnel manually tripped the reactor in anticipation of an automatic reactor trip. The Emergency Feedwater System, actuated automatically and was used to restore and maintain normal steam generator water levels. The plant was subsequently stabilized in Mode 3 (Hot Standby) conditions. Investigations revealed that the valve failed to close due to a mechanical key which disengaged from the motor shaft allowing the motor pinion gear to turn freely on the shaft. Vibration caused a setscrew used to secure the key to loosen. The root cause was determined to be inadequate work instructions leading to the previous installation of a setscrew that was too small to allow proper lockwiring. The procedure for motor pinion gear installation has been changed to include detailed instructions on motor pinion gear installation. However, the procedure will be evaluated to determine if additional guidance concerning the selection of setscrews is warranted.
368 | 3681991005 | 1991-02-01 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Arkansas 2 | P | CE | PO | 88 | On February 1, 1991 at 1722 hours, while operating at 88 percent power an automatic reactor trip was initiated by the Core Protection Calculators (CPCs) due to a loss of power to reactor coolant pump 2P-32B. The emergency feedwater system actuated automatically due to post trip steam generator water level response (shrink) and was used to restore water levels to normal. Other plant system responded as designed to the transient and no significant malfunctions of equipment occurred. Investigations revealed that the RCP motor power supply feeder breaker had tripped due to inadvertent actuation of a motor phase differential relay for the breaker. The relay is mounted in a hinged door on the front of the breaker cubicle and was actuated due to vibration of the door. A faulty racking motor being used to rack up a breaker adjacent to the RCP breaker caused the excessive vibration. The faulty racking motor was removed from service. An engineering evaluation is being conducted to determine the feasibility of using a different type of protective relay to enhance the system design. The CPCs functioned properly to initiate an automatic reactor trip upon loss of an operating RCP. There was no actual safety significance to this event.
368 | 3681995002 | 1995-09-01 | QP5 | Excessive Feedwater Flow | [45 empty] | Arkansas 2 | P | CE | PO | 98 | On September 1, 1995, at 1130, ANO-2 experienced an automatic reactor trip due to high level in the B Steam Generator (S/G). The trip was preceded by an automatic increase in Main Feedwater (MFW) flow due to the inadvertent opening of a flow orifice flush valve on a MFW flow instrument sensing line which caused a false indication of low flow to the B S/G. Subsequent investigation determined that a contract p ainter had stepped from a scaffold pole onto a small angle iron support above the B MFW header flow transmitter and inadvertently opened the flow orifice flush valve for the instrument sensing line with his foot, venting the high pressure side of the transmitter. The feedwater control system responded by increasing the speed of both MFW pumps and opening the B MFW regulating valve, which over fed the 'B' S/G and caused the reactor trip. The plant was stabilized in accordance with standard reactor trip recovery procedures for an uncomplicated reactor trip. The reactor was returned to criticality at 1526 on September 2, 1995. The root cause of this event was human error in that a contract painter did not utilize an appropriate work platform. Entergy management immediately suspended all plant painting and associated activities where trip sensitive equipment was located until further notice. The painter responsible was counseled on the seriousness of this event and a meeting was held with painting and housekeeping personnel to discuss management expectations.
368 | 3681995003 | 1995-09-02 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Arkansas 2 | P | CE | PO | 17 | During plant startup from a reactor trip on the previous day, an automatic reactor trip occurred on September 2, 1995, when power exceeded 17 percent raw excore power (average) and enabled the auxiliary Core Protection Calculator (CPC) trip on Axial Shape Index (ASI) with ASI in excess of the trip setpoint. The trip was uncomplicated with all safety systems responding as expected for plant conditions. ASI is the power generated in the lower half of the core less the power generated in the upper half of the core divided by the sum of these powers. The root cause of this event was attributed to personnel error on the part of the licensed operator who was assigned to monitor and control reactor power. There were several contributing factors, including feedwater and steam generator water level oscillations that diverted attention to the secondary side of the plant. ANO-2 Operations management provided lessons learned from this event to ANO-2 Senior Reactor Operators, including Shift Superintendents who then discussed it with their respective crews. to include a specific hold point at approximately 10 percent power to ensure that ASI is below the trip setpoint.
368 | 3682001002 | 2001-11-01 | QR3 | Reactivity Control Imbalance | [45 empty] | Arkansas 2 | P | CE | PO | 24 | While troubleshooting a dropped Control Element Assembly (CEA) with reactor power approximately 24 percent, an automatic actuation of the Reactor Protection System (RPS) occurred. The CEA Operator (CEAO) inadvertently selected the Mode Select Switch to a position that resulted in insertion of all CEAs in one group (consisting of two subgroups) instead of only the CEA that had dropped. This resulted in a deviation between the positions of the two subgroups and generated a penalty factor that caused a trip of the Core Protection Calculators. Plant response to the trip was normal and uncomplicated. All CEAs fully inserted and the plant was stabilized in hot standby conditions. Work practice root causes were that the CEAO did not monitor diverse CEA positions during CEA movement and did not apply self-checking to verify that the Mode Select Switch was in the correct position. A management methods root cause was that management expectations concerning peer checking during reactivity manipulations were not adequately understood and applied. The event was determined to have had minimal safety significance.
368 | 3682002002 | 2002-12-19 | QR5 | Turbine Trip | [45 empty] | Arkansas 2 | P | CE | PO | 100 | A trip of the Main Turbine while operating at 100 percent power resulted in automatic actuation of the Reactor Protection System and a reactor trip. Plant response was uncomplicated and the plant was promptly stabilized in hot standby conditions. The trip resulted from a failure of the Main Generator reverse power relay. The relay had been in service since initial plant construction in the late 1970s. Periodic testing and calibration of the relay had last been performed in 2000. Inspections and testing verified that the relay failure did not result from external conditions. Evidence obtained following the failure did not allow conclusive determination of the root cause, and the relay was sent to the manufacturer for further evaluation. The relay was replaced and the replacement was monitored during the plant startup. There have been no previous similar events at Arkansas Nuclear One.
368 | 3682009001 | 2009-03-13 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Arkansas 2 | P | CE | PO | 84 | On Friday, March 13, 2009, at approximately 21:51 CDT, Arkansas Nuclear One, Unit 2 was manually tripped from 84% power due to decreasing level in the “B” Steam Generator caused by the “B” Main Feedwater Regulating Valve moving in the closed direction without input demand to close. The trip was manually initiated at approximately the 25% Steam Generator water level. Due to the valve malfunction the system was unable to restore the Steam Generator water level before the 22.2% Emergency Feedwater System Control actuation set point was reached. The Emergency Feedwater System actuated, as designed, restoring Steam Generator water levels to normal. Post trip responses were normal with all plant safety systems functioning as expected. Investigation revealed that the most probable root cause of the event was a foreign substance in the clearance area of the armature, internal to a current-to-pressure (I/P) converter in the “B” Main Feedwater Regulating Valve positioner. The positioner was replaced and tested, and Unit 2 returned to 100% power operation, Mode 1, at 17:01 CDT on March 17, 2009.
368 | 3682009005 | 2009-12-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Arkansas 2 | P | CE | PO | 100 | On December 08, 2009, at 0837 Central Standard Time (CST), Arkansas Nuclear One, Unit 2 (ANO-2) was operating near 100 percent power when the 'A' Main Feedwater Pump (MFWP) was manually tripped in response to high thrust bearing temperature. The Loss of MFWP Abnormal Operating Procedure (AOP) was executed. A manual Reactor trip was initiated when the 'A' Steam Generator (SG) water level decreased to approximately 27 percent. The Emergency Feedwater (EFW) system automatically actuated at the designed setpoint of 22.2 percent to restore SG levels. The Loss of MFWP AOP contained instructions which limited the Main Turbine load reduction rate (plant power reduction rate) that was necessary to recover SG water levels prior to reaching the EFW automatic actuation setpoint. The ANO-2 plant simulator response had previously indicated that SG levels could be recovered following the loss of a MFWP from full power without requiring a Reactor trip. Following the subject event, the plant simulator software was revised to incorporate observed plant data. The Loss of MFWP AOP was revised to provide a mitigation strategy based on actual plant response data, and was validated using the revised ANO-2 plant simulator model. After replacement of the 'A' MFWP thrust bearing, ANO-2 returned to near full power on December 13, 2009, at approximately 1813 CST.
368 | 3682012001 | 2012-08-08 | QL7 | Degraded condenser vacuum | [45 empty] | Arkansas 2 | P | CE | PO | 100 | On August 08, 2012 at 0823 CDT, Arkansas Nuclear One Unit-2 (ANO-2) tripped from approximately one hundred percent power due to degraded main condenser vacuum. The 2C-5B Condenser Vacuum Pump (one of two condenser vacuum pumps) had been secured by taking the control handswitch to pull-to-lock by Operations personnel to perform routine oil level checks. Ambient temperatures were low enough to maintain condenser vacuum with one condenser vacuum pump (2C-5A) in service. When 2C-5B was secured, two solenoid valves failed to reposition the isolation valves on 2C-5B, which resulted in a significant air flow path from atmosphere through the vacuum pump, causing condenser pressure to increase to the main turbine trip setpoint. The main turbine tripped on high turbine exhaust pressure which resulted in an automatic reactor scram due to high reactor coolant system pressurizer pressure. The Emergency Feedwater Actuation System actuated for the “A” Steam Generator due to steam generator water level trending slightly below setpoint. After investigation and corrective maintenance, ANO-2 was reconnected to the electrical grid on August 09, 2012. The root cause investigation determined that the subject solenoid valves were installed in an environment with temperatures in excess of designed temperature ratings. This condition resulted in heat related binding of the solenoid valves and failure to reposition when de-energized. The planned corrective action to preclude recurrence of this root cause will implement a modification to change the solenoid valve location to allow proper heat dissipation.
368 | 3682013004 | 2013-12-09 | QR7 | Other Reactor Trip (Valid RPS Trip) | [7 empty] | X | [25 empty] | X | [11 empty] | Arkansas 2 | P | CE | PO | 100 | On December 9, 2013, at approximately 0747 CST, Arkansas Nuclear One, Unit 2 (ANO-2), experienced an electrical fault on the Unit Auxiliary Transformer (2X-02) buses resulting in a fire and catastrophic failure of the transformer. This caused an automatic reactor and main turbine trip, lockout of the Switchyard Auto Transformer, lockout of (ANO-2) Startup 3 Transformer (2X-03) and loss of power to Arkansas Nuclear One, Unit 1 (ANO-1) Startup 1 Transformer (X-03) The switchyard auto transformer supplies one of the two credited offsite sources supplying both Startup 3 Transformer (2X-03) and Arkansas Nuclear One, Unit 1 (ANO-1) Startup 1 Transformer (X-03). A loss of one of the two available offsite power sources for ANO-2 resulted in an auto-start of the ANO-2 Emergency Diesel Generator (2K-4B) to supply ANO-2 safety bus 2A-4 and initiation of the Emergency Feedwater (EFW) System. Investigations determined the most probable cause of the event that led to failure of the Unit Auxiliary Transformer began with a phase-to-ground fault on the 6900V ‘C’ phase non-segregated bus flexible link for 2X-02. Transformer 2X-02 protective relays designed to isolate the bus from an electrical fault actuated, but due to a disconnected lead, the Main Generator Lockout relays failed to actuate leading to 2X-02 failure. A root cause evaluation determined a flexible link for 2X-02 was not properly installed which led to an insulation breakdown at the bolted connection. The subsequent 2X-02 explosion and fire resulted from a non-landed wire due to a human performance error most likely occurring in 1995 that failed to connect the DC conductor to the output contacts for the protective relays.
368 | 3682014002 | 2014-04-03 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Arkansas 2 | P | CE | PO | 100 | On April 3, 2014, at approximately 1300 CST, Arkansas Nuclear One Unit 2 (ANO-2) tripped from 100% power due to a fault in 161kV Russellville East Line. The fault caused a momentary degraded voltage state on the 161kV and 500kV grid at ANO and an undervoltage condition for ANO-2 Startup #3 Transformer (SU3). This under voltage condition caused SU3 undervoltage relays to initiate a fast transfer of ANO-2 4160V bus (2A-1) and 6900V bus (2H-1), to Startup Transformer #2 (SU2). Buses ANO-2 6900V (2H-2) and 4160V (2A-2) were not allowed to fast transfer to SU2 because of operational restraints per design. The removal of power to 2A-2 caused an auto start of the ANO-2 Emergency Diesel Generator (2K-4B) due to under voltage on safety bus 2A-4 which is normally fed from 2A-2. Bus 2A-2 slow transferred back to SU3. 2K-4B did not tie to 4160V safety bus (2A-4) as voltage had recovered prior to the diesel reaching rated speed and voltage. Bus 2H-2 was de-energized causing the loss of two Reactor Coolant Pumps (RCPs) which led to a reactor trip on low RCP speed and the actuation of the Emergency Feedwater System (EFW) on low Steam Generator Level. It was determined that a lighting strike caused a three phase fault on the 161kV Russellville East Line causing the ANO-2 trip. The corrective action is for Entergy Arkansas to review the adequacy of 161kV Russellville East Transmission Line Lightning Protection System.
368 | 3682014003 | 2014-04-27 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Arkansas 2 | P | CE | PO | 95 | During severe weather on April 27, 2014, both units at Arkansas Nuclear One (ANO) were informed of a system-wide grid emergency and were ordered to come off-line as soon as possible. Both units commenced a rapid plant shutdown. ANO, Unit 2 (ANO-2) was at the end of the core life. During the shutdown, the Axial Shape Index (ASI) became more negative (power rising to the upper portion of the core) during the shutdown. This led to one channel of the Plant Protection System (PPS) to be actuated on an ASI auxiliary trip. At this time, the direction to manually trip the reactor was given, but before the action could be taken, an automatic reactor trip occurred due to the two-out-of-four PPS logic being made up for the ASI conditions.<br /><br /> The cause of this condition was not effectively executing the reactivity management plan by delaying insertion of Control Element Assemblies (CEAs) and not inserting CEAs deep enough to maintain ASI within the desired control band.<br /><br /> Training material is being modified to include details on the dynamic effects of ASI change that occurs at the end-of-cycle. Additionally, improvements to the guidance in the reactivity plans that involve rapid plant shutdowns are being made as are changes to the standards for use of CEAs during transients.
368 | 3682019001 | 2019-05-26 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Arkansas 2 | P | CE | PO | 100 | On May 26, 2019, the Arkansas Nuclear One, Unit 2 (ANO-2), reactor automatically tripped due to a fault and subsequent trip of Reactor Coolant Pump (RCP) 2P-32B. <br /><br /> The direct cause of the event was determined to be the loss of stator core compression coupled with broken compression finger welds allowing a finger to migrate into contact with the RCP rotor. The broken finger plate section damaged the stator insulation resulting in a short to ground. <br /><br /> The plant transient led to an automatic reactor trip due to a Plant Protection System actuation. After the reactor trip, the unit was stabilized in Mode 3 with Emergency Feedwater (EFW) initially being used to maintain plant temperature under automatic control.
368 | 3682020001 | 2020-12-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Arkansas 2 | P | CE | PO | 100 | On December 10, 2020, at 1608 CST, while in MODE 1 at 100 percent power, Arkansas Nuclear One, Unit 2 (ANO-2) experienced an automatic reactor scram due to low steam generator water level in the 'A' Steam Generator (SG). The low SG water level was caused by loss of power to the 'A' Feedwater Control System (FWCS) due to power supply failures in the 'A' FWCS cabinet. This resulted in main feedwater flow demand to the 'A' Main Feedwater Pump (MFP) and associated feedwater regulating valves to fail to minimum. Emergency Feedwater (EFW) actuated automatically due to low water level in the 'A' SG. The failure of the 'A' FWCS power supplies affected post-trip response of the 'B' FWCS, which resulted in water level in the 'B' SG rising to a level requiring manual trip of the 'B' MFP. EFW responded as designed to feed both steam generators automatically. The plant was stabilized in MODE 3. The other safety systems responded as designed. Electrical power was supplied from offsite power and maintained unit electrical loads as designed. The 'B' MFP remained available using approved plant procedures. <br /><br /> There were no consequences to the general safety of the public, nuclear safety, industrial safety, or radiological safety. No radiological releases have occurred due to this event.
369 | 3691987004 | 1987-02-18 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | McGuire 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON FEBRUARY 18, 1987 AT 2026, THE UNIT 1 REACTOR TRIPPED DUE TO LOW REACTOR COOLANT (NC) SYSTEM FLOW. A SURGE CAPACITOR ON NC PUMP MOTOR 1C SHORTED TO GROUND CAUSING THE MOTOR CIRCUIT BREAKERS TO TRIP ON HIGH GROUND FAULT CURRENT. THE DEFECTIVE CAPACITOR WAS REPLACED AND NC PUMP 1C WAS STARTED ON FEBRUARY 20, AT 0032. UNIT 1 ENTERED MODE 1, POWER OPERATION, ON FEBRUARY 20, AT 0500. UNIT 1 WAS IN MODE 1, POWER OPERATION, AT 100 PERCENT POWER AT THE TIME OF THE INCIDENT. THIS INCIDENT HAS BEEN ATTRIBUTED TO AN EQUIPMENT FAILURE. NC PUMP MOTOR 1C TRIPPED ON A GROUND FAULT DUE TO A FAILED SURGE CAPACITOR, RESULTING IN A REACTOR TRIP. THE HEALTH AND SAFETY OF THE PUBLIC WERE NOT AFFECTED BY THIS INCIDENT.
369 | 3691987009 | 1987-04-15 | QR8 | Spurious Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | POWER LEVEL - 100%. ON APRIL 15, 1987, AT 1014, THE UNIT 1 REACTOR TRIPPED DUE TO A TURBINE TRIPPED SIGNAL GENERATED WHILE STATION PERSONNEL WERE FUNCTIONALLY TESTING A TURBINE AUTO-STOP OIL PRESSURE SWITCH. A THREE-WAY SOLENOID VALVE USED IN PERFORMING THE TEST CAUSED A DOWNWARD PRESSURE SPIKE ON A COMMON HEADER WHICH WAS SENSED BY ANOTHER PRESSURE SWITCH COMPLETING THE 2 OUT OF 3 LOGIC FOR A SIGNAL TO TRIP THE REACTOR. THE MAIN TURBINE THEN TRIPPED DUE TO THE REACTOR TRIP. OPERATIONS RECOVERED THE UNIT FROM THE TRANSIENT USING THE REACTOR TRIP PROCEDURE. UNIT 1 RETURNED TO 100 PERCENT FULL POWER OPERATION AT 1308, ON APRIL 17, 1987. UNIT 1 WAS IN MODE 1, POWER OPERATION, AT 100 PERCENT POWER, AT THE TIME OF THIS INCIDENT. THIS INCIDENT HAS BEEN ATTRIBUTED TO A DESIGN DEFICIENCY DUE TO AN INAPPROPRIATE APPLICATION OF THE THREE-WAY SOLENOID VALVE; THIS VALVE DOES NOT COMPLETELY CLOSE A FLOW PATH TO THE LUBE OIL DRAIN RESERVOIR PRIOR TO OPENING A FLOW PATH TO THE LUBE OIL PRESSURE HEADER. THIS ALLOWS A SHORT TIME PERIOD WHEN THE TWO SEPARATE FLOW PATHS TRY TO EQUILIBRIATE PRESSURES, RESULTING IN A DOWNWARD PRESSURE SPIKE. THE SCHEDULING OF FUNCTIONAL TESTING OF THE TURBINE AUTO-STOP OIL PRESSURE SWITCHES WAS CHANGED FROM ALL MODES TO MODES 2 THROUGH 6.
369 | 3691987017 | 1987-08-16 | QR9 | Spurious Engineered Safety Feature Actuation | [6 empty] | X |  |  |  | X | [14 empty] | X | [13 empty] | X | [5 empty] | McGuire 1 | P | WE | SU | 8 | POWER LEVEL - 008%. ON AUGUST 16, 1987, WHILE PUTTING THE UNIT 1 TURBINE GENERATOR ON LINE, A MALFUNCTION OF THE TURBINE CONTROLS TRIGGERED A SAFETY INJECTION/REACTOR TRIP. AN UNUSUAL EVENT WAS DECLARED. ALSO VALVE 1NV-142 (VOLUME CONTROL TANK ISOLATION) ACTUATOR BURNED UP AFTER PERFORMING ITS SAFETY FUNCTION. A REACTOR COOLANT LEAK (APPROXIMATELY 40 GPM) ALSO OCCURRED DUE TO A CRACK IN THE LETDOWN LINE AT A DRAIN LINE. THE LEAK WAS STOPPED. THE UNIT REMAINED DOWN FOR REPAIRS. THE ACTUATOR FOR VALVE 1NV-142 WAS REPLACED. THE LETDOWN LEAK WAS REPAIRED. SIMILAR UNIT 1 WELDS ON VENTS AND DRAINS WERE INSPECTED - ONE CRACK FOUND AND REPAIRED. UNIT 2 SIMILAR WELDS WERE INSPECTED - NO PROBLEMS FOUND. SIXTEEN PIPE SUPPORTS WERE ALSO INSPECTED - NO DAMAGE FOUND. THE TURBINE CONTROLS ON UNIT 1 ARE SCHEDULED TO BE REPLACED; UNIT 2 TURBINE CONTROLS HAVE ALREADY BEEN REPLACED. THIS EVENT HAS BEEN ATTRIBUTED TO DESIGN DEFICIENCY BECAUSE THE TURBINE CONTROLS PERFORMED IN AN UNEXPECTED MANNER. THE DESIGN OF THE CONTROLS HAD PREVIOUSLY BEEN DETERMINED TO MERIT BEING REPLACED. THE UNIT WAS PLACED BACK ON LINE AUGUST 21, 1987.
369 | 3691987036 | 1987-12-28 | QR8 | Spurious Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 96 | POWER LEVEL - 096%. ON 12/28/87 AT 1322, DURING PERIODIC TESTING, UNIT 1 REACTOR TRIP OCCURRED WHEN ELECTRICAL MAINTENANCE (EM) PERSONNEL WERE DIRECTED TO THE WRONG REACTOR PROTECTIVE SYSTEM (7300 RPS) CABINET BY AN ERROR IN A SCHEMATIC DIAGRAM. THE ERROR IN THE SCHEMATIC DIAGRAM CAUSED THE PERSONNEL TO COMPLETE A 2 OUT OF 4 LOGIC REACTOR TRIP SIGNAL. A LOW-LOW LEVEL IN STEAM GENERATOR 1B DID NOT ACTUALLY EXIST. OPERATIONS IMPLEMENTED THE REACTOR TRIP RECOVERY PROCEDURE TO RECOVER FROM THE TRANSIENT. AT 2214, EM INITIATED A REACTOR TRIP SIGNAL WHEN THEY DID NOT FOLLOW PROCEDURE AND CAUSED A GENERAL WARNING ON TRAIN A OF THE SOLID STATE PROTECTION SYSTEM (SSPS) WHILE A GENERAL WARNING EXISTED ON TRAIN B OF THE SSPS. UNIT 1 WAS RETURNED TO MODE 1, POWER OPERATION, ON DECEMBER 29, AT 1249. THE REACTOR TRIP IS ASSIGNED A CAUSE OF DESIGN DEFICIENCY BECAUSE THE SCHEMATIC DIAGRAM WAS INCORRECT. ALSO PERSONNEL ERROR BECAUSE PERSONNEL DID NOT PURSUE ADEQUATE CHECKS ON THE DIAGRAM. THE SECOND REACTOR TRIP SIGNAL IS ASSIGNED A PERSONNEL ERROR, BECAUSE PERSONNEL INVOLVED DID NOT FOLLOW PROCEDURE. ALSO DEFECTIVE PROCEDURE BECAUSE NO PRECAUTIONS WERE IN THE PROCEDURE TO PREVENT EVENTS OF THIS TYPE. THE DIAGRAMS WERE MARKED AS INCORRECT AND CHANGES TO CORRECT UNITS 1 AND 2 DIAGRAMS WERE IMPLEMENTED. ALL OTHER 7300 DIAGRAMS WERE REVIEWED.
369 | 3691988001 | 1988-01-07 | QR5 | Turbine Trip | [45 empty] | McGuire 1 | P | WE | PO | 74 | On 01/07/88 at approximately 0700, the Unit 1 Generator started to experience an abnormal voltage and reactive load transient. Operations attempted to combat the transient by manually adjusting the Excitation Switchgear output. The transient became too severe, and at 0708, the Generator and Turbine tripped because of a loss of excitation to the Generator field. The Turbine Trip caused a Reactor Trip. The abnormal voltage and reactive load transient was caused by a malfunctioning firing circuit in the Excitation Switchgear. This firing circuit controls the amount of excitation applied to the Generator to control voltage and reactive load. Unit 1 stabilized from the Reactor Trip by approximately 0740. The Transmission Department repaired the firing circuit portion of the Excitation Switchgear and Unit 1 was returned to power operation on 01/07/88 at 2253. This event is assigned a cause of Other because the transient/trip was caused by a malfunction in the Excitation Switchgear Silicon Controlled Rectifier (SCR) firing circuit. The failure mode of the phase shifter circuits will be evaluated and filtered cooling to the excitation switchgear will be reviewed.
369 | 3691988005 | 1988-03-23 | QR8 | Spurious Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | On 03/23/88 at approximately 1051, Instrumentation and Electrical (IAE) personnel, while performing a monthly functional test, closed the Unit 1 Solid State Protection System (SSPS) Train A logic cabinet door and instantly heard a relay energize. Operations (OPS) was immediately alerted to a Turbine Trip/Reactor Trip annunciator and indication of Control Rod insertion. Among the numerous alarms and indications, a Safety Injection (SI) actuation and a Main Feedwater (CF) system isolation had occurred. The CF isolation tripped CF Pumps 1A and 1B due to high discharge pressure, which led to the Unit 1 Turbine Trip/Reactor Trip. Also, a Unit 1 Main-Steam (SM) system isolation occurred, but with no supporting isolation signals present. OPS implemented Reactor Trip, Safety Injection, and Notification Of Unusual Event procedures. The Train A SI and SM isolation signals were reset. Unit 1 was stabilized near no load conditions at approximately 1120 on 03/23/88. This event was assigned a cause of Other since the cause of the Unit 1 Train A SI and SM isolation signals could not be determined. IAE will inspect the SSPS Train A logic cabinet more closely during an upcoming outage. This event will be reviewed during Segment 4 of Licensed Operators Requalification Training.
369 | 3691988007 | 1988-04-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 1 | P | WE | PO | 100 | On 04/16/88 at 1033, valve 1CF-20, Steam Generator 1C Feedwater Regulating Valve, closed because of an unknown fault on the associated controller card in a control cabinet. Operations (OPS) recognized that Unit 1 would trip automatically so the Turbine Generator and Reactor were manually tripped. All systems and equipment responded as expected following the trip except that valve 1SV-7, Steam Generator 1C Power Operated Relief, opened approximately 10 psi lower than its setpoint band, and the open limit switch for valve 1SA-49, Steam Supply to Auxiliary Feedwater Pump Turbine, failed to actuate. OPS implemented the Reactor Trip and the Unit Fast Recovery procedure. Instrumentation and Electrical (IAE) replaced the faulty controller card, and Unit 1 was returned to service on 04/17/88 at 0501. This event is assigned a cause of Other since the component failure on the control card for valve 1CF-20 was due to unknown cause. IAE will study the failure of the open limit switch on valve 1SA-49 and determine the implications to other environmentally qualified equipment. The failed controller card will be analyzed by Westinghouse and a revision to this report will be submitted describing the test results.
369 | 3691988013 | 1988-06-20 | QR3 | Reactivity Control Imbalance | [45 empty] | McGuire 1 | P | WE | PO | 100 | On 6/20/88 at approximately 0005, while Operations (OPS) was shifting from the normal power supply to the alternate power supply on Shared Motor Control Center SMXS in order to prepare for testing on a Unit 2 load center, a Unit 1 Rod Control Urgent Failure alarm was received in the Control Room causing the Control Rods to drop into the core, thus initiating a High Negative Neutron Flux Rate Reactor Trip at 0005:52. The Turbine Generator automatically tripped on a Reactor Trip. OPS implemented the Reactor Trip recovery procedure to recover from the transient and initiated an emergency work request to troubleshoot the power supply for the Rod Control System. At approximately 1858, Instrument and Electrical (IAE) found and replaced failed auxiliary and primary power supplies for the Rod Control system. Unit 1 returned to power operation on June 21, 1988 at 0300. This event is assigned a Cause of Other because of the failure of the primary power supply for the Rod Control system. OPS will request Design Engineering evaluate reduncy requirements in the control system power supplies.
369 | 3691989004 | 1989-03-07 | F1 | Steam Generator Tube Rupture PWR (SGTR) | [5 empty] | X | [18 empty] | X | [20 empty] | McGuire 1 | P | WE | PO | 100 | On March 7, 1989 at 2345, an Alert condition was declared on Unit 1 because of indication of primary to secondary leakage in excess of 50 gpm. At 2346, Unit 1 was manually tripped from Mode 1, Power Operation, approximately 83% power because of indications of a steam generator tube leak in the B Steam Generator. All major plant equipment functioned properly, and the unit was stabilized in accordance with Station Abnormal Operating Procedures. The initial notifications to the State, local county authorities and the resident NRC inspector were made at 2358. The NRC Region II Office was notified at 0044 on March 8, 1989. The Technical Support Center and Operational Support Center were fully staffed and activated by 0132.The Crisis Management Center was staffed and activated at 0740. The event is assigned a cause of Other because of the rupture of a single tube in B steam generator. The results of the inspection and analysis of the tube failure will be addressed in an addendum to this LER.
369 | 3691989022 | 1989-08-26 | QR8 | Spurious Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | On August 26, 1989 at 0934, a Unit 1 Reactor Trip occurred because of a Reactor Coolant (NC) low flow signal that is interlocked with a permissive signal which blocks a Reactor Trip when the unit is less than 48 percent power (P-8 permissive). Unit 1 was operating in Mode 1, Power Operation, at 100 percent power prior to the trip. A low NC flow signal with P-8 permissive caused Reactor Trip Breaker "A" to trip the unit. The signal was caused by a failed Universal Board in the Solid State Protection System (SSPS) cabinet for Train "A". The Turbine Generator automatically tripped because of the Reactor Trip. All systems and equipment responded as expected following the trip with one exception. Operations personnel implemented the Reactor Trip recovery procedure to recover from the transient. At about 1000, Operations personnel made the required notification to the NRC. At 2220, Instrumentation and Electrical personnel discovered the failed Universal Board and replaced it. The SSPS Cabinet was tested after the board was replaced to ensure the train would operate properly. Unit 1 was returned to Mode 1, Power Operation, on August 28, 1989 at 1230. This event is assigned a cause of Equipment Failure / Malfunction. This event is Nuclear Plant Reliability Data System reportable. The board will be sent to Westinghouse for repair and failure analysis.
369 | 3691990001 | 1990-01-08 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | McGuire 1 | P | WE | PO | 100 | On January 8, 1990, at 1015, a Unit 1 Turbine Trip/Reactor Trip occurred when both Main Feedwater Pumps (CFPs) tripped on low suction pressure. Unit 1 was operating in Mode 1 (Power Operation) at 100 percent power prior to the trip. A trouble alarm was received for CFP A speed controller and immediately CFP A started reducing speed. Operations personnel initiated a manual turbine runback to compensate for the loss of feedwater flow from CFP A. Then CFP A speed controller within minutes started increasing speed. This attributed to the low suction pressure that tripped both CFP A and B. The speed controller malfunction was due to the strainer in the controller becoming clogged with sludge. The speed controller control oil is supplied by the Feedwater Pump Turbine Lube and Hydraulic Oil (LF/LP) System which share the oil purifier in the Main Turbine Lubricating and Purification Oil (LT) System. There were several anomalies as plant equipment responded to the Turbine Trip/Reactor Trip. Operations personnel implemented the Reactor Trip recovery procedure to recover from the transient. At 1148, Operations personnel made the required notification to the NRC. Unit 1 then entered a refueling outage for turbine repair. This event is assigned a cause of Other/Unknown because it could not be determined how excessive water in the LT and LF system resulted in sludge collecting in the strainer. Operations and Maintenance Engineering Services (MES) personnel are pursuing attempts to minimize the accumulation of sludge because of excess water in the LF and LT systems.
369 | 3691990027 | 1990-10-13 | QR8 | Spurious Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | On October 13, 1990, at 1033, Unit 1 experienced a Reactor Trip/Turbine Trip. Unit 1 was in Mode 1, Power Operation, at 100 percent power at the time of this event. The first out (FO) annunciator indicated an "SSPS General Warning - Rx Trip." Prior to the Reactor Trip, Instrumentation and Electrical (IAE) personnel were performing the bi-monthly periodic test on the Solid State Protection System (SSPS) Train B. The "General Warning" signal was generated because of the failure/malfunction of a Reactor Trip Breaker cell switch. The only Safety System Actuation that occurred as a result of the trip was the start of the Auxiliary Feedwater (CA) pumps. Operations (OPS) personnel implemented the Reactor Trip/Safety Injection procedure and then entered the Reactor Trip procedure. OPS personnel implemented the Unit Fast Recovery procedure to recover from the Reactor Trip. At 1200, OPS personnel made the required notification to the Nuclear Regulatory Commission (NRC). IAE personnel replaced the failed cell switch. OPS Control Room personnel returned Unit 1 to Mode 1 (Power Operation) on October 14, 1990, at 1825. This event has been assigned a cause of Equipment Failure/Malfunction because of the failed cell switch. This event is Nuclear Plant Reliability Data System reportable and Part 21 reportable. The switch will be sent offsite for further failure analysis.
369 | 3691990032 | 1990-11-17 | QR5 | Turbine Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | On November 17, 1990, at 0319, Unit 1 experienced a Turbine Trip, followed by a Reactor Trip. The trip was initiated by the B Low Pressure (LP) Turbine High Exhaust Hood Temperature signal. Prior to the event, Unit 1 was operating in Mode 1 (Power Operation) at 100 percent power. Operations (OPS) Control Room personnel implemented procedure EP/1/A/5000/01, Reactor Trip or Safety Injection, and then entered procedure EP/1/A/5000/1.3, Reactor Trip. OPS personnel made the required notification to the NRC per procedure RP/0/A/5700/10, NRC Immediate Notification Requirements. The motor driven Auxiliary Feedwater pumps started as required, due to a low low Steam Generator (S/G) water level. There were no other Safety System Actuations. OPS Control Room personnel entered procedure OP/1/A/6100/05, Unit Fast Recovery. On November 17, 1990, at 1821, Unit 1 entered Mode 1. It was determined by Instrument and Electrical (IAE) personnel that the trip signal was received because of a damaged LP Turbine Exhaust Hood Temperature instrument. To prevent recurrence of this event, Maintenance Engineering Services (MES) personnel will evaluate the use of a dual element thermocouple or possible use of a two out of two logic for the temperature signal. This event has been assigned a cause of Unknown since it cannot be determined what caused the temperature instrument to become damaged.
369 | 3691991001 | 1991-02-11 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | McGuire 1 | P | WE | PO | 100 | On February 11, 1991, A Unit 1 Reactor Trip occurred at 1355:13. Prior to the event, Unit 1 was operating in Mode 1 (Power Operation) at 100% power. The Reactor was tripped by a Nuclear Instrumentation (NI) Power Range Hi Flux Rate signal. The trip signal was initiated when offsite power to the unit was lost because a blackout occurred in the 230KV switchyard. The blackout as a result of a failed relay in conjunction with a post modification test being performed on a newly added relay circuit in the switchyard. Subsequent depressurization of the Main Steam (SM) system resulted in a Safety Injection (SI). An Unusual Event was declared at 1420 due to Loss of Power and SI. The Technical Support Center (TSC) was activated as a conservative measure and TSC personnel made the required notification to the NRC. A thorough technical review was performed on the event and, consequently, a decision was made by Station Management (with concurrence of the NRC) to restart the Reactor. Unit 1 was returned to Mode 2 (Startup) operation on February 13, 1991, at approximately 0345. This event is assigned causes of Inappropriate Action, Management Deficiency, and an Equipment Failure..
369 | 3691991004 | 1991-02-19 | QR8 | Spurious Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | On February 19, 1991, at 2142, Unit 1 experienced a Reactor/Turbine Trip. Unit 1 was in Mode 1 (Power Operation), at 100 percent power prior to this event. Prior to the Reactor Trip, Operations (OPS) management personnel were attempting to close the door on Reactor Trip Breaker (RTB) cubicle 1B. When the cubicle door was pushed closed, RTB 1B opened, tripping the Reactor. The Control Rods dropped into the Reactor core, thereby, generating a "NIS Hi Flux Rate Power Range Reactor Trip" trip signal. The only Safety System Actuation was the manual start of the Motor Driven Auxiliary Feedwater Pumps at 2143:58. OPS personnel implemented the Reactor Trip Or Safety Injection procedure and then entered the Reactor Trip procedure. OPS personnel returned Unit 1 to Mode 1 on February 21, 1991, at 1815. This event has been assigned causes of a Management Deficiency and a Possible Inappropriate Action.
369 | 3691992009 | 1992-06-25 | QR8 | Spurious Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | On June 25, 1992, A Unit 1 Reactor Trip occurred at 1312. Prior to the event, Unit 1 was operating in Mode 1 (Power Operation) at 100 percent power. The Reactor was tripped by a Nuclear Instrumentation Power Range Hi Flux Low setpoint and intermediate Range Hi Flux signal. The trip signal was initiated when Instrument and Electrical personnel inadvertently removed and re-inserted the Solid State Protection System Train A Ground Return Fuse. The removal of the Ground Return Fuse removed the Intermediate and Power Range Hi Flux Reactor Trip inputs and blocks. upon reinsertion of the fuse, a Reactor Trip was initiated because the inputs were reinstated but the blocks were not reinstated. A post trip review was performed and Unit 1 was returned to Mode 2 (Startup) on June 26, 1992 at 0430 and entered Mode 1 on June 26, 1992 at 0930. This event is assigned causes of Inappropriate Action and Management Deficiency.
369 | 3691992008 | 1992-07-26 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 1 | P | WE | PO | 100 | On July 26, 1992, at 0852:01, while operating in mode 1 (Power operation) at 99.5 percent power, Unit 1 experienced a Reactor Trip/Turbine Trip on Overtemperature Delta Temperature (OTDT). The initiating event was the loss of Main Feedwater Pump Turbine (FWPT) 1B condenser vacuum. The loss of vacuum caused FWPT 1B to trip, resulting in a Load Rejection (Turbine runback). Due to a problem with the mixing amplifier card which processes the Reactor Coolant average temperature (T-ave) signal to the condenser steam dump valves, T-ave exceeded the OTDT setpoint in two of four channels, causing the Reactor trip. No load conditions were achieved in approximately two hours. This event has been assigned a root cause of Defective Procedure, due to a technical deficiency. The investigation revealed that the condenser steam dump valves operated properly within the condenser steam dump Load Rejection Controller, but not at the correct time due to improper calibration of the mixing amplifier card. Procedure changes have been made to procedure IP/0/B/3001/03, Steam Dump Control System Calibration, to prevent recurrence of this problem.
369 | 3691993009 | 1993-11-06 | QR5 | Turbine Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | On November 6, 1993, at 0220:14, while operating in Mode 1 (Power Operation) at 100 percent power, Unit 1 experienced a Reactor Trip/Turbine Trip on Over Temperature Delta Temperature (OTDT). The initiating event was a large loss of turbine load caused by Turbine Governor and Interceptor Valve closure. The unit was stabilized in Mode 3 (Hot Standby) and an investigation into the cause of the valve closure was conducted. While a suspected cause was developed, it could not be confirmed. A decision was made to proceed with restart, and continue testing circuits monitoring generator and switchyard breaker position. During restart, a problem with the Interceptor valves was discovered. Both the Overspeed Protection Control (OPC) solenoid valves and a Train B Emergency Trip (ETC) solenoid valve were replaced and the Unit was returned to Mode 1 at 0405 on November 7, 1993. This event has been assigned a cause of Equipment Failure/Malfunction due to an unknown cause. Immediate corrective actions were to replace the three solenoid valves associated with the OPC header prior to returning the unit to service. Planned corrective actions include an evaluation of potential changes to the flush methods used on the Electro-Hydraulic High Pressure Fluid system. Also an evaluation of possible equipment modifications/replacements will be performed in conjunction with other problems identified with the OPC and ETC solenoid valves.
369 | 3691994004 | 1994-05-12 | QR5 | Turbine Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | On May 12, 1994, at 1353, Unit 1 experienced a Reactor trip. Prior to the event Unit 1 was in Mode 1 (Power Operation) at 100 percent power. The event occurred when a screwdriver rolled off a divider barrier in electrical board 1EB5, striking one or more relays in the reverse power circuitry for the Unit 1 Generator. This resulted in the opening of both Unit 1 Generator Power Circuit Breakers. A full load rejection was initiated, followed by a Reactor trip due to a Nuclear Instrumentation System Power Range High Negative Flux Rate Reactor Trip signal. This event is assigned a cause of Improper Use of Equipment because the divider barrier in an electrical panel was used as a tool rest. Corrective actions to be taken to prevent recurrence include communicating to Instrument and Electrical (IAE) personnel that divider barriers in electrical equipment are not to be used as tool rests and procedure changes to caution IAE personnel not to use divider barriers as tool rests. Unit 1 was returned to service on May 13, 1994, at 0643.
369 | 3691995001 | 1995-01-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 1 | P | WE | PO | 100 | On January 29, 1995, at 1822, a manual Reactor Trip was initiated on Unit 1 after Steam Generator (S/G) Feedwater Isolation Valve 1CF-26 moved to its fail-safe (closed) position. Operations (OPS) personnel quickly realized valve 1CF-26 was going closed. OPS personnel responded in a proactive and conservative manner and manually tripped the Reactor prior to receiving an automatic Reactor Trip on low-low level in S/G 1D. All systems responded as required. Prior to the event, Unit 1 was in Mode 1 (Power Operation) at 100 percent power. Unit 1 was returned to service on January 31, 1995 at 0955. This event is assigned a cause of Equipment Failure. The valve closed due to loss of power caused by a failed fuse in the control circuitry to the solenoid. An analysis of the failed fuse by the Duke Power Company Metallurgy Lab indicated the fuse failure occurred by brittle fracture through the fusible alloy button adjacent to the copper wire lead to one fuse cap. Corrective actions to prevent recurrence include the replacement of this type of fuse in applications deemed critical to plant operation.
369 | 3691995005 | 1995-09-27 | QL5 | Partial Closure of MSIVs | [45 empty] | McGuire 1 | P | WE | PO | 100 | Unit Status: Unit 1 - Mode 1 (Power Operations) at 100 percent power. Event Description: On September 27, 1995, at 0923, a manual Reactor Trip was initiated on Unit 1 after valve 1SM-0007AB, Main Steam Isolation Valve Steam Line A, moved to the fail safe (closed) position. Operations (OPS) personnel quickly realized that valve 1SM-0007AB was closed, and responded in a proactive and conservative manner to manually trip the Unit prior to receiving an Automatic Reactor Trip. All systems responded as required after the trip. Unit 1 was returned to service on September 30, 1995, at 0410. <br /><br /> Event Cause: A cause of Unknown, possible equipment failure, has been assigned. Extensive investigation efforts have been unable to determine an exact mode of failure for the equipment. <br /><br /> Corrective Action: As a conservative measure, the associated fuses, solenoid valve coils, some wiring terminations, and relays were replaced to eliminate recurrence due to any possible intermittent problem with any of these components which could have been undetected during the troubleshooting efforts.
369 | 3691995006 | 1995-10-01 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | McGuire 1 | P | WE | PO | 49 | Unit Status: Unit 1 - Mode 1 (Power Operation) at approximately 49 percent power. <br /><br /> Event Description: On October 1, 1995, at 1011, the Unit 1 Reactor tripped due to low Reactor Coolant (NC) system flow. A surge capacitor in NC Pump Motor 1D shorted to ground, causing the motor circuit breakers to trip on high ground fault current. Both the NC Pump Motor 1D supply breaker and safety breaker were tripped by their respective ground fault relays. Post trip conditions were normal. Unit 1 was returned to Mode 1 on October 2, 1995, at 1510. <br /><br /> Event Cause: A cause of Equipment Failure has been assigned due to a surge capacitor failure in the NC pump motor connection enclosure. Subsequent testing of the capacitor confirmed the capacitor had failed. <br /><br /> Corrective Actions: Maintenance personnel replaced the failed capacitor and tested associated circuits and equipment. Engineering personnel will evaluate the expected service life of these capacitors and determine if a replacement program is needed. Engineering personnel will also review current testing to determine if testing is adequate.
369 | 3691996001 | 1996-02-03 | QR6 | Manual Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 60 | Unit Status: Unit 1 - Mode 1 (Power Operations) at 60 percent power. Event Description: On February 3, 1996, during the performance of routine Train 1A Safety Injection Slave Relay Testing, a manual Reactor Trip was initiated when the 1A Reactor Coolant Pump Upper Thrust Bearing reached the administrative limit of 195 degrees. Prior to the trip, Operations personnel had noted a steady increase in the bearing temperature and had begun a rapid power reduction. At approximately 60 percent Reactor Power the administrative trip criteria for the pump was reached and the Reactor was manually tripped as directed by procedure requirements at 1419:15. As soon as the Reactor was tripped, the 1A Reactor Coolant Pump was tripped. All systems responded as required after the trip. Unit 1 was returned to service on February 5, 1996, at 0332.<br /><br /> Event Cause: A cause of Equipment Failure due to an unknown cause has been assigned. The increase in 1A Reactor Coolant Pump Upper Motor Bearing temperature was caused when the Component Cooling system flow control valve for the bearing failed in the closed position due to a failure in the associated control loop; however, the exact mode of failure could not be determined. <br /><br /> Corrective Action: The associated systems and components were evaluated/tested and determined to be operable.
369 | 3691997009 | 1997-09-06 | QC5 | Loss of Non-safety-Related Bus | [13 empty] | X | [30 empty] | X | McGuire 1 | P | WE | PO | 100 | Unit Status: Units 1 and 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On September 6, 1997, at 2146, the trip of an auxiliary supply breaker, while the Units were in an abnormal alignment, caused the loss of non-vital power to plant components on both Units. For Unit 1, this resulted in a trip of both Main Feedwater Pumps followed by a main Turbine and subsequent Reactor trip. For Unit 2, it resulted in the closure of the Main Steam Isolation Valves followed by a Reactor trip on Pressurizer high pressure. Additionally, the power loss resulted in loss of the automatic operating function for the Pressurizer Power Operated Relief Valves (PORVs) on both Units, and loss of indication from the Process Radiation Monitor associated with one set of the Control Room Ventilation Outside Air Intakes. This equipment was inoperable for a period of 62.5 minutes, exceeding Technical Specification (TS) limits of 60 minutes without implementation of required actions. Event Cause: The cause of the breaker trip has been determined to be heat build-up created by a loose cable connection on the load side of the breaker, actuating breaker thermal trip units. The cause of the loose connection is a construction/installation deficiency. A contributing factor is management deficiency due to lack of establishing adequate preventive maintenance. Failure to implement required TS actions with regard to the Pressurizer PORVs and Process Radiation Monitor is attributed to failure of Control Room personnel to recognize the need to do so. With the loss of KXA, multiple Control Room indications were lost. Due to the absence of these indications and lack of procedural direction to alert them, actions were not taken within the one hour requirement. Corrective Action: Corrective actions include evaluation of preventative maintenance on shared vital and auxiliary control and instrumentation buses, development of procedures for plant operation during loss of instrumentation and control buses, enhancement of existing procedural guidance, and training for all licensed operations personnel. To be reported through EPIX
369 | 3691998002 | 1998-02-09 | QR3 | Reactivity Control Imbalance | [45 empty] | McGuire 1 | P | WE | PO | 100 | Unit Status: Unit 1 Mode 1 at 100% Reactor Power Event Description: Intermittent operation of a fuse holder [EIIS:FUB] caused 8 control rods to drop into the core and 3 rods in control bank D to move in approximately 50 steps. Operators manually tripped the reactor prior to reaching an automatic reactor trip setpoint. Event Cause: A power supply failure occurred due to an intermittent loss of power to the rod control [EIIS: JD] gripper mechanism. The momentary loss of AC power to the functioning power supply was caused by intermittent operation of a fuse holder. Corrective Action: The fuse holder was replaced and other fuse holders were inspected and replaced as appropriate. Additional procedural guidance will be provided for replacing defective rod control power supplies on-line. The existing shutdown procedure on rod control power supply will be enhanced to check the integrity of the fuse holders. *NPRDS no longer exists, the failure will be reported through EPIX
369 | 3692000004 | 2000-05-25 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 1 | P | WE | PO | 100 | Unit Status: At the time of the ESF/RPS actuation, both Unit 1 and Unit 2 were in Mode 1 at 100% Power. Event Description: On May 25, 2000, Unit 1 experienced a failure of the output switch on vital inverter 1EVIA. This failure caused a loss of Channel 1 vital instrumentation and control power resulting in a false low Channel 1 steam generator (S/G) level input to the S/G Water Level Control System, commencing a feedwater system transient. Upon placing S/G water level control in Channel 2, the feedwater system transient continued in a manner which resulted in a trip of the 1A CF Pump due to high discharge pressure, followed by a Unit 1 reactor trip due to 1C S/G Low-Low Level. Upon receipt of subsequent Low-Low S/G Level inputs, the 1B Motor Driven Auxiliary Feedwater (CA) Pump and the Turbine Driven CA Pump auto-started. The lA Motor Driven CA Pump was manually started, as it did not auto-start since its control circuitry is supplied power from Channel 1 vital control power, which was lost. In addition, post-trip operator actions resulted in the auto-alignment of the CA pumps suction to the assured source when the normal non-safety related water supplies were isolated. Event Cause: Mechanical related failure of the 1EVIA inverter output switch. Failure to correctly follow procedure when aligning CA pump suction sources. Corrective Action: Replaced vital inverter switches as needed. Future modifications will eliminate switches of this design. Plant procedures revised to preclude inadvertent alignment of CA pump suction to the assured source. Operator training (RO only) will be reviewed to examine proficiency in the use of 2 column format procedures as related to this event.
369 | 3692002001 | 2002-03-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 1 | P | WE | PO | 100 | Event Description: On March 4, 2002, the 1A Steam Generator experienced decreasing level when its main feedwater supply valves failed closed. In response to the decreasing lA Steam Generator level, the Unit 1 reactor was manually tripped. After the trip, the 1A Steam Generator experienced a Lo-Lo level condition which automatically started the 1A and 1B Auxiliary Feedwater Pumps. There were no malfunctions of equipment needed to respond to the event. Event Cause: An electrical short in a capacitor located within the cabinet containing the lA Steam Generator main feedwater supply valves control circuitry caused a loss of electrical power to the control circuitry for these valves. Corrective Action: Failed components were replaced. McGuire will evaluate possible design changes to prevent a capacitor failure from causing a reactor trip due to a loss of electrical power to process control cabinet circuitry.
369 | 3692005006 | 2005-12-17 | QP5 | Excessive Feedwater Flow | [13 empty] | X | [30 empty] | X | McGuire 1 | P | WE | PO | 100 | Unit Status: At the time of the event, both Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On December 17, 2005, the 1A Steam Generator experienced High-High water level when its controlling channel for main feedwater flow failed low. A main feedwater isolation occurred along with a turbine trip, trip of both CF pumps, automatic start of the motor driven CA pumps, and reactor trip. All safety systems needed to respond to this event operated as designed. This event is considered to be of no significance to the health and safety of the public. Event Cause: The cause of this event was intermittent degraded voltage to transmitter 1A SG Channel 1 flow loop (1CFFT5000). Corrective Action: Selected components were replaced. Lessons learned from this event will be incorporated in appropriate training to further strengthen operator response time to steam generator level deviations.
369 | 3692008002 | 2008-06-26 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | McGuire 1 | P | WE | PO | 100 | Unit Status: At the time of the event Unit 1 and 2 were in Mode 1 at 100% power. Event Description: On June 26, 2008, the 1B Reactor Coolant (NC) pump motor tripped when the 6900 Volt feeder and safety breaker over-current protective relays sensed a ground fault which in turn caused a Unit 1 Reactor trip due to low NC system flow sensed by the Reactor Protection system. Unit 1 returned to Mode on June 29, 2008. This event is considered to be of no significance with respect to the health and safety of the public. Event Cause: Electrical testing determined an NC pump motor surge capacitor had shorted to ground. The cause of the failed surge capacitor was determined to be improper design. Corrective Actions: The failed surge capacitor was replaced. Replace all the Unit 1 NC pump motor surge capacitors during the Fall 2008 refueling outage. Replace all existing surge capacitors with a more robust design. Perform a detailed electrical system analysis to determine if NC pump motor surge capacitors can be eliminated.
369 | 3692010003 | 2010-06-12 | QR6 | Manual Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 44 | Event Description: On June 10, 2010, Unit 1 Shutdown Bank "B" Rod N7 dropped fully into the core. On June 12, 2010, Unit 1 Shutdown Bank "B" Rod J13 dropped fully into the core while Rod N7 was still dropped. As directed by procedures, Operators initiated a Unit 1 Reactor trip by manually actuating the Reactor Protection System. Subsequent to tripping Unit 1, the 1A and 1B Motor Driven Auxiliary Feedwater Pumps were manually actuated to maintain Steam Generator levels. Event Cause: A regulation card in a Rod Control System Power Cabinet experienced an intermittent connection due to a degraded solder joint. This intermittent connection caused a drop in the current supply to the Control Rod Drive Mechanisms (CDRMs) for Unit 1 Shutdown Bank "B" Rod N7 and Unit 1 Shutdown Bank "B" Rod J13. Current dropped to levels which allowed the CRDM grippers to drop Rods N7 and J13 into the core. Corrective Actions: The degraded Rod Control System Power Cabinet regulation card was replaced. Additional preventative maintenance strategies will be evaluated for identifying degraded solder joints on cards in the Rod Control System Power Cabinets. Replacement of selected cards in the Rod Control System Power Cabinets with an upgraded card will be evaluated.
369 | 3692011002 | 2011-01-20 | QR6 | Manual Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 28 | On January 20, 2011, while shutting down Unit 1 and Unit 2, operators experienced a loss of feed water (CF) to the Unit 1 Steam Generators. At the time of the event, Unit 1 was at 28% power and the operating crew was transferring steam supplies for the Unit 1 "B" (1B) CF Pump Turbine (CFPT) from the normal steam supply to the alternate steam supply. This required opening valve 1HM-95 to supply steam to the 1B CFPT while monitoring several parameters. Upon opening 1HM-95, the 1B CF pump discharge pressure increased to the trip set point and 1B CF pump tripped on high discharge pressure resulting in a loss of all CF flow. This was followed by an automatic main turbine trip and a manual trip of the reactor. The root cause for the CF pump trip is the use of equipment for a purpose it was not designed. Transferring steam supplies to the 1B CFPT uses a gate valve (1HM-95) which is not designed for throttling. Actions will be taken to discontinue the use of 1HM-95 as a throttle valve and utilize the new CFPT governor steam supply controls for governor modulation.
369 | 3692013001 | 2013-02-21 | QR5 | Turbine Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | On February 21, 2013 Unit 1 tripped (Reactor Protection System actuation) from 100% power as a result of a turbine trip signal initiated after operating main feedwater system (CF) pumps tripped. The CF pumps tripped as a result of the operating Condensate Booster Pumps (CBPs) tripping on emergency low suction pressure following an inadvertent trip of the 1C3 Heater Drain Tank (HDT) Pump. The 1A and Turbine Driven Auxiliary Feedwater System (CA) pumps automatically started (Engineered Safety Feature actuation) as designed following the CF pumps tripping. The 1B CA pump was removed from service prior to the event to support maintenance.<br /><br /> The 1C3 HDT Pump was inadvertently tripped by an operator investigating the cause of an extinguished "on" indicating light bulb which is part of the HDT pump start/stop pushbutton switch. The cause of the HDT pump trip was attributed to an administrative procedure that did not explicitly prohibit intrusive investigation of light bulbs having transient/trip potential. The HDT pump trip caused a secondary system pressure transient that resulted in premature tripping of the CBPs which ultimately led to the reactor trip and CA pump auto-start. The CBP trip was caused by inadequate venting of CBP Suction Header Pressure Switches (PS) and an accumulation of air voids in PS process tubing due to an inadequate slope configuration.<br /><br /> Immediate actions were taken to revise an administrative procedure to prevent intrusive investigation of bulbs having transient/trip potential. The slope of process tubing to the CBP suction header PSs was corrected and the PSs were vented, calibrated, and verified functional. Planned action will be taken to ensure the condensate system (CM) is filled and vented and a hotwell pump is running prior to venting the CBP suction header PSs.
369 | 3692013003 | 2013-11-14 | QR6 | Manual Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | On November 14, 2013, at 13:13, Unit 1 was manually tripped from 100% power due to 10 dropped control rods associated with Rod Control Power Cabinet 1AC. The remaining control rods fully inserted into the core following the manual reactor trip. Unit 1 was stabilized in Mode 3 at normal operating temperature and pressure. The motor-driven Auxiliary Feedwater Pumps 1A and 1B were manually started for steam generator level control. This event did not impact public health and safety.<br /><br /> The cause of the event was an inadequate modification, resulting in an over-voltage protection (OVP) setpoint too close to the normal output of both the primary and backup -24 VDC rod control power supplies. The design called for the OVP function to be implemented with an installed jumper configuration that set the OVP setpoint too close to the normal output voltage.<br /><br /> Actions were taken to replace other Unit 1 power supplies with available power supplies that will not shut down under similar conditions. Due to limited spares, immediate replacement was limited to all applicable primary supplies and two backup supplies on Unit 1. The remaining backup power supplies installed in Unit 1 and the susceptible Unit 2 power supplies will be replaced as part of the planned corrective actions.
369 | 3692018001 | 2018-02-16 | QR8 | Spurious Reactor Trip | [45 empty] | McGuire 1 | P | WE | PO | 100 | At 1014 [EST] hours on February 16, 2018, with Unit 1 in Mode 1 at approximately 100 percent power, the reactor was tripped when the 1B Reactor Auxiliary Trip Breaker was actuated during Train B Solid State Protection System (SSPS) testing. The trip was uncomplicated with all systems responding normally post-trip. Operations manually started the motor driven auxiliary feedwater pumps. The turbine driven auxiliary feedwater pump auto-started on low low steam generator level in two out of four steam generators. A Feedwater Isolation occurred as designed due to the Reactor Trip and low reactor coolant system average temperature. <br /><br /> The cause was determined to be: An improper discretionary action to perform hands on verification of the reactor trip breaker position on the part of the technician. This intrusive action was not required nor directed by the SSPS procedure. <br /><br /> The cause investigation did not identify any process, scheduling, procedural, training issues with the SSPS task, or component labeling issues at the control rod drive motor generator set output breakers, that directly influenced technician's decision to take the intrusive action resulting in the reactor trip.
369 | 3692019001 | 2019-05-03 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | McGuire 1 | P | WE | PO | 100 | At 1554 [EST] hours on May 3, 2019, with Unit 1 in Mode 1 at approximately 100 percent power, the reactor automatically tripped on Over Temperature Delta Teniperature following a pressure transient in the Reactor Coolant System. The trip was uncomplicated with all systems responding normally post-trip. Operations manually started the motor driven auxiliary feedwater pumps.<br /><br /> The cause was determined to be: The Control Room Supervisor and Reactor Operators involved failed to adhere to established administrative standards. <br /><br /> The Control Room Supervisor and Reactor Operators involved failed to perform the correct level of pre-job brief in accordance with administrative standards. Adherence to the administrative standards would have ensured proper consideration of human factors and contingency actions prior to performing manual manipulations of the pressurizer pressure master controller. The licensed operators involved were removed from duty and are being remediated.<br /><br /> Planned Action: Complete remediation of the licensed operators.
370 | 3701987003 | 1987-01-20 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | McGuire 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON JANUARY 20, 1987, AT 0953, WHILE UNIT 2 WAS OPERATING AT 100% POWER, THE UNIT 2 'HOTWELL LEVEL EMERGENCY LO' LEVEL INSTRUMENTATION ACTUATED A 2 OUT OF 3 TRIP LOGIC ALARM TRIPPING THE HOTWELL PUMPS (HWPS) AND THE CONDENSATE BOOSTER PUMPS (CBPS). MAIN FEEDWATER (CF) PUMPS 2A AND 2B THEN TRIPPED FOLLOWED BY A MAIN TURBINE AND REACTOR TRIP WHICH WAS DUE TO THE LOSS OF BOTH CF PUMPS. AT APPROXIMATELY 0955, FOLLOWING THE REACTOR TRIP, CF PUMP TURBINE (CFPTS) 2A AND 2B BEGAN TO OVERSPEED WHICH SUBSEQUENTLY CAUSED THE FAILURE OF THE SEALS IN CF PUMP 2A, ALLOWING WATER TO ENTER THE LUBE OIL SYSTEM. THE LACK OF LUBE OIL TO THE PUMP BEARINGS CAUSED THEIR DESTRUCTION AND SUBSEQUENT PUMP FAILURE. ALSO, THE OVERSPEEDING OF CFPT 2B CAUSED SEVERAL SHARP RISES IN THE DISCHARGE PRESSURE OF CF PUMP 2B WHICH IS BELIEVED TO BE THE APPARENT CAUSE OF A WATER HAMMER THAT RESULTED IN PIPING SUPPORT DAMAGE AROUND CF PUMP 2B. THIS INCIDENT IS ATTRIBUTED TO AN EQUIPMENT MALFUNCTION. THE INITIAL CAUSE OF THE TRANSIENT WAS A SPURIOUS ACTUATION OF THE 'HOTWELL LEVEL EMERGENCY LO' HOTWELL LEVEL INSTRUMENTATION. THERE WAS NO SUPPORTING EVIDENCE INDICATING THAT AN ACTUAL LEVEL TRANSIENT OCCURRED IN THE HOTWELL. UNIT 2 RETURNED TO POWER OPERATION ON JANUARY 24, 1987, BUT WAS HELD AT 58% POWER UNTIL CF PUMP 2A WAS REPAIRED.
370 | 3701987016 | 1987-09-06 | QR5 | Turbine Trip | [45 empty] | McGuire 2 | P | WE | PO | 100 | POWER LEVEL - 100%. AT 100% POWER ON SEPTEMBER 6, 1987 AT 1035, A UNIT 2 REACTOR/TURBINE TRIP OCCURRED DUE TO HIGH PRESSURIZER PRESSURE WHEN MAIN TURBINE GOVERNOR AND INTERCEPT VALVES CLOSED AS DIRECTED BY THE DIGITAL ELECTRO-HYDRAULIC (DEH) TURBINE CONTROL SYSTEM. THE GOVERNOR AND INTERCEPT VALVE CLOSE SIGNAL WAS GENERATED BY LOSS OF POWER TO A DEH TURBINE CONTROL SYSTEM RELAY WHEN POWER WAS LOST TO KXB. POWER WAS LOST ON AUXILIARY POWER PANELBOARD KXB DUE TO AN OVERCURRENT FAULT BREAKER TRIP CAUSED BY A GROUNDED MOTOR LEAD CONNECTOR (INSULATING TAPE HAD WORN ALLOWING CONNECTING LUG TO GROUND TO MOTOR FRAME) ON INSTRUMENT AIR (VI) COMPRESSOR A. OPERATIONS IMPLEMENTED THE REACTOR TRIP PROCEDURE. KXB FROM STATIC INVERTER KXB. UNIT 2 RETURNED TO MODE 1, POWER OPERATION, ON SEPTEMBER 7, AT 2110. THE CONNECTING LUG WAS REINSULATED IN THE CONNECTION BOX AND THE COMPRESSOR WAS RETURNED TO SERVICE. VI COMPRESSOR MOTORS B&C WILL BE INSPECTED FOR SIMILAR CONDITION. SIMILAR MOTORS IN OTHER APPLICATIONS WILL BE INSPECTED AND RETAPED AS NECESSARY.
370 | 3691987021 | 1987-09-16 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | McGuire 2 | P | WE | PO | 100 | POWER LEVEL - 000%. ON SEPTEMBER 16, 1987, INSTRUMENT AND ELECTRICAL (IAE) AND RELAY PERSONNEL WERE PERFORMING A TEST TO VERIFY OPERATION OF LOCKOUT RELAYS AND LIGHTS ON WHICH WIRING MODIFICATIONS HAD BEEN PERFORMED. AT 1016, WHILE A LOCKOUT RELAY AND ITS ASSOCIATED LIGHTS WERE BEING TESTED, 2 ASSOCIATED RELAYS ENERGIZED CAUSING THE 1B BUSLINE BREAKERS TO TRIP RESULTING IN A UNIT 1 BLACKOUT. THE BLACKOUT CAUSED A LOSS OF POWER TO INSTRUMENT AIR (VI) COMPRESSORS WHICH RESULTED IN THE CLOSURE OF THE UNIT 2 MAIN FEEDWATER REGULATOR VALVES. UNIT 2 SUBSEQUENTLY TRIPPED ON LOW-LOW STEAM GENERATOR LEVEL AT 1021. OPERATIONS RESTORED NORMAL POWER TO UNIT 1 BY ENERGIZING THE 1B BUSLINE AND STABILIZED UNIT 2 FROM THE REACTOR TRIP BY 1045. THE CAUSE OF THE EVENT WAS PERSONNEL ERROR. PLANNED CORRECTIVE ACTIONS INVOLVING EVALUATION OF VI COMPRESSOR ALIGNMENTS, COMMUNICATING IMPORTANCE OF USING AND NOT EXCEEDING PROCEDURES, AND A DESIGN REVIEW OF THE POWER SUPPLY ALIGNMENTS FOR VI COMPRESSORS HAVE BEEN INITIATED.
370 | 3701987019 | 1987-11-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 11/05/87 AT 0646, THE UNIT 2 REACTOR TRIPPED DUE TO A LOW-LOW LEVEL IN STEAM GENERATOR 2B. THE MAIN TURBINE TRIPPED BECAUSE OF THE REACTOR TRIP. OPERATIONS (OPS) DETERMINED THAT AN AIR BUBBLE FROM A UNIT 1 HEAT EXCHANGER HAD MIGRATED FROM UNIT 1 TO UNIT 2 THROUGH CROSSOVER PIPING TO THE UNIT 2 MAIN FEEDWATER PUMP TURBINE (CFPT) 2B CONDENSER WATERBOX. THE AIR BUBBLE CAUSED A LOSS OF COOLING EFFICIENCY IN THE CONDENSER RESULTING IN A LOW VACUUM IN THE CFPT 2B CONDENSER. CFPT 2B TRIPPED INITIATING A REACTOR/TURBINE RUNBACK; THE DIGITAL ELECTRO HYDRAULIC TURBINE CONTROL SYSTEM DID NOT RESPOND CORRECTLY, AND THE REACTOR TRIPPED ON A STEAM GENERATOR 2B LOW-LOW LEVEL SIGNAL. OPS VENTED THE AIR OUT OF THE MAIN FEEDWATER PUMP CONDENSER AND VACUUM WAS RESTORED TO THE CFPT 2B CONDENSER, AND UNIT 2 ENTERED MODE 1 (POWER OPERATION) AT 0945 ON 11/06/87. DURING AIR SPARGING OF UNIT 1 CONTAINMENT SPRAY (NS) HEAT EXCHANGER (HX) 1A, MECHANICAL MAINTENANCE PERSONNEL DID NOT OPEN THE HX VENT VALVE AS INSTRUCTED IN HE PROCEDURE; THEREFORE, THIS EVENT IS CLASSIFIED AS PERSONNEL ERROR. PERFORMANCE WILL INITIATE A SAFETY REVIEW OF THE NS HX CLEANING PROCESS RELATIVE TO AIR LEAKAGE INTO THE NUCLEAR SERVICE WATER (RN) HEADER AND OTHER RN COMPONENTS.
370 | 3701987021 | 1987-11-30 | QR5 | Turbine Trip | [45 empty] | McGuire 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON 11/30/87 AT APPROXIMATELY 1730, THE UNIT 2 MAIN GENERATOR BREAKERS OPENED, SHORTLY AFTER A UNIT 2 GENERATOR STATOR COOLING (KG) FLOW DIFFERENTIAL PRESSURE (D/P) LOW ALARM WAS DISPLAYED ON THE OPERATOR AID COMPUTER (OAC); THE TURBINE THEN TRIPPED ON OVERSPEED, AND A REACTOR TRIP RESULTED. THE REACTOR TRIP WAS DUE TO REVERSED WIRING ON THE LOW AND EMERGENCY LOW GENERATOR KG D/P SWITCH CIRCUITRY, COMBINED WITH CALIBRATION DRIFT ON THE LOW GENERATOR KG D/P SWITCH AND D/P GAUGE. UNIT 2 STABILIZED FROM THE REACTOR TRIP BY 1830. INSTRUMENT AND ELECTRICAL (IAE) CORRECTED THE WIRING PROBLEM ON DECEMBER 1, 1987, AND UNIT 2 WAS RETURNED TO POWER OPERATION. THIS EVENT IS ASSIGNED A CAUSE OF OTHER BECAUSE THE ORIGIN OF THE INCORRECT WIRING CONFIGURATION ON THE LOW AND EMERGENCY LOW GENERATOR KG FLOW D/P SWITCH CIRCUITS COULD NOT BE DETERMINED AND BECAUSE THE CALIBRATION DRIFT OF THE LOW GENERATOR KG FLOW D/P SWITCH AND PRESSURE GAUGE WAS DUE TO EQUIPMENT MALFUNCTION. UNIT 1 WILL BE CHECKED AND WIRING CORRECTION WILL BE MADE AS NECESSARY. PREVIOUSLY PLANNED KG SYSTEM MODIFICATION WILL BE REVIEWED TO ENSURE CRITICAL KG PRESSURE SWITCHES ARE REPLACED. LOOP CALIBRATIONS FOR THE GENERATOR KG FLOW D/P LOW AND EMERGENCY LOW CIRCUITRY WILL BE DEVELOPED.
370 | 3701988001 | 1988-01-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 2 | P | WE | PO | 100 | On 01/12/88 at 0420, a Unit 2 Steam Generator (S/G) C Level Deviation Alarm was received in the Control Room. Operations (OPS) personnel noticed Main Feedwater (CF) flow to S/G C was decreasing while CF Flow Control to S/G C, valve 2CF-20, had an open demand signal. OPS reduced Turbine Generator load and operated both CF pumps in manual. S/G 2C level returned to normal. Shortly after, the level in S/G 2C began to decrease and valve 2CF-20 indicated it was closed. At 0425:01, OPS tripped the Turbine and Reactor. The decreasing level in S/G 2C was due to valve 2CF-20 failing in the closed position which was due to a loss of air supply to the valve. OPS implemented the Reactor Trip recovery procedure. The air regulators on all 4 S/G CF flow control valves were replaced. Unit 2 was returned to power operation on 01/13/88 at 0211. This event is assigned a cause of Design and Construction/Installation deficiency because the air regulator for valve 2CF-20 failed due to it being improperly mounted. The mounting bracket used was designed for a field mount model and adapted for a panel mount regulator. The Unit 1 regulators will be replaced. Controls will be developed to prevent panel mounted regulators being used in field applications. The Critical Valve List will be reviewed to identify air regulators critical to plant operation and an inspection will be performed to change out regulators as needed.
370 | 3701988008 | 1988-07-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 2 | P | WE | PO | 100 | On 7/31/88 at 1917, valve 2CF-32AB, 2A Steam Generator main Feedwater Regulating Valve, failed in the closed position. Preventive Maintenance Inc. (PMI) personnel were removing a fan from above valve 2CF-32AB actuator when the fan was set on the electrical cable attached to valve 2CFSVO320, Feedwater Flow (CF) to Steam Generator (S/G) 2A Solenoid, and broke a wire in the cable. Valve 2CFSVO320 deenergize which failed the air supply to the actuator for valve 2CF-32AB, causing the valve to fail closed. With CF flow isolated to S/G 2A, the water level began to rapidly decrease. At 1918, Operations manually tripped the Unit 2 Reactor to prevent a automatic trip. Auxiliary Feedwater (CA) Motor Driven Pumps 2A and 2B auto-started at 1918 in response to the S/G 2A Low Low level signal. Operations stabilized Unit 2 at approximately 1948. Instrumentation and electrically repaired the broken wire on valve 2CFSVO320 and returned valve 2CF-32AB to service at approximately 2330. Operations returned Unit 2 to power operation at approximately 1015 on 08/1/88. This event is assigned a cause of Personnel Error because while removing a fan from above the valve 2CF-32AB actuator, PMI Mechanic A lost his footing and accidentally set the fan on the electrical cable to valve 2CFSVO320 causing a lo s of power to valve 2CFSVO320 and a resultant loss of air supply to valve 2CF-32AB.
370 | 3701989001 | 1989-03-03 | QR3 | Reactivity Control Imbalance | [45 empty] | McGuire 2 | P | WE | PO | 100 | On March 3, 1989 at 0819, while Operations personnel were performing a routine Rod Cluster Control Assembly Movement Test, on the Unit 2 Rod Control system, a High Negative Neutron Flux Rate Reactor Trip occurred because of control rods dropping into the core. The Turbine Generator automatically tripped because of the Reactor Trip. Operations personnel implemented the Reactor Trip recovery procedure to recover from the transient. At 0855, Operations personnel made the required notification to the NRC. Since it could not be determined what caused the Control Rods to drop, an Independent Technical Review was performed on the event; consequently, a decision was made by Station Management personnel at approximately 0230 on March 4, 1989 to restart the Reactor. Unit 2 was returned to Power Operation on March 4, 1989 at 0555. This event is assigned a cause of Unknown because it could not be determined during the course of this investigation what caused the control rods to drop into the core.
370 | 3701989002 | 1989-03-14 | QP2 | Partial Loss of Feedwater Flow | [10 empty] | X | [30 empty] | X |  |  |  | McGuire 2 | P | WE | PO | 98 | On March 14, 1989 at 0412, the Unit 2 Train B Main Feedwater Pump Turbine (CFPT) tripped. A Unit 2 Runback resulted because of the loss of the 2B CFPT. Operations personnel implemented procedure AP/2/A/5500/03, Load Rejection, and had completed all immediate actions when valve 2CM-420, Generator Load Rejection Bypass, failed to open as required on a runback signal. The failure of valve 2CM-420 to open prevented additional suction flow to be provided for the 2A CFPT, and consequently, levels in B and C Steam Generators (SGs) began to decrease. At 0415, the Unit 2 Reactor tripped because of a low-low level in 2B SG. The Main Turbine tripped because of the Reactor Trip. All three Auxiliary Feedwater pumps automatically started as required to recover SG levels. Unit 2 was in Mode 1, Power Operation, at 98% power at the time this incident occurred. This event has been assigned a cause of Other, Equipment Failure/Malfunction because of a failure of suction pressure switches on 2B CFPT and a broken air supply line to valve 2CM-420.
370 | 3701989003 | 1989-04-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 2 | P | WE | PO | 100 | On April 6, 1989 at 0503, a Unit 2 Reactor Trip occurred because of Low-Low Level in Steam Generator 2C. The unit was operating in Mode 1 (Power Operation) at 100% power prior to the trip. The Low-Low Level condition was caused by the failure of the bellows in the positioner for valve 2CF-20, Steam Generator 2C Main Feedwater (CF) Regulating Valve. The Turbine Generator automatically tripped because of the Reactor Trip. Operations personnel implemented the Reactor Trip recovery procedure to recover from the transient. At 0542, Operations personnel made the required notification to the NRC. Instrumentation and Electrical personnel completed the replacement of the failed feedback bellows in the positioner for valve 2CF-20 and the other 3 Unit 2 S/G CF flow control valves at 1459. The failed bellows was sent to the Duke Power Company Metallurgy Laboratory for analysis. The Refueling Outage Preventive Maintenance (PM) for the CF regulating valves will be revised to replace the feedback bellows assemblies on these valves. Unit 2 was returned to Power Operation on April 7, 1989 at 0123. This event is assigned a cause of Equipment Failure because of the failure of the feedback bellows in the positioner for valve 2CF-20.
370 | 3701991007 | 1991-07-14 | QR3 | Reactivity Control Imbalance | [45 empty] | McGuire 2 | P | WE | PO | 90 | On July 12, 1991, operations (OPS) personnel and Instrumentation and Electrical (IAE) personnel were performing the quarterly calibration on Power Range Neutron Flux Channels for Unit 2 to correspond with current Incore/Excore Correlation values. During this calibration, a Quadrant Power Tilt Ratio (QPTR) alarm was received after the first Neutron Flux Channel was returned to service. To comply with Technical Specifications (TSs), a load reduction to 91 percent power was required. During the subsequent power reduction, Group 1 of Control Rod Bank D failed to move properly causing a Control Rod misalignment greater than TS limits. To comply with TSs, Boron was added and the Control Rods were realigned. An Axial Flux Difference (AFD) oscillation resulted from the movement of the Control Rods and power reduction. Since the Control Rods would not move properly they were unavailable to dampen the oscillation. IAE personnel attempted to repair the Control Rod problem during the next day, but were unable to do so. At 0658, on July 14, 1991, OPS personnel initiated a manual Reactor Trip prior to exceeding Ts limits for AFD. OPS personnel implemented the Reactor Trip recovery procedure to recover from the transient. Unit 2 was in Mode 1 (Power Operation) at 90.5 percent power at the time of the Reactor Trip. This event is assigned a cause of Equipment Failure because the Control Rods would not properly insert into the core. Subsequent repairs were made to correct the problem and the Unit returned to Power Operation on July 16, 1991, at 0608.
370 | 3701991010 | 1991-09-25 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 2 | P | WE | PO | 100 | A Unit 2 Reactor T rip was manually initiated at 1450:50 on September 25, 1991. Prior to the event, Unit 2 was operating in Mode 1 (Power Operation) at 100 percent power. The trip was manually initiated by Operations Control Room personnel upon receipt of alarm panel 2AD-4, annunciator C-4 (Steam Generator D flow mismatch low CF flow). The annunciation resulted from Main Feedwater valve 2CF-26, Steam Generator D Containment Isolation Valve, movement to its fail-safe (closed) position upon loss of power to the controlling solenoid. The loss of power was caused by a voltage surge that blew fuse BA 11-12 in Terminal Board (TB) 1209. The voltage surge was caused by grounding both legs of Vital Battery EVCD as a result of the replacement of the control board indicator lamp for valve 2VX-33B, Containment Sample Supply Inside Isolation. This event has been assigned a cause of Possible Design, Manufacturing, Construction/Installation Deficiency because of damaged insulation resulting in a positive leg ground on the solenoid associated with valve 2CF-26. Corrective actions include inspection of surplus solenoids to ensure serviceable condition of the insulation.
370 | 3701991012 | 1991-11-08 | QR3 | Reactivity Control Imbalance | [45 empty] | McGuire 2 | P | WE | PO | 100 | On November 8, 1991, at approximately 1142, Operations (OPS) Control Room personnel were performing the monthly procedure PT/2/A/4600/01, Rod Cluster Control Assembly Movement Test. Shutdown Banks A and B moved properly. However, Shutdown Bank C dropped into the core as the Reactor Operator at the controls attempted to step this bank in. The Solid State Protection system subsequently generated a Negative Flux Rate Trip signal which automatically tripped the Reactor. OPS Control Room personnel also initiated a Manual Reactor Trip as required by the Reactor Trip procedure. Diesel Generator 2B was running at the time and the emergency breaker for Diesel Generator 2B opened due to an overload when a low-low level in Steam Generator A caused the Auxiliary Feedwater and Nuclear Service Water Pumps to start. Unit 2 was in Mode 1 (Power Operation) at 100 percent power prior to the trip. The Unit performed as expected during the transient and there were no nuclear safety significant problems. An investigation was performed and it was determined that an electronic equipment failure within the Shutdown Bank C input logic circuit had caused the stationary rod gripper coils to stay de-energized too long. An independent safety review was performed and it was determined that it was safe and prudent to restart the Reactor. Unit 2 was returned to Mode 1 on November 9, 1991, at 0510. This event is assigned a cause of Equipment Failure due to an electronic failure in the Rod Control system circuitry.
370 | 3701992004 | 1992-03-21 | QP5 | Excessive Feedwater Flow | [45 empty] | McGuire 2 | P | WE | PO | 63 | On March 21, 1992, at 0609, Unit 2 experienced a Turbine Trip/Reactor Trip as a result of a Hi Hi Steam Generator level on Steam Generator 2C. Investigation of the Reactor Trip revealed a failure of the valve positioner linkage on valve 2CF-20. Valve 2CF-20 is the Steam Generator Main Feedwater Control valve for Steam Generator 2C. The valve positioner on valve 2CF-20 had broken which resulted in erroneous "valve closed" feedback to the valve controller. Therefore, the controller opened valve 2CF-20 further, which increased the feedwater flow to SG 2C, above the required level. The Unit was in Mode 1 (Power Operation) at 63 percent power prior to the trip. Notification was made to the NRC at 0650, on March 21, 1992. This event has been assigned a cause of Equipment Failure due to a possible installation deficiency, because it cannot be conclusively determined what caused valve 2CF-20 valve positioner to fail. The valve positioner was replaced and the unit returned to Mode 1 on March 21, 1992, at 1557.
370 | 3701992006 | 1992-04-09 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | McGuire 2 | P | WE | PO | 100 | On April 9,1992, at 1303, Unit 2 experienced a transient which resulted in a Reactor Trip from 100 percent power. Pressure transmitter, 2CMPT5190, which controls valve 2CM-58, Condensate Cooler Bypass, failed low on a high differential pressure causing valve 2CM-58 to close. Condensate Booster Pumps A and C were in service and tripped on emergency low pump suction pressure. Hotwell Pump B automatically started. Condensate Feedwater Pump Turbines (CFPT) A and B tripped upon loss of all Condensate Booster Pumps. Generator Load Rejection Bypass Control Valve 2CM-420 did not adequately modulate as Condensate Booster Pump suction header pressure decreased. The loss of both CFPTs resulted in a Turbine Generator trip and subsequent Reactor trip. Units 1 and 2 were in Mode 1 (Power Operation) at 98 and 100 percent power, respectively, at the time of the event. Plant equipment responded as required and Operations personnel implemented procedure EP/2/A/5000/01, Reactor Trip or Safety Injection, and stabilized Unit 2 in Mode 3 (Hot Standby). This event is assigned causes of Equipment Failure and Unknown. The 4 hour notification was made to the NRC at 1518, on April 9, 1992, in accordance with procedure RP/0/A/5700/10, NRC Immediate Notification Requirements. The failed pressure transmitter was replaced.
370 | 3701992007 | 1992-05-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 2 | P | WE | PO | 100 | POWER LEVEL - 100%. ON MAY 20, 1992, UNIT 2 WAS OPERATING IN MODE 1 (POWER OPERATION) AT 100 PERCENT POWER. AT 2101, A UNIT 2 REACTOR TRIP OCCURRED DUE TO A LOW-LOW STEAM GENERATOR (S/G) LEVEL SIGNAL IN S/G 2A. THE LOW-LOW LEVEL CONDITION WAS CAUSED WHEN VALVE 2CF-32, S/G 2A MAIN FEEDWATER REGULATING VALVE, MOVED TO ITS FAIL-SAFE (CLOSED) POSITION UPON LOSS OF POWER TO A CONTROLLING SAFETY SOLENOID. THE LOSS OF POWER WAS CAUSED BY A FAILED FUSE IN THE CONTROL CIRCUITRY TO THE SOLENOID. THE TURBINE GENERATOR AUTOMATICALLY TRIPPED AS A RESULT OF THE REACTOR TRIP. OPERATIONS PERSONNEL IMPLEMENTED PROCEDURE EP/2/A/5000/01, REACTOR TRIP OR SAFETY INJECTION, AND STABILIZED UNIT 2 IN MODE 3 (HOT STANDBY). OPERATIONS PERSONNEL THEN IMPLEMENTED PROCEDURE OP/2/A/6100/02, CONTROLLING PROCEDURE FOR UNIT SHUTDOWN, BASED ON A DECISION BY OPERATIONS STAFF PERSONNEL TO BEGIN A SHUTDOWN OF UNIT 2 FOR S/G TUBE INSPECTION. UNIT 2 ENTERED MODE 5 (COLD SHUTDOWN) ON MAY 25, 1992, AT 0155. AN ANALYSIS OF THE FAILED FUSE WAS CONDUCTED BY THE DUKE POWER COMPANY APPLIED SCIENCE CENTER. THIS ANALYSIS INDICATED THE FUSE FAILED BY BRITTLE FRACTURE THROUGH THE FUSIBLE ALLOY BUTTON, ADJACENT TO THE EMBEDDED WIRE LOOP. THE FAILURE WAS THROUGH FUSIBLE MATERIAL CONTAINING GAS HOLES AND INTERGRANULAR CRACKING, INDICATING THE WIRE LOOP AND FUSIBLE ALLOY WERE NOT COMPLETELY BONDED. REPAIRS TO VALVE 2CF-32 WILL BE COMPLETED PRIOR TO UNIT 2 RETURNING TO SERVICE.
370 | 3701992009 | 1992-08-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 2 | P | WE | PO | 100 | On August 5, 1992, at 0323, while Unit 2 was operating in Mode 1 (Power Operation) at 100 percent power, a Reactor Trip occurred due to a Steam Generator (SG) Low-Low water level in SG 2B. The Low-Low level condition was caused when valve 2CF-23, SG 2B Main Feedwater Regulating Valve, moved to its fail-safe (closed) position upon loss of power to a controlling safety solenoid. This event is assigned a cause of Equipment Failure caused by loss of power due to a failed blocking diode which caused a blown fuse in the control circuitry to the solenoid. The Turbine Generator automatically tripped as a result of the Reactor Trip. Operations personnel implemented procedure EP/2/A/5000/01, Reactor Trip or Safety Injection, and stabilized Unit 2 in Mode 3 (Hot Standby). With the exception of several minor valve indication problems, all plant systems functioned properly. Repairs to valve 2CF-23 controlling solenoid valve were completed prior to Unit 2 returning to service.
370 | 3701992010 | 1992-08-24 | QR5 | Turbine Trip | [45 empty] | McGuire 2 | P | WE | PO | 100 | On August 24, 1992, at 1002:46, while operating in Mode 1 (power operation) at 100 percent power, Unit 2 experienced a Reactor Trip/Turbine Trip on Overtemperature Delta Temperature (OTDT). The initiating event was the loss of main Generator excitation caused by a failed indicating lamp in the circuit for the Generator Field Breaker. The contacts on the indicating-lamp base shorted electrically during an attempt to change the lamp. This caused the Field Breaker to open which caused the anticipatory protection circuit to pick up and; therefore, the Generator Power Circuit Breakers (PCBs) to open, initiating a full load rejection. Runback from the load rejection was not successful. No load conditions were achieved in approximately 30 minutes. This event has been assigned a root cause of Equipment Failure, due to failure of the indicating lamp associated with the circuit for the Generator Field Breaker. The indicating lamp and associated switch were replaced and appropriate measures will be taken to evaluate use of a different type lamp in an attempt to prevent recurrence of this problem.
370 | 3701993001 | 1993-02-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 2 | P | WE | PO | 100 | On February 22, 1993, at 0046, Unit 2 Control Room personnel reported hearing a sound resembling the 'harmonic vibrations' associated with the feedwater lines when operating at reduced load. The Senior Reactor Operator (SRO) directed the Reactor operator at the Controls (ROATC) to check the position of the Feedwater Control Valves. The ROATC discovered the Steam Generator (SG) 'C' feedwater flow was low and decreasing even though the controller output was increasing. A Turbine Generator load reduction was begun to compensate for the reduced feedwater flow. When the SG level approached the trip setpoint, the SRO instructed the ROATC to manually trip the Reactor which in turn caused an automatic Turbine trip. Subsequent investigation revealed that valve 2CF-20 (SG 'C' Feedwater Control Valve) failed to open on demand due to a signal air leak in the valve positioner pneumatic relay. Unit 2 was operating in Mode 1 (Power Operation) at 100 percent power at the time of the event. A cause of Equipment Failure has been assigned to this event. Corrective actions include replacement of all Feedwater Control Valve positioner pneumatic relays. In addition, a group of Nuclear Generation Department personnel previously working with the Secondary Valve Reliability Team are accelerating their review of problems associated with the Feedwater Control Valves in order to identify and correct the underlying causes.
370 | 3701993002 | 1993-03-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | McGuire 2 | P | WE | PO | 100 | A Unit 2 manual Reactor Trip was initiated by Operations Control Room Personnel after receipt of alarms indicating a low and decreasing feedwater (CF) flow to Steam Generator (SG) 2B. Control Room personnel assumed manual control of valve 2CF-23, Steam Generator 2B Main Feedwater Control Valve, and attempted to increase CF flow to SG 2B. The attempt was unsuccessful. As the SG water level approached 45 percent, the Senior Reactor Operator instructed the Reactor Operator at the Controls to manually exercise Reactor Trip Breakers A and B. The Reactor was tripped at 0416 on March 9, 1993. The manual Reactor trip was followed by an automatic Turbine Trip. Operations personnel immediately began recovery efforts. Unit 2 was operating in Mode 1 (Power Operation), at 100 percent power at the time of the event. An investigation revealed that the inner metallic bellows in the valve positioner relay for valve 2CF-23 failed as a result of fatigue cracking, causing the valve to close resulting in a loss of CF flow to SG 2B. Corrective actions included the replacement of all Unit 2 CF valve positioner relay bellows with relays which incorporate viton elastomer diaphragms as opposed to metallic bellows.
370 | 3701993008 | 1993-12-27 | QR3 | Reactivity Control Imbalance |  | X | [8 empty] | X |  |  |  |  | X | [23 empty] | X | [5 empty] | McGuire 2 | P | WE | PO | 100 | On December 27, 1993, Unit 2 experienced a loss of bus line 2B due to a failed insulator. This was followed by a failure of the Unit 2 Turbine Generator to runback. Bus line 2A subsequently tripped on an overcurrent condition. A Reactor Trip occurred at 2207 due to a Power Range High Flux Rate Signal, followed by a Turbine Generator trip and the opening of the 2A Generator breaker. This resulted in a loss of Unit 2 offsite power. The subsequent cooldown resulted in a Safety Injection and Main Steam (SM) line isolation at 2214. Valve 2SM-5, SM Isolation Valve Steam Line B, failed to close fully, resulting in the 2B Steam Generator emptying. Control Room personnel declared an Unusual Event at 2222. As a conservative measure, OPS Control Room personnel activated the Technical Support Center, Operations Support Center, and staffed the Emergency Operations Facility. Offsite power was restored to Unit 2 at approximately 2343. Causes of Possible Unanticipated Environmental Interaction, Vendor Fabrication Deficiency, Deficient Documentation, Inadequate Surveillance Program, and Inappropriate Action are assigned to the event. Unit 2 was in Mode 1 (Power Operation) at 100 percent power, prior to the event. Corrective actions included repairs to the failed SM isolation valve and replacement of the failed bus line insulator. Unit 2 returned to Mode 2 (Startup) operation on January 6, 1994, at approximately 2200.
370 | 3701996003 | 1996-05-22 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | McGuire 2 | P | WE | PO | 99 | Unit Status: Unit 2 - Mode 1 (Power Operation) at approximately 99 percent power. <br /><br /> Event Description: On May 22, 1996, at 0425, the Unit 2 Reactor tripped due to low Reactor Coolant (NC) system flow. The X phase in NC Pump Motor 2B stator shorted to ground, causing the motor circuit breakers to trip on high ground fault current <br /><br /> Event Cause: A cause of Design/Manufacturing Deficiency has been assigned in that the upper end turns of the stator windings were not sufficiently secured to the stator surge ring. This allowed excess movement and vibration in the windings and subsequent degradation of the insulating material on the windings. This degradation of the insulating material resulted in the ground fault on the X-phase of the stator winding. <br /><br /> Corrective Actions: NC Pump Motors 2D and 2C are being replaced with refurbished motors and NC Pump Motor 2B has been inspected, removed, and sent offsite for complete rewind. NC Pump Motor 2A was replaced with a rewound motor during refueling outage 2EOC-10 and is therefore not suspect. The remaining NC Pump Motor IA will be replaced with a rewound motor during 1EOC-11 refueling outage. Engineering personnel will evaluate the current periodic maintenance program for adequacy in inspecting for evidence of this type of, impending failure.
370 | 3701997002 | 1997-07-11 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | McGuire 2 | P | WE | PO | 100 | Unit Status: Unit 2 - Mode 1 (Power Operation) at 100 percent power. Event Description: On July 11, 1997, at approximately 0516 hours, Unit 2 Reactor Coolant (NC) Pump 2D tripped due to a ground fault in the motor stator winding. Subsequently, the reactor tripped on low flow in one of four loops with reactor power greater than P-8. This event is not considered to be significant with respect to the health and safety of the public. Event Cause: A design/manufacturing deficiency existed in the NC Pump motor. The inadequate tying down of the stator wiring end turns to the stator surge ring was found to have allowed excessive vibration of the stator windings. This caused degradation of the winding insulation during years of operation. The degradation resulted in a ground fault in the stator windings. Corrective Action: The 2D motor stator was replaced with a rewound spare. The two remaining NC Pump motor stators will be replaced during upcoming refueling outages for their respective Units. Upon completion of the NC Pump motor stator replacements, a long-term motor maintenance and monitoring program, consisting of on-line partial discharge testing and off-line electrical testing, will be implemented.
370 | 3691997009 | 1997-09-06 | QC5 | Loss of Non-safety-Related Bus | [10 empty] | X | [28 empty] | X | [5 empty] | McGuire 2 | P | WE | PO | 100 | Unit Status: Units 1 and 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On September 6, 1997, at 2146, the trip of an auxiliary supply breaker, while the Units were in an abnormal alignment, caused the loss of non-vital power to plant components on both Units. For Unit 1, this resulted in a trip of both Main Feedwater Pumps followed by a main Turbine and subsequent Reactor trip. For Unit 2, it resulted in the closure of the Main Steam Isolation Valves followed by a Reactor trip on Pressurizer high pressure. Additionally, the power loss resulted in loss of the automatic operating function for the Pressurizer Power Operated Relief Valves (PORVs) on both Units, and loss of indication from the Process Radiation Monitor associated with one set of the Control Room Ventilation Outside Air Intakes. This equipment was inoperable for a period of 62.5 minutes, exceeding Technical Specification (TS) limits of 60 minutes without implementation of required actions. Event Cause: The cause of the breaker trip has been determined to be heat build-up created by a loose cable connection on the load side of the breaker, actuating breaker thermal trip units. The cause of the loose connection is a construction/installation deficiency. A contributing factor is management deficiency due to lack of establishing adequate preventive maintenance. Failure to implement required TS actions with regard to the Pressurizer PORVs and Process Radiation Monitor is attributed to failure of Control Room personnel to recognize the need to do so. With the loss of KXA, multiple Control Room indications were lost. Due to the absence of these indications and lack of procedural direction to alert them, actions were not taken within the one hour requirement. Corrective Action: Corrective actions include evaluation of preventative maintenance on shared vital and auxiliary control and instrumentation buses, development of procedures for plant operation during loss of instrumentation and control buses, enhancement of existing procedural guidance, and training for all licensed operations personnel. To be reported through EPIX
370 | 3701998001 | 1998-02-22 | QR5 | Turbine Trip | [45 empty] | McGuire 2 | P | WE | PO | 100 | Unit Status: Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: On February 22, 1998 at 20:54 an automatic turbine trip occurred on Unit 2 due to a voltage regulator failure. A turbine trip with the Unit above 48 percent power automatically resulted in an automatic reactor trip. Event Cause: Failure of the Unit 2 main turbine-generator voltage regulator resulted in a Unit 2 turbine-generator trip. The failed component was a firing drawer circuit card. Further root cause of the failure is being investigated. Corrective Action: The failed component of the turbine-generator voltage regulator was identified and replaced. A root cause analysis is being performed. Any new conclusions from the cause analysis will be input into an evaluation of current plans for complete replacement of the voltage regulator system. __________________ *_/ NPRDS no longer exists, the failure will be reported through EPIX
370 | 3701999004 | 1999-07-15 | QR8 | Spurious Reactor Trip | [45 empty] | McGuire 2 | P | WE | PO | 100 | Unit Status: Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: On July 15, 1999 at 14:44, an automatic turbine trip occurred on Unit 2 in response to an inadvertent reactor trip signal (P4). A turbine trip with the reactor power above 48 percent resulted in an automatic reactor trip. The P4 signal was generated during the replacement and testing of Reactor Trip Breaker A (RTA). SSPS Train A was in test alignment during the event; consequently and as designed Train A Auxiliary Feedwater Pump did not automatically start and the RTA breaker did not automatically open. Operations personnel manually opened Train A reactor trip breaker and started the Train A Auxiliary Feedwater Pump. Event Cause: A 'switch lever arm' was misaligned during an inspection of a refurbished breaker. The breaker was subsequently located in the RTA cubicle: Inadequate procedural guidance during breaker receipt inspection is considered the primary cause for the misalignment of the lever arm. A contributing cause is inappropriate action. The misaligned lever arm resulted in an inadvertent P4 signal during subsequent installation testing. Corrective Action: Procedure enhancements will be made to clearly direct the actions to be taken when inspecting the reactor trip breakers. The installation testing procedure will be revised to improve the sequence of steps. Management reviewed expectations for procedure performance and work practices with appropriate maintenance crews emphasizing attention to detail. NRC FORM 366 *_/NPRDS no longer exists, equipment failures will be reported through EPIX
370 | 3702000002 | 2000-11-15 | QR6 | Manual Reactor Trip | [45 empty] | McGuire 2 | P | WE | PO | 100 | Unit Status: At the time of the RPS and ESF actuation, both Unit 1 and Unit 2 were in Mode 1 at 100% Power. Event Description: On November 15, 2000, McGuire Unit 2 experienced a main turbine runback caused by actuation of over-power-delta-temperature (OPDT) and over-temperature-delta-temperature (OTDT) runback logic. The OPDT and OTDT channels actuated following the opening of electrical circuit breaker KXB-37 which supplies power to the logic circuitry. The channels were not actuated by a valid OPDT or OTDT condition. Subsequent to the runback, the Unit 2 reactor was manually tripped when the OPDT and OTDT runback signals did not clear. The manual trip of the Unit 2 reactor represented an actuation of the Reactor Protection System (RPS). Following the Unit 2 reactor trip, an Engineered Safety Feature (ESF) actuated when the 2A and 2B Motor Driven Auxiliary Feedwater (CA) Pumps and the Unit 2 Turbine Driven CA Pump auto-started due to Lo-Lo Steam Generator (SG) levels. Plant equipment necessary to safely shutdown the unit operated correctly. Event Cause: This event was initiated by the opening of electrical circuit breaker KXB-37 which supplies power to the OPDT and OTDT circuitry. The cause of the open KXB-37 breaker could not be determined. Therefore, the cause of this event is classified as unknown. Corrective Action: Circuit breaker KXB-37 was replaced.
370 | 3702001001 | 2001-07-18 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | McGuire 2 | P | WE | PO | 100 | Unit Status: On 7/16/01, Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On 7/16/2001, Maintenance personnel were performing routine maintenance on pressure instrumentation associated with the Unit 2 Main Steam Lines. Maintenance personnel in the Control Room area placed Channel 2 of 2B steam line pressure in test in the 7300 process protection cabinets as required per the test procedure. Maintenance personnel in the field then incorrectly isolated Channel 3 steam line pressure transmitter. This satisfied the 2 of 3 protection logic initiating a Main Steam Isolation Signal. Closing the Main Steam Isolation Valves resulted in a Reactor Trip and a Main Turbine Trip. An automatic start of the three Auxiliary Feedwater Pumps (CA) occurred as a result of decreasing Steam Generator levels. Event Cause: Lack of attention to detail has been determined to be the cause of the wrong pressure transmitter being isolated. Corrective Action: The Maintenance personnel were counseled on the importance of maintaining a high level of attention to detail. Component verification process enhancements were implemented.
370 | 3702002002 | 2002-08-22 | QR6 | Manual Reactor Trip | [7 empty] | X | [25 empty] | X | [11 empty] | McGuire 2 | P | WE | PO | 100 | Event Description: On August 22, 2002, a pipe plug located on the bottom side of an oil vapor extractor canister housing on the generator hydrogen system dual tower gas dryer skid failed, resulting in a rapid loss of hydrogen and a fire. In response, operators manually tripped the Unit 2 reactor and dispatched the fire brigade. The fire brigade isolated the hydrogen source and extinguished the fire. Following the reactor and turbine trip, steam generator water levels continued to increase as a result of the 2B main feedwater pump turbine not going to the rollback hold position. Once the steam generator water levels reached their high-high setpoint, the main feedwater pumps automatically tripped due to a feedwater isolation signal. The loss of the main feedwater pumps resulted in an automatic start of the 2A and 2B motor driven auxiliary feedwater pumps. Event Cause: Inadequate maintenance work practices and a lack of proper coordination of a functional verification were the causes for this event. Corrective Action: Inspected the fire affected area and performed appropriate repairs. Removed the Unit 2 dryer from service. Revised the dryer operating procedures to ensure proper functional verifications following maintenance. Other similar procedures and maintenance work practices will be reviewed and revised as appropriate.
373 | 3731987003 | 1987-01-26 | QR5 | Turbine Trip | [45 empty] | La Salle 1 | B | GE | PO | 89 | POWER LEVEL - 089%. ON JANUARY 26, 1987, AT 1135 HOURS, WITH UNIT 1 OPERATING AT ABOUT 89% POWER, A REACTOR SCRAM OCCURRED DUE TO A TURBINE GENERATOR CONTROL VALVE (TCV) FAST CLOSURE. THE TCV FAST CLOSURE WAS DUE TO A MAIN GENERATOR LOCKOUT CAUSED BY A GENERATOR 1 BACKUP GROUND TRIP RELAY (1659-MP020) TRIPPING. THIS RELAY TRIPS ON A GENERATOR VOLTAGE IMBALANCE AFTER ABOUT A 1 SECOND TIME DELAY. THE ROOT CAUSE OF THE 1659-MP020 RELAY TRIPPING WAS DUE TO A BAD SET OF SECONDARY CONTACTS AND A ROLLER WHEEL THAT WAS MOUNTED HIGHER THAN THE REST IN THE POTENTIAL TRANSFORMER COMPARTMENT THAT FEEDS THE 1659-MP020 RELAY. THE SAFETY CONSEQUENCES OF THIS EVENT WERE MINIMAL. THE PLANT PERFORMED AS EXPECTED AND NO EMERGENCY CORE COOLING SYSTEMS INITIATED OR WERE MANUALLY STARTED. THE MISALIGNED ROLLER WHEEL WAS REMOVED AND THE SLIDE CONTACTS WERE CLEANED OR REPLACED AS APPROPRIATE. ELECTRICAL CONTINUITY WAS VERIFIED ON ALL THE POTENTIAL TRANSFORMER SECONDARY CIRCUITS WHILE SHAKING THE BEDPLATES.
373 | 3731987005 | 1987-01-31 | QR5 | Turbine Trip | [45 empty] | La Salle 1 | B | GE | PO | 58 | POWER LEVEL - 058%. ON 1-31-87, AT 1119 HRS, WITH UNIT 1 OPERATING AT ABOUT 58% POWER, A REACTOR SCRAM OCCURRED ON TURBINE STOP VALVE (TSV) FAST CLOSURE. THE TSV FAST CLOSURE WAS DUE TO A GENERATOR LOCKOUT TRIP THAT WAS CAUSED BY LOSS OF THE ALTERNATOR EXCITER FIELD. THE ROOT CAUSE OF THE LOSS OF THE ALTERNATOR EXCITER FIELD WAS THE DEGRADATION OF THE COLLECTOR BRUSHES THAT SUPPLIES EXCITATION VOLTAGE TO THE ALTERNATOR EXCITER, WHICH IN TURN SUPPLIES EXCITATION TO THE MAIN GENERATOR. THESE SUPPLY BRUSHES WERE ALLOWED TO DEGRADE DUE TO A FAILURE OF THE ELECTRICAL MAINTENANCE (EM) DEPARTMENT TO INSPECT THEM ON A WEEKLY BASIS. THE SURVEILLANCE PROCEDURE USED TO PERFORM THIS INSPECTION WAS A NEW PROCEDURE, AS OF 6-3-86, FOR THE EM DEPARTMENT AND HAD NOT BEEN PERFORMED DUE TO A LOW PRIORITY ASSIGNED TO THE SURVEILLANCE. THE DEFECTIVE BRUSHES WERE REPLACED AND THE EM DEPARTMENT HAS REEVALUATED THEIR PRIORITY 3 SURVEILLANCES AND THE FOREMAN ARE SCHEDULING THE COLLECTOR BRUSH INSPECTION SURVEILLANCE ON A WEEKLY BASIS.
373 | 3731987014 | 1987-03-19 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | La Salle 1 | B | GE | PO | 54 | POWER LEVEL - 054%. AT 1352 HOURS ON MARCH 19, 1987, WITH UNIT 1 IN OPERATIONAL CONDITION 1 (RUN) AT 54% POWER, A REACTOR SCRAM OCCURRED DUE TO A GENERATOR LOCKOUT AND SUBSEQUENT TURBINE TRIP (TURBINE STOP VALVE CLOSURE). THE GENERATOR LOCKOUT WAS CAUSED BY AN ELECTRICAL FAULT THAT OCCURRED ON THE NON-SEGREGATED BUS DUCTS FEEDING THE 6.9 AND 4.1 KV LOADS FROM THE UNIT AUXILIARY TRANSFORMER (UAT) TR-141. THE APPARENT CAUSE OF THE EVENT HAS BEEN DETERMINED TO BE MOISTURE INTRUSION INTO ONE OF THE BUS DUCTS, POSSIBLY OCCURRING AT THE POINT WHERE THE BUS DUCT PENETRATES THE TURBINE BUILDING. THE PLANT PERFORMED AS EXPECTED DURING THE EVENT. ALL PROTECTIVE RELAYING FUNCTIONED PROPERLY TO INTERRUPT AND ISOLATE THE FAULT AS WELL AS SHUTDOWN THE REACTOR. AN ENGINEERING EVALUATION HAS BEEN PERFORMED TO ALLOW OPERATION OF UNIT 1 WITH ALL AUXILIARY POWER SUPPLIED BY THE SYSTEM AUXILIARY TRANSFORMER (SAT). THE UAT AND ASSOCIATED BUS DUCTS REMAIN ISOLATED TO ALLOW FOR THE REPAIR/REPLACEMENT OF THE 6.9 AND 4.1 KV BUS BARS, BUS DUCTS, AND WALL PENETRATIONS DAMAGED BY THE FAULT.
373 | 3731987022 | 1987-05-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | La Salle 1 | B | GE | PO | 59 | POWER LEVEL - 059%. AT APPROXIMATELY 2359 HOURS ON MAY 28, 1987 WITH UNIT 1 AT 59% POWER (STEADY-STATE) AND BOTH TURBINE DRIVEN REACTOR FEED PUMPS (TDRFP) IN THREE ELEMENT AUTOMATIC CONTROL, A LICENSED OPERATOR WAS CYCLING THE NUMBER ONE TURBINE BYPASS VALVE IN ACCORDANCE WITH LASALLE OPERATING SURVEILLANCE LOS-TG-W1. THE BYPASS VALVE WAS RAMPING CLOSED WHEN THE 'B' TDRFP DISCHARGE FLOW DECREASED FROM 4.0 MLB/HR TO 0.1 MLB/HR INITIATING A DECREASE IN REACTOR WATER LEVEL. CONTROL OF THE 'B' TDRFP USING THE MOTOR SPEED CHANGER WAS NOT OBTAINED PRIOR TO THE REACTOR SCRAMMING ON LOW LEVEL (LEVEL THREE, +12.5 INCH REACTOR WATER LEVEL). THE CAUSE OF THE LOSS OF THE 'B' TDRFP IS NOT KNOWN. ADDITIONAL TESTING WILL BE PERFORMED ON THE 'B' TDRFP PRIOR TO UNIT STARTUP. THIS EVENT IS REPORTABLE PURSUANT TO THE REQUIREMENT OF 10CFR50.73(A)(2)(IV) DUE TO THE AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM.
373 | 3731987032 | 1987-09-17 | QP5 | Excessive Feedwater Flow | [45 empty] | La Salle 1 | B | GE | SU | 5 | POWER LEVEL - 005%. AT 0322 HOURS ON SEPTEMBER 17, 1987, WITH UNIT 1 IN OPERATIONAL CONDITION 2 (STARTUP) AT 5% POWER, THE UNIT SCRAMMED ON A LOW REACTOR WATER LEVEL SIGNAL DURING A CONTROLLED SHUTDOWN. REACTOR WATER LEVEL INITIALLY INCREASED TO A LEVEL WHICH TRIPPED THE MOTOR DRIVEN REACTOR FEED PUMP. THIS CAUSED A LEVEL DECREASE TO OCCUR WHICH RESULTED IN A UNIT SCRAM ON A LOW REACTOR WATER LEVEL SIGNAL. THE ROOT CAUSE OF THIS EVENT IS THE DIFFICULTY OF CONTROLLING REACTOR WATER LEVEL WITH THE FEEDWATER REGULATING VALVE (FRV) AT LOW FLOW, LOW POWER CONDITIONS DUE TO SYSTEM DESIGN. THE SAFETY CONSEQUENCES OF THIS EVENT WERE MINIMAL. ALL ACTUATIONS OCCURRED AS DESIGNED DURING THIS EVENT. DURING THE NEXT REFUELING OUTAGE FOR EACH UNIT, A LOW LOAD REGULATING VALVE WILL BE ADDED TO THE FEEDWATER SYSTEM, WHICH SHOULD PROVIDE IMPROVED FEEDWATER AND REACTOR WATER LEVEL CONTROL AT LOW FLOW, LOW POWER CONDITIONS. THIS EVENT IS REPORTABLE PURSUANT TO THE REQUIREMENTS OF 10CFR50.73(A)(2)(IV) DUE TO THE AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM.
373 | 3731987038 | 1987-12-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | La Salle 1 | B | GE | PO | 78 | POWER LEVEL - 078%. AT 0955 HOURS ON DECEMBER 16, 1987, WITH UNIT 1 IN OPERATIONAL CONDITION 1 (RUN) AT 77.5% POWER, UNIT 1 SCRAMMED ON LOW REACTOR WATER LEVEL (LEVEL 3, +12.5 INCHES) DUE TO A LEVEL TRANSIENT CAUSED BY FEEDWATER HEATER STRING ISOLATIONS. THE STRING ISOLATIONS OCCURRED WHILE OPERATING PERSONNEL WERE ATTEMPTING TO RESTORE THE '12C' LOW PRESSURE FEEDWATER HEATER TO A NORMAL OPERATING CONDITION. THE ROOT CAUSE OF THE EVENT WAS A DESIGN DEFICIENCY IN THE '11C' FEEDWATER HEATER WHICH CAUSED IT TO BECOME 'AIR-BOUND'. THIS HEATER WAS ORIGINALLY INTENDED TO HAVE A CONTINUOUS OPERATING VENT, BUT THE VENT WAS NEVER INSTALLED. WITH THE '11C' HEATER 'AIR-BOUND,' THE '12C' HEATER BECAME OVERLOADED AND A HIGH LEVEL SITUATION OCCURRED (IN THE '12C' HEATER) WHICH INITIATED A STRING ISOLATION. THE SAFETY CONSEQUENCES OF THIS EVENT WERE MINIMAL. ALL REQUIRED ACTUATIONS OCCURRED AS EXPECTED. MODIFICATIONS ARE SCHEDULED DURING THE NEXT UNIT 1 AND UNIT 2 REFUELING OUTAGES TO INSTALL A CONTINUOUS OPERATING VENT ON THE '11/21' AND '12/22' FEEDWATER HEATERS. THIS EVENT IS REPORTABLE PURSUANT TO THE REQUIREMENTS OF 10CFR50.73(A)(2)(IV) DUE TO THE AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM.
373 | 3731989009 | 1989-03-02 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | La Salle 1 | B | GE | PO | 86 | On March 2, 1989, Unit 1 was operating in Run Mode at 86% power and Unit 2 was operating in Run mode at 89% power. At 2302 hours a phase to ground fault occurred at the "C" phase lightning arrestor on the primary side of the Unit 2 System Auxiliary Transformer. The fault was automatically isolated by the tripping of switchyard Oil Circuit Breakers (OCB) 4-6 and 6-1 and the Unit 2 feeder breakers. All loads being fed from the SAT transferred to the Unit 2 Unit Auxiliary Transformer (UAT) except for bus 243 which was supplied by the 2B Diesel Generator which satisfactorily auto-started on undervoltage. Unit 2 remained on-line after the incident. <br /><br /> As a result of the transient on the 345 KV system, the Unit 1 Generator Protective Relaying sensed a high generator differential current on phase A and isolated the Unit 1 generator. The Unit 1 turbine tripped on load rejection resulting in a reactor scram from Turbine Control Valve (TCV) fast closure. Unit 1 proceeded into normal post-scram conditions with the exception of the temporary loss of the Service Air Compressor and the plant process computer. Problems were also encountered with the resetting of the scram logic. <br /><br /> The cause of this event was the phase to ground fault that occurred from the lightning arrestor top cap to a sparger head on the transformer deluge system. This was evident from the arc burning identified at the top of the lightning arrestor and at the sparger head. Apparently, the fault was caused by debris that had blown onto the lightning arrestor lead. The lightning arrestor was replaced and the Unit 2 SAT was tested for operability and returned to service at 0330 on March 5, 1989. The Unit 1 generator differential relays were recalibrated and the unit was returned to service on March 5, 1989. <br /><br /> This report is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the automatic actuation of an Engineered Safety Feature.
373 | 3731990006 | 1990-03-28 | QR5 | Turbine Trip | [45 empty] | La Salle 1 | B | GE | PO | 100 | On March 28, 1990 at 0337 hours Unit 1 was in Operational condition 1 (Run) at 100% power. At this time the B phase insulator between the Unit 1 east/west main power transformers and the switchyard, failed and flashed over to ground. As a result of this flashover, the B and C phase differential current relays both tripped causing the Unit 1 main generator to lockout, which resulted in a main turbine trip. This immediately caused the Unit 1 reactor to scram. Three Safety Relief Valves actuated to control reactor pressure.<br /><br /> The B phase insulator was replaced on March 29, 1990. The remaining insulators were inspected and no significant problems were noted. One additional insulator was replaced due to minor chipping. Unit 1 was started back up and the generator synchronized to the grid at 0310 hours on March 31, 1990. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature system.
373 | 3731990010 | 1990-06-26 | QR5 | Turbine Trip | [45 empty] | La Salle 1 | B | GE | PO | 75 | On June 26, 1990 at 0453 hours with Unit 1 in Operational Condition 1 (Run) at 75% power, a reactor scram occurred during the performance of LaSalle Limited Procedure LLP-90-027, "Unit 1 Turbine Stop Valve (TSV) Scram Functional Test". The scram occurred as designed, due to the closing of Turbine Stop Valves 1, 3, and 4 after #2 TSV was cycled and its open limit switch failed. It was discovered during the scram investigation that the #2 TSV Open Limit Switch (SVOS-2, non Reactor Protection System limit switch) had failed to the Not Open position. This failure occurred May 22, 1990 at 0359 hours, the last time this procedure was performed. At this time, the valve test logic of Turbine Electro Hydraulic Control system (EHC) sealed in the Master/Slave interlock. This prevents the other TSVs from closing while #2 TSV is tested.<br /><br /> On June 26, 1990 at 0453 hours, #2 TSV was tested and closed to about 90% open. When the valve fully opened, limit switch SVOS-2 toggled to the open position (due to a loose mounting of the switch, caused by vibrations). This broke the seal-in interlock. A second later, it toggled back to give a Not open alarm and commanded the other TSVs to go full close. <br /><br /> The Emergency Core Cooling Systems (ECCS) and the Reactor Core Isolation Cooling System were available during the event. All other systems operated as expected during the reactor scram with exception of the 1B Turbine Driven Reactor Feedwater Pump (TDRFP) which did not trip when the manual pushbutton was depressed. The 1B TDRFP was subsequently tripped by using the overspeed test switch. <br /><br /> The #2 TSV limit switch mounting bolts were tightened and its circuitry tested. Temporary System Changes and modifications will be installed to improve the logic to prevent recurrence of this type of event. The 1B TDRFP was tested and functioned as designed. <br /><br /> This event is being reported to the NRC pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered safety Feature System.
373 | 3731991006 | 1991-05-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | La Salle 1 | B | GE | PO | 80 | On May 19, 1991 at 0423 hours, with Unit 1 in Operational Condition 1 (Run) at 80% power (steady-state) and both Turbine Driven Reactor Feed Pumps (TDRFP) in three-element automatic control, the "A" TDRFP discharge flow decreased from 5.5 MLB/hr to 0.1 MLB/hr initiating a decrease in reactor water level. <br /><br /> Approximately three seconds after the loss of the "A" TDRFP flow, a reactor low level alarm annunciated. The licensed unit Reactor Operator (RO) immediately responded to the alarm and diagnosed the problem as loss of "A" TDRFP flow. The Operator placed the "A" TDRFP controller under manual control and attempted to manually increase flow. The "A" TDRFP failed to respond and since the "B" TDRFP could not turn the level decrease by itself the reactor scrammed at Level 3 (+12.5" reactor water level). All Reactor Protection actuations occurred as expected. There were no Emergency Core Cooling System (ECCS) or Primary Containment Isolation System actuations. The unit was placed in Hot Shutdown following the scram. <br /><br /> The cause of this event was the "A" TDRFP control valve spontaneously closing, effectively disabling the "A" feedwater turbine and pump flow control. The root cause for this closure is not known. After extensive "A" TDRFP testing, Unit 1 was restarted on May 21, 1991 and no problems have occurred since that time. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature System.
373 | 3731992003 | 1992-03-01 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | La Salle 1 | B | GE | PO | 89 | On March 1, 1992 at approximately 1635 hours, a Unit 1 steam seal header low pressure alarm was received in the control room. At LaSalle, sealing steam for the Main Turbine is produced from a Steam Seal Evaporator (SSE). Upon investigation of the alarm, the Nuclear Station Operator (NSO, licensed RO) observed that steam seal header pressure was downscale but the SSE shell water level was normal. <br /><br /> Prior to establishing an alternate steam seal source, condenser low vacuum alarms annunciated in the control room and seconds later the turbine tripped on low vacuum. The turbine trip caused a Unit 1 reactor scram due to Turbine Stop Valve closure. Recovery actions from the scram were normal and reactor parameters were stabilized. <br /><br /> The cause of this event was the loss of main turbine sealing steam. This resulted in a loss of condenser vacuum, turbine trip, and reactor scram. The root cause of this event appears to be loss of SSE condensate level control due to a partially plugged level instrument sensing line. <br /><br /> The turbine trip in this event initiated the reactor scram as required. Following the scram, reactor pressure was controlled by the Safety/Relief Valves (SRV's) and Turbine Bypass Valves. These events are consistent with the Updated Final Safety Analysis Report (UFSAR) analysis of this event.
373 | 3731993002 | 1993-01-26 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | La Salle 1 | B | GE | PO | 18 | On January 26, 1993 Unit 1 was in Operational Mode 1 (Run) at 18 percent power. <br /><br /> During the performance of LaSalle Operating Department Surveillance, LOS-MS-R2, 'Main Steam Safety Relief Valve Manual Cycling Test for Conditions 1, 2 or 3', Unit 1 Safety Relief Valve (SRV) 'A' (EPN 1B21-F013A) failed to close when operated by the Nuclear Station Operator (NSO). Several attempts were made to close the SRV but were unsuccessful. Upon the Shift Engineer's authorization, the reactor was manually scrammed, per LaSalle Operating Abnormal Procedure LOA-NB-02, at 2320 hours. The reactor mode switch was placed into the Shutdown position and scram recovery actions were initiated. 'A' SRV closed at 2334 hours, with no deliberate NSO action. Reactor pressure, at this point, had decreased to 340 psig. Other procedural actions were then taken to place the reactor into a Cold Shutdown condition. <br /><br /> Subsequent investigations revealed that 'A' SRV was pneumatically locked into a partially open position. This was caused by duct tape blocking the pneumatic operator's Air Valve Manifold Exhaust Port. The SRV was able to open but air was not allowed to exhaust and therefore the SRV would not fully close. The duct tape eventually ripped away from the port, allowing air to exhaust and thus closing the SRV. <br /><br /> This event is reportable to the Nuclear Regulatory Commission per the requirements of 10CFR50.73(a)(2)(iv) any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature (ESF) and 10CFR50.73(a)(2)(i)(A) completion of any Nuclear Plant Shutdown required by Technical Specification.
373 | 3731993011 | 1993-04-23 | QR6 | Manual Reactor Trip | [45 empty] | La Salle 1 | B | GE | PO | 99 | On April 23, 1993 Unit 1 was in Operational Condition 1 (Run) at 99 percent power. At 0833 hours, the '12A' Low Pressure Feedwater Heater (LP Heater) High Level Alarm was received in the Control Room, followed by auto isolation of the 'A' LP heater string. The loss of feedwater heater(s) procedure was entered and reactor power reduction to 900 MWe was immediately started.<br /><br /> At 0835, the '12C' and '12B' LP heaters alarmed on high level followed by auto isolation of the 'C' and 'B' strings. The LP heater bypass valve, 1CB007, was opened. In anticipation of a low reactor water level condition and the possibility of entering Reactor Instability Region, the Shift Engineer directed a manual scram. <br /><br /> Cause of the event was a disconnected feedback linkage on the 1HD065A valve positioner due to a loose jam nut. The exact cause of the jam nut not being tight is not known. <br /><br /> Instrument Maintenance training is being changed and a tailgate session will be conducted to include the lessons learned from this event. Air supply for the 11 and 12 heaters emergency drain valves has been isolated as an interim measure. A query will be made to the industry for similar events associated with this type and model control valve positioner. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(iv) due to the manual scram.
373 | 3731993015 | 1993-09-14 | QP2 | Partial Loss of Feedwater Flow |  | X | [13 empty] | X | [29 empty] | La Salle 1 | B | GE | PO | 100 | On September 14, 1993 Unit 1 was in Operational Condition 1 (RUN) at 100% power. At 1147 hours the System Auxiliary Transformer (SAT) experienced a differential current auto-trip due to water intrusion in the 4.1 kV ductwork and a fast transfer of loads to the Unit Auxiliary Transformer (UAT) occurred. During the bus transient, the 4.1 kV bus experienced lower than normal voltage. This low voltage condition caused the Feedwater Control System for the 1B Turbine Driven Reactor Feed Pump (TDRFP) to lock up. This caused speed and flow to decrease to zero. The 1A TDRFP was unable to make up the loss in flow, and the reactor scrammed on low reactor water level. Following the Scram the UAT was lost when the Generator separated from the Grid. This resulted in a loss of offsite power. All three diesel generators auto started and picked up the busses.<br /><br /> Reactor water level was restored and controlled initially by Reactor Core Isolation Cooling (RCIC), and later by Low Pressure Core Spray (LPCS). Reactor pressure was controlled by RCIC and the Safety Relief Valves (SRV). Due to a failure of the 1B Reactor Protection System (RPS) Motor Generator isolations were unable to be recovered initially. The Unit was later placed in Cold Shutdown. <br /><br /> This event is being reported pursuant to: <br /> 1. 10CFR50.73(a)(2)(i)(B) due to not meeting the limiting condition of operation (LCO) of Technical Specification 3.4.4. <br /> 2. 10CFR50.73(a)(2)(i)(C) due to deviating from plants Technical Specifications per 50.54(x) when LaSalle General Plant Abnormal Procedures (LGA) LGA-CM-01 and LGA-VP-01 were invoked. <br /> 3. 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature System (ESF) and the automatic actuation of RPS.
373 | 3731994010 | 1994-07-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | La Salle 1 | B | GE | PO | 56 | At 0336 hours on July 5, 1994, Unit 1 scrammed from a power level of 601 MWe and 56.4% Core Thermal Power. The unit had been in Operational Condition 1 (Run) with the 1B Turbine Driven Reactor Feed Pump (TDRFP, FW)[SJ] in 3 element control and the Motor Driven Reactor Feed Pump in manual. The 1A TDRFP was unavailable pending additional post modification testing of the feedwater control system. Just prior to the scram, a loss of the Reactor Water Level Control signal caused the 1B TDRFP to ramp to minimum speed, resulting in a decrease in Reactor Vessel level. The reactor scrammed on a Reactor Low Water Level Scram (12.5 inches). The lowest reactor vessel level during the transient was -6 inches. Normal level was restored using the Motor Driven Reactor Feed Pump. Subsequent investigation determined the cause of the feedwater transient was due to a failure of the Manual Control Board Unit. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(iv) as an event that resulted in automatic actuation of the Reactor Protection System. This revision updates the Corrective Action taken with respect to the failure of the Manual Control Board Unit.
373 | 3731994011 | 1994-07-08 | QP5 | Excessive Feedwater Flow | [45 empty] | La Salle 1 | B | GE | PO | 58 | On July 8, 1994, at 0550 hours, the unit was at 58% power preparing for power ascension. When the 1D Condensate Pump was started, the 1B Turbine Driven Reactor Feed Pump (TDRFP) developed flow swings of 2 million pounds per hour. Flow was stabilized with minor adjustments to the Motor Driven Reactor Feed Pump. the Manual/Automatic (M/A) station output signal, which produced oscillations in the control valve. During an attempted adjustment to the signal gain, a spike occurred resulting in a loss of speed on the 1B TDRFP, a loss of feed flow from the pump, and reduction of reactor vessel level. Repeated attempts to control level by use of the raise and lower pushbuttons at the manual and manual backup stations resulted in vessel level fluctuations until vessel level reached the 55.5 inch High Level Turbine trip and resulted in a Reactor Scram at 0947 hours. <br /><br /> The 1B Emergency Diesel Generator (EDG), which was synchronized to the grid for a scheduled surveillance, assumed an abnormal amount of current and VAR's as a result of the grid disturbance caused by the loss of the Unit 1 generator. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in automatic actuation of the Reactor Protection System.
373 | 3731994015 | 1994-12-12 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | La Salle 1 | B | GE | PO | 92 | On December 12, 1994, Unit 1 was in Mode 1 (Run) at 92% power. At 2132 hours, a Group 1 Main Steam Isolation Valve (MSIV) Primary Containment Isolation (PCIS) occurred due to a spurious Main Steam Line (MSL) High Flow signal on one PCIS channel while a calibration was being performed on the other channel. The closure of the MSIVs caused the Reactor to scram. All control rods fully inserted. Three Safety Relief Valves (SRVs) lifted and reset at appropriate pressures. Two additional scram signals were generated due to reactor level perturbation caused by the manual operation of SRVs to control reactor pressure. <br /><br /> The cause of the scram was a Group 1 Isolation signal initiated by the spurious trip and reset of MSL High Flow switch 1E31-N009C. This occurred during the performance of Instrument Surveillances LIS-MS-102 and LIS-MS-302. Investigation determined the 1E31-N009C Static-O-Ring Switch had failed. This switch was replaced. The failed switch was disassembled and inspected to determine the cause of failure. The cause of the failure was oil contamination of an internal switch assembly. Due to the age and isolated nature of the failure, the root cause can not be determined. <br /><br /> While performing a review of documents, it was discovered that an NTS item tracking the generation of a supplemental LER had been closed without submission of the required supplement. <br /><br /> This report is being submitted per 10 CFR 50.73(a)(2)(iv) due to an automatic actuation of the Reactor Protection System.
373 | 3731995014 | 1995-08-16 | QC4 | Loss of ac Instrumentation and Control Bus. | [10 empty] | X | [28 empty] | X | [5 empty] | La Salle 1 | B | GE | PO | 100 | On 8/16/95 at 2006 hours, LaSalle Unit 1 was operating at approximately 100% Power when the 1D Reactor Protection System (RPS)[JE] Electrical Power monitoring Assembly (EPMA) tripped resulting in the 1B RPS Run Trip. Loss of power to this bus resulted in numerous Primary Containment Isolations (PCIS) [NH], including isolation of the Reactor Building Ventilation System (VR) dampers on both units. Abnormal operating procedure LOA-VR-01, 'Recovery from a Group 4 Isolation or Spurious Trip of Reactor Building Vent', was entered to jumper isolation circuits such that the ventilation loss would not result in MSIV closure on high steam tunnel temperature. At 2013 hours, a Group I isolation occurred on Unit I due to high steam tunnel temperature, despite the installation of the bypass Jumpers. An automatic reactor scram occurred as a result of closure of the MSIVs. Following the scram, reactor level and pressure were controlled with the Reactor Core isolation cooling (RCIC) [BN] System and Safety Relief Valves (SRVs). Ventilation was restored on Unit 2 without incident. <br /><br /> An investigation was performed and the cause of the scram was a Group 1 isolation caused by MSIV closure due to Main Steam Line Tunnel high temperature <br /><br /> This is reportable per 10CFR50.73(a)(2)(iv) due to an automatic actuation of an engineered safety feature (ESF).
373 | 3731995016 | 1995-09-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | La Salle 1 | B | GE | PO | 100 | At 0400 hours on September 24, 1995, Unit 1 was in Operational Condition 1 (Run) and at 100% power. Surveillance LOS-FW-SR1, 'Turbine Feedwater Pump Surveillance', had begun on the 1B Turbine Driven Reactor Feed Pump(TDRFP). to the locked out position. When the 'trip test' push-button was depressed the 1B TDRFP unexpectedly tripped out and reactor water level started to decrease. In response to this the Unit NSO began to manually start the 1C Motor Driven Reactor Feed Pump (MDRFP), while a third operator began reducing reactor recirculation flow via the flow control valves. <br /><br /> Reactor level began to recover and during this recovery the 1B TDRFP unexpectedly returned to operation. With the three feed pumps feeding reactor level, the 55.5 inch High Reactor Water Level/Main Turbine Trip was quickly reached. The control room operators initiated a manual scram just before an automatic scram would have occurred due to the turbine trip. reactor safely shutdown. <br /><br /> The source of the failure was determined to be the emergency governor lockout valve sticking. A specific root cause for this failure could not be determined but the probable cause was foreign material intrusion from the turbine lube oil system.
373 | 3731996006 | 1996-05-12 | QR6 | Manual Reactor Trip | [45 empty] | La Salle 1 | B | GE | PO | 68 | At 0107 hours on May 12, 1996, Unit 1 was operating at a steady state power level of 88% when vibration levels on the main turbine-generator alternator exciter bearings increased. Operator actions in correcting the vibrations were unsuccessful and the reactor was manually scrammed. The high vibrations occurred when oil deflectors for the vibration probe assemblies installed at each exciter bearing rubbed the rotor shaft. The oil deflectors were determined to have an insufficient bore to maintain clearance with the rotating shaft to prevent rubbing. <br /><br /> During the event and subsequent reactor scram, all safety systems performed as designed. The operators initiated conservative actions which shut down the turbine-generator prior to vibration levels exceeding the operating range. The safety significance of this event was minimal and posed no threat to the health and safety of the public.<br /><br /> The root cause of this event was that the vendor did not use the correct drawing and manufactured the deflectors with the wrong inner diameter.
373 | 3731996007 | 1996-06-26 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | La Salle 1 | B | GE | PO | 100 | At 20:56 hours on June 26, 1996, a full Main Steam Isolation Valve (MSIV) isolation was received on Unit 1 during the Instrument Maintenance Department (IMD) instrument mechanics (IM's) performance of a surveillance for calibrating the Main Steamline High Flow Isolation switches. The MSIV isolation trip resulted in an automatic Reactor Scram of Unit 1 due to the Reactor Protection System (RPS) trip signal from the MSIV not full open trip logic. All Safety systems functioned as expected and the reactor safely shut down. <br /><br /> A Primary Containment Isolation System (PCIS) Group 1 half isolation trip on the A2 channel was in place due to the calibration of the 1B21-N010C switch and had not been reset. The IM had just completed actions for prepressurizing the high flow differential pressure switch to near reactor pressure, and was in the process of throttling open the flow switch high side isolation valve when a trip was received from the PCIS Group 1 channel B2 for main steam flow high trip. The A2 instrument and B2 instrument lines are shared. The combination of the A2 channel and B2 Channel trips resulted in the full PCIS Group 1 isolation of the MSIVs. <br /><br /> The root cause of the event was an Instrument Maintenance Department work practice deficiency in the proper technique for prepressurizing instruments. A contributing factor was a procedural weakness. The procedure did not include steps to reset the main steam high flow isolation trip channel prior to returning the instrument to service. This action would have reduced the probability of receiving a full PCIS Group 1 isolation from a pressure spike induced while valving in the instrument.
373 | 3731996008 | 1996-06-28 | QR6 | Manual Reactor Trip | [45 empty] | La Salle 1 | B | GE | SU | 1 | At 2315 hours on June 28, 1996, with Unit 1 at 1% power and Unit 2 at 100% power, the station declared all Core Standby Cooling Systems (CSCS), Emergency Core Cooling Systems (ECCS), and Diesel Generators (DG) inoperable due to foreign material identified on the floor of the service water tunnel. The tunnel is the source for the Essential Service Water System, Non-essential Service Water Systems and the Fire Protection systems. The foreign material had the potential to cause a common mode failure of the Essential Service Water System. Although the systems were declared inoperable, they were available. The foreign material was an injectable sealant foam substance which had been used since May, 1996, in the Lake Screen House (LSH) to seal water seepage cracks in a portion of the floor of the building (the ceiling of the service water tunnel). After the units were shutdown, sealant material was removed from the tunnel. Systems and components which would have been affected by the foreign material were inspected, cleaned and tested to verify operability prior to returning the units to service. The cause of the event was a breakdown in the procedural and work control process. The LSH crack repair had been incorrectly classified as minor facility maintenance and had not been adequately reviewed as a nuclear work request. Weaknesses in the policies and procedures for control of work of minor maintenance actions were identified and corrective actions scheduled.
373 | 3731998015 | 1998-08-19 | QP5 | Excessive Feedwater Flow | [45 empty] | La Salle 1 | B | GE | PO | 58 | While performing level control testing for the 1A Turbine Driven Reactor Feed Pump, automatic level control was lost when the Nuclear Station Operator (NSO) attempted to place it in 3 element automatic control, causing reactor water level to decrease. The NSO attempted to take manual level control, but this attempt was unsuccessful and reactor water level began to rise. At plus 50 inches increasing, the NSO inserted a manual reactor scram due to the feedwater/level transient. This reactor water level was a predetermined scram contingency which had been discussed during the pre-evolution brief prior to the feedwater testing. During the scram, all systems functioned as required. The cause of this event has been attributed to a failure of the Control Card associated with the Bailey Reactor Water Level Control System. The corrective action taken was to replace the failed card with a refurbished unit. There was no impact on the health and safety of the public. This is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
373 | 3731999003 | 1999-09-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | La Salle 1 | B | GE | PO | 93 | On September 2, 1999, following preventative maintenance on the 1B Turbine Driven Reactor Feed Pump (TDRFP) hydraulic control system, a Non-Licensed Operator (NLO) restored automatic control improperly, causing a sharp drop in 1B TDRFP speed and feed flow. An automatic reactor scram was received on low reactor level. The NLO was recovering from a prior error in which he had erroneously placed the controlling subloop of the hydraulic control system in manual. This action was not prescribed by the work scope. When he became aware of the error, he failed to notify the control room of the abnormal configuration, and returned the subloop to automatic control. While in manual, an error signal had developed that reduced the feed demand to minimum. The cause of this event was a personnel error on the part of the NLO. Additional causes include a lack of supervisory oversight and a lack of adherence to administrative control procedures. Corrective actions included an all station stand down to discuss recent human performance problems, counseling the NLO and operating crew, and improving procedural guidance for transferring TDRFP hydraulic control system sub-loops and locking out control oil. The safety significance of the event was minimal. The plant responded as designed, and the Emergency Core Cooling Systems were not challenged.
373 | 3732001001 | 2001-01-31 | QR5 | Turbine Trip | [45 empty] | La Salle 1 | B | GE | PO | 100 | On January 31, 2001, at 2147 hours, current from the "C" phase of the 345 KV power line between the Unit 1 main power transformer and the switchyard flashed to ground across a support insulator. The phase-to-ground fault activated the transformer protective relays, resulting in a turbine generator trip and reactor scram. The cause of the phase-to-ground fault was determined to be an excess of bird excrement that had built up on the support insulator. Corrective actions included replacement of the damaged insulator, and inspection and cleaning of the other insulators. An evaluation to determine how to prevent birds from roosting on the equipment was begun. The safety consequences of this event were minimal. All safety systems operated as expected. A turbine generator trip is an analyzed condition of moderate frequency. The reactor was safely shut down and recovery performed without incident.
373 | 3732003005 | 2003-11-27 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | La Salle 1 | B | GE | PO | 100 | On November 27, 2003, at 0052 hours, while swapping from the 1A Turbine Driven Reactor Feed Pump (TDRFP) to the Motor Driven Reactor Feed Pump (MDRFP), Unit 1 was manually scrammed due to decreasing reactor water level. Reactor Water Level had decreased to approximately 20 inches, and was continuing to drop even with the indicated MDRFP discharge flow meeting the expected demand. Troubleshooting determined that the lA TDFRP discharge check valve 1FW001A had stuck open, causing the flow from the MDRFP to circulate back through the lA TDFRP preventing it from reaching the reactor vessel. The cause was determined to be internal binding. Corrective actions were to inspect and repair 1FW001A, and to schedule inspections on similar check valves on both Units. Additionally, vendor recommended enhancements identified during the investigation will be incorporated for these valves.
373 | 3732006001 | 2006-02-20 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | La Salle 1 | B | GE | PO | 6 | On 2/20/06, Unit 1 was at approximately six percent power while shutting down for as scheduled refueling outage. At 0023 hours, approximately 20 minutes after the main turbine was taken offline, all of the main turbine bypass valves unexpectedly opened. The resulting drop in reactor and steam line pressure caused a Group 1 Primary Containment isolation and an automatic reactor scram. Following the scram, the operators observed that three control rods did not indicate fully inserted. Due to the inability to verify that shutdown criteria were met, a Site Area Emergency (SAE) was declared at 0028 hours in accordance with the current Emergency Action Level guidance. The SAE was exited and the site entered Recovery mode at 0427 hours, following determination that the reactor was in fact fully shutdown. The cause of the scram was a failed power supply in the main turbine EHC system. The three control rods failed to fully insert to position 00 due to friction from channel distortion. The EHC power supply was replaced, and actions were taken to address the channel distortion issue, including discharging fuel assemblies susceptible to channel bowing in the next operating cycle or placing them in non-control cell locations.
373 | 3732009001 | 2009-05-21 | QR5 | Turbine Trip | [45 empty] | La Salle 1 | B | GE | PO | 100 | On May 21, 2009, at 1635 CDT, LaSalle Unit 1 automatically scrammed from 100% power. The scram was due to a generator lockout signal caused by a failure of the surge arrester on the 'A' phase of the Unit 1 West Main Power Transformer (1W MPT). The safety significance of this event was minimal. All control rods fully inserted, all systems responded as expected to the scram, and Emergency Core Cooling Systems were not challenged. The voltage transient caused by the arrestor failure resulted in a number of invalid alarms and isolations on both Units. The cause of the surge arrester failure was determined to be a manufacturing defect. Corrective actions included verifying that the 1W MPT had not been damaged by the event, and replacing the failed surge arrester. Additionally, future procurements of station surge arresters will require that the vendor supply the test data.
373 | 3732011001 | 2011-02-01 | QR5 | Turbine Trip | [45 empty] | La Salle 1 | B | GE | PO | 100 | On February 1, 2011, at 1918 hours CST, LaSalle Unit 1 automatically scrammed from 100% power. The scram was due to a main generator load reject caused by a fault on the C-phase of the 1W Main Power Transformer (1W MPT). The safety significance of this event was minimal. All control rods fully inserted, all systems responded as expected to the scram, and Emergency Core Cooling Systems were not challenged. The root cause of the event was determined to have been external bushing flashover due to moist snow and ice buildup along the exterior bushing skirts of the 1W MPT that surpassed its flashover resistance (i.e., creep length rating) during unusually adverse weather conditions. Corrective actions included diagnosis of extent of damage along with the repair and restoration of the 1W MPT that included replacement of the C-phase bushing, the C corona ring and the MPT mechanical relief valve. Corrective action to prevent recurrence includes replacement of the MPT bushings with a more robust anti-flashover design that exceeds minimum Basic Insulation Level (BIL) rating.
373 | 3732013002 | 2013-04-17 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | La Salle 1 | B | GE | PO | 100 | On April 17, 2013, LaSalle Units 1 and 2 were operating in Mode 1 at 100% power, with a severe thunderstorm in progress. At 1457 hours CDT, lightning struck 138KV Line 0112, resulting in a phase-to-ground fault which subsequently cleared. At 1459 hours, a second phase-to-ground fault on Line 0112 occurred and all 345 KV oil circuit breakers (OCBs) in the main switchyard opened, resulting in a loss of offsite power and reactor scrams on both Units. All emergency diesel generators automatically started and loaded onto their respective busses. All control rods fully inserted, and all systems responded as expected.<br /><br /> An Unusual Event was declared due to a loss of offsite power for greater than 15 minutes. Offsite power was restored to all ESF busses by 2301 hours on April 17, 2013, and the Unusual Event was terminated at 0814 hours on April 18, 2013.<br /><br /> The root cause of the event was determined to be degradation of the 138kV switchyard grounding system that allowed a lightning induced fault to flash over onto the DC protective system. The ground system in the 138kV switchyard was repaired, and corrective actions include improving lightning shielding in the 138kV switchyard.
373 | 3732017003 | 2017-02-13 | QR5 | Turbine Trip | [45 empty] | La Salle 1 | B | GE | PO | 100 | On February 13, 2017, LaSalle County Station Unit 1 was in Mode 1 at 100 percent power and Unit 2 shut down for a planned refueling outage. At 2309 CST, a reactor scram signal was received on Unit 1 due to turbine control valves fast closure while the station was aligning back-feed operation to the Unit 2 main power transformer (MPT). The Unit 1 turbine trip was due to the main generator trip on differential current. The plant was placed in a stable condition with reactor pressure maintained by the turbine bypass valves and reactor water level controlled using feedwater. Unit 2 was unaffected by the event. <br /><br /> The root cause of the Unit 1 trip on differential current was a marginal generator differential relay design that was prone to responding to faults outside its zone of protection. Both units' 345 kV ring buses were connected together through the cross-tie bus, which allowed the Unit 1 generator to supply some of the electrical current that resulted in its differential circuit to create an unbalanced current that actuated the differential relay. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram. There were no safety consequences associated with the event since RPS and other emergency safety systems functioned as designed.
373 | 3732017005 | 2017-02-17 | QP5 | Excessive Feedwater Flow | [45 empty] | La Salle 1 | B | GE | PO | 30 | On February 17, 2017, at 2353 CST, during Unit 1 power ascension from a previous forced shutdown, operators inserted a manual scram as a result of a high reactor water level condition caused by a rapid change in feedwater flow. The high reactor water level trip occurred due to a failure of the feedwater regulating valve (FRV) 1FW005 positioner arm, which caused the regulating valve to be driven to the full open position. This resulted in a rapid increase of reactor water level that required operators to perform a manual reactor scram. The plant was placed in a stable condition, with no complications in achieving shutdown. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS). The safety significance of this condition was minimal, as plant equipment responded as expected for the event. The feedback drive arm and new positioner were installed on the Unit 1 FRV, which allowed the unit to restart following repairs. The FRV positioner feedback assembly had been installed in 2002, during a modification to upgrade of the air-operated valve assembly. This design has proven not to be robust enough for the FRV application.
374 | 3741987014 | 1987-06-23 | QR5 | Turbine Trip | [45 empty] | La Salle 2 | B | GE | PO | 68 | POWER LEVEL - 068%. AT 1253 HOURS ON JUNE 23, 1987, WITH UNIT 2 IN OPERATIONAL CONDITION 1 (RUN) AT 68% POWER, A REACTOR SCRAM OCCURRED DUE TO MAIN TURBINE STOP VALVE FAST CLOSURE (TURBINE TRIP). THE TURBINE TRIP WAS GENERATED BY A TRIP OF THE TURBINE THRUST BEARING WEAR DETECTOR. THE APPARENT CAUSE OF THE EVENT HAS BEEN DETERMINED TO BE A BUILDUP OF FOREIGN MATERIAL (SLUDGE) IN THE THRUST BEARING WEAR DETECTOR WHICH CAUSED IMPROPER OPERATION. THE PLANT PERFORMED AS EXPECTED TO SAFELY SHUTDOWN THE REACTOR. FOR EACH UNIT AT LASALLE, THE THRUST BEARING WEAR DETECTOR WAS INSPECTED AND CLEANED, AND THE OIL LINES LEADING TO THE DETECTOR WERE FLUSHED. PREVENTIVE MAINTENANCE WILL BE CONDUCTED AT EACH REFUELING OUTAGE ON THE DETECTORS IN ACCORDANCE WITH THE STATION'S SURVEILLANCE SCHEDULE. THIS EVENT IS REPORTABLE PURSUANT TO THE REQUIREMENT OF 10CFR50.73(A)(2)(IV) DUE TO THE AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM.
374 | 3741988003 | 1988-03-09 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | La Salle 2 | B | GE | PO | 84 | At 1732 hours on March 9, 1988, with Unit 2 in Operational Condition 1 (Run) at approximately 84% power, a valving error during an instrument surveillance caused the Reactor Recirculation (RR) pumps to trip off. This caused a large and rapid power reduction to approximately 40% power. While trying to stabilize the feedwater heaters and restart a RR pump, the Average Power Range Monitors (APRMs) were observed to be oscillating between 25-50% power (25% peak-to-peak). As preparations were being made to manually scram the reactor, an automatic scram occurred on APRM neutron flux high (118% trip) at 1739 hours. The scram was caused by neutron flux oscillations experienced while the unit was at a high rod line and low flow (natural circulation) condition. <br /><br /> The root cause of this event was personnel error for the initial transient, and procedural inadequacy for the scram. Although operating personnel were cognizant of the potential for (and observed) neutron flux oscillations, the operating procedures did not provide sufficient guidance for prevention/suppression of oscillations. The neutron flux oscillations seen by the APRMs and Local Power Range Monitors were occurring "in phase" across the core and were bounded by the APRM high neutron flux scram (118%). <br /><br />Operating procedures were revised to ensure prompt action (as recommended by General Electric SIL 380, Rev. 1) when the unit is operating at a condition which is susceptible to neutron flux oscillations. In addition, as a temporary measure, a Confirmatory Action Letter issued by NRC Region III requires the plant to be scrammed (manual) immediately in the event of a dual pump (RR) trip. <br /><br />This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the automatic actuation of the Reactor Protection System.
374 | 3741988012 | 1988-10-14 | QR6 | Manual Reactor Trip | [45 empty] | La Salle 2 | B | GE | PO | 39 | At 1126 hours on October 14, 1988 the Unit 2 reactor was manually scrammed from 25% power following a trip of both Reactor Recirculation (RR) pumps from fast speed to off during the performance of an instrument surveillance. The surveillance tests the response time of the RR pump trip (EOC-RPT) system breaker arc suppression, by tripping the RR pump motor high speed breakers. This event was caused by a procedural error which unintentionally interrupted the logic for completing the downshift to low speed. <br /><br />The manual scram was required by LaSalle Operating Procedures, which require a reactor scram whenever the actor is operating in natural circulation. <br /><br /> This event produced minimal impact to plant safety. Review of appropriate data following the scram confirmed that the reactor remained stable throughout the event. This was expected since the flow Control Line was approximately 63%. Instabilities are more likely when the reactor is operated at low core flows and relatively high (> 80%) Flow Control Lines. <br /><br /> As result of the scram the arc suppression response time test was suspended. This test will be completed during the refueling outage or during unit startup. <br /><br />The procedure which caused this event will be revised to eliminate the error, along with its companion procedure for Unit 1. <br /><br /> This event is reported in accordance with the requirements of 10CFR50.73(a)(2)(iv) because an Engineered Safety Feature actuated.
374 | 3741989011 | 1989-08-26 | QR8 | Spurious Reactor Trip | [45 empty] | La Salle 2 | B | GE | PO | 10 | On August 26, 1989, a controlled shutdown was in progress on Unit 2. While conducting LOS-TG-SA2, "Turbine Valve Leak Tightness surveillance," a Reactor Protection System (RPS) actuation occurred at 0414 hours. When the actuation signal was received, two of the four scram group lights of the RPS Bus A remained energized. This prevented some of the rods from receiving the normal automatic scram actuation. Rod motion appears to have initiated for these rods due to the Channel A backup scram actuation which occurred at the same time as the initial event. The Control Room Operator manually initiated a normal scram signal a few seconds later using the A2 and B2 scram pushbuttons. At this time all the remaining scram valves deenergized, indicating that the scram had occurred. <br /><br /> Before the turbine valve test was started, the Hathaway Sequence of Events alarm typer was turned off due to its constant printing caused by alarm relay chattering. As a result, the main source of information to be used in analyzing the reactor trip was not available. At the time of the trip, no plant parameters exceeded their trip setpoints. <br /><br /> As a result of the missing information, several scenarios were developed using available information in an attempt to determine the cause of the reactor trip. At this time a definite cause for the trip has not been determined. The investigations have concluded that a very brief (less than 15 milliseconds) disturbance in the RPS system allowed some of the scram contactors to trip, but was not present long enough to ensure all the contactors tripped. The source of this spurious signal is unknown. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature System.
374 | 3741990001 | 1990-02-06 | QR8 | Spurious Reactor Trip | [45 empty] | La Salle 2 | B | GE | PO | 100 | On February 6, 1990 at 0926 hours, while Unit 2 was in Operational Condition 1 (Run) at 99.8% power, during the performance of LaSalle Instrument Surveillance LIS-NR-403, 'Unit 2 Average Power Range Monitor (APRM) Rod Block and Scram Functional Test,' a full reactor scram occurred. Normally the surveillance only causes 991f-scrams. At the time of the occurrence, F APRM was tripped, per the procedure, which tripped Reactor Protection System (RPS) Channel A. While the RPS Channel 'A' half scram condition was in effect, E APRM spiked spuriously, causing RPS Channel B to trip and a full reactor scram occurred. <br /><br /> Additionally, it was also determined that all other expected automatic actions occurred as expected including Primary Containment Isolation signals when reactor water level reached 12.5 inches decreasing. <br /><br /> Initiation of the event was not due to an actual transient on a parameter which is monitored to protect the reactor core but due to spurious spike of APRM E. Troubleshooting E APRM was performed under Work Request L96857 in an attempt to determine the cause of the spurious spikes. The cause of the spikes could not be repeated or determined. <br /><br /> Unit 1 was not affected by this event. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(iv) due to an actuation of an Engineered Safety Feature.
374 | 3741990010 | 1990-09-12 | QR5 | Turbine Trip | [45 empty] | La Salle 2 | B | GE | PO | 100 | On September 12, 1990 at 0305 hours, with Unit 2 in Operational Condition 1 (RUN) at 99.9% power, the Unit 2 Nuclear Station Operator (NSO, Licensed Reactor operator) was performing the Turbine Generator Weekly Surveillance (LOS-TG-W1). After the NSO had performed the Generator Regulator Mode transfer switch portion of this surveillance, he noticed a severe transient on several generator output indications. A few seconds after this, the 2E Main Power Transformer B phase differential relay actuated when the current transformer feeding this relay shorted out to ground. As a result, the Unit 2 Main Generator locked out causing the Main Turbine to trip. This immediately caused the Unit 2 reactor to scram. Five Safety Relief Valves actuated to control reactor pressure.<br /><br /> The Initial cause of the transient could not be determined. The B phase Current Transformer that feeds the B phase differential relay scram was replaced. All affected circuits associated with the Generator's exciter (Alterex) have been tested prior to turbine roll up and once again after the unit was on line. No problems could be found. Unit 2 was restarted and the generator was synchronized to the grid at 0430 hours on September 21, 1990. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to the actuation of an Engineered Safety Feature System.
374 | 3741991010 | 1991-09-06 | QR6 | Manual Reactor Trip | [45 empty] | La Salle 2 | B | GE | PO | 32 | At 0415 hours, on September 6, 1991, with Unit 2 in Operational Condition One (RUN) at 85% power (965 MWe), the Electro-Hydraulic Control (EHC, EH)TG! Fluid Tank Hi/Lo level alarm annunciated after all four Main Turbine Control Valves had been cycled for required monthly Reactor Protection Surveillances.<br /><br /> A local investigation found that the EHC tank level was low. Also an EHC hydraulic oil leak was discovered at the #2 Main Turbine Control Valve. At 0525 hours, when it became apparent that the leak could not be controlled, a Unit shutdown was initiated. The reactor was manually scrammed at 0615 hours, from 32% power (361 MWe). Following the manual Scram, the turbine automatically tripped, on Main Generator reverse power. The leak stopped when the turbine tripped. <br /><br /> One leak was found at the half inch stainless steel tubing which supplies 1600 psig Relayed Emergency Trip System (RETS) hydraulic fluid to the #2 Control Valve. The cause of the leak has been attributed to broken and damaged piping supports that allowed the EHC lines to vibrate excessively. The damaged supports, allowed the RETS line and the 1 inch stainless steel tubing that supplies the 1600 psig Fluid Actuation Supply (FAS) to the #2 Main Turbine Control Valve to rub together, resulting in the failure of the RETS line. It was also identified that the RETS and FAS lines for the #4 Main Turbine Control Valve were also rubbing together. This had resulted in outer diameter wall thinning on the RETS line, however, no leakage occurred. <br /><br /> The hydraulic lines of #2 and #4 Control Valves were repaired. Four mechanical snubbers sprayed with fluid were replaced. All fluid soaked steam line insulation was replaced. All electrical cable jackets affected as well as the general area were cleaned. Repairs to the pipe supports recommended by the Nuclear Engineering Department were completed. <br /><br /> During the course of the event, 12 barrels of EHC fluid were added to restore the EHC reservoir to its normal level. The Mark I EHC system was supplied by General Electric. This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to a manual actuation of the Reactor Protection System.
374 | 3741991012 | 1991-09-24 | QR5 | Turbine Trip | [45 empty] | La Salle 2 | B | GE | PO | 100 | At 0015 hours, on September 24, 1991, with Unit 2 in Operational Condition One (Run) at 100% power (1112 MWe), the reactor scrammed on Neutron Monitoring (NR) IG! upscale trips as a result of a pressure/power transient induced by the Main Turbine Valves (EH) TG! closing. No testing or maintenance was being performed at the time of the event. All other equipment responded as designed. All Reactor Control Rods inserted, the Main Turbine Bypass Valves opened, the Motor Driven Reactor Feed Pump maintained reactor level and Safety Relief Valves (SRV's) S, U, K, and E (NB) SB! cycled and then reseated. <br /><br /> The root cause of the scram has not been determined. An analysis of the sequence of events by Commonwealth Edison and the General Electric Company indicates that a spurious signal in the Electro-Hydraulic Control (EHC) system either falsely signaled a Main Turbine overspeed condition or created a sudden demand signal to be at zero load. <br /><br /> The speed circuits of EHC System were replaced and calibrated. This was also the corrective actions to a similar event which occurred at the James A. Fitzpatrick Plant, New York Power Authority, on November 5, 1989. Also, the circuits associated with the #1 3KHz oscillator were replaced and calibrated. <br /><br /> The speed circuits will be continuously monitored until the next refueling outage. The Mark I EHC system was supplied by General Electric. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to an automatic actuation of the Reactor Protection System.
374 | 3741991014 | 1991-10-29 | QR5 | Turbine Trip | [45 empty] | La Salle 2 | B | GE | PO | 100 | At 0725 hours, on October 29, 1991, with Unit 2 in Operational Condition One (Run) at 100% power (1122 MWe), the reactor scrammed on Turbine Stop Valve closure due to the Main Turbine tripping on high #6 bearing vibration. At the time of this event, no related testing or maintenance was being performed.<br /><br /> All other equipment responded as designed. All Control Rods inserted, the Main Turbine Bypass Valves opened as required, the Motor Driven Reactor Feedwater Pump started and maintained reactor water level, and Main Steam Safety Relief Valves K, E, D, C, S and V cycled to control pressure and then reseated. <br /><br /> The root cause of the scram was a spurious trip from a Turbine Supervisory System Vibration Amplifier Circuit Card. The card has been replaced and its trip temporarily defeated. Administrative controls are in place to manually trip the turbine should actual high vibration be experienced on this bearing. The Turbine Supervisory System was supplied by General Electric. <br /><br /> This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv) due to an automatic actuation of the Reactor Protection System.
374 | 3741992004 | 1992-04-15 | QR6 | Manual Reactor Trip | [45 empty] | La Salle 2 | B | GE | PO | 18 | At 1510 hours, on April 15, 1992, with Unit 2 in Operational Condition One (Run) at 18% power (180 MWe), the reactor was manually scrammed as a conservative measure due to Main Turbine Bypass Valve cycling. Minor reactor pressure oscillations occurred when the Main Turbine Control Valves repositioned in response to an Electro-Hydraulic Control (EHC) System speed signal anomaly. All equipment responded as designed. All Reactor Control Rods inserted, three of the Main Turbine Bypass Valves and no Safety Relief Valves cycled due to the low power level. <br /><br /> The root cause of the speed signal anomaly has not been determined. The manual scram was initiated because of the excessive bypass valve cycling. An analysis of the events by Commonwealth Edison and the General Electric Company indicates that the erratic primary speed signal resulted in the EHC System switching from Load and Pressure Control to Speed Control and back again. The pressure increases and bypass valve cycling were responses to proper EHC Control System demand signals.<br /><br /> Insufficient operational data was obtained during the event and troubleshooting performed subsequent to the event did not result in a determination of the specific cause of the speed signal anomaly. The speed circuits, as well as the outputs of the low value gate and bypass valve amplifier will be monitored by recorders set to trigger on recurrence of the spurious signal throughout the fuel cycle. <br /><br /> This event is, reportable pursuant to the requirements of 10CFR50.73(a) (2) (iv) due to a manual actuation of the Reactor Protection System.
374 | 3741992012 | 1992-08-27 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | La Salle 2 | B | GE | PO | 80 | On August 27, 1992 at 0305 hours, Unit 2 experienced a Reactor Scram as a result of a Main Turbine trip which was caused by a Thrust Bearing Wear Detector signal. All rods successfully inserted as a result of the Automatic Scram signal. <br /><br /> During the scram response, both Turbine Driven Reactor Feed Pumps failed to trip from either remote manual operation, High Reactor Level 8 automatic trip, or local mechanical trip operation. As a result of this failure, the Reactor Water level increased to a level requiring the Main Steam Isolation Valves (MSIV) to be closed. <br /><br /> The MSIV closure resulted in the Safety Relief Valves (SRV) being used to control reactor pressure. During operation of two SRVs (A&B), remote position indication failed to show that the valves closed when demanded.<br /><br /> Also during the event, the Reactor Core Isolation Cooling (RCIC) System auto started due to a Level 2 initiation signal which resulted from a pressure spike sensed at the instrument racks containing the level transmitters for the RCIC initiation signal. <br /><br /> When reactor level was brought under control, a MSIV (Group I) Isolation High Steam Flow signal was received when a Main Steam Line was being unisolated. This occurred when the MSIV was opened with approximately 760 psi differential pressure across the valve. <br /><br /> Root cause investigations were performed to determine the reason for all the above noted failures. This is reportable pursuant to 10CFR50.73(a)(2)(iv) due to an automatic reactor scram.
374 | 3741992016 | 1992-11-16 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | La Salle 2 | B | GE | PO | 100 | POWER LEVEL - 100%. At 0122 on November 16, 1992, LaSalle County Station's Unit 2 scrammed from approximately 80% power following a load reduction from 100% power as a result of a feedwater transient that was caused by a loss of all Station Air (SA) Compressors. Operating Personnel isolated cooling water to the Unit 2 SA Compressor as part of a scheduled Out of Service. This resulted in cooling water being isolated from the running Unit 1 and Common SA Compressors due to the Unit 2 Turbine Building Closed Cooling Water System (TBCCW) being cross-tied to the Unit 1 and Common SA Compressors while refuel outage activities were being performed on the Unit 1 TBCCW System. Due to the loss of cooling water, the Unit 1 and Common SA Compressors tripped on high lube oil temperature. This resulted in a reduction of Instrument Air pressure. The loss of air pressure, combined with its subsequent restoration, resulted in a feedwater transient that resulted in a Main Turbine trip due to high reactor water level. The turbine trip caused a reactor scram. The root cause of this event is an inadequate review of the Out of Service. A contributing factor to the cause of this event is a lack of administrative control over the abnormal lineup of the TBCCW Systems. The procedure used for cross-tying the SA Compressor's cooling water to the other unit did not provide provisions for positive administrative control over this abnormal lineup nor did it provide provisions for alerting operating personnel that the abnormal lineup existed. Corrective actions include counseling the individuals involved, and revising the procedure utilized for cross-tying SA Compressor Cooling Water to the other unit to provide provisions for positive control over this abnormal lineup. In addition, engraved plaques have been placed at the applicable SA Compressor Supply, Return, and Cross-Tie Valves to instruct operators to verify cooling water will be available to the required SA Compressors prior to repositioning them.
374 | 3741994001 | 1994-01-18 | QR5 | Turbine Trip | [45 empty] | La Salle 2 | B | GE | PO | 7 | On January 18, 1994, Unit 2 was in Operational Condition 2 (startup). Work on Main Steam Isolation Valve (MSIV) Limit switches was in progress. At 0133 hours during the Main Turbine Shell Warming Process, first stage pressure increased sufficiently to cLear the thirty (30) percent bypass of the Turbine Stop Valve Closed Scram. A Reactor Scram occurred as the Turbine Stop Valves were already in a closed position.<br /><br /> All components functioned as designed. The required notifications were made, and equipment was returned to normal operating status. <br /><br /> An investigation was performed and the root cause was determined to be Operator Personnel Error. The Operator at Lowed himself to become distracted white being interviewed by an off-site evaluator and did not closely monitor the shell warming process. <br /><br /> This is reportable per 10CFR50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature (ESF) and unplanned automatic Reactor Protection System (RPS) Reactor Scram.
374 | 3741994004 | 1994-06-21 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | La Salle 2 | B | GE | PO | 100 | On June 21, 1994, Unit 2 was in operating condition 1 (Run) operating at approximately 1110 MWe. At approximately 2230 hours, the feed breaker from 6900 Volt Switchgear 251 to 6900-480/277 Volt Transformers 231A and 231B tripped. The supply breaker to Transformers 231A and 231B opening resulted in the loss of power to numerous pieces of balance of plant equipment. Several air operated valves were affected by the loss of power: the 'A' Turbine Driven Reactor Feed Pump Minimum Flow valve failed open, all Condensate/Condensate Booster Minimum Flow valves failed open, and the 'A' Heater Drain Pump Forward valve failed closed. The failing of these valves resulted in a reduction of feedwater flow to the reactor. Due to this loss of feedwater flow, a Level 3 reactor scram was received. The plant responded as expected to this event.<br /><br /> The cause of the breaker tripping was a degraded trip output Silicon Controlled Rectifier (SCR) on the Transformer 231B 6900 KV ground fault relay. <br /><br /> This event is being reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv) due to an actuation of an Engineered Safety Feature (ESF) and unplanned automatic Reactor Protection System (RPS) reactor Scram.
374 | 3741994006 | 1994-08-25 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | La Salle 2 | B | GE | PO | 100 | On August 25, 1994, Unit 2 was in Operating Condition 1 (Run) operating at approximately 1118 MWe. At approximately 0328 hours, the Main Turbine Control Valves (CV) began to drift closed. In response to this closure, the Main Turbine Bypass Valves (BPV) began to open sequentially to control Reactor pressure. Approximately 13 seconds after the CV's began to close the BPV's closed, which resulted in an increase in Reactor pressure. The increasing pressure collapsed voids in the core which increased moderation and in turn caused power to increase. When Reactor pressure reached approximately 1023 psig, a Reactor Scram occurred due to reaching the Average Power Range Monitor (APRM) Hi Flux Scram setpoint. <br /><br /> The apparent cause of the CV and BPV movement was due to high frequency noise on three of the cards in the Electro-Hydraulic Control circuitry. <br /><br /> An additional contributing cause was nine cards were found not fully seated in their connectors. <br /><br /> This event is being reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv) due to an actuation of an Engineered Safety Feature (ESF) and unplanned automatic Reactor Protection System (RPS) reactor Scram.
374 | 3741994008 | 1994-10-19 | QR5 | Turbine Trip | [45 empty] | La Salle 2 | B | GE | PO | 100 | On October 19, 1994, Unit 2 was in operational Condition 1 (Run). Turbine Control Valve oscillations were first observed at 1015 hours. Plant personnel were unable to immediately determine the cause of the oscillations and as a result, Turbine Electro-hydraulic Control (EHC,EH)[TG] piping, which was subjected to the same oscillations hydraulically, began to leak. The piping eventually broke due to low cycle fatigue. A Main Turbine trip occurred due to the loss of EHC fluid pressure, and the reactor scrammed on high neutron flux when the turbine control valves closed.<br /><br /> Reactor Core Isolation Cooling (RCIC, RI)[BN] and Anticipated Transient Without Scram-Recirc Pump Trip/Alternate Rod Insertion (ATWS-RPT/ARI) initiated on spurious low reactor water level (Level 2, -50') signals. Six Safety Relief Valves (SRVs) opened sequentially following the turbine trip. The required notifications were made, and troubleshooting and investigation were initiated. <br /><br /> An investigation was performed, and the root cause for the EHC control valve oscillations was due to a faulty connector on the EHC permanent magnet generator (PMG) 30 Vdc power supply. The faulty connector allowed the 30 Vdc power to cycle between the house supplied power supply and the PMG power supply. <br /><br /> EHC piping and the electrical connector were repaired and an extensive inspection of EHC piping was completed prior to starting up Unit 2.
374 | 3741996002 | 1996-02-04 | QR6 | Manual Reactor Trip | [45 empty] | La Salle 2 | B | GE | PO | 100 | At 2037 hours, on February 4,1996, Unit 2 was in operational Condition 1 (Run) at 100 % power when it was manually scrammed per LOA-AP-06 'Actions on Transformer Trouble Alarm'. At 2005 hours, the control room received a 2E Main Power Transformer trouble alarm and dispatched an Equipment Operator (EO) to investigate. The EO found no cooling fans or cooling pumps running even though all power supplies and breaker line-ups were normal. The Shift Engineer directed an emergency load reduction per LGP-3-1 'Power Changes'. When Transformer cooling could not be restored the unit was manually scrammed.<br /><br /> All systems responded as designed with the exceptions of the 2A Circulating water pump which tripped on the electrical load transfer, and the Electric - Hydraulic control (EHC) system pressure was low for turbine control pressure. <br /><br /> The cause of the event was determined to be the loss of transformer cooling caused by an open circuit in the transformer cooling logic.
374 | 3731996008 | 1996-06-29 | QR6 | Manual Reactor Trip | [45 empty] | La Salle 2 | B | GE | SU | 5 | At 2315 hours on June 28, 1996, with Unit 1 at 1% power and Unit 2 at 100% power, the station declared all Core Standby Cooling Systems (CSCS), Emergency Core Cooling Systems (ECCS), and Diesel Generators (DG) inoperable due to foreign material identified on the floor of the service water tunnel. The tunnel is the source for the Essential Service Water System, Non-essential Service Water Systems and the Fire Protection systems. The foreign material had the potential to cause a common mode failure of the Essential Service Water System. Although the systems were declared inoperable, they were available. The foreign material was an injectable sealant foam substance which had been used since May, 1996, in the Lake Screen House (LSH) to seal water seepage cracks in a portion of the floor of the building (the ceiling of the service water tunnel). After the units were shutdown, sealant material was removed from the tunnel. Systems and components which would have been affected by the foreign material were inspected, cleaned and tested to verify operability prior to returning the units to service. The cause of the event was a breakdown in the procedural and work control process. The LSH crack repair had been incorrectly classified as minor facility maintenance and had not been adequately reviewed as a nuclear work request. Weaknesses in the policies and procedures for control of work of minor maintenance actions were identified and corrective actions scheduled.
374 | 3741999002 | 1999-08-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | La Salle 2 | B | GE | PO | 70 | On August 21, 1999, at 2251 hours, during a down power, Unit 2 feedwater flow and reactor water level began to oscillate due to a failure of the 2A Turbine Driven Reactor Feedwater Pump (TDRFP) hydraulic control system. Efforts by the reactor operator to restore level control were ineffective, and at 2255 hours the reactor automatically scrammed on low reactor water level. The root causes of the scram were inadequate maintenance on the 2A TDRFP servo valve 2FW163AA, and the failure of the control room crew to take proper action in response to a reactor level transient. Corrective actions include: repairing the servo valve; reinforcing operator standards associated with command and control, communications, and pre-job briefs; and improving operator knowledge deficiencies through training. The safety significance of the event was minimal. The plant responded as designed, and the Emergency Core Cooling Systems were not challenged.
374 | 3741999003 | 1999-11-16 | QR5 | Turbine Trip | [45 empty] | La Salle 2 | B | GE | PO | 100 | On November 16, 1999, at 1834 hours, Unit 2 operators manually scrammed the reactor from approximately 80 percent power due to the unexpected fast closure of the Main Turbine Combined Intercept Valves. The cause of the unexpected fast closure was subsequently identified as a failure of the intercept valve amplifier card and operational amplifier card in the electro-hydraulic control (EHC) circuitry. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. The Emergency Core Cooling Systems were not challenged. The failed cards were replaced and sent to General Electric for failure analysis. The new cards were calibrated, and Unit 2 was returned to full power on November 20, 1999.
374 | 3742000003 | 2000-06-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | La Salle 2 | B | GE | PO | 98 | At 0728 hours on June 22, 2000, LaSalle Unit 2 experienced an automatic reactor scram due to low reactor water level. The low reactor water level was caused by a loss of flow from the 2A turbine driven reactor feed pump (TDRFP). The root cause of the event was the intrusion of wear products into the high pressure control oil pressure regulating relief valve (2FW199A). The wear products became lodged between the relief valve seat and disk, which allowed the oil system pressure to be relieved. This caused the 2A TDRFP control valve to close, and the loss of flow from the 2A TDRFP. The resulting reactor water level transient led to the automatic scram. The corrective action was to install duplex oil filters on the 2A and 2B TDRFP high pressure control oil systems. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. The Emergency Core Cooling Systems were not challenged.
374 | 3742000006 | 2000-12-01 | QP5 | Excessive Feedwater Flow | [45 empty] | La Salle 2 | B | GE | PO | 33 | On December 1, 2000, at 1105 hours, during power ascension from refuel outage L2R08, operators were placing the 2B Turbine Driven Reactor Feedwater Pump (TDRFP) on line. A reactor water level transient occurred that resulted in an automatic high level trip of the main turbine and an associated reactor scram. All equipment operated as expected during the post-trip plant response. The investigation has identified two root causes for this event. There was a human performance component, primarily related to inadequate evolution preparation including failure to perform a Heightened Level of Awareness (HLA) briefing. The second root cause is poor design combined with materiel conditions in the Feedwater and Reactor Level Control system that results in sluggish response of the control system leading to an increased operational challenge. Corrective actions include revising the TDRFP startup procedure, requiring a High Level Activity brief as part of the Reactor Feedwater start up procedure, and a review of the system design and material condition for improvements. The safety consequences of this event were minimal. All systems operated as expected. A turbine trip is an analyzed condition of moderate frequency. The reactor was safely shut down and recovery performed without incident.
374 | 3742001001 | 2001-04-06 | QR5 | Turbine Trip | [45 empty] | La Salle 2 | B | GE | PO | 100 | At 0909 hours on April 6, 2001, LaSalle County Station, Unit 2 automatically scrammed from 100 percent power due to a blown fuse in the feedwater (FW) control system that occurred during maintenance. The blown fuse resulted in multiple failures in the FW control logic, and caused both Reactor Recirculation (RR) pumps to downshift to slow speed. The FW control failures and the level swell from the RR pump downshifts caused a high reactor water level, and the main turbine stop valves to close. This caused an automatic reactor scram due to turbine stop valve closure with reactor power above 25 percent power. The root cause of this event was an inadequate maintenance risk assessment performed for the work. The corrective action to prevent recurrence is to revise the Exelon Nuclear Conduct of Maintenance Manual, 0.5, Maintenance Risk Assessment, to require an evaluation of the risk to the plant for maintenance activities that involve work on an energized circuit with the potential to create a fault in the circuit. The safety consequences of this event were minimal. A RR pump trip, a turbine generator trip, and a loss of FW flow are analyzed conditions of moderate frequency (Updated Final Safety Analysis Report (UFSAR) Chapter 15). The plant responded as described in the referenced UFSAR Chapter. The reactor was safely shut down and recovery performed without incident.
374 | 3742001002 | 2001-05-27 | QR5 | Turbine Trip | [45 empty] | La Salle 2 | B | GE | PO | 80 | At 0618 hours on May 27, 2001, LaSalle County Station, Unit 2 automatically scrammed from 80 percent power. The automatic reactor scram occurred during main turbine control valve (TCV) testing. The root cause of this event was Electrohydraulic Control fluid contamination of a connector for TCV #3 in combination with higher than normal baseline vibration during TCV testing. The contamination resulted in an incorrect TCV #3 position indication which caused TCV #3 to be mispositioned and the remaining TCVs to open further than usual to maintain pressure. When TCV #1 was closed for testing, the combination of the abnormal position of the remaining control valves and an existing main turbine "A" coupling misalignment created an unbalanced load across the high pressure turbine. This resulted in increased vibration, which reached the trip setpoint for the turbine. The corrective action to prevent recurrence included cleaning and replacement of the seal of the fouled connector during the forced outage. The safety consequences of this event were minimal. The turbine generator trip is described as an event of moderate frequency in Chapter 15 of the Updated Final Safety Analysis Report (UFSAR). The plant response was consistent with the referenced UFSAR chapter.
374 | 3742001003 | 2001-09-03 | P1 | Total Loss of Feedwater Flow |  |  | X | [10 empty] | X |  |  |  | X | [26 empty] | X | La Salle 2 | B | GE | PO | 100 | On September 3, 2001, Unit 2 ESF Bus 241Y lost power due to actuation of the Division 1 undervoltage (UV) protective circuit. This caused the feedwater level control circuits to lose power. At 1728 hours, the operators inserted a manual scram because reactor water level could not be controlled. Following the scram, reactor level continued to decrease until High Pressure Core Spray and Reactor Core Isolation Cooling automatically initiated and injected to restore level. All systems operated as designed. Safety relief valves were manually actuated to control reactor water level. All control rods fully inserted. The root cause of this event was that fuses failed in the potential transformer portion of the Division 1 UV protective circuit. This scram was inserted due to loss of feedwater flow at 100% power. This transient is bounded by loss of feedwater event with a single failure. The loss of a single ESF bus caused the loss of some ESF systems. The redundant systems were available and operated as necessary to remove decay heat and control reactor vessel level and pressure.
374 | 3742001004 | 2001-09-07 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | La Salle 2 | B | GE | PO | 75 | On September 7, 2001, at 0024 hours, during power ascesion from a forced outage, at 75 percent power, LaSalle Unit 2 was manually scrammed due to 2 low pressure heater string isolations. All systems operated as designed. There were no ECCS actuations or primary containment isolations. The lowest reactor water level reached was minus 20 inches. All control rods fully inserted. The cause of the event was that the 21A and 21C low pressure heaters were lined up to use the emergency heater drains instead of the normal heater drains. At high power levels the emergency heater drains can not pass the full condensate flow required which caused the feedwater heaters to isolate when the high level trip set points were reached. The manual scram was initiated per procedure to prevent a loss of feedwater flow at less than 100% power due to low pressure heater string isolation. This transient is bounded by loss of feedwater event even if the event occurred at 100% power.
374 | 3742003001 | 2003-01-10 | QP4 | Partial Loss of Condensate Flow | [45 empty] | La Salle 2 | B | GE | PO | 90 | On January 10, 2003, at 1156, Unit 2 was manually scrammed in anticipation of an automatic scram due to decreasing reactor water level. The event was initiated by a trip of the 2B Condensate/Condensate Booster (CD/CB) pump on instantaneous overcurrent. The electrical perturbation, along with a latent failed level switch on the heater drain tank, caused the 2A and 2C Heater Drain pumps to trip. This resulted in a low suction pressure trip of both Turbine Driven Reactor Feed Pumps. When the Operators could not maintain reactor water level, a manual scram was inserted. Reactor water level was restored using the Motor Driven Reactor Feed Pump following the scram. The cause of the trip of the 2B CD/CB pump was a broken lug on the 6.9 kV cable connection to the B phase of the motor. Corrective actions include repairing the termination such that stresses on the connection are limited, and inspecting the terminations to other large motors. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. The Emergency Core Cooling Systems were not challenged.
374 | 3742003004 | 2003-07-07 | QR5 | Turbine Trip | [10 empty] | X | [29 empty] | X |  |  |  |  | La Salle 2 | B | GE | PO | 100 | On 7/7/03, while at 100 percent power, the LaSalle Station Unit 2 main power “B" phase disconnect in the switchyard catastrophically failed, resulting in a main generator trip and reactor scram. The electrical transient tripped the three circulating water pumps, which resulted in the loss of normal heat removal. While controlling reactor pressure and level using the safety relief valves (SRV), the resulting shrink and swell transients caused four additional scram signals on low reactor level. The cause of the disconnect failure could not be established. The cause of the additional scram signals was the lack of an operating strategy for these conditions. The safety significance of this event was minimal. A reactor scram with a loss of the main condenser is an analyzed event. Reactor level and pressure were maintained using Reactor Core Isolation Cooling and the safety relief valves, and the High Pressure Core Spray System was available throughout the event. Corrective actions include development of a condition monitoring program to inspect and monitor the condition of the insulators, and evaluating the adequacy of current switchyard inspection and maintenance procedures.
374 | 3742009001 | 2009-08-15 | QR5 | Turbine Trip | [45 empty] | La Salle 2 | B | GE | PO | 100 | On August 15, 2009, at 1606 hours (CDT), Unit 2 was at 100% power performing weekly. Main Turbine overspeed surveillance testing. During the surveillance, the Main Turbine unexpectedly tripped on an overspeed signal from the Digital. Electro-Hydraulic Control (DEHC) system, causing a reactor scram, The safety significance of the event was minimal. The speed of the Main Turbine was confirmed to have been normal at the time of the trip. All control rods fully inserted, and all systems responded as expected to the scram. The cause of the Main Turbine trip was a failed communication chip on the VCMI card in the DEHC system. The root cause of the event was the failure to adequately understand the impact of a diagnostic alarm from the VCMI card, due to a lack of Vendor information. The failed card was replaced. Other corrective actions include a review of all DEHC alarms to determine their potential impact on plant operations, and revising the DEHC alarm procedures appropriately.
374 | 3732013002 | 2013-04-17 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | La Salle 2 | B | GE | PO | 100 | On April 17, 2013, LaSalle Units 1 and 2 were operating in Mode 1 at 100% power, with a severe thunderstorm in progress. At 1457 hours CDT, lightning struck 138KV Line 0112, resulting in a phase-to-ground fault which subsequently cleared. At 1459 hours, a second phase-to-ground fault on Line 0112 occurred and all 345 KV oil circuit breakers (OCBs) in the main switchyard opened, resulting in a loss of offsite power and reactor scrams on both Units. All emergency diesel generators automatically started and loaded onto their respective busses. All control rods fully inserted, and all systems responded as expected.<br /><br /> An Unusual Event was declared due to a loss of offsite power for greater than 15 minutes. Offsite power was restored to all ESF busses by 2301 hours on April 17, 2013, and the Unusual Event was terminated at 0814 hours on April 18, 2013.<br /><br /> The root cause of the event was determined to be degradation of the 138kV switchyard grounding system that allowed a lightning induced fault to flash over onto the DC protective system. The ground system in the 138kV switchyard was repaired, and corrective actions include improving lightning shielding in the 138kV switchyard.
374 | 3742013002 | 2013-04-25 | QR6 | Manual Reactor Trip | [45 empty] | La Salle 2 | B | GE | PO | 56 | On April 25, 2013, Unit 2 was in Mode 1 at approximately 56% power. The east condenser waterbox was being dewatered in order to address a condenser tube leak. Waterbox isolation valves 2CW007A and 2CW007C had been closed using their motor operators; however, in order to minimize leak-by, an attempt was made to manually seat the valves. These valves are 144 inch butterfly valves with no internal stops. Outlet isolation valve 2CW007C was seated without incident, but inlet valve 2CW007A was inadvertently moved past its closed position, which allowed flow from the running circulating water pumps to fill the waterbox.<br><br> At 2005 hours CDT, the Main Control Room was informed that a large amount of water was coming from the open waterbox upper manways. An attempt was made to close the manways; however, at 2019 hours, the 2A and 2B circulating water pumps tripped on high condenser pit water level, requiring Unit 2 to be manually scrammed.<br><br> The root causes of the event were determined to be a lack of strict procedural adherence on the part of the operators performing the waterbox dewatering task, and inadequate procedure quality. Corrective actions include coaching in accordance with company policies, and clarifying revisions to the circulating water dewatering procedure.
374 | 3742014001 | 2014-08-05 | QL5 | Partial Closure of MSIVs | [45 empty] | La Salle 2 | B | GE | PO | 100 | On August 5, 2014, at approximately 1734 hours CDT, Unit 2 automatically scrammed from 100% power on high neutron flux, followed by a Group I containment isolation. Following the Group I isolation, the control room operators noted that the position indication for valve 2B21-F022C, the inboard 2C Main Steam Isolation Valve (MSIV), showed dual indication rather than full closed. <br /><br /> Troubleshooting of the 2C MSIV determined that the valve stem disk had separated from the stem, which allowed the main disk to drop into the main steam flow path. The resulting reactor pressure transient added positive reactivity, which caused the high neutron flux scram. Increased steam flow in the other three main steam lines resulted in a nearly simultaneous high main steam line flow Group I containment isolation. <br /><br /> The cause of the stem-disk separation on the 2C MSIV was fretting wear attributable to marginal design. The root cause of the event was a legacy decision made in 2008 deferring installation of a manufacturer upgrade that would have prevented the failure. Corrective actions include installing the upgrade on all MSIVs on both units, and reviewing previous deferral decisions made using the same decision-making process.
374 | 3742017001 | 2017-01-23 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | La Salle 2 | B | GE | PO | 99 | On January 23, 2017, operators initiated a manual scram of the LaSalle County Station Unit 2 reactor as a result of observing a generator run-back due to a generator stator winding cooling (GC) system malfunction. Initial troubleshooting identified the most likely cause was plugging in the 'A' GC heat exchanger, based on inspection of the GC system flow-path components. The GC system was realigned to the 'B' heat exchanger until inspections could be performed in the upcoming refueling outage, and the unit was re-started on January 24, 2017.<br /><br /> Further inspections of the GC components were performed while the unit was shut down for a planned refueling outage. These inspections determined the cause of the GC system failure was stem-disc separation in the 'A' GC heat exchanger inlet valve. The valve was repaired during the refueling outage. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of the Reactor Protection System (RPS). There were no safety consequences associated with the event since there was no loss of safety function, and the RPS functioned as designed.
374 | 3742018001 | 2018-08-31 | QR6 | Manual Reactor Trip | [45 empty] | La Salle 2 | B | GE | PO | 29 | On August 31, 2018, while operating at approximately 29 percent power, a reactor manual scram signal was inserted on Unit 2 due to main condenser vacuum degrading. The turbine was tripped following the scram. During the scram, one control rod did not fully insert but was manually fully inserted. The plant was in a stable condition, with reactor pressure being maintained by the turbine bypass valves, and reactor water level was controlled using feedwater. Except for the single control rod insertion, required safety systems and shutdown equipment performed as expected, and there was no impact to Unit 1. This condition was reported on August 31, 2018 (ENS 53576) in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a reactor protection system (RPS) actuation. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in a valid actuation of the RPS. <br /><br /> The condition was attributed to localized impingement degradation of a turbine building miscellaneous equipment drain header resulting in through-wall failure. Corrective actions were taken to install a robust welded temporary patch on the drain header, with a header replacement scheduled for the upcoming Unit 2 refueling outage L2R17 (2019), and revise procedures to incorporate lessons learned. <br /><br /> A root cause investigation identified additional corrective actions necessary to address weaknesses in the original design of the header susceptibility to localized impingement (on both units), revisions to training materials and procedures, and training and communications to engineering staff regarding piping failure mechanisms.
382 | 3821987007 | 1987-03-07 | QR5 | Turbine Trip | [45 empty] | Waterford 3 | P | CE | PO | 56 | POWER LEVEL - 056%. AT APPROXIMATELY 0900 HOURS MARCH 7, 1987 WATERFORD STEAM ELECTRIC STATION UNIT 3 WAS AT 56% POWER WHEN HYDRAULIC FLUID WAS UNISOLATED TO THE NUMBER 4 MAIN TURBINE GOVERNOR VALVE TO FACILITATE VALVE TESTING. AT HIGH POWER LEVELS THIS VALVE IS KEPT CLOSED BY ISOLATION OF HYDRAULIC FLUID TO PREVENT WEAR DUE TO VIBRATION. SINCE THE HIGH PRESSURE AND EMERGENCY TRIP FLUID LINES HAD BEEN INADVERTENTLY REVERSED DURING THE LAST REASSEMBLY OF THE VALVE, EMERGENCY TRIP PRESSURE WAS BLED OFF RESULTING IN RAPID CLOSURE OF ALL TURBINE GOVERNOR AND INTERCEPT VALVES. WITH ONE STEAM BYPASS CONTROL SYSTEM (SBCS) VALVE OUT OF SERVICE, THE IMMEDIATE RESPONSE OF THE SBCS WAS INSUFFICIENT TO LIMIT THE REACTOR COOLANT SYSTEM (RCS) PRESSURE TRANSIENT AND A REACTOR TRIP OCCURRED AT 0901 HOURS ON HIGH RCS PRESSURE. THE HYDRAULIC LINES ON THE NUMBER 4 GOVERNOR VALVE WERE RESTORED TO THEIR PROPER CONNECTIONS AND THE VALVE WAS TESTED AND REISOLATED. THE SBCS CIRCUITRY WAS TESTED AND SHOWN TO RESPOND PROPERLY. THE INOPERABLE SBCS VALVE HAS BEEN REPAIRED. MAINTENANCE PROCEDURES WILL BE REVISED TO EMPHASIZE THE IMPORTANCE OF MARKING LINES OR LEADS PRIOR TO DISASSEMBLY. SINCE ALL SAFETY SYSTEMS FUNCTIONED AS DESIGNED THERE WAS NO SAFETY SIGNIFICANCE TO THIS EVENT.
382 | 3821987008 | 1987-03-15 | QP5 | Excessive Feedwater Flow | [45 empty] | Waterford 3 | P | CE | PO | 100 | POWER LEVEL - 100%. AT 1544 ON MARCH 15, 1987, WATERFORD STEAM ELECTRIC STATION UNIT 3 WAS OPERATING AT 100% POWER WITH THE FEEDWATER CONTROL SYSTEM IN AUTOMATIC WHEN A REACTOR TRIP OCCURRED DUE TO A HIGH WATER LEVEL IN NUMBER 1 STEAM GENERATOR. DUE TO A MALFUNCTION IN THE FEEDWATER CONTROL SYSTEM, WATER ENTERED THE STEAM GENERATORS AT AN EXCESSIVE RATE AND OPERATIONS PERSONNEL HAD INSUFFICIENT TIME TO GAIN MANUAL CONTROL OF STEAM GENERATOR LEVEL BEFORE THE HIGH LEVEL TRIP SETPOINT WAS REACHED. THE CAUSE OF THIS EVENT WAS DUE TO AN INTERMITTENT MALFUNCTION OF THE FEEDWATER CONTROL SYSTEM. THE SPECIFIC CAUSE OF THE MALFUNCTION HAS NOT BEEN DETERMINED, HOWEVER SEVERAL MINOR PROBLEMS WERE IDENTIFIED AND CORRECTED, INCLUDING A BURNED REACTOR TRIP OVERRIDE RELAY, LEAKING VENT PLUGS ON A FEEDWATER FLOW TRANSMITTER, A SHORTED WIRE IN THE FEEDWATER CONTROL CABINET, AND A SUSPECT FEEDWATER FLOW SQUARE ROOT EXTRACTOR. TEMPORARY RECORDERS WERE INSTALLED FOR APPROXIMATELY ONE MONTH TO MONITOR FEED FLOW, STEAM FLOW, FEED FLOW DEMAND, COMPENSATED FLOW ERROR, AND PUMP SPEED TO ENSURE THE CORRECTIVE ACTION TAKEN ELIMINATED THE MALFUNCTION.
382 | 3821987012 | 1987-04-13 | QR3 | Reactivity Control Imbalance | [45 empty] | Waterford 3 | P | CE | PO | 100 | POWER LEVEL - 100%. AT 1230 APRIL 13, 1987, WATERFORD STEAM ELECTRIC STATION UNIT 3 WAS OPERATING AT 100% POWER WITH CONTROL ELEMENT ASSEMBLY CALCULATOR (CEAC) 1 OUT OF SERVICE WHEN A FUNCTIONAL TEST WAS STARTED ON CORE PROTECTION CALCULATOR (CPC) CHANNEL C. BECAUSE OF AN INADEQUATE PROCEDURE CEAC 2 WAS DISABLED INSTEAD OF CPC C AS PLANNED. THIS CAUSED A CEAC FAILURE FLAG TO BE SENT TO ALL FOUR CPCS WHICH PRODUCED TRIPS IN ALL CPC CHANNELS, RESULTING IN A REACTOR TRIP. THE PLANT WAS RESTARTED ON APRIL 14 AND POWER ASCENSION COMMENCED THAT NIGHT. AT 0701 APRIL 15, WITH THE PLANT AT 50% POWER, THE REACTOR POWER CUTBACK SYSTEM WAS PLACED IN AUTOMATIC PRIOR TO STARTING THE SECOND MAIN FEEDWATER PUMP, BECAUSE OF INADEQUATE PROCEDURES. THIS CAUSED GRAVITY INSERTION OF A SUBGROUP OF FOUR CEAS. ALTHOUGH OPERATORS WERE SUCCESSFUL IN STABILIZING PRIMARY PARAMETERS, THE SUBSEQUENT STEAM GENERATOR EVENT TRANSIENT CAUSED A HIGH STEAM GENERATOR LEVEL REACTOR TRIP. ALL SAFETY SYSTEMS FUNCTIONED PROPERLY IN BOTH EVENTS. THE PROCEDURES INVOLVED IN BOTH EVENTS WILL BE THOROUGHLY REVIEWED AND REVISED. OPERATIONS AND MAINTENANCE PERSONNEL HAVE BEEN INSTRUCTED ON THE IMPORTANCE OF RECOGNIZING AND MAKING CHANGES TO INADEQUATE PROCEDURES.
382 | 3821987012 | 1987-04-15 | QR8 | Spurious Reactor Trip | [45 empty] | Waterford 3 | P | CE | PO | 50 | POWER LEVEL - 100%. AT 1230 APRIL 13, 1987, WATERFORD STEAM ELECTRIC STATION UNIT 3 WAS OPERATING AT 100% POWER WITH CONTROL ELEMENT ASSEMBLY CALCULATOR (CEAC) 1 OUT OF SERVICE WHEN A FUNCTIONAL TEST WAS STARTED ON CORE PROTECTION CALCULATOR (CPC) CHANNEL C. BECAUSE OF AN INADEQUATE PROCEDURE CEAC 2 WAS DISABLED INSTEAD OF CPC C AS PLANNED. THIS CAUSED A CEAC FAILURE FLAG TO BE SENT TO ALL FOUR CPCS WHICH PRODUCED TRIPS IN ALL CPC CHANNELS, RESULTING IN A REACTOR TRIP. THE PLANT WAS RESTARTED ON APRIL 14 AND POWER ASCENSION COMMENCED THAT NIGHT. AT 0701 APRIL 15, WITH THE PLANT AT 50% POWER, THE REACTOR POWER CUTBACK SYSTEM WAS PLACED IN AUTOMATIC PRIOR TO STARTING THE SECOND MAIN FEEDWATER PUMP, BECAUSE OF INADEQUATE PROCEDURES. THIS CAUSED GRAVITY INSERTION OF A SUBGROUP OF FOUR CEAS. ALTHOUGH OPERATORS WERE SUCCESSFUL IN STABILIZING PRIMARY PARAMETERS, THE SUBSEQUENT STEAM GENERATOR EVENT TRANSIENT CAUSED A HIGH STEAM GENERATOR LEVEL REACTOR TRIP. ALL SAFETY SYSTEMS FUNCTIONED PROPERLY IN BOTH EVENTS. THE PROCEDURES INVOLVED IN BOTH EVENTS WILL BE THOROUGHLY REVIEWED AND REVISED. OPERATIONS AND MAINTENANCE PERSONNEL HAVE BEEN INSTRUCTED ON THE IMPORTANCE OF RECOGNIZING AND MAKING CHANGES TO INADEQUATE PROCEDURES.
382 | 3821987016 | 1987-05-25 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Waterford 3 | P | CE | PO | 100 | POWER LEVEL - 100%. ON MAY 25, 1987, WATERFORD STEAM ELECTRIC STATION UNIT WAS OPERATING AT 100% POWER WITH THE FEEDWATER CONTROL SYSTEM IN AUTOMATIC. AT 1340 HOURS A FUSE IN THE FEEDWATER CONTROL SYSTEM FAILED OPEN WHICH CAUSED THE B MAIN FEEDWATER PUMP (MFWP) TO GO TO MINIMUM SPEED. EACH MFWP CAN SUPPLY 63% FEEDWATER FLOW, SO STEAM GENERATOR LEVELS DECREASED RAPIDLY. DUE TO THE NATURE OF THE FAILURE, THE PUMP DID NOT RESPOND TO MANUAL CONTROL, AND A REACTOR TRIP ON LOW STEAM GENERATOR LEVELS OCCURRED AT 1343 HOURS. NO CONDITIONS COULD BE IDENTIFIED WHICH WOULD HAVE CAUSED THE FUSE TO BLOW. THE FAILURE WAS THEREFORE CLASSIFIED AS A RANDOM FUSE FAILURE. AS A PRECAUTION THE ASSOCIATED CIRCUIT CARD WAS REPLACED. THE EMERGENCY FEEDWATER SYSTEM FUNCTIONED PROPERLY THROUGHOUT THE EVENT AND THE AUXILIARY FEEDWATER PUMP WAS AVAILABLE HAD IT BEEN NEEDED. SINCE ALL PROTECTIVE FEATURES FUNCTIONED AS DESIGNED, THERE WAS NO THREAT TO THE HEALTH AND SAFETY OF THE PUBLIC OR PLANT PERSONNEL.
382 | 3821987020 | 1987-07-31 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Waterford 3 | P | CE | PO | 100 | POWER LEVEL - 100%. AT APPROXIMATELY 2000 HOURS JULY 31, 1987, WATERFORD STEAM ELECTRIC STATION, UNIT 3 WAS OPERATING AT APPROXIMATELY 100% POWER WHEN CIRCULATING WATER WAS ISOLATED FROM A MAIN CONDENSER WATERBOX FOR CLEANING. THE CONDENSER LEVEL AND PRESSURE CHANGES INDUCED BY THIS REDUCTION IN HEAT REMOVAL CAUSED A LEVEL INCREASE IN THE A MAIN FEEDWATER PUMP (MFP) TURBINE CASING DRAIN TANK. THE A MFP SUBSEQUENTLY TRIPPED ON HIGH LEVEL IN THIS TANK. THE REACTOR POWER CUTBACK SYSTEM (RPCS) ACTED PROPERLY TO REDUCE TURBINE LOAD, BUT FAILED TO DROP CONTROL ELEMENT ASSEMBLIES TO REDUCE REACTOR POWER. THE REACTOR SUBSEQUENTLY TRIPPED ON HIGH PRESSURIZER PRESSURE. THE ROOT CAUSE OF THIS EVENT IS THAT THERE IS INSUFFICIENT OPERATING MARGIN BETWEEN THE HIGH LEVEL MFP TRIP AND LOW HOTWELL LEVEL CONDENSATE PUMP TRIP SETPOINTS TO ACCOMMODATE SUCH TRANSIENTS UNDER HIGHLY ADVERSE CONDITIONS. PROCEDURES HAVE BEEN CHANGED TO REQUIRE MONITORING OF ADDITIONAL PARAMETERS AND SLOWER VALVE OPERATION DURING WATERBOX ISOLATION. IN ADDITION, WHEN SIMILAR CONDITIONS EXIST POWER WILL BE REDUCED PRIOR TO WATERBOX ISOLATION. THE SEMICONDUCTOR WHICH CAUSED THE RPCS MALFUNCTION WAS REPAIRED. SINCE ALL SAFETY SYSTEMS WHICH WERE REQUIRED FUNCTIONED PROPERLY, THERE WAS NO EFFECT ON PUBLIC HEALTH AND SAFETY AS A RESULT OF THIS EVENT.
382 | 3821987028 | 1987-12-11 | QL5 | Partial Closure of MSIVs | [13 empty] | X | [30 empty] | X | Waterford 3 | P | CE | PO | 90 | POWER LEVEL - 090%. ON DECEMBER 11, 1987, WATERFORD STEAM ELECTRIC STATION UNIT 3 WAS OPERATING AT 90% POWER WHEN A REACTOR TRIP OCCURRED DUE TO THE INADVERTENT SHUTTING OF A MAIN STEAM ISOLATION VALVE (MSIV). AT 0754 HOURS, WITH THE AUXILIARY FEEDWATER PUMP TAGGED OUT AND THE HIGH PRESSURE STEAM SUPPLY TO MAIN FEEDWATER PUMP (MFWP) TURBINE A ISOLATED, MSIV TESTING WAS IN PROGRESS WHEN MSIV #2 WENT PARTIALLY SHUT DUE TO A FAILED SOLENOID VALVE. THIS RESULTED IN A CORE PROTECTION CALCULATOR TRIP DUE TO A LARGE DIFFERENCE IN REACTOR COLD LEG TEMPERATURES. THE MSIV CLOSURE ALSO CAUSED A STEAM GENERATOR (SG) SECONDARY SIDE PRESSURE RELIEF VALVE TO LIFT. BOTH MFWP'S TRIPPED AFTER THE REACTOR TRIP, BUT THE EMERGENCY FEEDWATER SYSTEM FUNCTIONED PROPERLY THROUGHOUT THE EVENT TO MAINTAIN SG LEVELS. THE MSIV WENT PARTIALLY SHUT BECAUSE A SOLENOID VALVE (SV) STUCK OPEN DURING TESTING ALLOWING BOTH HYDRAULIC SYSTEM DUMP VALVES TO BE OPEN SIMULTANEOUSLY AND DRAIN THE HYDRAULIC FLUID FROM THE MSIV ACTUATOR. THE SV WAS REPLACED AND THE MSIV TESTED SUCCESSFULLY PRIOR TO RESTARTING THE PLANT. THE SV HAS BEEN RETURNED TO THE MANUFACTURER FOR ANALYSIS AND RECOMMENDATIONS. SINCE ALL PROTECTIVE FEATURES FUNCTIONED AS DESIGNED, THERE WAS NO THREAT TO THE HEALTH AND SAFETY OF THE PUBLIC OR PLANT PERSONNEL.
382 | 3821988001 | 1988-01-01 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Waterford 3 | P | CE | PO | 13 | At 1327 hours on January 1, 1988, Waterford Electric Station Unit 3 was operating at approximately 13% power when the reactor tripped due to out-of-range Axial Shape Index (ASI). ASI, a measure of core power distribution, causes an auxiliary trip of the Core Protection Calculators (CPCs) if ASI is out of its allowed band and power is greater than approximately 17%. This condition occurs during a startup conducted before most of the xenon produced during previous operation has decayed. The enabling of this trip is based on raw excore detector signals, but operators were not previously aware of this fact. Operators were maintaining power at approximately 13 to 15% by compensated power indications when the Reactor tripped after a short withdrawal of Control Element Assemblies. This event is reportable as an automatic protective system actuation. <br /><br />The root cause of this event was inadequate procedures since sufficient guidance is not provided for ASI control during reactor startup. Information on CPC monitored ASI at low powers has been disseminated. Procedures have been revised so that reactor power signals used by CPCs to determine ASI will be monitored, and allowable operating margins to the ASI and power limits provided. Since all protective features functioned as designed, there was no threat to the health and safety of the public or plant personnel.
382 | 3821988002 | 1988-01-26 | QR6 | Manual Reactor Trip | [45 empty] | Waterford 3 | P | CE | PO | 86 | At 1019 hours on January 26, 1988, Waterford Steam Electric Station Unit 3 was at 86% power when the Reactor was manually tripped due to high temperature on Reactor Coolant Pump (RCP) 2B Upper Thrust Bearing (UTB). The UTB temperature had been slowly rising for 3 days. At 0730 hours it was noted that the temperature was near the limit and a shutdown was anticipated later in the day. At 1000 hours temperature began to increase markedly and a rapid shutdown was commenced. At 1019 hours the UTB temperature exceeded the predetermined limit and the Reactor was manually tripped. Steam Generator levels dropped low enough to actuate the Emergency Feedwater (EFW) System but not low enough to initiate EFW Flow. RCP 2B was secured after the Reactor trip. All automatic systems and protective features functioned as designed. <br /><br />The root cause of this event was a clogged oil strainer in the UTB lube oil system. RCP 2B UTB overheating due to a clogged strainer has now resulted in three forced outages. During the recovery from this event the small mesh strainer was replaced with a larger mesh strainer. There was no indication of damage to RCP 2B or its motor. Since the Reactor was manually tripped to avoid damage to plant equipment, there was no safety significance to this event.
382 | 3821988016 | 1988-06-14 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Waterford 3 | P | CE | PO | 12 | At 2246 hours on June 14, 1988, Waterford Steam Electric Station Unit 3 was operating at approximately 12% power when the Reactor tripped due to low Steam Generator (SG) water level. Prior to the trip, Turbine Generator (TG) control had been transferred from Throttle to Governor Valves when an Overspeed Protection Control (OPC) signal caused the Governor and Intercepter valves to close. The TG stabilized at 1800 rpm. The OPC Test Switch was then placed in test to reseat an OPC solenoid valve which was believed to be stuck open. When the switch was returned to normal, TG Governor Valves reopened, causing a sudden increase in steam demand resulting in a large swell in SG levels. The rise in SG Downcomer Level caused the Feedwater Isolation Valves to shut, tripping Main Feed Pump "A". SG levels subsequently lowered to the low level trip setpoint as feed was being restored. SG levels were restored and the plant was stabilized in hot standby. <br /><br /> The root cause of the event was equipment malfunction. A circuit card for Governor Valve Number Two failed causing the valve to remain at least 25% open. The circuit card was replaced. The cause of the MFP trip is under investigation. Procedures are being revised to include precautions for OPC testing. Since all safety systems functioned as designed, there was no safety significance to this event.
382 | 3821988033 | 1988-12-08 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Waterford 3 | P | CE | PO | 100 | At 1311 hours on December 8, 1988, Waterford Steam Electric Station Unit 3 was operating at 100% power when a transient induced by the cycling of Power Distribution Panel (PDP) 3014AB breakers caused the reactor to trip on low Departure from Nucleate Boiling Ratio (DNBR). The PDP cover slipped while being removed for maintenance, causing one-half of the PDP breakers to open. The maintenance personnel closed the breakers causing pressurizer pressure instrument control loops to reenergize; this appeared to the Steam Bypass Control System and Reactor Power Cutback System (RPCS) as a large load rejection. Steam bypass control valves quick-opened and the RPCS actuated. Due to the loss of power to Main Turbine (MT) control circuits, the MT was not setback by the RPCS. With the resulting steam demand greater than reactor power, Reactor Coolant System (RCS) pressure decreased and the Core Protection Calculators tripped the reactor on anticipated low DNBR. <br /><br />The root cause of this event is inadequate administrative control of work performed on or around equipment that could cause a plant trip or safety system actuation. A directive is being developed to aid in the planning and approval of high risk tasks. Since safety systems functioned to protect the plant, there was no danger to the health or safety of the public or plant personnel.
382 | 3821989013 | 1989-07-15 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Waterford 3 | P | CE | PO | 100 | On July 19, 1989, Waterford Steam Electric Station Unit 3 was operating at 100% power when a rapidly decreasing level was observed in Steam Generator number 1. The Main Feedwater Regulating valve for this steam generator was found closed. The controller for the valve was switched to manual and the valve was opened in an attempt to restore the steam generator level. When it became apparent that the level could not be restored before receiving a low Steam Generator level Reactor trip, a manual Reactor trip was initiated. <br /><br /> The root cause for the event was attributed to a circuit failure in the position control circuitry for the Main and Startup Feedwater Regulating valves for Steam Generator number 1. The circuit card containing the failed component was replaced and the system restored to normal. During the course of this event no threat to the health or safety of the public or plant personnel existed.
382 | 3821989017 | 1989-08-19 | QR3 | Reactivity Control Imbalance | [45 empty] | Waterford 3 | P | CE | PO | 23 | At 1319 hours on August 19, 1989, an automatic reactor trip of Waterford Steam Electric Station Unit 3 occurred while operating at 23% power. The trip was initiated by the Plant Protection System (PPS) in response to variations in core axial shape index (ASI), a measure of core power distribution, induced by the down power required for an abnormal control element assembly (CEA) configuration. This event is reportable as an automatic reactor protection system actuation.<br /><br /> The root cause of this event is equipment malfunction. During routine CEA operability testing, CEA 18 would not move in either direction. After repairs were made to CEA control circuitry, CEA 18 was inserted below the Technical Specification (TS) limit of 145 inches while verifying response. CEA 18 would not withdraw, necessitating a reactor power reduction per TSs. While attempting to control ASI subsequent to the power reduction, the reactor tripped. The defective equipment has been replaced and tested satisfactorily. Because protective features functioned as designed, the health and safety of the general public or plant personnel was not adversely affected by this event.
382 | 3821989024 | 1989-12-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Waterford 3 | P | CE | PO | 100 | At 1109 hours on December 23, 1989, control room operators initiated a manual reactor trip of Waterford Steam Electric Station Unit 3 while operating at 100% power. The trip was initiated in response to decreasing level in Steam Generator (SG) #1 after Main Feed Regulating Valve (MFRV) #1 unexpectedly failed shut. Shortly after the reactor trip, MFRV #1 opened inadvertently. A Reactor Coolant System (RCS) cooldown and a corresponding RCS pressure drop to approximately 1640 psia resulted, generating a Safety Injection Actuation Signal (SIAS). An Emergency Feedwater Actuation Signal (EFAS) was also generated during the post-trip transient.<br /><br /> The root cause of this event was an anomaly in the MFRV pneumatic control system aggravated by cold weather effects on system components. A degraded diaphragm in the MFRV volume booster led to the inadvertent shutting of MFRV #1. All safety systems functioned as designed; therefore, this event did not threaten the health and safety of the general public or plant personnel.
382 | 3821990002 | 1990-03-22 | QR3 | Reactivity Control Imbalance | [45 empty] | Waterford 3 | P | CE | PO | 100 | At 2133 hours on March 22, 1990, an automatic reactor trip occurred at Waterford Steam Electric Station Unit 3 while the plant was operating at 100% power. The reactor trip was initiated by the Plant Protection System when two control element assemblies (CEAs) dropped to the fully inserted position while their drive mechanisms were being transferred from their normal power supply to the control element drive mechanism system (CEDMCS) hold bus. This event is reportable by reason of the occurrence of an automatic reactor protection system actuation. <br /><br /> The root cause of this event was an equipment malfunction. Inspections subsequent to the trip revealed that several electrical connectors used to transmit power from the CEDMCS panels to a CEA drive mechanism were damaged from misalignment during previously performed maintenance. This condition disrupted the power supply circuitry of the CEA drive motors affected, causing disengagement of the drive mechanisms for these CEAs. The damaged components in the power supply circuitry were replaced and operationally checked to be satisfactory. All plant protective features functioned as designed and no threat was posed to the health or safety of the general public or plant personnel during this event.
382 | 3821990003 | 1990-03-29 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [10 empty] | X |  |  | X | [27 empty] | X |  |  | X | Waterford 3 | P | CE | PO | 100 | At 0730 hours on March 29, 1990, with Waterford Steam Electric Station Unit 3 at 99.9% power, a severe transient on the 230 KV power transmission grid at Taft, Louisiana, resulted in a reactor trip. The transient was initiated when an Occidental Chemical Company employee caused a fault at the 230 KV substation owned by the chemical company. The reactor coolant pumps slowed to less than 96.5 % of normal speed as voltage dropped. This generated a low multiplier in the Core Protection Calculators and a reactor trip occurred due to an anticipatory Departure from Nucleate Boiling Ratio trip signal. This event is reportable as an automatic reactor protection system actuation. This supplement is submitted for potential generic interest with respect to off-site grid conditions. <br /><br /> As a result of this system transient, a degraded voltage condition occurred on the 4.16 KV 'B' safety bus when a 'B' bus tie breaker opened automatically which de-energized the 'B' safety bus. Emergency Diesel Generator 'B' started and re-energized the 'B' safety bus as designed. The root cause of this event was a grid voltage drop on the Louisiana Power and Light Company 230 KV system caused by a fault at Occidental Chemical Company. Because plant protective features functioned as designed, this event did not threaten the health or safety of the general public or plant personnel.
382 | 3821990012 | 1990-08-25 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Waterford 3 | P | CE | PO | 100 | At 1802 hours on August 25, 1990, with Waterford Steam Electric Station Unit 3 at 100% power, a severe voltage transient on the southeastern Louisiana 230 KV power transmission grid resulted in a reactor trip. The transient was initiated when a fault attributed to a lightning strike occurred at the Waterford 230 KV switchyard. One circuit breaker exploded and burned. The rapid reduction in load on the main generator, combined with an inoperable steam bypass control system caused reactor coolant system temperature and pressure to increase. A reactor trip occurred due to high pressurizer pressure. This event is reportable as an automatic reactor protection system actuation. <br /><br /> As a result of this system transient, voltage on the Waterford 230KV switchyard decayed to 33 KV over a two second period. An investigation concluded that the in-plant safety bus voltage level did not drop low enough for a sufficient duration to actuate the undervoltage relays associated with the emergency diesel generators. <br /><br /> The root cause of this event was the severe grid disturbance, which is attributed to a lightning strike. Because plant protective features functioned as designed, this event did not threaten the health or safety of the general public or plant personnel.
382 | 3821991011 | 1991-05-28 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Waterford 3 | P | CE | PO | 34 | At 0809 hours on May 28, 1991, the Waterford Steam Electric Station Unit 3 main turbine was manually tripped due to a loss of governor control. After the turbine trip, an automatic reactor trip occurred when the electrical bus powering two reactor coolant pumps failed to transfer from the unit auxiliary transformers to the startup transformers upon loss of the main turbine. During the subsequent transient, a Main Steam Isolation Signal actuation occurred. This event is being reported as unplanned actuations of engineered safety features. <br /><br /> The root cause of this event was a faulty relay that prevented the electrical bus transfer. A contributing cause to this event was an inadequate procedure that, during troubleshooting of the main turbine digital electro hydraulic system, caused the loss of governor control. Another contributing cause to this event was a ground in a maintenance cabinet that caused main turbine load fluctuations. The faulty relay was replaced, the procedure revised and the cause of the ground removed. Plant protective features functioned as designed; therefore, this event did not threaten the health or safety of the general public or plant personnel.
382 | 3821991013 | 1991-06-24 | QP5 | Excessive Feedwater Flow | [45 empty] | Waterford 3 | P | CE | PO | 25 | At 1315 hours on June 24, 1991, the reactor at Waterford Steam Electric Station Unit 3 was manually tripped due to high water level in Steam Generator (SG) #2. Four SG #2 high level reactor pre-trip alarms were received prior to manually initiating a reactor trip. A main steam isolation signal was manually actuated subsequent to the reactor trip as a result of excessive cool down rate. This event is reportable as an unplanned reactor protection system actuation. <br /><br /> The root cause of this event is SG #2 startup feedwater regulating valve failing open while at approximately 25 percent reactor power. A process analog control (PAC) card in the valve control circuitry failed, resulting in a constant open signal to SG #2 startup feedwater regulating valve. The PAC card was replaced and PAC card performance will be trended as part of the Long Term Reliability Program. Plant protective features functioned as designed; therefore, this event did not threaten the health or safety of the general public or plant personnel.
382 | 3821991019 | 1991-08-25 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Waterford 3 | P | CE | PO | 100 | On August 25, 1991, at 0214 hours while performing OP-903-107, Plant Protection System Functional Test, the plant received a Safety Injection Actuation Signal (SIAS), Containment Isolation Actuation Signal (CIAS), and Main Steam Isolation Signal (MSIS). Subsequently, a Reactor Trip occurred on loss of power to the Control Element Drive Mechanism motor generator sets due to the SIAS. Operations Control Room personnel entered the Emergency Operating Procedures and carried out the immediate operator actions. Recovery was performed in accordance with OP-902-006, Loss of Main Feedwater Procedure. The root cause of the event was an unforseen design problem. When the Matrix Relay Hold pushbutton (Cutler-Hammer Model #10250T506) was pushed, the speed of insertion was rapid enough such that the energization of the test coils occurred before the energization of the hold coils, resulting in an actuation of the SIAS, CIAS, and MSIS functions under test. A modification is being considered by System Engineering to replace the pushbutton with a three 3) position spring return handswitch.
382 | 3821991022 | 1991-11-17 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Waterford 3 | P | CE | PO | 100 | At 0324 hours on November 17, 1991, while performing OP-903-107, Plant Protection System Functional Test, the plant received a Safety Injection Actuation Signal (SIAS), Containment Isolation Actuation Signal (CIAS), and Main Steam Isolation Signal (MSIS). Subsequently, a reactor trip occurred on loss of power to the Control Element Drive Mechanism motor generator sets due to the SIAS. Operations Control Room personnel entered the Emergency Operating Procedures and carried out the immediate operator actions. Recovery was performed in accordance with OP-902-006, Loss of Main Feedwater Procedure. Inspection of the test cabinet revealed a loose wire connection in the CD matrix test circuitry. The loose wire connection was tightened and a system retest was performed satisfactorily. <br /><br /> The cause of this event was a test circuit malfunction which was caused by a loose connection on TB701 Terminal 2. The cause of the loose connection could not be positively determined and may have existed for some time. Waterford 3 is implementing a design change to install test circuit enhancements.
382 | 3821993001 | 1993-03-04 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Waterford 3 | P | CE | PO | 100 | On March 4, 1993 at 2045, Waterford 3 was operating at 100% power when a reactor trip occurred as a result of two nearly simultaneous power supply failures. The failures deenergized elements of two channels of the Plant Protection System (PPS) which satisfied the coincidence logic and resulted in the reactor trip. <br /><br /> The first failure appears to be the result of age-related degradation of a frequency detection card in a static uninterruptible power supply. The second power supply was lost when its supply breaker opened during the subsequent electrical transient. Further analysis indicates that several of the power supply output capacitors were degraded.<br /><br /> In addition to replacing failed components, corrective action will include review of other applications of this equipment and the addition of periodic checks to identify power supply degradation. Since the PPS "failed safe," as expected, and generated the required reactor trip, this event posed no risk to the health and safety of the public.
382 | 3821993002 | 1993-06-15 | QP5 | Excessive Feedwater Flow | [45 empty] | Waterford 3 | P | CE | PO | 100 | On June 15, 1993, at 1604 hours, Waterford 3 was operating in Mode 1 at 100% power when the reactor tripped due to a high Steam Generator level caused by the failure of the Feedwater Control System (FWCS). <br /><br /> The root cause of this event was the failure of the square root extractor in the feedwater flow circuit for FWCS #1. The failure caused calculated feedwater flow to drop to zero and generated a high demand signal from FWCS #1 which, in turn, caused the #1 Feedwater Regulating Valve to go fully open and overfeed the #1 steam generator.<br /><br /> Corrective action for this event includes, in part, replacement and analysis of failed components, review of alarm set points (two expected alarms were not received during the event), operator training, and reevaluation of Feedwater Control System troubleshooting practices. This event posed no risk to the health and safety of the general public or plant personnel. Similar events include LER's 85-041, 87-008, 89-013, and 91-013.
382 | 3821994007 | 1994-04-26 | QR1 | RCS Low Pressure (RPS Trip) PWR | [45 empty] | Waterford 3 | P | CE | PO | 70 | At 0808 on April 26, 1994, a Reactor Power Cutback and Turbine Setback to 50% governor valve position occurred while placing the Reactor Power Cutback system in service at 70% reactor power. An automatic reactor trip occurred approximately 2 minutes later due to a low Pressurizer Pressure Core Protection Calculator Auxiliary trip set at 1860 psia. The Reactor Power Cutback actuation was caused by the presence of an erroneous Feedwater pump 'B' trip input signal to the Reactor Power Cutback circuitry. The subsequent low Pressurizer pressure and reactor trip resulted from the cooldown induced by a mismatch between turbine power and reactor power following the Reactor Power Cutback. The root cause of the erroneous Feedwater pump 'B' trip input signal was found to be a failure of a Westinghouse model BFD44S non-safety relay which provides 'B' Feedwater pump trip status input to the Reactor Power Cutback circuitry. Immediate corrective actions included replacing the faulty relay and removing the Reactor Power Cutback system from service. Subsequent corrective actions will include, in part, evaluations and enhancements along with event review by operations personnel. This event did not compromise the public health and safety.
382 | 3821995002 | 1995-06-10 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Waterford 3 | P | CE | PO | 100 | On June 10, 1995, a fault recorder at the Waterford Switchyard recorded a single phase fault. Subsequent inspection identified a failed C phase lightning arrestor on a Substation Transformer. At approximately the same time, with the plant in mode 1 at 100% power, a reactor trip occurred, and one of the two independent offsite power sources was lost. Shortly thereafter, a report was received from the Turbine Generator Building (TGB) operator of smoke in the TGB switchgear. The 4.16 KV non-safety related A2 bus in the TGB switchgear caught fire causing damage to the bus and surrounding cables and components. The fire damage was limited mainly to the Unit Auxiliary Transformer Feeder Breaker supplying the A2 bus and the adjoining meter cabinet. The root cause of the fire in the A2 switchgear was the improper automatic bus transfer from the Unit Auxiliary Transformer to the Startup Transformer and the root cause of the reactor trip was low Departure from Nucleate Boiling Ratio. During the recently completed Refueling Outage, a new automatic bus transfer scheme was installed at Waterford 3. This event did not compromise the health and safety of the public.
382 | 3821996006 | 1996-05-17 | QR3 | Reactivity Control Imbalance | [45 empty] | Waterford 3 | P | CE | PO | 100 | On May 17, 1996 at 2008 hours, with the plant in mode 1 at 100% power, a reactor trip occurred without any precursor alarms. The cause of the trip was the loss of both Control Element Drive (CED) Motor/Generator (M/G) Sets due to a failed voltage regulator based on heat related accelerated aging. The electrolytic capacitors on both M/G Set Overvoltage Relays were replaced and the retest was satisfactory. Also the 'A' M/G Set Voltage Regulator was replaced and the retest was successful. The plant responded as designed and the trip/actuation signals were generated when required. The plant was maintained throughout this event such that the health and safety of the general public was not compromised.
382 | 3821998014 | 1998-07-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Waterford 3 | P | CE | PO | 92 | On July 16, 1998, at approximately 1100 CDT, while operating in Mode 1 at 92% reactor power, the reactor was manually tripped due to rapidly decreasing levels in both steam generators (SG) caused by a reduction in Feedwater Pump Turbine (FWPT) 'A' speed. Following the manual reactor trip, Emergency Feedwater Actuation System (EFAS) was actuated by SG low level, initiating Emergency Feedwater flow to both SGs. Emergency Feedwater (EFW) flow control valve logic to SG#1 malfunctioned, requiring manual operator action to control SG level. The root cause of the reduction in FWPT 'A' speed and loss of Steam Generator Feedpump (SGFP) was attributed to a short circuit in the FWPT 'A' speed control relay due to condensation. The most probable root cause of the EFW flow control valve logic malfunction was an intermittent failure of a mercury wetted nuclear relay card (NRC) in the EFW flow control valve level control mode circuit. The manual reactor trip and EFW flow control valve logic malfunction condition did not compromise the health and safety of the public.
382 | 3821999006 | 1999-06-14 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Waterford 3 | P | CE | PO | 100 | On June 14, 1999, at 1307 hours, while at 100% power, Waterford 3 experienced an automatic reactor trip when the A1 7KV electrical bus was lost. An investigation of the event has determined the most probable cause of loss of the A1 7KV electrical bus and subsequent reactor trip to be a spurious actuation of a relay on either Reactor Coolant Pump 1A or 2A. Immediately following the trip, Operations personnel entered Emergency Entry Procedure, OP-902-000 and subsequently Uncomplicated Reactor Trip Recovery Plan Procedure, OP-902-001. The plant was stabilized in Mode 3, Hot Standby. Various plant components were walked downed and tested to determine the root cause of the event. Although the root cause of this event is indeterminate, the Reactor Protection System performed as designed. A low Departure from Nucleate Boiling Ratio (DNBR) trip was initiated due to decreasing speed of Reactor Coolant Pumps (RCPs) 1A and 2A, which was caused by the loss of the A1 7KV Bus. Required plant systems responded and the appropriate trip/actuation signals were generated. The health and safety of the general public were not compromised during this event.
382 | 3821999011 | 1999-08-01 | QR6 | Manual Reactor Trip | [45 empty] | Waterford 3 | P | CE | PO | 100 | On August 1, 1999, at 2136, with Waterford 3 operating at 100% power, an alarm for Middle Seal Pressure Low on Reactor Coolant Pump (RCP) 2B was received. Upon investigation, Operations personnel discovered lowering RCP seal pressures, along with dropping Controlled Bleed-Off (CBO) flow and increasing CBO temperature. Operations personnel entered the appropriate Off-Normal procedure for a reactor coolant pump malfunction. Initial actions were to attempt to lower CBO temperature by lowering Component Cooling Water (CCW) temperature to the RCP heat exchanger. Attempts to lower CBO temperature were unsuccessful. Within 13 minutes, CBO temperatures increased to 204 degrees F, CBO flow dropped to zero gallons per minute, and middle and upper seal pressures dropped to 100 psi. Operations personnel manually tripped the reactor and secured RCP 2B. The cause of this event is believed to be fatigue-induced failure of the rotating baffle of RCP 2B. This event did not compromise the health and safety of the public.
382 | 3821999014 | 1999-09-10 | QR6 | Manual Reactor Trip | [45 empty] | Waterford 3 | P | CE | PO | 100 | On September 10, 1999, with Waterford 3 operating normally at 100% power, a Plant Monitoring Computer (PMC) alarm for Middle Seal Pressure Low on Reactor Coolant Pump (RCP) 2B was received. Upon investigation, Operations personnel discovered decreasing RCP seal pressures, along with decreasing Controlled Bleed-Off (CBO) flow. Operations personnel entered the appropriate Off-Normal procedure for a reactor coolant pump malfunction. CBO flow decreased to zero gallons per minute (gpm), and middle and upper seal pressures also decreased. Operations personnel manually tripped the reactor and secured RCP 2B. Initial disassembly involved removal of the seal for RCP 2B and inspection of the rotating baffle. Initial inspection showed the baffle's joint securely attached. However, the baffle had an observed through-wall crack 360 degrees around the inner surface of the inner cylinder. The cause of this event is believed to be fatigue-induced failure of the rotating baffle of RCP 2B. Corrective actions include replacing the one-piece rotating baffle with a more robust two-piece rotating baffle, completing and finalizing a Finite Element Analysis of the baffle, realigning RCP 2B, and revising the RCP maintenance procedure to include checking and correcting, as necessary, the RCP shaft shoulder to baffle joint for perpendicularity and flatness. This event did not compromise the health and safety of the public. A previous plant shutdown due to failure of the RCP 2B baffle was documented in LER 99-011-00 dated August 31, 1999.
382 | 3822001003 | 2001-02-13 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Waterford 3 | P | CE | PO | 80 | On February 13, 2001 with reactor power at approximately 80% power, a secondary transient resulted in a reactor trip. During power escalation following replacement of a Tracker Driver Card on Steam Generator Feed Pump 'A' Speed Controller, turbine valve testing was being performed. Turbine Governor Valve (GV) #3 oscillated twice during testing. The resulting secondary transient caused a reactor trip initiated by a Core Protection Calculator generated Variable Over Power Auxiliary Trip. Emergency Feedwater Actuation Signals (EFAS) 1 and 2 automatically initiated on Steam Generator (SG) Level-Low starting all 3 Emergency Feed Water (EFW) pumps but no flow was delivered to the SGs. This is expected, following a reactor trip. The root cause of this event was determined to be failure of the GV #3 PARC 7300 Card. The circuit card was replaced and sent to the vendor for analysis. This event is reportable pursuant to 50.73(a)(2)(iv)(A) as an automatic actuation of the Reactor Protection System. This event did not compromise the health and safety of the public. This event is not considered a Safety System Functional Failure (SSFF).
382 | 3822005005 | 2005-11-11 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Waterford 3 | P | CE | PO | 100 | On November 11, 2005, at approximately 20:34, with the plant operating at 100% power (Mode 1), Waterford 3 manually tripped the reactor due to lowering Main Condenser vacuum, caused by a loss of all Circulating Water (CW) Pumps. Subsequently Emergency Feedwater Actuation Signals (EFAS-1 and EFAS-2) were received due to low Steam Generator Levels. The plant was then maintained in Mode 3 with both Steam Generators being fed from the Auxiliary Feedwater System with Steam Generator levels in the normal operational band for Mode 3. Failure Mode identified a degraded timer relay in the CW Pump discharge valve control circuit as the most likely cause. The relay was replaced prior to plant restart. Emergency Feedwater actuated automatically. Adequate water level was maintained in the Steam Generator to ensure decay heat removal from the RCS. The event is not considered a Safety System Functional Failure. The event did not compromise the health and safety of the general public.
382 | 3822009005 | 2009-10-19 | QR6 | Manual Reactor Trip | [45 empty] | Waterford 3 | P | CE | PO | 100 | On October 19, 2009, at approximately 09:44 with the plant operating at 100% power (Mode 1), Waterford 3 manually tripped the reactor due to lowering condenser hotwell level caused by a stuck open moisture separator reheater relief valve. The Plant Protection System (PPS) responded as designed, resulting in an uncomplicated reactor trip. Subsequently, Emergency Feedwater Actuation Signals (EFAS-1 and EFAS-2) were received due to low Steam Generator (SG) levels which is an anticipated response to the reactor trip with the plant at or near full power. The emergency feedwater system did not receive a signal to send water to the steam generators. The plant was then maintained in Mode 3 with both steam generators being fed from the main feedwater system with steam generator levels in the normal operational band for Mode 3. Failure Mode Analysis (FMA) identified a broken pilot valve spring on the stuck open moisture separator heater relief valve. The pilot valve spring was replaced on all six moisture separator heater relief valves prior to unit restart. Adequate water level was maintained in the steam generators to ensure decay heat removal from the Reactor Coolant System (RCS). The event is not considered a safety system functional failure. The event did not compromise the health and safety of the general public.
382 | 3822013001 | 2013-01-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Waterford 3 | P | CE | PO | 91 | On January 21, 2013 at 15:51 CST, Waterford 3 experienced an automatic reactor trip from approximately 91% power due to lowering Steam Generator (SG) #1 level following the unexpected closure of Main Feedwater Regulating Valve #1 due to an instrument air line failure. Emergency Feedwater (EFW) Actuation Signals (EFAS-1 and EFAS-2) were received due to low SG levels, which is an anticipated response to the reactor trip with the plant at or near full power. SG #1 received EFW system flow for a short period of time. The plant stabilized in Mode 3 with levels in both SG’s restored to normal operating band with the Main Feedwater (MFW) system. Adequate water level was maintained in the SG’s during the transient to ensure decay heat removal from the Reactor Coolant System (RCS). This condition did not compromise the health and safety of the general public. This condition is reportable pursuant to 10CFR50.73(a)(2)(iv)(A) due to the automatic actuation of the Reactor Protection System (RPS) and due to the automatic actuation of the EFW system.
382 | 3822015005 | 2015-06-03 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Waterford 3 | P | CE | PO | 100 | On June 3, 2015, at 1705, the reactor was manually tripped due to low Steam Generator (SG) levels caused by a loss of the 'A' Main Feedwater (MFW) Pump. During the transfer of electrical buses, the 'B' train electrical buses failed to transfer to the Startup Transformer and were de-energized. The loss of 'B' power caused the loss of the remaining MFW pump and the Emergency Diesel Generator (EDG) on that side to automatically start and load the safety buses. The loss of MFW resulted in an Emergency Feedwater Actuation Signal (EFAS) with both SGs being fed by Emergency Feedwater (EFW) to restore level. The Emergency Operating Procedure (EOP) for a reactor trip due to the loss of MFW was entered. This event was caused by (1) the failure to identify the failure mechanism for repeated failures of non-safety related normal level control valves and (2) the relay's timed contact sets not changing state due to an unknown equipment problem. Corrective actions include rebuilding valves with identified similar deficiencies, changing the frequency of the Preventive Maintenance (PM) procedures for level control valves, and establishing a relay replacement PM and identifying electrical control circuit system enhancements.
382 | 3822015008 | 2015-10-03 | QR8 | Spurious Reactor Trip | [45 empty] | Waterford 3 | P | CE | PO | 100 | On October 3, 2015, at 2307 CDT, Waterford 3 experienced an automatic reactor trip and all Control Element Assemblies (CEAs) inserted into the core. Emergency Feedwater (EFW) actuated following the plant trip as expected, but was not required to maintain Steam Generator level. The plant entered the Emergency Operating Procedure for an uncomplicated reactor trip. <br /><br /> The trip was due to Core Protection Calculators (CPC) Channels B and C generating a High Local Power Density (LPD) / Low Departure from Nucleate Boiling Ratio (DNBR) trip due to erroneous signals from Control Element Assembly Calculator (CEAC) 2. Follow up investigation has determined that the direct cause of this event was a failed resistor on a circuit card in CEAC-2. The card was a High Level Multiplexer Gate (Mux) Card (Systems Engineering Laboratories, Model Number 160-100311) in the Multipurpose Acquisition Control System (MACS) Chassis of the CEAC. The direct cause has been corrected by replacing the card. Corrective actions include replacement of additional high level mux cards in a phased approach, development of a performance monitoring plan to identify CEAC card degradation, a full re-analysis of the CPC/CEAC system for Single Point Failure (SPF) vulnerabilities, and implementation of a CPC/CEAC reliability plan.
382 | 3822017002 | 2017-07-17 | B1 | Loss of Offsite Power (LOOP) |  | X | [13 empty] | X | [29 empty] | Waterford 3 | P | CE | PO | 100 | On July 17, 2017, at 1606 CDT, Waterford 3 experienced an automatic reactor scram due to a loss of forced circulation, which was the result of a loss of off-site power to the safety and non-safety electrical busses. Prior to the scram, plant operators manually tripped the main turbine and generator due to overheating of the isophase bus duct due to the failure of a shunt assembly connection in the duct to Main Transformer 'B'. The automatic electrical bus transfer did not occur due to relay failures in the fast dead bus transfer system. Both 'A' and 'B' Emergency Diesel Generators started and loaded as designed to re-energize the 'A' and 'B' safety busses. The loss of off-site power caused a loss of both Main Feedwater pumps, resulting in an automatic actuation of the Emergency Feedwater system.<br /><br /> The Root Cause of this event was the design change procedure used for modifications to the fast dead bus transfer circuitry did not include guidance to detect the susceptibility of the relays to DC coil inductive kick. The faulty relays in the fast bus transfer circuit were replaced prior to plant startup. <br /><br /> An Unusual Event was declared at 1617 CDT due to loss of off-site power to safety buses for >15 minutes. <br /><br /> All required safety-related equipment responded as expected during this event.
382 | 3822019005 | 2019-05-16 | QR5 | Turbine Trip | [45 empty] | Waterford 3 | P | CE | PO | 100 | On May 16, 2019, at 1348, Waterford 3 experienced an automatic reactor trip due to Steam Generator 1 high level, which occurred following a main turbine trip and reactor power cutback. The automatic reactor trip due to Steam Generator 1 high level was caused by feedwater control shifting to manual during reactor power cutback due to a deviation between Steam Generator level channels. Because feedwater control was in manual, the system could not lower feed water flow in response to rising Steam Generator level. Main Feedwater Isolation Valves #1 and #2 closed on high Steam Generator levels. Emergency Feedwater automatically actuated as expected for Steam Generator #1 and #2. Main Feedwater was restored to both Steam Generators by 1629. <br /><br /> The main turbine trip was caused by a loss of excitation within the main generator field. The cause of the loss of excitation was determined to be a short between 2 diode modules within the rotating rectifier circuit of the Main Exciter. The Main Exciter was mechanically disassembled and the failed fuses and diode modules in the rotating rectifier wheel were replaced. The entire rotating rectifier assembly was refurbished and/or repaired as appropriate. The exciter control system was fully calibrated prior to startup. <br /><br /> All required safety-related equipment responded as expected during this event.
382 | 3822020003 | 2020-11-02 | QR3 | Reactivity Control Imbalance | [45 empty] | Waterford 3 | P | CE | PO | 42 | In preparation for the return to service from an outage, operators were unable to achieve the desired voltage while attempting to place Control Element Drive Mechanism (CEDM) motor generator set B in service. A faulty voltage regulator was removed from the system, repaired onsite, and reinstalled. <br /><br />On November 2, while paralleling MG set B with MG set A, an automatic reactor trip occurred due to a ground on the voltage regulator card’s neutral circuit. All control rods inserted and there were no complications. The plant was stabilized in Mode 3. The direct cause of the ground on MG Set B was incorrectly installed voltage regulator insulator stand-offs allowing a short to ground to occur when the system was put into service. The voltage regulator was repaired, tested, and installed. Procedural changes to prevent repetition are being made.
387 | 3871987013 | 1987-04-02 | QP5 | Excessive Feedwater Flow | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | POWER LEVEL - 100%. ON APRIL 2, 1987, AT 0726 HOURS, AN AUTOMATIC ACTUATION OF THE REACTOR PROTECTION SYSTEM OCCURRED. UNIT ONE HAD BEEN OPERATING AT 100% RATED POWER PRIOR TO THE ACTUATION. THE REASON FOR THE SCRAM WAS HIGH REACTOR VESSEL WATER LEVEL CAUSED BY A NEAR-INSTANTANEOUS RAMPING OF THE FEEDWATER PUMPS. LEVEL WERE STEADY AT APPROXIMATELY 980 PSIG AND +36 INCHES (197 INCHES ABOVE THE TOP OF ACTIVE FUEL) RESPECTIVELY. AT 0726 HOURS, THE FEEDWATER MASTER CONTROLLER OUTPUT, WHILE IN AUTO AND 3-ELEMENT CONTROL, RAMPED RAPIDILY FROM THE NORMAL STEADY-STATE LEVEL TO MAXIMUM. AS A RESULT OF THIS INCREASE IN DEMAND, THE REACTOR FEEDPUMPS INCREASED FLOW TO THE VESSEL. VESSEL LEVEL SURGED FROM +36 INCHES TO +54 INCHES IN APPROXIMATELY 20 SECONDS. WHEN LEVEL REACHED +54 INCHES, A TURBINE TRIP/REACTOR SCRAM OCCURRED. FOLLOWING THE SCRAM, VESSEL LEVEL DECREASED TO A MINIMUM OF APPROXIMATELY -26 INCHES (135 INCHES ABOVE THE TOP OF ACTIVE FUEL) RESULTING IN THE INITIATION OF THE REACTOR CORE ISOLATION COOLING SYSTEM. VESSEL LEVEL WAS RESTORED TO +36 INCHES. DUE TO THE CLOSURE OF THE TURBINE STOP VALVES (I.E, TURBINE TRIP) FOUR SAFETY RELIEF VALVES LIFTED. THE VALVES RESEATED SUCCESSFULLY FOLLOWING THE ACTUATION.
387 | 3871988006 | 1988-03-04 | QR5 | Turbine Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | At 1207 hours on March 4, 1988, with Unit 1 operating at 100% power, a System Operating Technician inadvertantly bumped a sensitive protective relay in the 230 KV Switchyard while performing calibration on another relay. The relay tripped, causing switchyard breakers to open, isolating Unit 1 from the Power Grid. The resulting generator load unbalance tripped the Main Turbine, via Control Valve Fast Closure, which resulted in a Reactor Protection System actuation, causing a scram. All equipment operated per design during the transient, ESF Systems were not challenged and no operator actions were required to place the unit in a stable condition. System Operating and Substation personnel have been advised of the incident and cautioned about bumping sensitive relays. The subject relay, which protruded about six inches out of the front of the relay panel, was replaced with a flushmounted relay and protective barriers have been installed above and below the subject relay to protect against bumping.
387 | 3871988010 | 1988-06-18 | QR5 | Turbine Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | At 1621 on June 1, 1988, an Unplanned Engineered Safety Feature (ESF) actuation occurred on Unit 1. A ground fault which occurred on a distant 500 KV transmission line resulted in apparent ground fault relay misoperation. A Generator Load Unbalance (Load Reject) occurred and resulted in a Turbine Control Valve Fast Closure, Turbine Trip, and Reactor Scram. All systems responded properly to the transient. No off-site release occurred. The Unit was placed in a stable condition. <br /><br />The cause of the relay misoperation could not be determined. Extensive followup testing could not duplicate the failure. As a result, the trip function of the relay was blocked from service. Monitoring equipment was installed and relay response will be recorded. Redundant fault detection will provide fault protection in the interim.
387 | 3871989001 | 1989-01-04 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [6 empty] | X | [8 empty] | X | [20 empty] | X |  |  |  |  | Susquehanna 1 | B | GE | PO | 60 | At 0240 hours on January 4, 1989, Unit 1 experienced an automatic shutdown following a Reactor Protection System actuation. In anticipation of the scram, Operations reduced power from 100% to 60% to minimize the effect of the anticipated transient. Operations inadvertently isolated Instrument Air to instrumentation which eventually resulted in a loss of Main Condenser vacuum, a Main Turbine trip, and an ensuing reactor shutdown. All equipment operated per design during the transient and ESF systems were not challenged. The event has been determined to be reportable per 10CFR50.73(a)(2)(iv), in that an unplanned RPS actuation occurred. A contributing factor leading into this event was the reduced reliability of the Unit 1 I/A system due to planned maintenance activities. Loss of status control and omissions from the Unit 1 I/A Operating Procedure are considered the root causes. Corrective actions will consist of implementing programmatic changes to provide an improvement in the system of tracking equipment and valve status. The Unit 1 I/A Operating Procedure will be revised to include the omitted section.
387 | 3871989002 | 1989-01-12 | QP5 | Excessive Feedwater Flow | [45 empty] | Susquehanna 1 | B | GE | PO | 20 | At 0415 hours on January 12, 1989, with Unit 1 operating at approximately 20% power, a reactor scram occurred due to actuation of the Reactor Protection System (RPS). Operations was in the process of transferring from Startup Level Control to Auto Feedwater Level Control when control of level was lost due to a rapid increase in feedwater flow rate. The reactor level reached the +54" level which results in a trip of the main turbine. The large cold water addition caused reactor power to increase past 24%, which resulted in the RPS actuation upon turbine trip. The required plant equipment response during the transient was per design. The cause of the event was attributed to cognitive operator error. A cooldown of 101 degrees F was experienced over the first hour following the scram. This exceeded the Tech Spec maximum cooldown rate of 100 degrees F per hour during a one hour period, but was not immediately identified. As a result, Tech Spec Action requirements were not properly implemented. As a result, Tech Spec Action requirements were not properly implemented. An engineering analysis concluded that no adverse effects on the reactor coolant system structural integrity occurred as a result of the temperature deviation. Training was conducted for all licensed operators prior to assuming shift duties before the next startup. Enhancements for clarity purposes were made to the operating procedure. The post transient evaluation procedure was revised to add an additional review of post transient reactor coolant temperatures by the Shift Technical Advisor. Operations Training, stressing the importance of paying close attention to detail when monitoring reactor cooldown rated, was completed.
387 | 3871989027 | 1989-12-24 | QR5 | Turbine Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | At 0824 hours on December 24, 1989, Unit 1 experienced a Reactor Protection System (RPS) actuation resulting in an automatic scram from 100% power. A loss of electrical power supply (primary and backup) to the 230KV Switchyard services resulted in tripping of main distribution system switchyard breakers and subsequent Main Generator load reject/main turbine trip. The RPS actuation was the result of main turbine control valve fast closure as per design. All major equipment operated during the transient per design and no additional Engineered Safety Feature (ESF) systems were challenged. This event has been determined to be reportable per 10CFR50.73 (a) (2) (iv), in that an unplanned ESF actuation occurred. Both power supplies to the 230KV switchyard were lost due to unrelated events. The primary source was lost by a vehicle hitting a power line pole. The backup source was lost due to an electrical component failure in the backup generator exciter field circuit. Both power supplies were restored to service. A task force is evaluating the existing 230KV switchyard station services power supplies for reliability and for consideration of possible improvements.
387 | 3871991008 | 1991-07-31 | QC4 | Loss of ac Instrumentation and Control Bus. | [10 empty] | X | [28 empty] | X | [5 empty] | Susquehanna 1 | B | GE | PO | 100 | At 1034 hours on July 31, 1991, with Unit 1 and Unit 2 operating at 100% power, a RPS SCRAM and MSIV isolation occurred on Unit 1 when a switchyard fault detection relay mis-operated resulting in de-energization of one of Susquehanna's offsite AC circuits coincident with a pre-existing half-scram/half MSIV isolation signal condition. Unit 2 experienced a half-scram as a result of the loss of the offsite AC circuit. Both Units automatically responded to the transient as designed including an ECCS injection by the HPCI system and SRV actuations on Unit 1. Subsequent Unit 1 ESF actuations occurred: RPS logic actuations during control of reactor level and pressure by Operators; RWCU isolation during restoration; and automatic swap of HPCI suction supply on high suppression pool level. The following conditions prohibited by the plant's Technical Specifications occurred on Unit 1: A reactor level indicating switch was determined to have been inoperable in excess of the required LCO Action time; a reactor coolant sample could not be obtained in the required time period; shutdown cooling was not established within 1 hour of meeting the pressure permissive; and COLD SHUTDOWN was not achieved within 24 hours after entering Tech Spec 3.4.6.1 Action. Unit 1 was stabilized in accordance with the Emergency Operating procedures and brought to COLD SHUTDOWN. The half-scram condition on Unit 2 was reset. An Event Review Team performed root cause investigations for all transient and recovery related issues. Corrective actions include hardware replacement, procedure revisions, personnel training and a review of offsite power switchyard operation and communications relative to effects on Susquehanna operation. At no time were there any safety consequences or compromise to public health or safety.
387 | 3871992017 | 1992-11-12 | QR5 | Turbine Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | At 1014 hours on November 12, 1992 with Unit 1 operating at 100% power, a reactor scram occurred when the Main Turbine tripped during surveillance testing on the Feedwater Control System. All major equipment operated per design during the transient, Emergency Core Cooling Systems (ECCS) were not challenged and no abnormal operator actions were required to place the unit in a stable condition. The reactor scram was caused by a turbine control valve fast closure that resulted from a turbine master trip actuation. The turbine master trip was caused by a failed relay in the Feedwater C High Level Turbine Trip Channel coincident with surveillance testing of the Reactor Feedwater A High Level Turbine Trip channel. Root cause for the relay failure was attributed to a design misapplication problem. This event was determined to be reportable per 10CFR50.73(a)(2)(iv) in that an unplanned Engineered Safety Feature (ESF) actuation occurred when the RPS initiated an automatic reactor scram following turbine control valve fast closure with power greater than 24%. The plant was safely shut down and there were no safety consequences or compromise to public health or safety during this incident, nor would there have been under different initial operating conditions. The transient is within the bounds of a turbine trip as analyzed in Chapter 15 of the FSAR. The design misapplication problem was corrected and all of the Agastat relays associated with the Main Turbine and RFPT high water level trip logic were replaced on Unit 1. Following replacement of the relays, surveillance testing on the Feedwater Control System was successfully completed. It was verified that the design application for the Unit 2 comparable trip logic was acceptable.
387 | 3871993008 | 1993-07-12 | QR5 | Turbine Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | At 1635 hours on July 12, 1993, with Unit 1 operating at 100% power, a reactor scram occurred, per design, when the Main Turbine tripped. All major equipment operated per design during the transient, Emergency Core Cooling Systems (ECCS) were not challenged and no abnormal operator actions were required to place the unit in a stable condition. The reactor scram was caused by a turbine control valve fast closure that resulted from a turbine master trip actuation. The turbine master trip was caused by Main Turbine high vibration as a result of failure of two turbine blades on the 'C' Low Pressure Turbine. The turbine blade failure was caused by electrical system torsional induced vibration. This event was determined to be reportable per 10CFR50.73(a)(2)(iv) in that an unplanned ESF actuation occurred when the RPS initiated an automatic reactor scram following turbine control valve fast closure with power greater than 24%. The plant was safely shut down and there were no safety consequences or compromise to public health or safety during this incident, nor would there have been under different initial operating conditions. This transient was within the bounds of a turbine trip as analyzed in Chapter 15 of the FSAR. Repairs were made to the turbine and an inertia ring was installed, at the manufacturer's recommendation, to minimize the potential for high cycle fatigue as a result of excited torsional vibrations. Subsequent inspections, testing, torsional test reports for both (Unit 1 and Unit 2) Susquehanna units and analytical results all reinforced the initial 8/12/93 root cause conclusion and the corrective actions taken.
387 | 3871996006 | 1996-08-01 | QR5 | Turbine Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 98 | At 0533 hours on August 1, 1996, with Unit 1 operating in Condition 1 (Power Operation) at 98% power, a reactor scram occurred, per design, when the Main Turbine tripped on indicated high vibration. Both Reactor Recirculation pumps also tripped, per design, and all control rods fully inserted. Reactor water level dropped to +6.6 inches and all reactor Level 3 (+13 inches) isolations occurred per design. Reactor pressure peaked at 1127 psig, momentarily cycling Safety Relief Valves G, K, L, M and N. All Primary Containment parameters remained normal throughout the event. The cause of the turbine trip was attributed to a false, spurious signal from the turbine #1 bearing's vibration instrument loop. The investigation also concluded that the response to some precursor alarms, which may have precluded the turbine trip, was less than adequate. The plant was safely shut down and there were no safety consequences or compromises to public health or safety during this event, nor would there have been under different initial operating conditions. This transient is within the bounds of a turbine trip as analyzed in Chapter 15 of the Susquehanna FSAR. The components of the #1 bearing vibration monitoring loop which most likely could have caused the false, spurious signal were replaced. Training on expectations and sensitivity to alarms was completed. Actions to prevent recurrence include additional monitoring of vibration data, procedural enhancements, failure analysis of removed components, enhancing significance reviews of events to better identify precursors to more significant events and evaluation of design changes to eliminate unnecessary single failure design and obsolete equipment.
387 | 3871997006 | 1997-02-25 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Susquehanna 1 | B | GE | PO | 64 | POWER LEVEL - 064%. On February 25, 1997, at 1723 hours with Unit 1 in Condition 1 (Power Operation) at 64% power, the unit was manually scrammed due to a loss of condenser vacuum. Condenser vacuum was lost when the Unit 1 Offgas System isolated on a false high-high hydrogen signal from an electrical short caused by water intrusion into a hydrogen analyzer from an in-plant work activity. Neither the common nor the Unit 1 Offgas recombiner could be restored to operation as a result of solenoid valve problems. The plant was safely shutdown and there were no safety consequences or compromises to public health or safety during this event, nor would there have been under different initial operating conditions. generated due to water intrusion as a result of maintenance activities in the vicinity. While provisions had been made to capture and divert the fluid, the collection device became plugged and overflowed. Subsequent investigation indicated that less than adequate assessment of risk associated with work activities contributed. Procedural inadequacies for Offgas System operation inhibited the successful swap to the Common recombiner and complicated the recovery of the Unit 1 recombiner. The corrective actions include: repair of the hydrogen analyzer and subject solenoid valves; completion of a risk assessment review for work presently in the field; procedural revisions; training of involved personnel on this event; evaluation of training frequencies; reinforcement of standards with Maintenance Supervision; additional oversight on in-plant work activities; and performance of an assessment of the treatment of Maintenance Rule Non-Risk Significant Systems.
387 | 3871998016 | 1998-10-03 | QR5 | Turbine Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | On October 3, 1998 at 1424 hours, with Unit 1 in Mode 1 (Power Operation) at 100 % power, the generator backup lockout relays tripped, tripping the generator and in-turn causing a reactor SCRAM via a turbine control valve fast closure signal. The unit responded as expected to the SCRAM. All control rods inserted. Reactor water level dropped below 13 inches and all isolations were completed. Reactor water level was restored using feedwater. The recirculation pumps tripped due to the end-of-cycle recirculation pump trip (EOC-RPT). Four safety relief valves (SRVs) lifted and re-seated. There were no diesel starts or Emergency Core Cooling system (ECCS) initiation associated with this event. The cause of the event was a pitted contact on the main generator potential transformer circuitry, resulting in a false signal to the generator ground circuitry. Completed corrective action included refurbishment of main generator potential transformer (PT) disconnect contacts and testing of associated relay circuits. Corrective actions to be completed include 1) evaluation of maintenance activities, 2) reviewing this event with appropriate Nuclear Department personnel, and 3) revising maintenance procedures to incorporate additional contact maintenance on a routine basis. The plant responded to the generator trip and subsequent reactor SCRAM as expected. There were no safety consequences or comprises to public health and safety as a result of this event.
387 | 3871999003 | 1999-07-01 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | On July 1, 1999, at 0208 hours with Unit 1 in Mode 1 (Power Operation) at 100 percent power, the neutron monitoring system received a high neutron flux upscale trip, which caused a reactor SCRAM. The inadvertent closing of the "C" outboard Main Steamline Isolation Valve thus isolating one main steamline caused the high neutron flux. The other three steamlines experienced high flow that caused all MSIVs to isolate. As a result of the SCRAM, water level dropped to approximately -46 inches. Reactor water level was restored by using the High Pressure Coolant Injection (HPCI) System (auto-initiated) and the Reactor Core Isolation Cooling (RCIC) System. Reactor pressure peaked at 1048 psig and was controlled by cycling the Safety Relief Valves (SRVs). All SRVs re-seated after use. There were no diesel starts or challenges to the containment associated with this event. During this event, the "C" outboard MSIV exhibited excessive leakage, thus causing the total maximum leakage pathway Technical Specifications limit for the main steamline penetrations to be exceeded. The minimum leakage pathway for these penetrations remained below the analyzed limit. The inadvertent closing of the "C" outboard MSIV was caused by a stem-poppet separation. The cause of the "C" outboard MSIV stem to poppet failure was due to loss of pre-load on the stop plate bolting. The loss of the pre-load was due to actual clearances being less than the design tolerances, insufficient detail for assembling the stop plate to poppet connection, and inadequate torquing values for the stop plate bolting. Corrective actions that were completed include (1) the "C" outboard MSIV was repaired, (2) three additional MSIVs were inspected and reworked, and (3) the appropriate maintenance procedures were revised to include the new torquing criteria. Corrective actions remaining to be completed include (1) revisions to appropriate procedure to include revised inspection and torquing criteria, (2) inspection of similar Unit 1 MSIVs, (3) inspection of similar Unit 2 MSIVs, and (4) evaluation of potential solutions for MSIV leakage failures with a recommended course of action for improving MSIV performance. Since the plant performed as expected during this event and the total minimum pathway leakage from the main steam line penetrations was below the analyzed limit, there were no safety consequences or compromises to public health and safety.
387 | 3872002004 | 2002-04-22 | QR6 | Manual Reactor Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 17 | At 01:15 on April 22, 2002 with Unit 1 in Mode 1 (Power Operation) at 17% power, plant operators initiated a manual reactor scram in response to anomalous core flow indications observed following a recirculation pump trip that had occurred at 00:16. Following the pump trip, power and flow values plotted on the Unit's power to flow map were found to be in a position left of the natural circulation line. This was unexpected because a second recirculation pump continued to provide forced circulation. While no power flux oscillations were observed, Operations Management elected to scram the reactor because operators were uncertain about core flow indications and plant procedures did not provide a clear response to the observed conditions. Investigation revealed that past industry and internal experience provided insight into the flow instrumentation logic that resulted in a plotted position left of the natural circulation line. Susquehanna's previous response to this information did not adequately educate operators on, or initiate procedural changes to address, this anticipated instrument behavior. To preclude recurrence of this event, procedures now direct operators to utilize a core plate differential pressure correlation in lieu of core flow instrumentation during low flow, single-loop operation. Should an operator plot a point to the left of the natural circulation line despite this tool, procedures have been modified to provide clear direction for reactor scram. Operators have been trained on these changes. This event is reportable for Unit 1 as an unplanned actuation of systems that mitigate the consequences of significant events per 10CFR50.73(a)(2)(iv)(A). There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
387 | 3872003006 | 2003-09-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | At 00:53 on September 24, 2003 with Unit 1 in Mode 1 at 100% power, an automatic reactor scram occurred in response to low reactor water level conditions. While performing required testing of the 'C' Reactor Feed Pump Turbine (RFPT), a control room operator incorrectly manipulated the 'C' RFPT lockout key switch instead of the Reset pushbutton thus causing the turbine to trip. Although the 'A' and 'B' Reactor Feed Pumps increased speed in an attempt to maintain reactor inventory levels, the reactor automatically scrammed when water level reached the Low-Level RPS initiation setpoint. HPCI and RCIC automatically initiated to assist the operating Feed Pumps with level restoration. Numerous Primary Containment Isolations occurred as designed during the transient. Susquehanna was designed to withstand a single RFPT trip without experiencing a Rx Low-Level Scram. This event suggests that previous changes made at Susquehanna have affected the plant's integrated response to the loss of a single RFPT and have cumulatively resulted in a reduction of the originally designed operating margin. The RFPT trip has been attributed to human performance error. Error prevention techniques will be reinforced to support desired human performance attributes. The scram that resulted following the human performance error has been attributed to the reduction in operating margin resulting from inadequate identification of operating margin requirements in plant change processes. Corrective actions have been initiated to strengthen station operating margin controls within plant change processes. This event is reportable for Unit 1 as an unplanned actuation of systems that mitigate the consequences of significant events per 10 CFR 50.73(a)(2)(iv)(A). There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
387 | 3872004003 | 2004-04-21 | QR6 | Manual Reactor Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 17 | At 16:35 on April 21, 2004 with Unit 1 in Mode 1 at 17% power, Susquehanna Unit 1 was manually scrammed in response to main turbine bearing high vibrations experienced during startup turbine testing. The turbine had been replaced during the recently completed Unit 1 refueling outage. After approximately 35 minutes of turbine operation at 1800 rpm and no load, a rub developed in the vicinity of bearing # 2. Vibration increased to levels warranting turbine trip as directed by operating procedure. Despite the turbine trip, the rub continued to cause localized heating thus creating a rotor bow condition and a steady vibration increase. The Reactor Protection System was manually initiated and condenser vacuum was broken to allow for a more rapid decrease in turbine speed and, subsequently, vibration levels. Plant response to the manual reactor scram was in accordance with design. Causes cited for this event include: (1) Turbine startup vibration trip limits were not set sufficiently low to preclude rub induced high vibration (2) Vibration change rates were not monitored and used as a response input to high vibration conditions and (3) Project management did not establish contingency plans in sufficient depth to handle all potential vibration issues. After implementing corrective actions to address these deficiencies and performing a thorough evaluation to ensure equipment had not been adversely impacted by the high vibration, the turbine was successfully started and loaded in accordance with the established startup procedure. The manual RPS actuation and the subsequent manual initiation of the Reactor Core Isolation Cooling system, to assist with reactor level control, are unplanned actuations of systems that mitigate the consequences of significant events and are, therefore, being reported per 10CRF50.73(a)(2)(iv)(A). There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
387 | 3872006004 | 2006-06-15 | QR8 | Spurious Reactor Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | On June 15, 2006 with Unit 1 in Mode 1 at 100% power, the Control Room completed preparations to transfer Division B of the Reactor Protection System (RPS) from its normal power supply to its alternate source. The transfer momentarily de-energizes that division of RPS and results in a half-scram. During the 2006 Refuel Outage, a new Power Range Neutron Monitoring System (PRNMS) was installed. Because of differences in the original monitoring system logic and PRNMS logic, the transfer resulted in a full scram. The event was determined to be reportable under 10 CFR 50.72; reference ENS Notification EN #42642. Following the automatic scram, the Unit 1 reactor water level decreased to ˜-36". Reactor Core Isolation Cooling (RCIC) initiated and was within the instrumentation tolerance for the Level 2 setpoint of -38" to initiate High Pressure Coolant Injection (HPCI). Once reactor water level recovered, the normal feedwater system was utilized to maintain the normal operating level (+35"). Level 3 (+13") and Level 2 (-38") Primary Containment Isolation signals were received and all safety systems functioned as expected. The actuation of RPS, RCIC and HPCI systems and Primary Containment isolations are unplanned actuations of systems that are designed to mitigate the consequences of significant events and are reportable per 10 CFR 50.73(a)(2)(iv)(A). This event resulted in no actual adverse consequences to the health and safety of the public.
387 | 3872006006 | 2006-11-25 | QR5 | Turbine Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | On November 25, 2006 with Susquehanna Unit 1 in Mode 1 at 100%, the reactor automatically scrammed as a result of a turbine trip in response to a generator lockout. The main generator automatic voltage regulation circuitry did not positively respond to changes to the offsite grid which resulted in a loss of generator field and a subsequent unit shutdown. Investigation suggests that improper active/reactive current compensator (ARCC) settings in the automatic voltage regulation system were a probable contributor to this shutdown. In addition, a decision to forego modification of the automatic voltage regulators in a manner described in GE TIL 961-3, may also have contributed to the inability of Susquehanna's units to adequately respond to the grid disturbances. At the root of these suggested contributors to the shutdown, it has become apparent that there is a lack of sufficient, in-house understanding of the automatic voltage regulator response to a changing grid configuration. Until planned corrective actions are sufficiently completed, the Unit 1 Main Generator Voltage Regulator is being maintained in manual to ensure continued station operation during grid disturbances. In response to this event, the station intends to implement measures to ensure appropriate personnel fully understand generator control and protection schemes. Appropriate ARCC setting changes will also be established. Additionally, General Electric Technical Information Letter 961-3 will be re-evaluated and implemented if such action will enhance the unit's ability to respond correctly to grid disturbances. This situation is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an unplanned actuation of a system designed to mitigate the consequences of a significant event. There were no actual adverse consequences to the health and safety of the public as a result of this event.
387 | 3872010002 | 2010-04-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Susquehanna 1 | B | GE | PO | 32 | On April 22, 2010, at 1051 hours, Susquehanna Steam Electric Station Unit 1 experienced an automatic reactor scram, from 32% power, on low reactor water level (ENS 45866). The low level condition occurred during planned testing of a new digital feedwater Integrated Control System (ICS), which included upgrades to the feedwater level control system, the reactor feed pump turbine speed controls, and the reactor recirculation speed controls. During testing at low power conditions, the second of three reactor feed pumps (RFP) was placed in automatic flow control mode for the first time with the goal of parallel automatic operation of two RFPs. A reactor water level transient occurred when the second RFP began feeding into the reactor. The resulting concurrent flow reduction of both RFPs quickly lowered water level to the low level scram setpoint. Corrective actions were taken to adjust the ICS speed controller gain and master feedwater level controller gain. At approximately 2301 hours on May 14, 2010, Unit 1 automatically scrammed from 66% power due to a main turbine trip on high reactor water level (ENS 45930). The high level condition occurred during additional planned testing of the digital ICS, which involved the trip of one of the four condensate pumps. The high reactor water level transient was attributed to a large feedwater flow/steam flow mismatch caused by insufficient gain on the ICS master feedwater level control system master water level controller in response to large transient conditions. Corrective actions were taken to increase the system gains for large transients using "gap" control on the ICS level controller and flow controller. The root cause analyses concluded the process used in the development and implementation of the ICS gains/tuning factors did not adequately use risk considerations, independent oversight, analytical tools and techniques, operating experience and appropriate resource management. Also, the station's post-event analysis of the April scram did not adequately evaluate the extent of condition or extent of cause and represents a missed opportunity to prevent the May scram. Planned corrective actions include providing guidance for developing and implementing control system tuning parameters, using the plant simulator for non-training purposes and post-event analysis. There were no actual adverse consequences to the health and safety of the public as a result of these events. The RPS responded as expected. All control rods fully inserted. These events are being reported under 10 CFR 50.73(a)(2)(iv)(A) due to the actuation of the RPS and RCIC.
387 | 3872010003 | 2010-07-16 | QR6 | Manual Reactor Trip | [8 empty] | X | [26 empty] | X | [9 empty] | Susquehanna 1 | B | GE | PO | 89 | On July 16, 2010, at approximately 1641 EDT, the Susquehanna Steam Electric Station Unit 1 reactor was manually scrammed due to a large unisolable circulating water system leak in the main condenser area. All control rods fully inserted. Reactor water level lowered to -28 inches causing Level 3 (+13 inches) isolations. The Integrated Control System (ICS) Feedwater Level Control (FWLC) system detected the scram condition and automatically entered setpoint setdown mode, which placed the non-lead Reactor Feedpumps (RFPs) in idle mode, and initiated transition to startup level control mode. During this transition, ICS FWLC did not transfer to single element control due to a higher than expected steam flow signal, and concurrent feedwater flow oscillations resulted in an increase in reactor water level. Reactor water level reached Level 8 (+54 inches) which resulted in the trip of all three RFP turbines, the High Pressure Coolant Injection (HPCI) system, and the Reactor Core Isolation Cooling (RCIC) system to shutdown. The circulating water system was shut down and the main steam isolation valves were manually closed. Reactor water level was restored and maintained within normal operating range using the RCIC system. Pressure control was initiated using the HPCI system in the pressure control mode. All safety systems operated as expected. No steam relief valves opened. It was estimated that approximately one million gallons of water leaked into the condenser bay area. The cause of the unisolable circulating water system leak was due to the condenser waterbox manway gasket rolling out of position. Investigation concluded that the gasket reached the point where it could no longer maintain system pressure and rolled out of position due to gasket creep (i.e., inadequate gasket preload to maintain joint integrity). The gasket extrusion was the result of inadequate preload, rather than a system pressure transient or a material defect. Corrective actions taken for Unit 1 included inspection and replacement of gaskets. The root causes were determined to be less than optimal system manway and isolation valve design, less than adequate risk informed decision making resulted in the failure to adequately address previous Circulating Water (CW) system leaks, and inadequate procedure quality, use and adherence resulted in the loss of CW pressure boundary integrity and inadequate mitigation of the CW leak. Planned actions to prevent recurrence included revising procedures to address gasket installation procedure deficiencies, revising procedures to address isolating individual waterboxes, and developing revisions to processes and procedures to improve risk informed decision making. There were no adverse consequences to the health and safety of the public as a result of this event. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) due to the manual actuation of the RPS, RCIC and HPCI system.
387 | 3872011002 | 2011-01-25 | QR6 | Manual Reactor Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 65 | On January 25, 2011, Susquehanna Steam Electric Station Unit 1 reactor was manually scrammed due to an unisolable extraction steam system leak in the 1C Feedwater Heater Bay area (EIIS: SJ). Reactor power was lowered from 98.4% to 65% prior to the scram. Non-safety-related electrical equipment exposed to the condensing steam began malfunctioning. Attempts to isolate the source of the leakage were unsuccessful. Based on continued indications of an unisolable steam leak, the decision was made to shut down the unit. The mode switch was placed in shutdown. All rods inserted. Reactor water level lowered to minus 31 inches causing a Level 3 (plus 13 inches) isolation. The Reactor Core Isolation Cooling System (RCIC) (EIIS: BN) automatically initiated on a minus 30 inch level signal and was manually secured after water level was restored. Reactor water level was maintained at the normal operating band using feedwater. No steam relief valves opened. All safety systems (RPS and PCIS) operated as expected. The direct cause of the unisolable leak was the loss of a bleeder trip valve cover plug. The two root causes were 1.) Less than adequate (LTA) management oversight of the work activity and work planning process and 2.) Deficient work instruction and task assignment for the Bleeder Trip Valve (BTV) repair task. Corrective actions were to replace and seal weld the cover plug on the affected valve and to seal weld the cover plugs on other valves of similar design. Other key corrective actions included planning procedure changes related to threaded pipe assemblies, evaluation and training of maintenance foremen, implementation of a more risk informed screening process, procedure changes and an enhanced coaching card on procedure use and adherence, and management observations using the revised coaching card. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to the manual scram and the Reactor Protection System initiation. There were no actual adverse consequences to the fuel, any safety-related plant equipment, or to the health and safety of the public as a result of this event since the dose consequences from the additional leakage would not have exceeded regulatory limits.
387 | 3872013002 | 2013-06-07 | QR6 | Manual Reactor Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 7 | At approximately 1203 hours on June 7, 2013, Susquehanna Steam Electric Station Unit 1 was manually scrammed during reactor startup. The pressure setpoint was being adjusted to the normal operating setpoint, from 750 psig to 934 psig, when all turbine bypass valves unexpectedly opened. Reactor Feed Pumps tripped and Main Turbine, High Pressure Coolant Injection (HPCI), and Reactor Core Isolation Cooling (RCIC) received trip signals on the high level setpoint Level 8 (+54 inches) due to the resultant reactor level swell. The reactor operator then inserted a manual scram. All control rods inserted. Reactor water level lowered to approximately -10 inches causing Level 3 (+13 inches) isolations. There were no automatic emergency core cooling system initiations. No steam relief valves opened during the event. All safety systems operated as expected.<br><br> This was reported as a 4-hour report in accordance with 10 CFR 50.72 (b)(2)(iv)(B) and as an 8-hour report in accordance with 10 CFR 50.72 (b)(3)(iv)(A). This event is also reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A).<br><br> The apparent cause was failure of the Electro-Hydraulic Control (EHC) "B" pressure setpoint potentiometer due to equipment aging associated with corrosion, oxidation or dust build up on the potentiometer coil and/or wiper. Two causal factors were identified: 1) Less than adequate life cycle management based on delay in the project to replace the EHC system with a digital replacement and 2) Less than adequate periodic maintenance to prevent oxidation and corrosion buildup on the pressure set potentiometer. Key corrective actions planned include: 1) Updating the PM activity to include other motor operated potentiometers in EHC and increasing the frequency to every two years, 2) Replacing the Unit 1 and Unit 2 pressure setpoint motor operated potentiometers during next forced or refuel outage, and 3) continuing with the project to replace the EHC system.<br><br> There were no adverse consequences to the health and safety of the public as a result of this event.
387 | 3872015007 | 2015-11-12 | QL5 | Partial Closure of MSIVs | [45 empty] | Susquehanna 1 | B | GE | PO | 98 | On 11/12/2015 at 1132 hours, the Unit 1 'B' Inboard Main Steam Isolation Valve, HV141F022B, closed during the performance of SI-183-207, Quarterly Functional Test of Main Steam Line 'C' Flow Channels FIS-B21-1 N008A&B and Main Steam Line 'D' Flow Channels FIS-B21-1N009A&B. This resulted in an automatic SCRAM of Unit 1 on high reactor pressure. <br /><br /> This event was reported under 10 CFR 50.72(b)(2)(iv)(B) and 10CFR 50.72(b)(3)(iv)(A) per the guidance of NUREG 1022, Revision 3, Section 3.2.6. This event is also being reported as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A). <br /><br /> The root cause is that the station did not evaluate recommendations made in 2011 by the Boiling Water Reactor Owners Group Instrument and Controls (BWROG l&C) Maintenance Committee to mitigate Primary Containment Isolation System (PCIS) Group 1 Surveillance Testing Risk. It was also determined as a causal factor that there was not specific guidance contained in SI-183-306 (24 Month Calibration Main Steam C/D) which led to an inaccurate field decision when determining the cause of the extinguished light. <br /><br /> Planned corrective actions include evaluating the BWROG l&C Maintenance Committee Recommendation to mitigate PCIS Group 1 Surveillance Testing Risk and then design and implement the proposed modification. Additionally, l&C personnel will perform a review of the population of BWROG recommendations that were issued between January 2011 and December 2013 to ensure they were evaluated. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
387 | 3872017005 | 2017-06-08 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | On June 8, 2017 at 1527 hours, the reactor automatically scrammed due to a loss of Main Turbine-Electro-Hydraulic Control (EHC) logic power causing a high neutron flux, Reactor Protection System (RPS) trip. The safety systems operated as expected. Secondary Containment differential pressure lowered to 0" WG due to a trip of the normal operation of the Reactor Building Ventilation system. The differential pressure was restored by the initiation of Standby Gas Treatment System. <br /><br /> The scram was caused directly by a DC+ (direct current, positive) test lead (Maxi Grabber) that inadvertently contacted with the grounding screw, causing a short and momentary loss of EHC logic power. Immediate action was taken to validate that there was no damage to the +30 VDC (volts DC) EHC logic. The root cause for this event is an insufficient focus on the High Risk Activity of adjusting the EHC power supply, and inadequate risk mitigating actions for that activity. <br /><br /> The condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the RPS, including reactor scram. Although no safety system functional failure occurred, this event is also reportable pursuant to 10CFR 50.73(a)(2)(v)(C) as a condition that could have prevented fulfillment of a safety function. There were no actual, or potential consequences to the health and safety of the public as a result of this event.
387 | 3872020001 | 2020-05-03 | QR5 | Turbine Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 76 | On May 3, 2020 at approximately 08:21, Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to a main turbine trip. Both divisions of the Reactor Protection System (RPS) actuated and all control rods inserted. This event was reported by Event Notification 54691 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the RPS (including reactor scram), as well as associated isolation and actuation of other systems listed in 10 CFR 50.73(a)(2)(iv)(B). <br /><br /> The direct cause of the event was an electrical path from a replacement current transformer inside the main transformer to the low voltage bus causing a ground on the 24 kV System (Main Generator). The apparent cause of the ground was a current transformer with the incorrect insulation characteristics installed as a result of the wrong current transformer being supplied to Susquehanna. Corrective actions included removing the current transformer and replacing it with a bus bar. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
387 | 3872021003 | 2021-07-21 | QR5 | Turbine Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 100 | On July 21, 2021, at approximately 18:26, Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to a main turbine trip. Both divisions of the Reactor Protection System (RPS) actuated and all control rods inserted. This event was reported by Event Notification 55370 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). <br /><br /> The cause of the event was a dislodged de-ionizing baffle plate that contacted the ‘C’ isophase bus causing a ground fault. The root cause was determined to be accelerated wear of the de-ionizing baffle tack welds due to increased isophase bus forced air. Corrective actions included replacement and tack welding the dislodged and loose baffle plates and implementing an Engineering Change to modify the Unit 1 Main Generator-end ‘A’ and ‘C’ isophase bus de-ionizer baffle plates to install an aluminum retaining rod to secure the baffle plates together. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
387 | 3872021005 | 2021-11-30 | QR8 | Spurious Reactor Trip | [45 empty] | Susquehanna 1 | B | GE | PO | 80 | At approximately 12:54 on November 30, 2021, Susquehanna Steam Electric Station, Unit 1, experienced an automatic reactor scram during Turbine Valve Cycling surveillance testing. During the fast closure portion of the surveillance test on Main Stop Valve 4 (MSV-4), a closure of Turbine Control Valve 4 (CV-4) occurred, resulting in a Division II Reactor Protection System (RPS) actuation. While the Division II half scram signal was actuated, a Division I RPS actuation occurred, resulting in a full reactor scram. All control rods inserted and operators placed mode switch to shut down. <br /><br /> Event Notification 55616 reported this event in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system in 10 CFR 50.73(a)(2)(iv)(B). <br /><br /> The CV-4 fast closed due to transient voltage from a ground fault on the CV-4 Fast Acting Solenoid (FASV) field wiring. The previous single point vulnerability review for the system failed to identify and mitigate this failure mechanism. The Electro-hydraulic Control fluid pressure perturbation from the simultaneous closure of MSV-4 and CV-4 resulted in the Division II RPS actuation. Further review identified a recommended modification to dampen pressure in the system was never installed based on vendor recommendation. Key corrective actions include, in part, replacement of the CV-4 FASV wire and installation of orifices in accordance with the General Electric Technical Information Letter 1212-2 guidance. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
388 | 3881987006 | 1987-04-16 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Susquehanna 2 | B | GE | PO | 100 | POWER LEVEL - 100%. AT 0820 HOURS ON APRIL 16, 1987 WITH UNIT 2 OPERATING AT 100% POWER, A SPURIOUS MAIN STEAM ISOLATION VALVE (MSIV) ISOLATION OCCURRED, CAUSING AN AUTOMATIC REACTOR SCRAM. THE UNIT RESPONDED TO THE TRANSIENT AS DESIGNED INCLUDING AN AUTOMATIC EMERGENCY CORE COOLING SYSTEM (ECCS) INJECTION BY THE HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM FOR VESSEL LEVEL CONTROL, AS WELL AS MULTIPLE REACTOR CORE ISOLATION COOLING (RCIC) INJECTIONS. OPERATOR ACTION WAS TAKEN TO REDUCE THE NUMBER OF SAFETY RELIEF VALVE (SRV) LIFTS AND CONTROL REACTOR PRESSURE TO ESTABLISH AN ORDERLY COOLDOWN. CONDITIONS WITHOUT THE USE OF THE REACTOR RECIRCULATION PUMPS. THIS EVENT WAS DETERMINED TO BE REPORTABLE PER 10CFR 50.73(A)(2)(IV) IN THAT AN UNPLANNED ENGINEERED SAFETY FEATURE (ESF) ACTUATION OCCURRED WHEN THE REACTOR PROTECTION SYSTEM (RPS) INITIATED AN AUTOMATIC REACTOR SCRAM. AFTER EXTENSIVE INVESTIGATION, INCLUDING CONFIRMATION OF THE PROPER OPERATION OF THE MSIV ISOLATION LOGIC CHANNELS, THE MOST PROBABLE CAUSE OF THE MSIV ISOLATION WAS BELIEVED TO BE SPURIOUS ACTUATION OF TWO MAIN STEAM LINE LOW PRESSURE SWITCHES. MEASURES HAVE BEEN TAKEN TO PREVENT INADVERTENT BUMPING OF THESE SWITCHES. AS A PRECAUTION ONE OF THE MAIN STEAM LINE LOW PRESSURE SWITCHES WAS REPLACED DUE TO THE FACT IT HAD GIVEN SPURIOUS SIGNALS PREVIOUSLY ON NOVEMBER 7, 1986.
388 | 3881990002 | 1990-02-06 | QR5 | Turbine Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 100 | At 0906 hours on February 6, 1990, with Unit 2 operating at 100% power, main generator power/load unbalance signal, created when the 500 KV switchyard main distribution breaker opened, caused a main turbine trip. In accordance with plant design, the turbine control valves closed and an automatic reactor scram occurred. All major equipment operated per design, the turbine control valves closed and an automatic reactor scram systems were not challenged and no abnormal operator actions were required to place the unit in a stable condition. The cause of this event was attributed to a loose "States" link in the differential current relay circuit of the 500 KV switchyard circuit breaker which connects Unit 2 to the Power Grid. High circuit resistance caused by the loose connection resulted in protective relay operation which opened the 500 KV circuit breaker, isolating the main generator from the Power Grid resulting in the power/load unbalance trip signal. The loose "States" link was replaced and checks were made of the wiring terminations and "States" links on all related accessible relay and control panels to confirm that the connections are proper in order to preclude a recurrence.
388 | 3881990005 | 1990-05-28 | QP5 | Excessive Feedwater Flow | [45 empty] | Susquehanna 2 | B | GE | PO | 100 | At 0256 hour on May 28, 1990, an automatic actuation of the Reactor Protection system occurred on Unit 2. The unit had been operating at 100% rated power prior to the actuation. Feedwater control system transmitter PDT-C32-2N004B failed downscale which resulted in the feedwater master controller increasing to 100% demand. Reactor water level increased from the steady state level of +35 inches to +54 inches. When vessel level reached +54 inches, the main and feed pump turbines tripped. Tripping of the Main Turbine resulted in a fast closure of the turbine stop and control valves. Fast closure of the turbine stop and control valves resulted in a reactor scram. The lowest vessel level observed during the transient was approximately -26 inches. The Reactor Core Isolation Cooling system was manually initiated to restore reactor vessel level to an acceptable value. A component failure in the amplifier circuit card for feedwater control system transmitter PDT-C32-2N004B caused the transmitter to fail downscale which in turn resulted in the feedwater master controller increasing to 100% demand. The event has been determined to be reportable per 10CFR50.73 (a) (2) (iv), in that an automatic actuation of the Reactor Protection system occurred when the feedwater level transmitter failed The event was within the design basis of the plant and system responses which were needed to mitigate the consequences of the event actuated. The event did not pose any significant safety consequences and there was no compromise to the health and safety of the public. The amplifier circuit card in PDT-C32-2N004B was replaced with a new amplifier card and the transmitter was recalibrated. The failed amplifier circuit card is being sent to Rosemount to perform a failure analysis to determine exact cause of failure.
388 | 3881991012 | 1991-08-06 | QR5 | Turbine Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 100 | At 0727 hours on August 6, 1991 Unit 2 received simultaneous SCRAM and dual recirculation pump trip signals causing an automatic unit shutdown. All plant systems responded as expected in response to the transient. All reactor parameters were stabilized and the SCRAM was reset by 0740. The event was initiated when three of four main turbine stop valves (EIIS code: SB) unexpectedly closed far enough to produce Reactor Protection System (RPS) and End of Cycle-Recirculation Pump Trip (EOC-RPT) signals that the stop valves had closed. The stop valve closure signal was due to water intrusion into an electrical junction box causing a short-circuit in the Unit 2 turbine stop valve (TSV) control logic. The source of the water was a sealing steam leak from the #2 stop valve. The water-damaged components were replaced and post maintenance testing was performed. A temporary deflection shield was installed to inhibit water intrusion of the panel. Further modifications to prevent recurrence were implemented during a subsequent non related Unit shutdown on 8/22/91 (non reportable). Maintenance was performed on the #2 stop valve during the shutdown. On 8/28/91, during Unit startup, the #2 TSV was inspected and no leakage was found. Since all plant systems responded per design in response to the transient, there were no safety consequences or compromises to health or safety of the public.
388 | 3881992001 | 1992-03-18 | C1 | Loss of Vital Medium Voltage ac Bus (>600 V and <10 kV) |  |  | X | [13 empty] | X | [28 empty] | Susquehanna 2 | B | GE | PO | 100 | On March 18, 1992, with Unit 2 operating in Condition 1 at 100% power and Unit 1 in refueling, Condition 5, at 0% power, the 'B' Emergency Diesel Generator (EDG) was being run for its monthly surveillance test. At 0831 hours on 3/18/92, the 'B' EDG tripped on "Generator Loss Of Field". While in the process of substituting in the 'E' EDG for the 'B' EDG, the Operator reset a relay target on Engineered Safeguard System (ESS) 4.16 KV Bus 2C. When the relay target was reset at 0949 hours on 3/18/92, the bus locked out. The loss of the ESS Bus 2C resulted in several ESF actuations including, auto start of the 'C' EDG, Reactor Water Cleanup and Containment Instrument Gas (CIG) containment isolations and Unit 2 Reactor Building HVAC Zones II and III isolations. Additional bus loads, including Drywell cooling fans were lost and additional isolations occurred. Because the CIG system became isolated from the Main Steam Isolation Valves (MSIV), operators manually scrammed Unit 2 in anticipation of MSIV closure. Following the scram, reactor water level reached Level 3 (+13") resulting in Level 3 isolations. Unit 2 was taken to Cold Shutdown. The root cause of this event was attributed to misoperation of a primary bus differential relay, which occurred when the target reset pushbutton was depressed by the Operator. Following electrical investigation/evaluation of the bus and its protective circuitry, power was restored to the bus at 2053 hours on 3/18/92. The subject relay was tagged to identify that in the event a relay target is observed, Operations should contact Systems Engineering prior to resetting. The relay will be replaced at a later date and more thoroughly examined/tested to aid in understanding the misoperation resulting from resetting the target. All similar relays on Unit 2 were inspected and those on Unit 1 will be inspected prior to startup from its 1992 refueling outage. Repairs were completed on the 'B' EDG and it was restored to operable status. There were no safety consequences or compromise to public health or safety as a result of this event.
388 | 3881994002 | 1994-01-20 | QR5 | Turbine Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 100 | At 0150 hours on January 20, 1994, with Unit 2 in Condition 1 at 100% power, a reactor scram occurred, per design, when the Main Turbine tripped due to a loss of main generator stator cooling. Reactor water level dropped to + 2 inches. Reactor Level 3 isolations occurred per design. Reactor pressure peaked at 1083 psig, momentarily cycling Safety Relief Valves A, B, C, D, H, R and S. All Primary Containment parameters remained normal throughout the event. The loss of generator stator cooling was caused by failure of mechanical linkage in a controller for a temperature control valve on the stator cooling water system. Failure of the controller resulted in the temperature control valve closing, resulting in loss of cooling water flow to the generator stator. The plant was safely shutdown and there were no safety consequences or compromise to public health or safety during this event, nor would there have been under different initial operating conditions. This transient is within the bounds of a turbine trip as analyzed in Chapter 15 of the FSAR. The controller was repaired and the unit was returned to operation. Investigations into longer term actions to prevent recurrence are in progress.
388 | 3881995005 | 1995-04-15 | QR5 | Turbine Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 100 | At 0907 hours on April 15, 1995, with Unit 2 operating at 100% power, while isolating the unit output from the South Bus in the Susquehanna 500 kV Switchyard for scheduled maintenance, a reactor scram occurred, per design, when a generator load reject was received. All major equipment operated per design during the transient, Emergency Core Cooling Systems (ECCS) were not challenged and no abnormal operator actions were required to place the unit in a stable condition. The reactor scram was caused by a turbine control valve fast closure that resulted from a generator load rejection. The generator load rejection was caused by an incorrectly configured auxiliary cam switch in a 500 kV Switchyard motor operated disconnect. The mispositioned auxiliary cam switch initiated the open breaker flashover protection scheme that cleared the North Bus at the Susquehanna 500 kV Switchyard and tripped the Unit 2 generator lockout relays. The cause of the incorrectly configured auxiliary cam switch has been attributed to insufficient control and planning of work details during maintenance. This event was determined to be reportable per 10CFR50.73(a)(2)(iv) in that an unplanned ESF actuation occurred when the RPS initiated an automatic reactor scram following turbine control valve fast closure with power greater than 24%. The plant was safely shutdown and there were no safety consequences or compromise to public health or safety during this incident, nor would there have been under different initial operating conditions. This transient is within the bounds of a generator full load rejection transient as analyzed in Chapter 15 of the FSAR. The incorrectly configured auxiliary cam switch has been properly adjusted.
388 | 3881996004 | 1996-07-14 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Susquehanna 2 | B | GE | PO | 100 | On July 14, 1996, at 1801, with Unit 2 in Condition 1 (Power Operation) at 100% power, the unit was manually scrammed when an auxiliary bus failed to energize following the transfer of its power source from the generator feed to the offsite power feed. The reactor was manually scrammed prior to the reactor vessel water level reaching + 13 inches. Reactor Core Isolation Cooling (RCIC) System and High Pressure Coolant Injection (HPCI) System initiated when the reactor vessel water level reached -30 and -38 inches, respectively. Feedwater level control was re-established and RCIC and HPCI were placed in standby. All plant systems functioned as expected except the scram discharge volume inboard vent and drain valves did not open immediately after the reset of the scram, most likely caused by a sticking pilot valve. The failure of the auxiliary bus to energize is directly attributable to two leads not being terminated on a protective relay for one of the bus tie breakers due to personnel error. When the tie breaker was closed from the control room, the bus protective relaying actuated. The unterminate leads created a false unbalanced load on the bus. Per design, the protective relaying immediately initiated a trip and lock-out of the auxiliary bus thus deenergizing the bus. The two leads were terminated and the auxiliary bus and the start-up bus were walked down to assure that there was no equipment damage or any evidence of a fault on the buses. No equipment damage or faults were found. Appropriate station personnel were briefed on the event. The personnel involved in the error were placed on administrative leave pending final disposition. Additional supervisory oversight was added for non-Nuclear Maintenance work group activities. Also, the lessons learned from this event will be applied to non-Nuclear Maintenance work group activities. There was no safety consequence or compromise to the public health or safety as a result of this event.
388 | 3881998009 | 1998-06-29 | QR5 | Turbine Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 55 | On June 29, 1998 at 0319 hours, with Unit 2 in Condition 1 (power operation) at 55% power, the "A" Moisture Separator experienced a drain tank high level condition. This condition initiated a turbine trip, which in turn resulted in a reactor SCRAM. The most likely cause of the Moisture Separator high level is believed to be the accumulation of water in one or more of the cross-around pipes between the High Pressure Turbine and the Moisture Separator. As power was being increased, system dynamics were such that the accumulated water was swept into the Moisture Separator. This event was determined to be reportable to the Commission per 10CFR 50.73(a)(2)(IV) as a result of actuation of the Reactor Protection System (RPS). The plant response to this event was as expected. There were no Emergency Core Cooling System (ECCS) initiations or injections, no emergency diesel generator starts, and no Main Steam Relieve Valve lifts. All equipment important to safety was available throughout the event. As such, there were no safety consequences or compromises to public health and safety. The safety and welfare of the public was not compromised. Corrective actions include: procedural changes to add assurance that water is removed from the cross-around piping; monitoring temperature of piping drains to assure flow; and the performance of an independent study to review issues associated with this event.
388 | 3881998010 | 1998-07-02 | QR8 | Spurious Reactor Trip | [45 empty] | Susquehanna 2 | B | GE | SU | 1 | On July 2, 1998, at 0417 hours, with Unit 2 in Condition 2 (Startup) at about 0.1% power, a Division I Intermediate Range Monitor (IRM) upscale trip was received, shortly followed by a Division II IRM upscale trip, resulting in a Reactor SCRAM. Both upscale trips were a result of the misoperation of the IRM range switches. Just prior to the upscale IRM trips, a licensed operator had continuously withdrawn control rod 34-23 from position 00 to position 24. This resulted in a reactor period, calculated post event, of approximately 30 seconds. Following the SCRAM, the reactor responded as expected, and there were no Emergency Core Cooling System (ECCS) initiations or injections. There were four fundamental root causes for this event: (1) the operating crew failed to exercise proper sensitivity to reactivity manipulations during the startup and did not demonstrate a profound respect for the reactor core, (2) the operating crew team dynamics failed when the team members did not establish and maintain their roles, (3) management and supervisory oversight failed to recognize operator practices leading to this event, and (4) operators failed to apply the knowledge of reactor physics fundamentals and associated skills gained through training during the reactor startup beyond the initial criticality of the reactor. This event is reportable per 10CFR50.73(a)(2)(iv) as a automatic actuation of an Engineered Safety Feature (ESF), in this case. The Reactor Protection System (RPS), which resulted in a reactor SCRAM. There were no safety consequences as a result of this event and the health and safety of the public was not compromised. No safety limits were approached and the event is entirely bounded by the plant accident analysis. Corrective actions include: (1) procedure and startup sequence changes, (a) requiring proper single notch withdrawal restraints through the point of adding heat, (b) leaving the IRM recorders on fast speed until above IRM range 7, and (c) ensuring the SRMs are responsive throughout this power range, (2) operator training on this event, and management's expectations with regard to reactivity control; (3) establishment of various teas to ensure reactor reactivity changes are adequately controlled and monitored, and (4) establish a self-assessment program for reactivity to assess in-plant performance against clearly defined standards.
388 | 3881999003 | 1999-06-08 | QR5 | Turbine Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 100 | At 1206 hours on June 8, 1999, with Unit 2 in Mode 1 (Power Operation) at 100% power, a unit primary lockout signal, created when one of the three single-phase main transformers failed, caused a Main Turbine trip. In accordance with plant design, the Turbine Control Valves closed and an automatic reactor scram occurred. All major equipment operated per design during the transient. Emergency Core Cooling Systems (ECCS) were not challenged and no abnormal operator actions were required to place the unit in a stable condition. The cause of the event was attributed to a failure of a neutral bushing in the 'A' Main Transformer due to a defective subcomponent. Failure of the bushing caused an electrical arc in the transformer resulting in a pressure spike inside the transformer oil tank and subsequent generator load rejection. Inadequate processing (human error, other utility personnel) by PP&L, of a 1990 manufacturer advisory for the defective bushing, led to its installation. The entire 'A' Main Transformer was replaced along with an acceptable bushing. The remaining in-service Unit 1 and Unit 2 main transformers were inspected for the defective bushings and none were found. Two spare bushings were found defective and segregated to prevent use. Any defective bushings of the same type will be prevented from being procured and installed through administrative processes. Personnel that process manufacturer advisories will be provided with information on this event. A review of manufacturer advisories will be conducted. The plant was safely shutdown, and there were no safety consequences or compromises to public health or safety during this event.
388 | 3882002004 | 2002-09-30 | QC4 | Loss of ac Instrumentation and Control Bus. | [45 empty] | Susquehanna 2 | B | GE | PO | 72 | On September 30, 2002 with Unit 2 in Mode 1 (Power Operation) at 100% power, electricians working at an Uninterruptable Power Supply (UPS) inappropriately configured panel breakers in a manner that energized a large set of capacitors. A Reactor Recirculation pump runback caused by the resulting momentary electrical transient reduced power to 72%. The electrical transient also resulted in an Off gas system shutdown and a slow degradation of condenser vacuum. At 72% power, an automatic reactor scram occurred, in accordance with plant design, when the Main Turbine tripped on low condenser vacuum. The automatic Main Turbine trip occurred sooner than proceduralized setpoint information indicated it should have, thus precluding a manual intervention that was planned upon attainment of a predetermined condenser pressure. Poorly worded work instructions associated with the UPS panel work were responsible for the inappropriate breaker alignment. Additionally, a malfunctioning UPS panel breaker permitted establishment of the erroneous configuration despite breaker closure logic that should have prevented the alignment. ECCS was not challenged during this event. No abnormal operator actions were required to place the plant in a stable condition. The malfunctioning UPS panel breaker will be replaced. The plant procedure that governs work instruction development will be modified to improve the content and format of future work plans. Preventative maintenance tasks will be developed to ensure proper operation of the malfunctioning UPS panel breaker and other similar UPS breakers. Finally, turbine trip setpoint information contained in Operating procedures has been revised to reflect actual trip settings. This event is reportable for Unit 2 as an Unplanned RPS Actuation per 10 CFR 50.73(a)(2)(iv)(A). There were no actual adverse consequences to plant equipment or to the health and safety of the public as a result of this event.
388 | 3872002006 | 2002-10-03 | QR6 | Manual Reactor Trip | [7 empty] | X | [25 empty] | X | [11 empty] | Susquehanna 2 | B | GE | SU | 1 | At approximately 0230 hours on October 3, 2002, a fire occurred on Startup Transformer (ST) No. 20.The transformer fire was extinguished by the transformer's automatic deluge system. Unit 1 was in MODE 1 - Power Operation operating at 100% power and Unit 2 was in MODE 2 -Startup. Unit 2 was manually scrammed due to a loss of both Reactor Recirculation pumps. Unit I continued operation at 100% power. The fire was extinguished quickly and caused no significant impact to adjacent systems or structures. An Emergency Plan Unusual Event was declared at 0315 when it was determined that two explosions also occurred. The Unusual Event was terminated at 0552 on October 3, 2002.ST No. 20 was replaced and declared operable on October 10, 2002. This event was reported in LER 50-387/2002-006-00, PLA-5534 dated October 15, 2002. This supplement to that LER provides the final conclusions of PPL's investigation of the transformer failure. The conclusion of this investigation was that the root cause was an undetectable internal fault. This internal fault could have originated from several possible sources. It was also determined that the primary and backup lockout relays did not actuate as expected during the event. The lockout relays provide electrical protection for the ST-20 Startup Transformer and function automatically to protect the transformer. The failure of the primary and backup lockout relays to actuate did not cause the event. Corrective actions have been developed and implemented with sufficient breadth to address the possible causes of both the transformer and the protective relay failures. No safety barriers were affected by this event. There were no consequences to the health and safety of the public as a result of this event.
388 | 3882005003 | 2005-04-28 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Susquehanna 2 | B | GE | PO | 75 | At approximately 0700 hours on 4/28/2005 with Unit 2 in Mode 1 at 100% power, the Control Room received a B Phase Main Transformer alarm. Operators were dispatched and found the cooling system for the transformer not operating. Without cooling, plant alarm procedures require removal of the transformer from service. Reactor power was reduced from 100% to 75% while attempting to restore transformer cooling to minimize any adverse impact to the transformer. Attempts to restore the B Main Transformer cooling were unsuccessful and the reactor was manually scrammed at 0719 hours. The event was determined to be reportable under 10 CFR 50.72, reference ENS Notification EN #41646. Following the manual scram, the Unit 2 electrical output breakers automatically opened as designed removing the electrical load from the Main Transformers. The other plant systems also responded per design. RPV water level decreased to -30" due to the SCRAM, which resulted in RCIC initiating. Normal Feedwater and RCIC systems restored water level. The manual scram and subsequent injection of the RCIC system are considered unplanned actuations of systems that mitigate the consequences of significant events and are reportable per 10 CFR 50.73(a)(2)(iv)(A). This event resulted in no actual adverse consequences to the health and safety of the public.
388 | 3882005005 | 2005-06-06 | QR5 | Turbine Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 100 | At 1233 hours on 6/6/2005 with Unit 2 operating in Mode 1 at 100% power, the reactor automatically scrammed as a result of a turbine trip from a generator lockout. The main generator excitation system had failed to positively respond to changes to the offsite grid, which resulted in a loss of generator field, causing the lockout. Although plant data was inconclusive in determining what initiated the event, the most probable cause was an increased resistance in the main generator exciter field circuitry. Based on the unplanned actuation of RPS, this event was determined to be reportable under 10 CFR 50.72, reference ENS Notification EN #41746. Following the automatic scram, two Main Steam Safety Relief Valves opened and then closed to initially control reactor pressure. The Main Steam Bypass Valves were subsequently able to control pressure. Several balance of plant systems were impacted by the generator voltage perturbation but there were no unusual electrical transients or challenges to the station's safety-related electrical systems. All plant safety systems responded per design. Reactor water level dropped to -6 inches and was restored to +35 inches by normal feedwater level control. There were no challenges to containment or evidence of fuel failure. The automatic scram was an unplanned actuation of a system designed to mitigate the consequences of a significant event and is reportable per 10 CFR 50.73(a)(2)(iv)(A). This event resulted in no actual adverse consequences to the health and safety of the public.
388 | 3882011003 | 2011-08-19 | QR5 | Turbine Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 100 | On August 19, 2011, at 10:46 hours, Susquehanna Steam Electric Station (SSES) Unit 2 automatically scrammed from 100 percent power due to a main turbine trip. The main turbine trip occurred during the performance of the quarterly functional surveillance test of the reactor water high level trip channels for feedwater / main turbine. The surveillance test was being performed for the first time since the 2011 upgrade of the Unit 2 feedwater level control system with a digital Integrated Control System (ICS). As part of the test, operations personnel transferred the reactor water level input signal from average level to narrow range 'B' biased as required by the procedure. The main turbine and feedwater trip system design uses three narrow range reactor water level channels in a two-out-of-three trip logic. When the first narrow range reactor water level channel ('2A') was tested, an unexpected automatic main turbine trip occurred. ENS notification (47172) was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iv) for an event or condition that resulted in the actuation of the RPS when the reactor was critical, and 10 CFR 50.72(b)(3)(iv)(A) due to a valid actuation of the RPS. This Licensee Event Report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A). This event had no impact to the health and safety of the public. The direct cause was an incorrectly terminated internal jumper. The wiring anomaly in the ICS Level 8 turbine trip logic circuitry resulted in one of the Level 8 trip logic contacts being jumpered out of the channel trip circuitry, causing a Unit 2 main Turbine Trip from the initiation of one single channel instead of the designed two-out-of-three channel logic. The root causes for this event are 1) Conflicting and unclear procedure requirements, and less than adequate (LTA) reinforcement of management expectations for work package content resulted in a key visual check of internal jumpers being omitted from the scheme check work package during its preparation. Therefore, testing failed to check and discover the miswired jumper, 2) LTA procedure adherence during development of engineering change functional testing resulted in insufficient testing of the ICS Level 8 main turbine trip logic, and 3) The work order review process weaknesses related to procedure content, procedure adherence, reinforcement of expectations, and definition of work order scope resulted in the review of the ICS Level 8 scheme check work package not identifying the missing key internal jumpers. This resulted in a missed opportunity to identify the incorrectly terminated conductor. Corrective actions include 1) Revise the control scheme testing procedure to clearly identify the specific responsibilities of the preparer, technical reviewer and the implementer of scheme checks and to align scheme check work order content to meet requirements of SSES maintenance work practices, 2) Require the use of risk managed defenses for functional test procedure development and field installation activities for risk significant modifications, 3) To improve the use of and compliance with procedures on a sustainable basis, and reinforce through observation, the use of the SSES Station Fundamentals Tool Kit that the 'Procedures' core fundamental and supporting behaviors shall be maintained, and 4) Conduct reinforcement sessions regarding management's expectation for scheme check work order preparation, technical review and implementation support.
388 | 3882012002 | 2012-11-09 | QR6 | Manual Reactor Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 90 | At approximately 0117 hours on November 9, 2012, with power at approximately 90%, plant operators scrammed Susquehanna Unit 2 and tripped Reactor Feed Pump Turbines A, B, and C due to a loss of the Integrated Control System (ICS). All control rods inserted and both reactor recirculation pumps tripped at -38 inches. Reactor water level lowered to -52 inches causing Level 3 (+13 inches) and Level 2 (-38 inches) isolations. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) both automatically initiated. HPCI was overridden prior to injection and RCIC was utilized to restore reactor water level to the normal band. All isolations and initiations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected.<br /><br /> Following the manual scram due to the ICS failure, a second scram signal was received at approximately 0420 hours on November 9, 2012 due to low water level during recovery from the initial scram. Reactor water level was +15 inches at the time of the trip. All initiations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected.<br /><br /> The initial scram and other associated system actuations were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B), 10 CFR 50.72(b)(3)(iv)(A), and 10 CFR 50.72(b)(2)(iv)(A) in EN 48496. The second scram signal was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) in EN 48500. These events are also reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> The root cause of the initial scram was less than adequate evaluation of deficiencies associated with ICS core switch design, testing, and mitigating strategies that resulted in delayed resolution without understanding risk implications. The root cause of the second scram was Operations and Engineering did not emphasize the avoidance of a second scram on RPV Level 3 through standards, policies, administrative controls, procedures, and associated training. Key corrective actions included: 1) replacing the core switches with a newer version of the switches and enabling loop protection algorithms on Unit 1 and Unit 2, 2) various procedure changes to provide margin to a secondary scram including changes to the scram off-normal procedures, and training.<br /><br /> There were no adverse consequences to the health and safety of the public as a result of this event.
388 | 3882012003 | 2012-12-16 | QR8 | Spurious Reactor Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 99 | On December 16, 2012, at approximately 0156 hours, the Susquehanna Steam Electric Station (SSES) Unit 2 reactor automatically scrammed during the performance of quarterly channel functional test of the turbine control valve (CV) fast closure channels of the Reactor Protection System (RPS). Both the High Pressure Cooling Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems automatically initiated and injected water into the reactor vessel. At approximately 0210 hours on December 16, 2012, a second reactor scram signal was received due to reactor water level lowering to +13 inches. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in the automatic actuation of the RPS, and the HPCI and RCIC systems. <br /><br /> 0156 hours Scram - No direct cause of the unexpected Division 1 scram signal was identified. This conclusion is based on laboratory results from the disassembly and inspection of the #1 Turbine CV. The root cause of the scram was SSES failed to incorporate industry best practices with other impacted work groups for half scram reduction. 0210 hours Scram - The root causes are: The ICS design control value of +18 inches for setpoint setdown did not provide adequate margin to prevent operational overlap with the RPS low level scram setpoint of +15 inches; and the ICS reactor water level setpoint setdown was not reset prior to raising the ICS reactor water level <br /><br /> .Key completed corrective actions include: replaced the Unit 1 CV #1 Fast Acting Solenoid Valve and Shutoff Valve; revised the Unit 1 and 2 quarterly turbine valve cycling surveillance procedure to require the use of an RPS test box; inspected all four Unit 1 Fast Acting Solenoid Valves for secure butt splice connections; revised ON-100(200)-101 to specify reactor water level band that would not create a reactor low water level scram; revised OP-245-001 and hard card OP-245-001-01 to provide direction for resetting the ICS setpoint setdown. Key planned corrective action: provide training to all operators on specific lessons learned as they pertain to reactor level control. Include this training in initial license and licensed operator requal training. There were no actual consequences to the health and safety of the public as a result of this event.
388 | 3882012004 | 2012-12-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Susquehanna 2 | B | GE | PO | 18 | At approximately 1731 hours on December 19, 2012, with the unit operating at approximately 18% power, Susquehanna Steam Electric Station Unit 2 automatically scrammed on low reactor pressure vessel (RPV) level (Level 3, +13 inches) while transitioning the 'A' reactor feed pump from discharge pressure mode to flow control mode. All control rods inserted and both reactor recirculation pumps tripped. Reactor water level lowered to approximately -29 inches causing Level 3 (+13 inches) isolations. There were no automatic Emergency Core Cooling System initiations. No steam relief valves opened during the event. All safety systems operated as expected. The scram and associated actuations were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) in EN 48607 at 2029 on December 19, 2012. These events are also reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iv)(A). The root causes of the event were: 1) decision making without a formal evaluation of impacts that reflected a conditioned operator response and inadequate risk evaluation of activities and 2) missed opportunities to identify and provide compensation for the design of the integrated control system logic interface with the valve breaker power. Key corrective actions included: 1) providing operator training, 2) providing an equipment reliability update to crews, 3) issuing an Operations directive to minimize the knowledge based decisions, 4) revising the Units 1 and 2 reactor feed pump operating procedures, and 5) placing caution signs on the applicable valve breakers indicating that opening the breakers impacts Integrated Control System (ICS) logic. Key corrective actions planned include: 1) defining operator specific skill of the craft work activity actions in an Operations administrative procedure, 2) implementing changes to the station procedure use and adherence procedure, and 3) creating new or revised guidance on the need to identify actions to respond to or compensate for single point vulnerabilities. There were no adverse consequences to the health and safety of the public as a result of this event.
388 | 3882013003 | 2013-09-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Susquehanna 2 | B | GE | PO | 14 | On September 14, 2013, at approximately 0330 hours, the SSES Unit 2 reactor was manually scrammed following the loss of all Reactor Feedwater Pumps (RFPS) due to high reactor water level. This occurred while transitioning the feedwater Integrated Control System (ICS) for the 'A' RFP from flow control mode to discharge pressure mode. Reactor water level rose to +54 inches causing a trip of the reactor feedwater pumps. Operations subsequently took the mode switch to shutdown to manually scram the reactor. All control rods inserted. There were no automatic Emergency Core Cooling System initiations. No steam relief valve opened during the event. No containment isolations occurred. All safety systems operated as expected. The Reactor Core Isolation Cooling (RCIC) system was manually initiated for reactor water level control until a RFP was recovered. RCIC was manually shut down once a RFP was restored. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A), for an event or condition that resulted in the manual actuation of the RPS and RCIC system.<br /><br /> Root cause of the event: The overall process for implementation of ICS logic block code changes lacked the required level of process rigor and formality for maintaining digital control systems with the potential to affect reactivity and reactor water level. This challenged the operator's ability to maintain precise control of the plant.<br /><br /> Key planned corrective actions: 1) Develop procedural guidance to implement the HURST software configuration management tool for post-maintenance testing of ICS software changes, and 2) Develop procedural guidance for installing/verifying code changes to the ICS software.<br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
388 | 3882015003 | 2015-04-10 | QL7 | Degraded condenser vacuum | [45 empty] | Susquehanna 2 | B | GE | PO | 37 | On April 10, 2015, at 2100 hours, a planned shutdown for the Susquehanna Unit 2 refueling outage commenced. With shutdown in progress and at approximately 37% power for balance of plant operations, a pre-job brief was conducted in preparation for placing an Auxiliary Boiler in service and placing the Main Turbine Steam Seals on Auxiliary Steam. At 2129 hours, the 'A' Auxiliary Boiler was placed in service per procedure OP-027-001, "Aux Boiler System," and the Main Turbine Steam Seals were placed on auxiliary steam via valve 221008, "SJAE and Steam Seal Aux Supply !so Vlv." At approximately 2330 hours, the procedure was resumed which directed closure of valve 221008 when Auxiliary Boiler temporary load is no longer needed. At this point, temporary load was no longer needed but auxiliary steam was still flowing through valve 221008, supplying steam to the Unit 2 Main Turbine Steam Seals. The valve was subsquenty closed, which isolated steam to the U2 Main Turbine Steam Seals, allowing air in-leakage into the Main Condenser, causing condenser vacuum to degrade. At 2346 hours, Unit 2 automatically scrammed from approximately 37 percent power due to a the Main Turbine trip on loss of condenser vacuum. Root Cause: Personnel involved with auxiliary boiler startup did not adhere to Operator Fundamentals and effectively apply appropriate Human Performance error-reduction tools specific to understanding and anticipating the impact of component operation prior to its operation. Completed Action: Procedure OP-027-001, "Auxiliary Boiler System," was revised to caution operators of the potential for isolating auxiliary steam to the Main steam seals and/or Steam Jet Air Ejectors when securing temporary loading of the auxiliary boilers. Key Planned Action: Provide initial licensed and non-licensed operator classroom and job performance measure or dynamic learning activity training with focus on: STAR, Questioning Attitude, Pre job Brief, and understand and anticipate the impact of component operation prior to its operation. Safety Significance: There were no actual consequences to the health and safety of the public as a result of this event.
388 | 3882016004 | 2016-05-13 | QR6 | Manual Reactor Trip | [45 empty] | Susquehanna 2 | B | GE | PO | 100 | At 23:55 on 5/12/16, Unit 2 experienced an electrical transient resulting in a loss of 2B246 Reactor Building Engineered Safeguard System (ESS) Division 480 volt Motor Control Center (MCC) and 2Y246 208/120 Volt Alternate Current (AC) Instrument Panel. With the loss of the Reactor Building ESS Division 480 volt MCC, several drywell cooling fans were lost leading to an increase in drywell pressure. At 0110 on 5/13/16 Unit 2 was manually scrammed. All rods inserted as expected. Reactor water level lowered to -27 inches and was immediately restored by normal feedwater level control. Level 3 (+13 inch) Primary Containment Isolation System (PCIS) isolations occurred, along with an initiation of the Reactor Core Isolation Cooling (RCIC). <br /><br /> The direct cause of the transient was found to be a phase to ground short between a cable and a protruding screw in MCC bucket 2B246091, Drywell Area Unit Cooler 2V411B Breaker. The apparent cause is the vendor did not comply with Specification E1116, Rev 3 with this order of buckets. Immediate corrective actions included the repair of 2B246 which has been completed. A plan has been developed to review a sample of the 480 VAC MCC breakers and is being tracked by maintenance and system engineering.
388 | 3882020001 | 2020-02-14 | QL7 | Degraded condenser vacuum | [45 empty] | Susquehanna 2 | B | GE | PO | 98 | On February 14, 2020 at 00:25, Susquehanna Steam Electric Station (SSES) Unit 2 reactor was manually scrammed due to rising Main Condenser backpressure caused by a loss of the Unit 2 Offgas Recombiner. This event was reported by Notification EN 54525 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the Reactor Protection System (RPS) (including reactor scram), as well as associated isolation and actuation of other systems listed in 10 CFR 50.73(a)(2)(iv)(B), including the Reactor Core Isolation Cooling (RCIC) system. <br /><br /> The most probable cause was an inadvertent closure (drifting closed) of the Unit 2 Offgas Recombiner System Inlet Control Valve. Stroking, disassembly, reassembly, and air operated valve diagnostics alleviated the cause of the inadvertent closure. <br /><br /> There were no actual safety consequences associated with the condition.
388 | 3882021003 | 2021-10-11 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Susquehanna 2 | B | GE | PO | 95 | On October 11, 2021, at approximately 13:21, Susquehanna Steam Electric Station Unit 2 reactor automatically scrammed due to a main turbine trip. Both divisions of the Reactor Protection System (RPS) actuated and all control rods inserted. This event was reported by Event Notification 55514 in accordance with 10 CFR 50.72(b)(2)(iv)(A), (b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). <br /><br /> The event was caused by the 500kV switchyard primary plant interface relay inadvertently tripping open the main generator output breakers due to a transient voltage resulting from a ground applied on the primary switchyard battery system. This led to a load reject trip of the main turbine that resulted in an automatic scram. <br /><br /> Key corrective actions included removing the ground from the 125 VDC primary switchyard battery system, implementing an increased time delay for trip signals to the primary plant interface relay, and lifting redundant shield grounds on the station side of the relay. Additionally, primary plant interface inputs will be hardened, as appropriate. <br /><br /> There were no actual consequences to the health and safety of the public as a result of this event.
389 | 3891987001 | 1987-03-03 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | POWER LEVEL - 100%. ON 3-3-87, UNIT 2, WHILE OPERATING IN MODE 1 AT 100% POWER, TRIPPED ON LOW STEAM GENERATOR (S/G) LEVEL WHILE INSTRUMENT AND CONTROL PERSONNEL WERE PERFORMING THE AUXILIARY FEEDWATER ACTUATION SYSTEM (AFAS) MONTHLY FUNCTIONAL TEST. THE TRIP OCCURRED WHEN REDUNDANT POWER SUPPLIES WERE LOST TO ONE OF THE AFAS CHANNELS, WHICH CAUSED A B SIDE MAIN FEEDWATER ISOLATION VALVE (MFIV) TO CLOSE LEADING TO THE LOW S/G LEVEL. THE ROOT CAUSE OF THIS EVENT INVOLVES A COMBINATION OF DESIGN, PROCEDURAL, AND PERSONNEL ERRORS WHICH LED TO THE LOSS OF AFAS CHANNEL POWER. PLANT MANAGEMENT AND MANUFACTURER REPRESENTATIVES HAVE DECIDED TO RAISE POWER SUPPLY OVER-VOLTAGE PROTECTION SETPOINT TO 15 VOLTS TO PREVENT RECURRENCE. APPROPRIATE CHANGES WILL ALSO BE MADE TO THE VENDOR'S TECHNICAL MANUAL.
389 | 3891987002 | 1987-03-05 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 40 | REACTOR TRIP OCCURRED DUE TO LOW STEAM GENERATOR (S/G) LEVEL. THE TRIP OCCURRED WHEN THE B MAIN FEEDWATER REGULATING VALVE (MFRV) ACTUATOR MALFUNCTIONED, PREVENTING PROPER FEED FLOW TO THE B S/G. THE UNIT WAS PERFORMING A POWER ASCENSION IN MODE 1 AT 40 PERCENT POWER AT THE TIME OF THE EVENT. THE ROOT CAUSE OF THE EVENT WAS A MALFUNCTION OF THE MFRV ACTUATOR. THE ACTUATOR WAS REPLACED AND THE VALVE FUNCTIONED PROPERLY.
389 | 3891987003 | 1987-04-09 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | St. Lucie 2 | P | CE | PO | 100 | POWER LEVEL - 100%. ON APRIL 9, 1987, INSTRUMENT AND CONTROL MAINTENANCE PERSONNEL WERE PERFORMING MONTHLY SURVEILLANCE TESTING OF THE ENGINEERED SAFETY FEATURES ACTUATION SYSTEM. DURING THE TESTING PROCESS, IT WAS NOTED THAT THE ANNUNCIATOR P-18 DID NOT ILLUMINATE. AFTER THE COMPLETION OF THE TEST, I&C PERSONNEL STARTED TO TROUBLESHOOT AND DURING THE TROUBLESHOOTING SEQUENCE, A JUMPER WAS PLACED ON THE WRONG TERMINAL OF THE MAIN STEAM ISOLATION SIGNAL (MSIS) ACTUATION PUSHBUTTON CIRCUITRY CAUSING THE ACTUATION OF A MSIS WHICH RESULTED IN THE CLOSURE OF THE MAIN FEEDWATER ISOLATION VALVES AND THE MAIN STEAM ISOLATION VALVES. THIS RESULTED IN AN AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL. THE ROOT CAUSE OF THE EVENT WAS A COGNITIVE PERSONNEL ERROR OF I&C PERSONNEL PLACING A JUMPER ON THE WRONG TERMINAL OF THE MSIS PUSHBUTTON CIRCUITRY DUE TO MISINTERPRETATION OF THE CIRCUIT WIRING DIAGRAM. THE PERSONNEL INVOLVED WERE COUNSELED AND INFORMATION WILL BE FORWARDED TO THE PLANT TRAINING DEPARTMENT FOR EVALUATION.
389 | 3891987004 | 1987-04-22 | QR5 | Turbine Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | POWER LEVEL - 100%. ABSTRACT DURING NORMAL FULL POWER OPERATION MAINTENANCE PERSONNEL PERFORMING AMMETER CALIBRATIONS JUMPERED THE WRONG TERMINALS, CAUSING THE LOSS OF A NON SAFETY-RELATED LOAD CENTER, WHICH CAUSED A TURBINE TRIP, RESULTING IN AN AUTOMATIC REACTOR TRIP. THE ROOT CAUSE OF THE EVENT WAS PERSONNEL ERROR. CORRECTIVE ACTIONS INCLUDED COUNSELLING PERSONNEL, A TERMINAL BOARD LABELLING EVALUATION, CORRECTING A WIRING DISCREPANCY, AND ADDITIONAL ADMINISTRATIVE CONTROLS.
389 | 3891987007 | 1987-11-25 | QR5 | Turbine Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 50 | POWER LEVEL - 050%. ON 25 NOVEMBER 1987, ST. LUCIE UNIT TWO WAS OPERATING AT 50 PERCENT POWER STEADY STATE IN MODE 1. AT 2331 HOURS, THE REACTOR TRIPPED ON LOSS OF LOAD DUE TO A TURBINE TRIP. THE TURBINE TRIPPED ON A MAIN GENERATOR LOCKOUT. THE FAILURE OF THE MAIN GENERATOR EXCITER BEARING CAUSED THE ARMATURE OF THE PERMANENT MAGNET GENERATOR (PMG) TO GRIND INTO ITS STATOR. WHEN THIS OCCURRED, THE PMG DISCONTINUED SUPPLYING VOLTAGE TO THE EXCITER OF THE MAIN GENERATOR. THE TRIP WAS UNCOMPLICATED AND THE UNIT WAS QUICKLY STABILIZED IN MODE 3, HOT STANDBY. THE ROOT CAUSE OF THE EVENT WAS A PERSONNEL ERROR DURING THE PERFORMANCE OF THE WEEKLY GENERATOR EXCITER GROUND CHECK ON WHICH A PROLONGED GROUND RESULTED IN THE FAILURE OF THE GENERATOR EXCITER BEARING. THE FOLLOWING CORRECTIVE ACTIONS HAVE BEEN IMPLEMENTED: REPLACED THE PMG AND THE EXCITER BEARING, REMOVED THE EXCITER BEARING THERMOCOUPLE TO PREVENT FUTURE GROUNDING OCCURRENCE OF THIS TYPE, PROCEDURES HAVE BEEN REVISED TO ENSURE ANY FUTURE GROUNDS ARE RECOGNIZED, AND TRAINING WAS GIVEN TO ALL ELECTRICAL MAINTENANCE PERSONNEL FOR BETTER UNDERSTANDING OF THE EXCITER GROUND CHECK.
389 | 3891989005 | 1989-06-26 | QP5 | Excessive Feedwater Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 22 | On June 26, 1989 at 2347 hours, St. Lucie Unit 2 reactor tripped on loss of load from 22% power during turbine startup. The loss of load reactor trip was a result of a turbine trip due to high steam generator level in the 2A steam generator. The trip was uncomplicated and the unit was quickly stabilized in Mode 3, Hot Standby. <br /><br /> The root cause of the event was cognitive personnel error by utility-licensed operators due to less than adequate communication between the shift crew performing the turbine startup evolution. <br /><br /> The utility-licensed operators were counseled on the need for well controlled evolutions, in which good communication is of the utmost importance by all participants, as a short term corrective action. The plant training group will evaluate this event to determine appropriate training requirements and methods.
389 | 3891989007 | 1989-09-23 | QR3 | Reactivity Control Imbalance | [45 empty] | St. Lucie 2 | P | CE | PO | 96 | At 0558 on September 23, 1989, with St. Lucie Unit 2 in Mode 1 at 100% power, the unit experienced a dropped Control Element Assembly (CEA) in Regulating Group 1. The Reactor Control Operator (RCO) manually reduced main turbine load to match reactor power. At 0613, as the control rods were being inserted, four CEAs in Regulating Group 5, the lead bank, dropped in the core. The RCO immediately tripped the reactor from 96% power due to the multiple drop CEAs. The Standard Post Trip Actions were completed and the unit was quickly stabilized in Hot Standby, Mode 3. <br /><br /> The most probable cause of the event was a blown fuse causing the initial dropped CEA. The apparent cause for the four CEAs to drop was due to the tripping of the CEA Subgroup breaker. The root cause for the subgroup breaker trip has not been conclusively identified; however, testing the subgroup breaker revealed that the breaker tripped at a current less than designed. <br /><br /> The following corrective actions have been implemented: replaced the blown fuse and replaced the CEA Subgroup breaker.
389 | 3891990001 | 1990-01-14 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | St. Lucie 2 | P | CE | PO | 50 | On 14 January, 1990, St Lucie Unit 2 was in mode 1 and performing power ascension towards 100%A power following a reactor startup from a maintenance outage. The turbine startup procedure was being utilized. The 2B Steam Generator Feed Pump and 2B Condensate Pump were in service. Reactor power was approaching 50% with the turbine power increasing at 4.0 Megawatts per minute when the 2B Steam Generator Feed Pump low suction pressure alarm was received. Utility licensed operators attempted to start the 2A condensate Pump but it would not start. The 2B Steam Generator Feed Pump tripped on low suction pressure. The pump was unable to be restarted. The Steam Generator water levels decreased to the automatic trip setpoint and the unit automatically tripped at 2325. The 2C Auxiliary Feedwater Pump tripped on overspeed upon receiving an Auxiliary Feedwater Actuation Signal. Standard Post Trip Actions were performed and the unit was stabilized in Mode 3. <br /><br /> The second condensate pump could not be started prior to the trip because it control fuses had not been re-installed following outage work. Procedures have been changed to ensure the availability of the second condensate and feedwater pump further in advance for being needed and to clarify the power ascension procedure. The 2C Auxiliary Feedwater Pump was returned to service. A cognitive personnel error by the utility licensed operators led to the automatic reactor trip.
389 | 3891992001 | 1992-04-21 | QR3 | Reactivity Control Imbalance | [45 empty] | St. Lucie 2 | P | CE | PO | 15 | On 21 April 1992, with Unit 2 in Mode 1, a plant shutdown was in progress for a scheduled refueling outage. Difficulty in maintaining Axial Shape index within limits was expected during the downpower. When reactor power reached approximately 15% three of four local power density pre- trips in the reactor protection system alarmed. The nuclear plant supervisor directed a manual reactor trip at 0238. On the manual reactor trip the turbine did not trip automatically, but remained tied to the system grid carrying approximately 90 megawatts. Several additional attempts were made to trip the turbine from the manual pushbuttons in the control room. The turbine was tripped locally at the front standard using the emergency trip lever at 0241. "Standard Post Trip Actions" were performed as per EOP-1 and the plant was stabilized in Mode 3, Hot Standby. <br /><br /> The root cause of the reactor trip was inadequacy in the core axial shape index management guidelines. The root cause of the failure of the turbine to trip either automatically or by manual pushbutton was the failure of the turbine trip controls to perform their function because of a relay problem and particulate matter blocking a solenoid valve drain port. <br /><br /> Corrective actions for this event: Procedural changes have been implemented to provide additional guidance on axial shape index control. Additional guidance has been incorporated into EOP-1 on actions to take for a reactor trip with no subsequent turbine trip. A design change to the setpoint of the local power density pre-trip was also implemented. Modifications to the turbine control system were made allowing the turbine trip valves to be tested while the unit is online. Modifications were made to the control circuitry of the turbine providing continuous monitoring of wiring continuity. The effectiveness of these corrective actions will be evaluated for implementation on Unit 1.
389 | 3891992004 | 1992-07-08 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On July 8, 1992 at 1134 hours with St. Lucie Unit 2 in mode 1 at 100% power, the reactor was manually tripped due to low (A) Steam Generator water level. Standard Post Trip Actions were performed as per EOP-1. Normal Steam Generator water levels were regained, two sets of safety function status checks were performed as per EOP-2 Reactor Trip Recovery and the plant was stabilized in Mode 3, Hot Standby. <br /><br /> The root cause of the reactor trip was a failed Lead/Lag circuit in the 2A Feedwater Regulating valve control system, which initiated the level transient of the 2A Steam Generator. The purpose of the Lead/Lag circuit is to provide fast initial valve response to a Steam Generator water level step change. <br /><br /> Corrective Actions for this event: 1) The Lead/Lag circuitry for the 2A Steam Generator Feedwater Regulating Valve Control System was removed from service after an engineering evaluation identified that the Lead/Lag circuitry had a negligible composition effect. 2) A final design charge by FP&L Engineering will address a possible permanent deletion of the Lead/Lag circuits from the Steam Generator water level control circuitry or a new replacement for both Units 1 and 2, 3) A review of other single point vulnerabilities related to this type of component failure in the Feedwater and Condensate systems will be performed by Technical Staff and I&C Maintenance. 4) Extensive simulator training was previously performed utilizing a Loss of Main Feedwater scenario. However, the Training Department will evaluate this specific event for inclusion into the Licensed Operator requalification program.
389 | 3891992005 | 1992-07-10 | QR5 | Turbine Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On July 10, 1992 at 1018 hours with St. Lucie Unit 2 in mode 1 at 100% power, the reactor automatically tripped on loss of load while performing turbine trip valve tests. Prior to the trip, Operations personnel were testing turbine trip valve 20/ET using recently installed on-line testing circuitry. This new on-line testing circuitry was installed during the 1992 refueling outage due to the failure of the turbine to trip following a manual reactor trip (Reference LER # 389-92-001-00) <br /><br /> The root cause of the reactor trip was a design inadequacy which failed to accurately predict the sharp pressure transient that occured. A contributing factor is that the post modification testing did not detect the pressure transient. This design inadequacy was contributed to, by the lack of experience in the industry with regard to on-line testing of the turbine trip solenoid valves. The cause of the trip was an unforeseen and previously undetected pressure transient imposed on the turbine generator hydraulic control oil system during on-line testing. <br /><br /> Corrective Actions for this event: 1) The on-line testing of the turbine trip solenoid valves (20/ET, 20-1/OPC, 20-2/OPC) has been suspended. 2) Testing of the 'Loss of Load' trip signal was conducted while Unit 2 was shutdown due to the trip. The results of the testing validated the cause of this event as described in this LER. 3) Further evaluation of the solenoid valve test modifications will be performed prior to the next Unit 1 refueling outage. 4) Pre-installation testing will be performed for the Unit 1 solenoid valve test modifications. 5) Unit 1 post modification testing will be performed prior to start up, utilizing the lessons learned from Unit 2. 6) Perform the same solenoid valve test modifications on Unit 2, during the next scheduled refueling outage.
389 | 3891992006 | 1992-08-10 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | St. Lucie 2 | P | CE | PO | 73 | On August 10, 1992, St. Lucie Unit 2 was in Mode 1, operating at 73% power. At 2023 hours, a non-licensed utility operator reported to the control room that there was a fire in the 2C Condensate Pump motor electrical lead box. The fire team was dispatched to extinguish the fire and the reactor was manually tripped at the direction of the Assistant Nuclear Plant Supervisor. Standard Post Trip Actions were performed, all safety functions were met, and the unit was stabilized in Mode 3, Hot Standby. <br /><br /> The fire in the 2C Condensate Pump motor electrical lead box was the result of one of the energized motor leads becoming disconnected from its feeder cable. The cause of the motor lead becoming disconnected was due to the lead having been bent at a sharp angle where it entered the barrel of the lug, a situation that was created due to the short length of the motor leads. The root cause of this event has been attributed to lack of procedural guidance on minimum bend requirements for cable routing and terminations. <br /><br /> Corrective actions taken as a result of this event include: extinguishing the fire and stabilizing the unit in Mode 3, inspecting the motor leads on the 2A and 2B Condensate Pumps to ensure proper installation, revising Electrical maintenance and non-utility contractor procedures to discuss the minimum bend requirements, and the Training Department will review this event for use in maintenance staff training.
389 | 3891993007 | 1993-05-21 | QR3 | Reactivity Control Imbalance | [45 empty] | St. Lucie 2 | P | CE | PO | 72 | On May 21, 1993, St. Lucie Unit 2 was manually tripped from 72% power by utility-licensed operators approximately ten seconds after seven Control Element Assemblies (CEA's) fully inserted into the core. The dropped CEAs were confirmed by the presence of rod bottom lights, CEA reed switch position transmitter indication, and decreasing reactor coolant system average coolant temperature. Standard Post Trip Actions were carried out and the unit was placed in a stable condition in Mode 3. <br /><br /> Initial investigation revealed that several CEA power supply breakers were open and/or fuses blown which was indicative of an electrical fault. Subsequently, two grounded CEA cables associated with CEA's 54 and 61 were discovered in electrical penetration D-1 to the containment shield building. The root cause of the electrical grounds was investigated and could not be confirmed. However, a probable failure scenario is that mechanical damage to the conductor's insulation occurred during the fabrication and/or installation of the conductor bundle. <br /><br /> Corrective Actions for this event: 1) Isolated grounded conductors in electrical penetration D-1 and relanded affected CEA cables to available spare penetration modules in penetration D-1, 2) Replaced the subgroup breaker associated with subgroup sixteen and individual disconnect breakers for CEA's 8, 54, 60, and 61, 3) Performed an Engineering Evaluation on multiple CEA drops and effects on Departure from Nucleate Boiling Ratio and Local Power Density which concluded that no Specified Acceptable Fuel Design Limits (SAFDL) were exceeded, 4) During the 1994 Unit 2 refueling outage, penetration D-1 was inspected, and the grounded modules were replaced. 5) A local leak rate test on penetration D-1 was performed with satisfactory results, and 6) The failed components were examined by the equipment vendor and an independent laboratory for root cause analysis.
389 | 3891993008 | 1993-11-02 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | St. Lucie 2 | P | CE | PO | 45 | On November 2, 1993, St Lucie Unit 2 was in Mode 1, operating at 45% power. At 0443 hours the control room annunciator for the main generator hydrogen system panel actuated. Utility licensed operators checked the hydrogen gas temperatures and saw that the average cold gas temperature was increasing. Before any attempts to reduce the hydrogen gas temperatures could be initiated, the average cold gas temperature reached the limit in the off-normal procedure. At 0447 hours, in accordance with Off-Normal Operating Procedure 2-200030 'Main Generator', a manual reactor and turbine trip were initiated. Standard Post Trip Actions were performed as per EOP-1. Safety function status checks were performed as per EOP-2 Reactor Trip Recovery and the plant was stabilized in Mode 3, Hot Standby. <br /><br /> The root cause for the increase in the main generator hydrogen gas temperatures was due to the operation of the turbine cooling water system with two turbine lube oil coolers lined up to receive turbine cooling water flow and only one turbine cooling water pump available. The turbine cooling water operating procedure permits the isolation of one lube oil cooler that is not in use to maximize flow to those cooling systems in service. Based on plant conditions at 45%, utility licensed operators decided to maintain both turbine lube oil coolers in service. <br /><br /> Corrective Actions for this event: 1) Plant personnel verified that the turbine lube oil cooling system configuration was the cause for the event by reproducing system conditions just prior to the trip. 2) Utility operators isolated a turbine lube oil cooler. 3) The generator vendor verified that the hydrogen gas temperatures experienced during this event would not adversely affect the main generator. 4) I&C verified that the turbine cooling water and component cooling water temperature control valves were operating properly. 5) The plant operating procedure will be enhanced to clarify requirements for operation of the turbine cooling water system.
389 | 3891994003 | 1994-04-23 | QR8 | Spurious Reactor Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 29 | On April 23, 1994 Unit 2 was at 29% reactor power, following a refueling outage. Instrumentation and Control Maintenance (ICM) was performing Linear Power Range Safety and Control Channel Monthly Calibration procedure number 2-1220052 on Reactor Protective System (RPS) channel B, which required the channel to be in bypass. RPS channel D High Power, High Rate of Change of Power (HRCP), Thermal Margin/Low Pressure (TM/LP), Loss of Load and Local Power Density (LPD) bistables were in trip per the Technical Specifications as the Linear Power Range Nuclear Instrumentation card had failed its monthly calibration. Upon commencing channel B calibration the coincidence logic of 2/4 was satisfied and the reactor tripped at 1318. The utility licensed operators carried out Emergency Operating Procedure-01, Standard Post Trip Actions, and Emergency Operating Procedure-02, Reactor Trip Recovery. The plant was stabilized in mode 3, Hot Standby.<br /><br /> The root cause of the reactor trip was an improperly wired bypass circuit on the RPS channel B Local Power Density bistable. With RPS channel D High Power, High Rate, TM/LP, Loss of Load and LPD bistables in trip and channel B bistables in bypass a trip should not have occurred. Testing by Instrumentation and Control Maintenance (ICM) after the trip indicated that the channel B LPD bypass circuit did not function. The reason was due to a wiring error from the original fabrication. The wiring error did not impact the normal RPS safety function, however ft did prevent the LPD trip unit in channel B from being bypassed. <br /><br /> Corrective actions for this event: 1) ICM repaired RPS channel B LPD bypass circuit, 2) ICM tested all Unit 2 RPS channel bypass circuits satisfactorily and Unit 1 RPS channel bypass circuits will be tested during the next Unit 1 refueling outage, 3) ICM completed calibration of RPS channel B and channel D Linear Power Nuclear Instrumentation and 4) The RPS vendor has been notified of the wiring error in the bypass circuit.
389 | 3891995002 | 1995-02-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On February 21, 1995, at 1317 hours, St. Lucie Unit 2 automatically tripped from 100%, power, due to low water level in the 2A Steam Generator. In accordance with Emergency Operating Procedure (EOP)-1, Standard Post Trip Actions were performed. When all safety function status checks were satisfactorily completed, the operating staff exited EOP-1 and entered EOP-2, 'Reactor Trip Recovery'. Normal Steam Generator water levels were regained and the Unit was stabilized in Mode 3. <br /><br /> The event was initiated when level transmitter LT-9011 failed high. The most likely root cause of the level transmitter failure was determined, by the vendor, to be due to coalescing of microscopic conductive particulates in the fill fluid which acts as a short circuit between the center diaphragm of the transmitter and one of the sensor cell capacitor plates. <br /><br /> Corrective Actions for this event include: 1) Verification that no other components failed in the Feedwater Control System. 2) A bench test on LT-9011 to confirm the level transmitter had failed. 3) A new level transmitter for LT-9011 was placed in service. 4) The failed transmitter was sent to the manufacturer for a detailed failure analysis. 5) Engineering is evaluating the failure analysis, to determine the appropriate actions to prevent reoccurrence of this event and its impact on other plant transmitters.
389 | 3891996001 | 1996-01-05 | QR5 | Turbine Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 35 | On January 5, 1996, St. Lucie Unit 2 was operating at 35 percent power after returning to service following a refueling outage. generator hydrogen cooler temperature control valve (TCV) failed to control properly, causing the temperature control valve to fully close. This valve regulates the flow of cooling water from the main generator hydrogen coolers. At 1636 the unit was manually tripped by utility licensed operators due to increasing main generator cold gas temperatures. All safety functions were satisfactorily met following the trip and the plant was stabilized in Mode 3. Several unexpected Steam Generator (SG) low level indications were received following the trip and were subsequently found to be caused by partial sensing line blockage from accumulated corrosion products. <br /><br /> This event was caused by the failure of a hydrogen cooler temperature control valve controller to maintain the TCV in the proper position. Closure of the TCV caused a reduction in cooling water flow from the hydrogen coolers, resulting in increased cold gas temperatures in the main generator. <br /><br /> Corrective actions: 1)The TCV controller setting was adjusted prior to returning Unit 2 to service. 2) Additional controllers in other plant systems were inspected for proper operation. 3) Post maintenance testing of controllers is being reviewed for adequacy. 4) Operations is evaluating generic implications and will require additional oversight for this evolution in the future. 5) Controller setpoints will be reviewed for on into a data base. 6) Unit 2 SG level instrumentation sensing line blockage was cleared, and instrument performance was reviewed on Unit 1. 7) SG level sensing lines and others deemed susceptible will be blown down in the future as part of a preventative program. 8) Plant procedures wi be enhanced to facilitate early detection of instrument response abnormalities.
389 | 3891996002 | 1996-06-06 | QR6 | Manual Reactor Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On June 6, 1996, St. Lucie Unit 2 was operating in Mode 1 at 100 percent power. At 1232,.a temperature control valve (TCV) for the main generator hydrogen cooling system closed causing main generator hydrogen gas temperature to increase above the limiting value for continued operation. Operators initiated a manual reactor and turbine trip in accordance with approved plant procedure. All safety functions were satisfactorily met and the plant was stabilized in Mode 3. Following the trip, a steam driven auxiliary feedwater pump tripped on over speed and a main feedwater pump tripped due to low system flow. Steam generator feedwater continued to be supplied by redundant pumps. <br /><br /> The cause of this event was the failure of a positioner feedback arm on the main generator hydrogen cooler temperature control valve. Failure of this component caused the valve to close and interrupt cooling water flow from the hydrogen cooling system. <br /><br /> Corrective actions: 1) Modifications were made to the hydrogen cooler TCV to eliminate the feedback assembly and reduce vibration. 2) Other temperature control valves were assessed and additional modifications made. 3) A plant modification is being evaluated to improve main feedwater pump performance. 4) A safety relief valve on the main feed system was modified to prevent unnecessary lifting. 5) Pressurizer response during the event was analyzed and a training bulletin was issued to clarify system response expectations. 6) A modification was implemented to eliminate the cause for the over speed of the steam driven auxiliary feedwater pump.
389 | 3891999005 | 1999-06-04 | QR3 | Reactivity Control Imbalance | [45 empty] | St. Lucie 2 | P | CE | PO | 49 | On June 4, 1999, St. Lucie Unit 2 was in Mode 1 at approximately 49 percent reactor power. An event response team was in the process of trouble shooting recent control element assembly anomalies. Unit 2 was held in reduced power pending the event response team trouble shooting results. At 0313 hours, four sub group 21 control element assemblies fully inserted into the core during replacement of the sub group 21 power supply. A Utility licensed operator, the nuclear plant supervisor, immediately directed a manual reactor trip. The plant was stabilized in Mode 3 for repairs. Repairs were implemented, and plant restart and power ascension commenced on June 11, 1999. The control element assembly drop event was caused by procedural inadequacies that did not require verification of the proper seating of a power switch. This resulted in loss of power to the control element assemblies when their sub group was transferred off the hold bus. Loss of power to the sub group 21 control element assemblies was corrected by resealing the sub group 21 power switch. Procedure changes are planned to correct the lack of procedural guidance for CEA sub group power switch replacement. The event response team conducted other corrective actions related to the original control element assembly anomalies.
389 | 3892001001 | 2001-03-14 | QR8 | Spurious Reactor Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On March 14, 2001, St. Lucie Unit 2 was in Mode 1 operation at 100 percent reactor power. At 1752 hours, the reactor automatically tripped when both control element assembly motor generator sets output breakers opened. With the exception of a few minor equipment issues, the trip was uncomplicated. Control room operators performed standard post trip actions. Long term thermal degradation caused the failure of the 2B control element assembly motor generator set voltage regulator, and subsequently lead to the opening of both motor generator sets output breakers. The 2A and 2B motor generator sets voltage regulators were replaced, and the unit was on-line on March 18, 2001.
389 | 3892003001 | 2003-04-01 | QL7 | Degraded condenser vacuum | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On April 1, 2003, St. Lucie Unit 2 was in Mode 1 operation at 100 percent power. At approximately 1500 hours, control room operators noted that the backpressure in the St. Lucie Unit 2 main condenser was slowly increasing. The operators attempted to perform the off-normal operating procedure for loss of condenser vacuum and recover condenser vacuum by placing the hogging ejectors (hoggers) in service. However, the operators performed a manual reactor trip at approximately 1603 hours when condenser backpressure reached the procedurally defined limit. The plant was stabilized in Mode 3 with feedwater supplied by the main feedwater system. The cause for the manual reactor trip was a reduction of main condenser vacuum caused by a combination of increased air in-leakage to the condenser via a corrosion induced through-wall hole in the steam jet air ejector piping and the degraded function of the 2A condenser hogger. The 2A hogger degraded operation was caused by an out-of calibration steam supply pressure gage. The faulty piping was replaced during the Spring 2003 St. Lucie Unit 2 refueling outage. The steam supply pressure gage that lead to degraded 2A hogger operation was replaced, and the hoggers were inspected during the outage with no significant findings noted. FPL is evaluating the planned and preventative maintenance practices for the hoggers.
389 | 3892003003 | 2003-06-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 22 | On June 11, 2003, St. Lucie Unit 2 was in Mode 1 at approximately 22 percent reactor power with steam generator level controlled by the low power feedwater control system. The 15 percent feedwater bypass valve, LCV-9005, failed closed at approximately 0122 hours and the 2A steam generator high/low level alarm occurred as water level decreased. Control room operators attempted to control the 2A steam generator level using the 100 percent feedwater bypass valve along with the main feedwater isolation valve. At 0129 hours level in the 2A steam generator exceeded the high high level setpoint and the resultant automatic turbine trip caused an automatic reactor trip on loss-of-load. The unit was stabilized in Mode 3. All safe shutdown equipment operated as designed, resulting in this event having no adverse impact on the health and safety of the public. LCV-9005 failed closed due to valve stem separation that was caused by vibration induced fatigue. An anticipatory manual reactor trip was not performed because the control room supervisors failed to provide effective command and control. Major corrective actions include the repair of LCV-9005, extent of condition review, immediate training for all licensed operators, removing involved control room supervisors from licensed activities until remedial training completed, and training of the event in Licensed Operator Continuing Training
389 | 3892003004 | 2003-12-04 | QR6 | Manual Reactor Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 60 | On December 4, 2003, St. Lucie Unit 2 was in Mode 1 at 100 percent power. At approximately 1600 hours, the control room operators were informed that the lower motor bearing area of condensate pump 2A was "hot and smoky." At 1605 hours, a rapid down power was initiated to reach 45 percent power in order to remove condensate pump 2A from service. At 1632 hours, the operators manually tripped the reactor from 60 percent power due to the rapidly degrading condition of the 2A condensate pump. The plant was stabilized in Mode 3. All safe shutdown equipment operated as designed. There were no human performance issues related to the downpower or manual trip. The most probable cause of the lower motor bearing failure was determined to be improper lubrication. Plant procedures incorrectly identified that the bearing was factory sealed and required no lubrication. Corrective actions include the planned inspection and repair of the 2A condensate pump and motor, correction of the procedural error, identification of other motors with incorrect bearing classifications, and increased predictive maintenance vibration and thermography analyses for those motors until the bearings are lubricated and/or replaced.
389 | 3892003005 | 2003-12-20 | QR5 | Turbine Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On December 20, 2003, St. Lucie Unit 2 was in Mode 1 at 100 percent power. At 0948 hours St. Lucie Unit 2 automatically tripped from full power on loss of generator field current. Except for the overspeed trip of the 2C turbine-driven auxiliary feedwater pump, the plant trip response was uncomplicated as all safe shutdown equipment operated as designed. There were no human performance issues associated with the trip. Vendor assisted trouble shooting efforts identified that the failure of the main generator voltage regulator current regulator instant limiter module was the most likely root cause the December 20, 2003 trip. St. Lucie Unit 2 was returned to full service on December 28, 2003. The faulty module was replaced, and a temporary multi-channel recorder was installed to monitor key areas of the main generator automatic voltage regulator circuitry. This monitoring equipment will remain installed until the fall 2004 refueling outage.
389 | 3892004004 | 2004-12-25 | QP4 | Partial Loss of Condensate Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On December 25, 2004, St. Lucie Unit 2 was operating in Mode 1 at 100 percent reactor power. At 0651 hours, the control room operators performed a manual trip of the reactor after high temperatures were observed locally at the 2B condensate pump motor terminal box subsequent to the annunciation and indication of high motor current in the control room. Auxiliary feedwater initiated as expected from a full power reactor trip. The trip was uncomplicated as all safety-related equipment responded as required to the plant trip. The 2B condensate pump motor over current condition was caused by the failure of the "A" phase motor lead that was the result of incorrect original construction motor lug installation. Corrective actions included swapping the 2A condensate pump motor with the 2B pump,changes to the 4.16 and 6.9 kV motor overhaul program to check lug installation, and inspection of 4.16 and 6.9 kV motor lug installations.
389 | 3892004005 | 2004-12-27 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | St. Lucie 2 | P | CE | PO | 10 | On December 27, 2004, Unit 2 was in Mode 1 at 10 percent reactor power preparing to latch the turbine. At 1751 hours, the turbine was latched and the "A" steam generator inventory took a step increase. Approximately 140 seconds following the turbine latch, the 2A main feedwater (MFW) pump automatically tripped on high level in the "A" steam generator. With no MFW pump in service, the "B" steam generator narrow range water level decreased to the low level 40 percent reactor protection system pre-trip on 2 of 4 channels and the operators manually tripped the reactor at 1721 hours. The operators performed standard post-trip actions and stabilized the plant in Mode 3. The event was caused by a combination of human error and the malfunction of a main feedwater regulating valve controller that allowed the steam generator overfeed condition that ultimately resulted in manual reactor trip due to low steam generator water level. Corrective actions included controller replacement, procedure revisions, and training on the event. The unit was returned to service on January 2, 2005.
389 | 3892005003 | 2005-08-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On August 11, 2005, St. Lucie Unit 2 was in Mode 1 operation at 100 percent reactor power. Personnel errors by a non-licensed maintenance supervisor caused a de-energization of two electrical buses which resulted in a partial loss of feedwater event and manual reactor trip based on lowering steam generator levels. The event occurred when the maintenance supervisor opened the incorrect breaker cubicle during an equipment clearance order walkdown, and caused the spurious operation of a lockout relay when the breaker cubicle door was closed. In addition to the manual reactor trip, there were automatic actuations of the A train emergency diesel generator and auxiliary feedwater system. Safety related equipment responded to the event as required. Corrective actions included maintenance stand-downs and training. There were no adverse safety consequences as a result of this event.
389 | 3892006001 | 2006-01-20 | QL6 | Condenser Leakage | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On January 20, 2006, with St. Lucie Unit 2 in Mode 1 at 100 percent power, a Main Condenser high conductivity/sodium annunciator was received in the control room. Chemistry confirmed that the high sodium level was due to seawater intrusion fron the 2B2 Main Condenser waterbox. In accordance with the "Secondary Chemistry - Off Normal Procedure," 2-0610030, a rapid down power was initiated. The Shift Manager, based on Chemistry input and procedure direction, continued the down power and removed the unit from service rather than remain critical at a low power level. All systems worked as designed and the reactor was manually tripped at approximately 25 percent power in accordance with plant operating procedures without incident. All control rods fully inserted and the Steam Generator (SG) Safety Relief Valves did not actuate. Feedwater to the SG was supplied by the Main Feedwater (MFW) pumps during the shutdown and later transferred to the Auxiliary Feedwater (AFW) pumps. All safe shutdown equipment operated as designed with no equipment failures or impact to the health and safety of the public.
389 | 3892006004 | 2006-06-15 | QR5 | Turbine Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 45 | On June 15, 2006, St. Lucie Unit 2, while returning to power from the SL2-16 outage, initiated an unplanned manual reactor/turbine trip due to a severe DEH leak on the number 1 throttle valve actuator [EIIS:FCV]. Operation procedures 2-E0P-01 "Standard Post Trip Actions," and 2-EOP-2, "Reactor Trip Recovery," were completed without contingencies and Unit 2 was stabilized in Mode 3. The DEH leak ceased upon turbine trip and all control rods fully inserted. No main steam safety valves [EIIS:SJ] lifted, Feedwater to the steam generator was supplied by the main feedwater pumps [EIIS:SJ] and all safe shutdown equipment operated as designed. The leak was a result of improper torquing by a contractor of the cap screws used to attach a blind flange to the actuator, which ultimately led to the failure of the interfacing o-ring under the high DEH pressure. The Root Cause determined the failed o-ring was the result of poor contractor workmanship and inadequate procedure guidance for torque verification following o-ring installation during rebuilding of the actuator at the vendor's facility.
389 | 3892008002 | 2008-06-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On June 4, 2008, St. Lucie Unit 2 was in Mode 1 at 100% power while Plant instrument and control (I&C) personnel were performing maintenance on the 5B Feedwater (FW) Heater High Level Limit Switch LS-11-26B, when two taped energized leads were being routed through a conduit elbow came in contact with the conduit and grounded. The ground resulted in the 28 Heater Drain Pump being tripped on low level and the 2A Main Feedwater Pump tripping on low suction pressure 50 seconds after the heater drain pump tripped. The reactor was manually tripped in anticipation of a low steam generator level auto-trip. All safe shutdown equipment operated as designed with no impact on the health and safety of the public. The root cause of the event was determined to be a failure to implement adequate process controls to minimize risk during level switch replacement, and the drifting of the pressure switch (PS-12-14A) set point resulting in a premature actuation of the switch during a feed water transient. This ultimately resulted in a manual reactor trip. Corrective actions included, development of specific procedural direction for controlling energized leads during work evolutions using the risk management process, design modifications to address vulnerability when performing maintenance on level switches, and evaluation of industry best practices for training and handling of energized leads.
389 | 3892008003 | 2008-06-07 | QP4 | Partial Loss of Condensate Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On June 7, 2008, St. Lucie Unit 2 was operating normally in Mode 1 at 100% power when operators observed that the 2B condensate pump and 2B steam generator feedwater pump had tripped and steam generator water levels were rapidly decreasing. Operators took action to manually trip the Unit in accordance with plant procedures. An investigation determined the 2B condensate pump "B" phase motor leads had overheated and failed due to high resistance at the lug crimp connections. All safe shutdown equipment operated as designed and there was no adverse impact on the health and safety of the public. The root cause of the event was determined to be undetected epoxy resin in the motor lead cables resulting from not having specific hold points to detect epoxy resin in the motor rewind specification during the a vendor vacuum pressure impregnation process. Contributing causes included not understanding the adverse effects epoxy contamination could have on connections and the lack of controls for contamination in the controlling specifications. Corrective actions included revising motor rewind specification (SPEC-E-008) to ensure epoxy is not applied to the motor leads during the Vendor's vacuum pressure impregnation process.
389 | 3892009002 | 2009-04-01 | QL7 | Degraded condenser vacuum | [45 empty] | St. Lucie 2 | P | CE | PO | 92 | On April 1, 2009, St. Lucie Unit 2 was operating in Mode 1 at 94% power when Unit 2 experienced a continuing reduction of condenser vacuum and an increase in the debris filter system (DES) differential pressure resulting from the ingress of algae from the Atlantic Ocean into the intake canal. Previous attempts to control the debris were unsuccessful and Unit 2 was manually tripped at 92% power at 18:05 in accordance with Off-Normal Operating Procedure 2-0620030, "Circulating Water System". All systems functioned normally, and the plant was stabilized at normal operating temperature and pressure. A non-emergency notification was made to the NRC at 20:51, April 1, 2009. There was no impact on Unit 1. The loss of vacuum was caused by a greater than expected influx of a unique strain of algae which challenged the debris filter screening system and current design of the weir pit which allows recirculation of debris back into the intake canal. Corrective actions taken include a daily Staff Biologists' analysis of biota entering the intake canal with reports provided to the Shift Manager, actions to review weir design, preventive maintenance and cleaning of the weir pit, and development of a new procedure for Intake Intrusion Mitigation.
389 | 3892010002 | 2010-04-15 | QR6 | Manual Reactor Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On April 15, 2010, St. Lucie Unit 2 was operating in Mode 1 at 100% power when the Unit was manually tripped due to premature lifting of the 2B moisture separator re-heater (MSR) safety valve. The Unit initially commenced a rapid down power evolution as a result of the lifting safety valve followed by a manual reactor trip at approximately 95% power. All control element assemblies (CEA) fully inserted on the trip and all systems functioned as designed; the plant was stabilized at normal operating temperature and pressure in Mode 3. A non- emergency notification to the NRC was made due to manual reactor protection system (RPS) actuation and auxiliary feedwater (AFW) system actuation. The primary root cause of the event was determined to be less than adequate material (LTA) design for the MSR safety valve pilot spring. Corrective actions included replacement of pilot valve springs for each of the four Unit 1 and 2 MSR safety valves (MSRV) with either new (CR) alloy steel or Inconel springs prior to startup of Unit 2 and ensure that replacement of MSRVs for Unit 1 are procured with appropriate spring materials and drawings to reflect the same.
389 | 3892011002 | 2011-06-06 | QR8 | Spurious Reactor Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On June 6, 2011 St . Lucie Unit 2 was in Mode 1, when an unplanned automatic reactor trip occurred. The trip occurred while Operators were performing a reactor protection system (RPS) test in which the Operator inadvertently moved the matrix relay trip select switch one position too far, causing the reactor trip circuit breakers (TCBs) to open. Upon reactor trip all CEAs fully inserted into the core, auxiliary feedwater actuation system (AFAS) initiated as designed on low steam generator water level and was restored using auxiliary feedwater. All safety related systems functioned as designed. A root cause evaluation (RCE) determined the trip was a result of latent single human error vulnerability in the test methodology. Contributing causes included human error during performance of the test and inadequate "problem resolution" which required the matrix relay hold pushbutton to be depressed during performance of the entire test. This event is reportable under 10 CFR 50.73 (a) (2) (iv) (A) , as any event or condition that resulted in a manual or automatic reactor trip and actuation of the auxiliary feedwater system. Corrective actions include procedure revisions to test methodology to remove the human error vulnerability and replacement of the RPS matrix relay hold pushbuttons with rotary switches.
389 | 3892012001 | 2012-05-11 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 99 | On May 11, 2012 at 0355 EDT St. Lucie Unit 2 was at 99% power when an unplanned reactor scram occurred. Operators manually scrammed the reactor and turbine due to lowering of the 2A steam generator (SG) level caused by erratic behavior of the 2A SG main feedwater regulating valve (MFRV) FCV-9011. Unit 1 was operating at reduced power (29%) due to power ascension from the Extended Power Up-rate (EPU) refueling outage. The Unit 2 reactor trip was uncomplicated and all control rod assemblies (CEAs) fully inserted. In accordance with plant design, all three auxiliary feedwater (AFW) pumps started in response to an auxiliary feedwater actuation signal (AFAS) due to low SG level. No other automatic safety system actuations were required and none occurred. Reactor coolant system (RCS) heat removal was maintained with AFW and atmospheric dump valves (ADV). The Offsite power grid was available and stable. The root cause for failure of the 2A SG MFRV was determined to be untimely corrective actions and sub-quality parts for the travel sensor (Xact) on the position feedback mechanism provided by the Vendor. Corrective actions included procedure revisions and replacement of travel feedback sensors.
389 | 3892013001 | 2013-05-31 | QL7 | Degraded condenser vacuum | [45 empty] | St. Lucie 2 | P | CE | PO | 40 | On May 31, 2013 at 0712 EDT, St. Lucie Unit 2 was in Mode 1 at 40% reactor power when it was manually scrammed. Unit 2 was scrammed prior to securing the 2A1 Circulating Water Pump (CWP) due to high differential pressure on the debris filter system (DFS) as a result of an algae intrusion. At the time of the trip, the 2A2 Circulating Water Pump had been removed from service for maintenance.<br /><br /> The reactor trip event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of reactor protection system (RPS). This event had no significant safety consequence. Given the response of the plant and the actions taken, the health and safety of the public was not affected by this event.<br /><br /> The high differential pressure on the 2A1 DFS was the result of the incorrect installation of a debris backwash valve and internal binding of a flush-water check valve. The bound check valve caused a false low DFS transmitter differential pressure that prevented the DFS strainer from initiating a backwash and masked the problem with the debris backwash valve. To correct the problem, the debris backwash valve was properly reinstalled, and the flushwater check valves associated with the DFS differential pressure transmitter were replaced with a more robust design.
389 | 3892013004 | 2013-11-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On November 14, 2013 Unit 2 was in Mode 1 at 100 percent power when the 2B Steam Generator Train A main feedwater isolation valve (MFIV) HCV-09-2A spuriously stroked closed. This resulted in a manual reactor trip of Unit 2 due to rapidly lowering steam generator water level. The reactor trip was normal and uncomplicated. All safety related systems functioned as designed. There were no automatic safety system actuations as a result of the trip. <br /><br /> The MFIV closure was a result of corrosion of two relays (3Y/671 or 20X/671) located inside the relay box caused by internal water intrusion in the conduits. Immediate corrective actions included replacing the degraded relays and installing internal conduit seals. An immediate extent of condition inspection and replacement resulted in installation of conduit seals and replacement of three degraded relays. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a manual actuation of reactor protection system (RPS). All plant systems responded as designed and there was no safety significance associated with this event.
389 | 3892014002 | 2014-11-12 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On November 12, 2014 Unit 2 was in Mode 1 at 100 percent power when the 2B steam generator main feedwater isolation valve (MFIV) HCV-09-2B spuriously stroked closed. This resulted in a manual reactor trip of Unit 2 due to rapidly lowering steam generator water level. The reactor trip was normal and uncomplicated. All safety related systems functioned as designed. There were no unexpected automatic safety system actuations as a result of the trip.<br /><br /> A root cause evaluation (RCE) determined the spurious closure of the MFIV was a result of an insufficient preventive maintenance (PM) strategy to detect and mitigate environmental conditions that would affect the MFIV HCV-09-2B relay box. Corrective actions included replacement of the relays in the MFIV relay boxes and moving or eliminating the relay components by modification. This condition is reportable in accordance with the following requirements: 1) 10 CFR 50.73(a)(2)(i)(A)and 2) 10 CFR 50.73(a)(2)(iv)(A). This supplement revises the cause, corrective actions and operating experience (OE) for this event. This event was determined to have minimal safety significance and no impact on the health and safety of the public.
389 | 3892017004 | 2017-10-26 | QR5 | Turbine Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On October 26, 2017, at 0212 hours with St. Lucie Unit 2 in Mode 1 at 100% power, the reactor automatically tripped due to a loss of load following a failure within the turbine control system. The reactor trip was uncomplicated and all control rod assemblies fully inserted. Following the trip, one of the low power feedwater valves LCV-9005, did not properly maintain steam generator level which resulted in an actuation of the A-train auxiliary feedwater system. During the auxiliary feedwater actuation, one main feedwater isolation valve did not reposition closed as expected, but this did not impact heat removal. The main feedwater system remained available. <br /><br /> The failure within the turbine control system was caused by design deficiencies. Planned corrective actions include modifications to improve protective circuits, the addition of coolers and use of conformal coatings on printed circuit boards in the modules.<br /><br /> The problem with LCV-9005 was due to a latent design error that resulted in the setting of an incorrect stroke length for the control valve. This was corrected by adjusting the stroke length of the valve. <br /><br /> This report is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) for system actuations of the reactor protection system and the auxiliary feedwater system. <br /><br /> During this event offsite power remained operable and energized. All other equipment responded to the event as expected per the existing plant conditions; therefore, this event had no impact on the health and safety of the public.
389 | 3892018002 | 2018-10-12 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On October 12, 2018 at 1353 EDT with St. Lucie Unit 2 in Mode 1 at 100% Reactor power, an unplanned automatic Reactor trip occurred due to a failure of a supply breaker to the non-safety related 2A1 6.9kv bus during a transfer of the bus power supply from the 2A Auxiliary Transformer to the 2A Startup Transformer. The breaker failure caused a fire in the cubicle that was extinguished by onsite personnel. <br /><br /> The initial breaker problem developed after it was placed in service. However, there was no viable option to unload the breaker before opening. A team was formed to determine the options for resolving the condition. The option chosen was to use normal procedures with contingencies in place. The failure occurred as the damaged breaker was removed from service. The fault inside the breaker was the result of a ruptured SF6 gas vessel due to an inadequate design. <br /><br /> The failed breaker has been removed from service, and similar breakers susceptible to interrupter vessel failures are being evaluated for replacement. Additionally, action plans are being developed that will allow similar beakers to be unloaded in the event of future interrupter vessel failures. <br /><br /> Following the uncomplicated trip, the plant was maintained in Mode 3. Therefore, this event had no safety significance.
389 | 3892021001 | 2021-01-20 | QR5 | Turbine Trip | [45 empty] | St. Lucie 2 | P | CE | PO | 100 | On January 20, 2021 at 1822 EST with Unit 2 in Mode 1 at 100% power, the reactor automatically tripped on Reactor Protection System Loss of Load Actuation concurrent with an unexpected deenergization of the 480V Motor Control Center 2B2. The trip was uncomplicated with all systems responding normally post trip. Operations stabilized the plant in Mode 3. Auxiliary feedwater automatically actuated on the 2A steam generator post trip. Decay heat removal transitioned from auxiliary feedwater to main feedwater through the 2B main feedwater pump to both steam generators and the steam bypass control system to the main condenser. <br /><br /> A breaker failure caused two of the four undervoltage relays in the Diverse Turbine Trip system to deenergize to their failed condition creating an unexpected trip path for actuation. The cause of this event was a legacy drawing issue from 1983 that resulted in inadvertently mis-assigning power to two of the four undervoltage (UV) relays to the incorrect train of power when the system was later modified in 2019. <br /><br /> The failed breaker has been removed from service, and field configuration of Diverse Turbine Trip relay power supplies was immediately corrected such that the loss of a single power supply will not result in turbine trip. <br /><br /> Automatic reactor trips are analyzed events in the Updated Final Safety Analysis Report. The trip was uncomplicated. Therefore, this event had no impact on the health and safety of the public.
390 | 3901996004 | 1996-02-19 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Watts Bar 1 | P | WE | PO | 15 | On February 19, 1996, at approximately 1502 EST, the operators in the Main Control Room (MCR) manually tripped the main turbine due to a loss of normal feedwater and a corresponding decrease in steam generator (SG) level. The motor driven auxiliary feedwater (MDAFW) pumps were started to recover SG levels. At approximately 1504 EST, the reactor was manually tripped when SG levels could not be recovered. During this event, the turbine driven auxiliary feedwater (TDAFW) pump started and aligned to essential raw cooling water. With prompt operator action, the SG levels were recovered and the plant stabilized in Mode 3. <br /><br /> The cause of this event was the failure of the hotwell level control system to maintain an adequate water supply for the hotwell pump's net positive suction head due to a design deficiency. The deficient design involved the sense line attachment location to the condenser which provided a false indication and signals to control systems of high hotwell level as the main turbine is loaded. The automatic start of the TDAFW pump was as designed. raw cooling water was determined to be pressure switch actuations due to the MDAFW pump pulsations experienced at low flow conditions. <br /><br /> Corrective actions include design and modifications to the hotwell level indication, operating procedure enhancements for maintaining hotwell level during reactor startup conditions, and modifications to the TDAFW pressure switch control logic.
390 | 3901996009 | 1996-03-13 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Watts Bar 1 | P | WE | PO | 49 | On March 13, 1996, with Unit 1 in Mode 1 at approximately 49 percent reactor power and generator load at 480 MWe, TVA operators initiated a manual turbine trip followed by a manual reactor trip. The manual turbine trip resulted from the failure of the main condenser to maintain adequate vacuum to sustain turbine operation. The cause of loss of vacuum is attributed to the isolation of condensate flow to the main feedwater pump turbine (MFPT) condenser 1B. <br /><br /> Prior to the event on February 29, 1996, condensate bypass supply and discharge valves had been closed during maintenance activities on the MFPT 1B. When power was increased on March 13, 1996, the inlet isolation valves automatically closed which completely isolated condensate flow to MFPT 1B. With condensate isolated, the gland seal steam was no longer being condensed and was pulled into the suction of the vacuum pumps. The vacuum pumps were then unable to remove non-condensables which resulted in loss of vacuum to the main condenser. <br /><br /> The manual reactor trip resulted from loss of feedwater to the steam generators when the number 2 heaters isolated and severed the suction source to the standby feedwater pump. All equipment functioned as designed except the MFPT 1B condenser outlet valve which did not close when feed flow exceeded 40 percent. All control rods fully inserted and the plant was stabilized in Mode 3. <br /><br /> Corrective actions include operating procedure revisions, verification of proper operation of automatic MFPT condenser flow switch and setpoint isolation logic, and a design modification to provide a direct flow path from the MFPT condensers to the main condenser.
390 | 3901996014 | 1996-04-16 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 83 | On April 16, 1996, at 1034 hours EDT, Unit 1 was operating in Mode 1 at 83 percent rated thermal power (RTP) when the governor valves (GV) to the high pressure turbine automatically closed resulting in loss of turbine load from 1000 MWe. In response, the licensed unit operator manually tripped the turbine which automatically tripped the reactor since RTP was greater than 50 percent. All control rods inserted normally and the unit was stabilized in Mode 3. In accordance with the plant design, the automatic reactor trip was followed by a main feedwater isolation resulting in a start of all auxiliary feedwater pumps. <br /><br /> The subsequent investigation determined that the cause was due to the interface of the automatic self-check circuit of the Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuit (AMSAC) system with that of the overspeed protection controller (OPC) of the main turbine. Corrective actions included the disabling of the AMSAC self-test circuitry.
390 | 3901996016 | 1996-04-28 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Watts Bar 1 | P | WE | PO | 72 | On April 28, 1996, at 1109 EST, WBN Unit 1 in Mode 1 experienced an automatic turbine trip from 72 percent power due to the trip of the Main Feedwater Pump (MFP) 1A, while MFP 1B was removed from service for maintenance. Trip logic was satisfied when MFP 1A tripped due to high condenser backpressure coincident with MFP 1B shutdown for Maintenance to repair a leaking valve. The primary side'responded as expected. The Reactor Coolant System (RCS) performed as required, and the control rods all dropped and were confirmed to be fully inserted. The Auxiliary Feedwater pumps started as designed and flow was controlled to limit the cooldown. <br /><br /> The cause of the event was inadequate written instructions. System Operating Instruction (SOI)-2 & 3.01, 'Condensate and Feedwater System,' caused valves to be positioned such that MFP 1A tripped. When MFP 1B was removed from service, the turbine above seat drain valves were opened in accordance with the procedure to prevent condensate buildup above the steam supply valves. With the valves open, additional steam and condensate dumped directly to the condenser resulted in pressure buildup in MFP 1B condenser with only bypass cooling available. A contributing cause was the design of the vacuum line connection between Main Feedwater Pump Turbines (MFPTs). Difficulty in maintaining vacuum in an isolated condenser had been previously recognized and a modification to tie the pump turbine condensers to the main condenser had been issued and staged for implementation. <br /><br /> Corrective actions included (1) revising SOI-2 & 3.01 to remove the step that opens the above seat drain valves for the stop valves when shutting down a MFPT, (2) providing a vacuum line which directly connects the MFPT condenser to main condenser, and (3) revising the condenser low vacuum alarm setpoint to provide early warning prior to trip setpoint. Power ascension was resumed after the MFPs were placed in service following the completion of the vacuum line modification.
390 | 3901997002 | 1997-01-22 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Watts Bar 1 | P | WE | PO | 100 | POWER LEVEL - 100%. On January 22, 1997, at 1350 EST, while the plant was operating in Mode 1 at 100 percent reactor thermal power in steady state producing 1208 MWe, both turbine driven main feedwater pumps (TDMFPs) tripped on low turbine condenser vacuum. With both TDMFPs inoperable, the main turbine and reactor tripped at 1351. The Auxiliary Feedwater System automatically responded as designed to control steam generator levels and the plant was then stabilized in Mode 3. The TDMFP trip conditions on low turbine condenser vacuum were met after one of two TDMFP condenser drain tank pumps had been turned off at the local junction box with both TDMFPs running causing increasing fluid level in combination with a pre-existing failure of the TDMFP condenser drain tank level switch. The B pump handswitch had apparently been inadvertently bumped by a painter to the 'off' position while working on the local junction box. Corrective actions consist of replacement of the failed level switch float assembly, review and replacement of similar float switch assemblies as necessary, installing protective covers over the turbine condenser drain tank pump local handswitches to prevent accidental operation, and conducting stand down meetings with applicable workers on configuration control expectations.
390 | 3901997006 | 1997-03-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | POWER LEVEL - 100%. On March 6, 1997, at approximately 0517 EST, while Unit 1 was operating at 100 percent RTP, the reactor automatically tripped due to low-low water level in steam generator No. 4. Three conditions led to the low-low level; (1) the main feed pump B (MFP B) shaft fractured and broke in half at approximately 0513, (2) the standby main feed pump was temporarily out-of-service for recirculation line repairs, and (3) flow was partially restricted to steam generator No. 4 at the inlet nozzle. When the shaft broke, the resulting damage caused the pump turbine to trip resulting in an automatic balance of plant runback to 85 percent. Operators further reduced the load to approximately 54 percent, as directed by procedure, to arrest decreasing steam generator water level, since the SBMFP was unavailable. However, steam generator No. 4 was experiencing high inlet pressure due to foreign material obstruction at the feedwater inlet. It decreased to the low-low level trip setpoint at 0517 causing an automatic reactor/turbine trip and subsequent Auxiliary Feedwater System (AFW) actuation at 0518. Operators responding to the trip monitored and observed steam generator No. 4 level off with feed flow approaching steam flow and believed the transient was beginning to reverse, therefore did not initiate a manual reactor trip prior to the automatic trip. AFW responded as designed to control steam generator water levels. The plant was then stabilized in Mode 3. Corrective actions consist of inspecting and repairing hardware, restoring equipment to service, evaluating component failures and material applications, and improving personnel awareness.
390 | 3901997010 | 1997-04-20 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | At 0125 EDT on April 20, 1997, the WBN Unit 1 main generator pneumatic circuit breaker (PCB) opened initiating a turbine trip and a subsequent automatic reactor trip. Investigations found that the turbine trip was initiated by operation of the generator backup relay, relay 121GB. Operation of this relay results in the opening of the main generator PCB and closure of the steam supply to the turbine. Meggar testing was performed to establish a possible cause for the operation of the protective relay. For the A phase main transformer high side potential device (PD) circuit, a low meggar reading was found. Additional troubleshooting found evidence that the phase A capacitance tap connector from the 500KV bushing to the PD had experienced arcing. Moisture was also found in the bushing well and the lubricant around the bushing well was blackened indicating a fault on the A phase capacitance tap connector. Once this problem was found, the capacitance tap bushing area was cleaned and new lubricant was applied. In addition, the exposed surfaces of the connector were sealed with an RTV sealant. Resistance tests were subsequently performed with the readings found to be normal. Due to the problems found on the A phase, the B and C phase capacitance tap connectors were inspected even though the PD circuits meggar tested satisfactorily. No problems were found on the B phase. C phase was found to have lost a portion of its lubricant, and the remaining lubricant was blackened but no significant burn odor was noted. The same type of repairs performed on the A phase were made to both the B and the C phases.
390 | 3901997015 | 1997-10-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 1 | P | WE | SU | 12 | On October 19, 1997 at 0950 EDT during Unit 1 startup, the reactor was in Mode 1, approximately 12% power. The turbine was at 1800 RPM and preparing for connection to the grid. Steam generator levels began decreasing due to isolation of the inservice feedwater heaters. Auxiliary feedwater was manually initiated and reactor power was manually decreased to 4% using control rods. The reactor was manually tripped due to decreasing steam generator levels, The feedwater heaters isolated on high-high level. The main control room alarms for high feedwater heater levels did not alarm. All other systems responded to the initiating event as expected and within analyzed parameters. There were no abnormal radiological conditions throughout the event. The cause of the event was isolation of the high pressure feedwater heater strings due to high level with a contributing cause of failure of the high level alarms in the heaters to provide annunciation in the control room. The high level in the A1 and B1 heaters was due to a failure to recognize that additional operator attention was required to control the level in the A1 and B1 heaters with the C1 heater isolated, during turbine roll and main generator synchronizing. The procedure was revised to caution operators on the impact of feedwater heaters out of service during this period. The high-high alarm level switches on the feedwater heaters were repaired and verified to be operable.
390 | 3901998001 | 1998-03-07 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On March 7, 1998 at 0026 EDT, the reactor was in Mode 1, approximately 100% power of 3411 Mw thermal and 1209 Mw electrical. The unit had been on line for 137 days. The reactor automatically tripped after receiving a turbine trip signal. The turbine tripped due to a low bearing oil pressure signal received during the performance of technical requirements procedure 1-TRI-47-1, "Main Turbine Oil Trip Devices TGOP, SOBP, and EOP Monthly Test." The cause of the event was an upward set point drift (81 psig as found vs 45 psig required) of pressure switch 1-PS-47-72, (pressure switch provides a redundant signal to dump EHC fluid and trip turbine on low auto-stop oil pressure), and a pressure regulator 1-RFV-47-945 failing to maintain oil pressure during the test performance. This loss of pressure condition occurred when in the "Test" position and opening one of the trip device valves. It resulted from failure of one of the two regulator valves in the main supply header for auto-stop oil. The combination of the drop in pressure with the upward setpoint drift resulted in the turbine trip and subsequent reactor trip. Both the pressure switch and the relief valve were replaced. The other pressure switches were calibrated and setpoints adjusted as needed. When the turbine reached 1800 RPM prior to generator synchronization, technical requirement procedure 1-TRI-47-1 was successfully performed.
390 | 3902001001 | 2001-06-29 | QL7 | Degraded condenser vacuum | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On June 29, 2001, at 1728, Watts Bar Unit 1 was in Mode 1 at 100% power. At this time the unit was manually tripped when the main condenser back-pressure reached procedure limits. The rise in the back-pressure was caused by reduced condenser circulating water (CCW) flow which resulted from cooling tower fill material obstructing the intake flume screens to the CCW pumps. All safety systems responded as required during the event. Auxiliary Feedwater initiated due to reactor trip with low Tavg, as required. All control rods inserted properly. The root cause of this event was inadequate design output. The design allowed support schemes other than those in the issued design document to be used as needed for cooling tower fill repairs and/or replacement. The supports installed most likely failed in this event due to a combination of various loads. Corrective actions included inspection and removal of the loose cooling tower fill material, clarification of design output, and enhanced program controls for intake flume screen cleaning.
390 | 3902001002 | 2001-09-04 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | While operating at 100% power, the Watts Bar Unit 1 reactor was manually tripped at approximately 1305 EDT on September 4, 2001, due to the level of steam generator (SG) number 1 approaching the Lo-Lo level setpoint. The immediate cause of the trip is considered to be the loss of the 1-I Vital AC Inverter which caused the SG number 1 feedwater regulating valve to close. All control rods inserted properly in response to the reactor trip. The Auxiliary Feedwater (AFW) System actuated in response to the trip, as expected. However, subsequent to the initial actuation signal, additional operator action was required to start the 1A-A and 1B-B motor driven AFW pumps. The root cause for this event was determined to be the failure of the 5 watt resistor R12 on the sensing and current limiting card installed in Vital Battery Charger 6-S. Corrective actions include the replacement of the blown inverter fuses, the replacement of the failed card with subsequent load testing performed, some operating instruction revisions to provide verification of AC input breaker closure and DC output before closing DC output breakers, and a revision to the procurement data sheet for sensing and current limit board requiring additional factory burn in of new boards.
390 | 3902001004 | 2001-12-19 | QR8 | Spurious Reactor Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On December 19, 2001, an invalid AMSAC signal was initiated that resulted in a turbine/reactor trip. The unit was operating at 100% power at the time of the event and work was in process for the placement of a clearance (tagout) to support the implementation of a design change to the control instrumentation for the Turbine Driven Auxiliary Feedwater (TDAFW) pump. The clearance activities opened the breakers which supply power to the instrumentation. The loss of power to the instruments resulted in an invalid steam generator (SG) lo lo level (12%) signal and satisfied the logic (3 out of 4 SGs less than 12% level) for the initiation of an AMSAC signal. All control rods inserted properly and the Auxiliary Feedwater (AFW) system started, as required, in response to the AMSAC signal and the reactor trip. The cause of the event was inadequate interface requirements in the planning and scheduling of trip sensitive activities along with inadequate implementation of the clearance preparation process. The corrective actions included the review of open on-line clearances, development of a standard for the tagging of low voltage equipment, establishment of a formal process which reviews plant work activities for trip sensitive actions, counseling of involved personnel, training on the lessons learned from the event, identification and labeling of trip sensitive breakers, development of an instruction to define the expectations for independent review and to provide controls for the operation and tagging of low voltage breakers.
390 | 3902002003 | 2002-07-13 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On July 13, 2002, at approximately 1622 EDT, while the plant was in Mode 1, at 100% power, Watts Bar Unit 1 experienced an automatic turbine/reactor trip when a C-Phase Main Transformer differential relay actuated This occurred because a bolted cable splice associated with a C-phase current transformer (CT) came into contact with the CT junction box; thereby shorting the differential relay protection circuit to ground. The apparent factors contributing to this short circuit condition include temperature, cable splice material, vibration, and configuration of the splice inside the junction box. All control rods inserted properly in response to the reactor trip. The Auxiliary Feedwater (AFW) System actuated in response to the trip, as designed. Plant response was in accordance with design with no complications. Operations shift personnel performance was in accordance with applicable procedures. Subject to confirmatory laboratory testing, the root cause of this event was determined to be inadequate work instructions that allowed lower temperature rated tape to be used on a cable replacement and/or inadequate application of splice material. Corrective actions include revision and training on TVA's engineering and maintenance procedures for high temperature jacketing material, laboratory analysis of damaged splices, and reinspection and taping of similar vulnerable cable splices.
390 | 3902003001 | 2003-03-10 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On March 10, 2003, at 0012 Eastern Standard Time, with Watts Bar 1 at 100 percent power, a Generator Backup Relay unexpectedly actuated causing an automatic turbine/reactor trip. The relay actuated due to a ground fault caused by a broken o-ring in the C phase main transformer's high side bushing capacitance tap connector. Plant safety equipment performed as designed which included the auto-start of the auxiliary feedwater system. The root cause of this event was inadequate preventive maintenance procedure. Corrective actions include repairing the connector, revising preventative maintenance (PM) procedures, and a design change to the affected single point vulnerability relay scheme.
390 | 3902003003 | 2003-08-25 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On August 25, 2003, Watts Bar (WBN) Unit 1 was operating at 100 percent power when there was an operation of the 2 out of 3 logic for the Sudden Pressure Relays (SPRs) for Main Transformer Bank 1C. The actuation of the relays resulted in a turbine trip and a subsequent reactor trip at approximately 0945 EDT. All control rods inserted as required and the safety systems actuated as designed including the motor and turbine driven pumps for the Auxiliary Feedwater (AFW) System. AFW pump 1B-B was available but not operable at the time of the trip due to work on an associated penetration room cooler. The pump started as required. There was no loss of safety function. Unit 1 was stabilized in Mode 3. The immediate cause of the trip was the actuation of the SPRs which were initiated by a worker bumping into the junction box that houses the relays in the switchyard. Subsequent to this, it was identified that the design of the SPR configuration was sensitive to actuation when force was applied to the relay housing junction box. Corrective actions include a modification to improve the vibration isolation of the SPRs and the installation of a permanent protective barrier fence with access gate around each of the four SPRs, pipe, hydraulic hose, junction box, and support installations to prevent accidental impact during normal plant operations. Trip hazard signs have been placed on the fence barrier.
390 | 3902004001 | 2004-01-18 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On January 16, 2004, with Watts Bar Nuclear Plant Unit 1 at 100 percent power, an automatic turbine trip occurred in response to an invalid trip signal (P-4), which then caused an automatic reactor trip because reactor power was above 50 percent power (P-9). The auxiliary feedwater system started as designed. Surveillance Instruction 1-SI-99-10-B, "31 Day Functional Test of SSPS Train B and Reactor Trip Breaker B," Revision 22, was in progress when an instrument mechanic inserted test leads to take a voltage reading across the P-4 contacts without realizing that the multi-test meter was in the ohms reading position. The result of the volt-ohm meter being in the ohm position was to create a current path equivalent to P-4 contact closure which energized Train B turbine trip bus. The root cause of this event was determined to be a failure of the involved individuals to follow expectations to "stop" when unexpected conditions occurred. A contributor to the event was improper use of test leads for connection to multi-test meters. Corrective actions included: 1) appropriate personnel action, 2) requiring an additional management observer to be present during the future test performances, 3) providing lessons learned and reinforcing expectations to site personnel on the use of human performance error reduction tools and appropriate test equipment, 4) and placing affected procedures on administrative hold until precautions are added.
390 | 3902004002 | 2004-09-19 | QR3 | Reactivity Control Imbalance | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On September 19, 2004, at approximately 0452 hours Eastern Daylight Savings Time (EDT), Unit 1 was in Mode 1, steady state operation at 100 percent power when the operators received simultaneously Control Rod Urgent Failure, RPI Trouble, and rods at bottom alarms. Four control rods, F14, B6, K2, P10, in control bank B group 2, fell to bottom of core and initiated the rods at bottom alarm. This event resulted in a rapid power drop to about 67 percent which then stabilized at approximately 85 percent. During this transient, operators took manual control of the main feedwater regulating valves, Operators responded to the rods at bottom indications by manually tripping the reactor at approximately 0456 EDT. Systems functioned as expected in automatic with the exception of the loop number 1 Reactor Coolant Pump which failed to transfer to its respective start bus on generator lockout. The remaining control rods inserted properly in response to the reactor trip. The Auxiliary Feedwater (AFW) System actuated in response to the trip, as expected. The root cause of the reactor trip was a malfunction of a rod control power cabinet circuit (i.e., a failed transistor on the phase control circuit card). Corrective actions included the replacement of three circuit board cards in the rod control power cabinet and stand down meetings to brief the oncoming crews of this event.
390 | 3902006004 | 2006-05-30 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | At 17:00:02 on May 30, 2006, main turbine vibration began increasing rapidly as indicated by a HI-HI alarm. At 17:00:16, the control room crew manually tripped the reactor and turbine when vibration reached the trip setpoint of 14 mils. Shortly after the plant trip, secondary chemistry parameters indicative of river water ingress began increasing. Following plant shutdown and cooldown, turbine and condenser inspections revealed a single blade from the last row (L-0) on the governor end of low pressure turbine (LPT) C (nearest LPT to generator) had fractured just below the rotor disk surface, causing damage to other blades on row L-0, L-0 fixed blades, surrounding turbine subcomponents, and several main condenser tubes below. Eddy current testing of all blade roots on the failed rotor identified seven more blade roots with cracks. The root cause of the reactor trip was failure of a blade on the governor end of the LPT C rotor. The corrective actions included replacement of the LPT C rotor and repairs of collateral damage to affected main condenser tubes. TVA has also limited operation at higher back pressures. TVA also chose to increase monitoring of turbine parameters (bearings, oil quality, shaft orbits, thrust movement, etc.) during startup to ensure reliability of turbine protection subsystems.
390 | 3902006005 | 2006-07-31 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On July 31, 2006, at approximately 12:13 EDT, the control room unexpectedly received an exciter field overcurrent alarm, followed immediately thereafter (< 1 sec) by the generator field breaker opening, and a turbine/reactor trip. An event team was assembled subsequent to the plant trip. The most likely cause was determined to be in the main generator automatic excitation control circuitry. Corrective action taken was to return the plant to service while monitoring several input and output signals associated with the automatic controls so that any subsequent events could be captured and analyzed. The excitation system would also be operated in TEST mode instead of AUTOMATIC to preclude the possibility of an additional plant trip. Since restarting the plant, there have been several instances where the output of the Maximum Excitation Limiter (MXL) circuit board in the automatic excitation control circuitry has changed significantly (+14 volts dc to -15 volts dc) with no corresponding change on any of the inputs. Had the automatic circuit been in service, the MXL output change would have driven the excitation controls into a loss of the exciter field which was the case during the plant trip. Based on this data, during the current refueling outage, the MXL circuit board will be removed to determine if a discreet component on the device has failed and an inspection performed of the interface wiring to the MXL circuit board to determine if degraded wiring caused the failure. As a result of the plant trip, the actuation of the Reactor Protection and the Auxiliary Feedwater Systems were reported in accordance with 10 CFR 50.72(b)(2)(iv) and 10 CFR 50.72(b)(3)(iv), respectively. This event is also being reported as this Licensee Event Report in accordance with 10 CFR 50.73 (a)(2)(iv).
390 | 3902008002 | 2008-08-07 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 1 | P | WE | PO | 53 | During a planned shutdown on August 7, 2008, unexpected annunciator alarms were received in the control room that indicated hi level in the A and B feedwater heater strings. The reactor was manually tripped when indication was received that the third string, C, was beginning to isolation. An event team was assembled subsequent to the plant trip. The cause was determined to be a failed air line on the Heater Drain Tank bypass to condenser valve. This air line failure was most likely due to vibration fatigue caused by improper installation. Corrective action was taken to replace this line in accordance with vendor requirements. As a result of the plant trip, the actuation of the Reactor Protection and the Auxiliary Feedwater Systems were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), respectively. This event is also being reported as this Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv).
390 | 3902008004 | 2008-09-20 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | During normal plant operation on September 20, 2008, unexpected annunciator alarms were received in the control room indicating an automatic reactor trip based on a loss of electrical load. Subsequently, the control room was informed by a Nuclear Assistant Unit Operator that he had tripped open the Exciter Field Breaker, leading to the turbine trip and successive reactor trip. The cause of this event has been determined to be human performance error in that the NAUO failed to recognize the need to utilize error reduction techniques when opening the exciter field breaker cabinet door. Corrective action has been taken to add the applicable information to operator requalification programs. As a result of the plant trip, the actuation of the Reactor Protection and the Auxiliary Feedwater Systems were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), respectively, as ENS notification 44506. This event is also being reported as this Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A).
390 | 3902010001 | 2010-05-21 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On May 21, 2010 at 1936 hours with Watts Bar Nuclear Plant, Unit 1 at 100 percent rated thermal power, the reactor tripped automatically in response to a turbine trip signal generated by closure of the Main Turbine Throttle/Stop Valves. Following reactor trip, main feedwater isolation occurred due to reactor trip coincident with low Reactor Coolant System TAVG, which then resulted in automatic startup of the Auxiliary Feedwater System. The most probable cause was determined to be an intermittent failure of a circuit card in the Westinghouse Mark IV Analog Electro-Hydraulic (AEH) turbine control system that caused the servo control valves for all four Main Turbine Throttle Valves to close their respective valves. TVA replaced the suspect circuit cards in the AEH control system. All safety systems performed their required functions in response to this event. This event is reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iv).
390 | 3902010003 | 2010-11-14 | QR6 | Manual Reactor Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 93 | At 06:45 Eastern Standard Time (EST) on 11/14/2010, Watts Bar Nuclear Plant, Unit 1 initiated a rapid load reduction in response to rising oil temperature in Main Bank Transformer 1A (MBT-1A). The high oil temperature in MBT-1A was attributed to a loss of forced-oil-air cooling due to a faulted motor starter which overloaded the control power transformer (CPT) that provided control power to the main bank cooling circuits. Loss of the CPT de-energized all six main bank coolers. Each main bank cooler has a circulating oil pump and four fans. The load reduction rate was not sufficient to reverse the temperature rise, so a manual reactor trip was initiated at 06:52 EST to prevent exceeding the 80oC maximum oil temperature operating limit. Following the reactor/turbine trip the plant entered the appropriate shutdown procedures to stabilize the plant at Hot Standby Conditions. No overcooling transient occurred and no safety injection signals were initiated for this event. The damaged components were replaced and additional corrective actions are being implemented to prevent recurrence. Corrective action included changes to the maintenance procedures and design changes to the main bank cooler circuits to eliminate single point vulnerabilities, to the extent practical. This event is reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iv).
390 | 3902011004 | 2011-05-29 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On May 29, 2011, 01:55 Eastern Daylight Saving Time (EDT) with Watts Bar Nuclear (WBN) Unit 1 at 100% rated thermal power, the reactor tripped automatically on a Main Generator/Turbine trip due to loss of main generator excitation, which resulted from a spurious fault signal from the Extended Gate Controller (EGC) in the Automatic Voltage Regulator (AVR). The most probable cause of the spurious signal was an intermittent fault in a ribbon cable to the EGC. Following cooldown to no-load equilibrium conditions, main feedwater isolation occurred due to Reactor Trip coincident with low Reactor Coolant System TAVG. Main feedwater isolation resulted in a Main Feed Pump Turbine (MFPT) trip signal which resulted in the automatic startup of the AFW System. No overcooling transient occurred and no safety injection signal was initiated for this event. <br /><br /> Plant personnel immediately entered appropriate trip response procedures and stabilized the plant. <br /><br /> The EGC circuit has been bypassed to prevent further spurious trips. The ribbon cable will be replaced at the next outage, and EGC output will be monitored for approximately one cycle to confirm no spurious trip signals before placing the EGC back in service. <br /><br /> This event is reported as an LER in accordance with 10 CFR 50.73(a)(2)(iv) for the valid actuation of the reactor protection system and the auxiliary feedwater system.
390 | 3902012004 | 2012-08-28 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On August 28, 2012, at 0332 hours with Watts Bar Nuclear Plant (WBN) Unit 1 at 100 percent rated thermal power, the reactor tripped automatically on low-low steam generator (SG) #2 level. Incorrect configuration of test equipment during testing of a Pressurizer Pressure channel induced a fault into the channel, and the channel fuse and upstream circuit breaker cleared on this fault. Loss of the upstream circuit removed power from the #2 main feedwater regulating valve circuitry, causing the valve to fail closed and resulting in loss of main feedwater to SG #2. Low-low level in SG #2 resulted in an automatic reactor trip and initiation of the auxiliary feedwater system. Plant personnel immediately entered appropriate trip response procedures and stabilized the plant in Mode 3. All safety systems functioned as designed. The root cause of this event is that procedure detail was inadequate to ensure correct configuration of the test equipment by inexperienced technicians. Procedures for circuit-intrusive activities with similar consequences were identified, placed on administrative hold, and will be updated to ensure procedural guidance meets procedure writing requirements. This event is reported as an LER in accordance with 10 CFR 50.73(a)(2)(iv)(A) for the automatic actuation of the reactor protection system and the auxiliary feedwater system.
390 | 3902013004 | 2013-06-28 | QR8 | Spurious Reactor Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On June 28, 2013, an A-phase ground fault occurred on the Roane 500kV transmission line approximately 22 miles from Watts Bar Nuclear Unit 1 (WBN1). Concurrently, WBN1 experienced a reactor trip due to the actuation of the 1A Main Bank Transformer Feeder Differential Relay. The 500kV transmission line fault was caused by a tree that fell onto the A-phase of the transmission line. The tree was cut by a local land owner.<br /><br /> Operations personnel stabilized the plant using the Auxiliary Feedwater (AFW) System and the main steam dump valves. The secondary-side steam generator (SG) atmospheric relief valves, SG power operated relief valves (PORVs) and SG safety valves were not challenged during the transient. The Reactor Coolant System (RCS) responded to the initial plant transient as expected without actuating Pressurizer PORVs or initiating Safety Injection signals.<br /><br /> The cause of the event was determined to be an incorrectly de-terminated current transformer neutral conductor that caused a differential relay imbalance in the summation circuit during the faulted conditions.
390 | 3902014003 | 2014-07-13 | QR6 | Manual Reactor Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On July 13, 2014 at 1937 [EDT], Watts Bar Nuclear Plant operators manually tripped the Unit 1 reactor due to automatic isolation of all low pressure feedwater heaters. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed.<br /><br /> All Control and Shutdown rods fully inserted. All safety systems responded as designed and the unit was stabilized in Mode 3, with decay heat removal via Auxiliary Feedwater, steam dumps and the main condenser, with the station in a normal shutdown electrical alignment.<br /><br /> The need to manually trip the reactor was determined to be the result of two separate age related failures associated with the control scheme of the #7 Heater Drain Tank (HDT). The root cause of these failures was that replacement preventative maintenance (PM) tasks did not exist for these components. The components in question were replaced and corrective actions have been developed to generate replacement PMs for both components. In addition, replacement PMs will be developed for similar critical components of the Secondary Systems based on EPRI Guidance
390 | 3902015001 | 2015-02-21 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Watts Bar 1 | P | WE | PO | 100 | On February 21, 2015 at approximately 10:32 am Eastern Standard Time (EST), the Watts Bar Nuclear Plant Unit 1 reactor was manually tripped by control room operators due to a decreasing main condenser vacuum. Subsequent to the reactor trip, the Auxiliary Feedwater system actuated. Control and Shutdown rods fully inserted into the reactor core, and safety systems responded as designed. The unit was stabilized in Mode 3, with decay heat removal via Auxiliary Feedwater and the Steam Generator Atmospheric Dump Valves. The Main Steam Isolation Valves were closed and remained closed during the event.<br /><br /> Tennessee Valley Authority (TVA) has determined that the decreasing condenser vacuum was due to a failure of an expansion joint boot seal in the "C" zone of the main condenser. This seal functions as the expansion joint between the condenser and low pressure turbines. The failure of the seal was due to a non-optimal vulcanization process and inadequate overlap in a joint splice, which significantly weakened the seal and allowed seal water to permeate the seal, further weakening the joint. The failed main condenser boot seal was replaced with a new boot seal on the "C" zone of the condenser. As a preventative measure, the boot seals on the "A" and "B" zones were also replaced.
390 | 3902016004 | 2016-03-22 | QR5 | Turbine Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On March 22, 2016, at 1131 Eastern Daylight Time, the Watts Bar Nuclear Plant Unit 1 (WBN1) reactor tripped due to the actuation of the Over Temperature Delta Temperature bistables. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated. All control rods inserted upon the reactor trip and safety systems functioned as expected. <br /><br /> An investigation into the cause of the trip determined that a failure of a Valve Position Limit up/down counter circuit card in the Analog Electro-Hydraulic Turbine Control System resulted in the closure of the turbine high pressure governor valves, resulting in an automatic reactor trip and turbine trip on WBN1. The failed card was replaced and WBN Unit 1 was returned to service. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A).
390 | 3902017004 | 2017-05-02 | QR6 | Manual Reactor Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 26 | On May 2, 2017, at 1945 Eastern Daylight Time (EDT) and on May 4, 2017 at 1710 EDT, Watts Bar Nuclear (WBN) Plant Unit 1 reactor was manually tripped due to a failure of the Reactor Coolant Pump (RCP) Board 1C normal feeder breaker to close during the planned power transfer to unit power following plant startup. Concurrent with each reactor trip, the Auxiliary Feedwater system actuated as designed. All control and shutdown rods fully inserted. All safety systems responded as designed for both events. <br /><br /> For the first event, the cause was incorrectly attributed to a high resistance contact resulting in the normal feeder breaker failing to close. In the investigation following the second event, a relay associated with the RCP Board 1C control circuit was found incorrectly configured due to a human performance issue, which resulted in a standing trip signal on the RCP normal feeder breaker. To prevent recurrence, procedures will be revised to address material control of pretested components.
390 | 3902017004 | 2017-05-04 | QR6 | Manual Reactor Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 28 | On May 2, 2017, at 1945 Eastern Daylight Time (EDT) and on May 4, 2017 at 1710 EDT, Watts Bar Nuclear (WBN) Plant Unit 1 reactor was manually tripped due to a failure of the Reactor Coolant Pump (RCP) Board 1C normal feeder breaker to close during the planned power transfer to unit power following plant startup. Concurrent with each reactor trip, the Auxiliary Feedwater system actuated as designed. All control and shutdown rods fully inserted. All safety systems responded as designed for both events. <br /><br /> For the first event, the cause was incorrectly attributed to a high resistance contact resulting in the normal feeder breaker failing to close. In the investigation following the second event, a relay associated with the RCP Board 1C control circuit was found incorrectly configured due to a human performance issue, which resulted in a standing trip signal on the RCP normal feeder breaker. To prevent recurrence, procedures will be revised to address material control of pretested components.
390 | 3902018005 | 2018-10-27 | QR6 | Manual Reactor Trip | [45 empty] | Watts Bar 1 | P | WE | PO | 21 | On October 27, 2018, at 1533 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant Unit 1 reactor was manually tripped due to the number 3 Reactor Coolant Pump (RCP) normal feeder breaker failing to close during the planned power transfer to unit power following startup. Concurrent with the reactor trip, the Auxiliary Feedwater (AFW) system actuated as designed. All safety systems responded as designed. <br /><br /> During the post trip investigation, it was discovered that the normal feeder breaker for the number 3 RCP was left in the racked down (disconnected) position. The apparent cause of this event was operations personnel failed to properly implement the requirements of system status control procedures. Corrective actions include revising the system operating instructions controlling the RCP normal feeder breaker position and implementing additional training on system status control. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as a manual actuation of the Reactor Protection System (RPS) and the automatic actuation of the AFW system.
390 | 3902019003 | 2019-08-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On August 31, 2019, at 2055 Eastern Daylight Time (EDT), the Watts Bar Nuclear Plant (WBN) Unit 1 reactor was manually tripped due to a loss of Steam Generator (SG) number 2 level control. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. All Control and Shutdown rods inserted properly. All safety systems responded as designed. <br /><br /> This event was likely caused by diaphragm case bolt relaxation. This relaxation resulted in additional load on the bolt holes of the diaphragm, causing tearing and failure. Corrective actions include replacement of the defective diaphragm and revising the diaphragm case bolt torque requirement in the vendor manual and maintenance procedure. <br /><br /> This condition is being reported as a safety system actuation in accordance with 10 CFR 50.73(a)(2)(iv)(A).
390 | 3902020001 | 2020-02-19 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 1 | P | WE | PO | 100 | On February 19, 2020, at 0936 Eastern Standard Time (EST), the Watts Bar Nuclear Plant (WBN) Unit 1 reactor was manually tripped due to a loss of control of Steam Generator (SG) number 3 level. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. All Control and Shutdown rods inserted properly. All safety systems responded as designed.<br /><br /> The direct cause of the event was a stuck pushbutton on the main feedwater regulating valve (MFRV) controller/hand station which provided a closing signal when an open signal was demanded. This occurred when performing a maintenance activity that placed the hand station in manual. This hand station was replaced following this event. In addition, a cause analysis has determined that manual control for automatic functions is not recognized as risk significant, therefore appropriate elimination/mitigation strategies are not utilized under controllable circumstances. Corrective actions include revising plant procedures to classify activities that replace automatic control availability with manual control action as risk significant and require risk evaluation and mitigation strategies. <br /><br /> This condition is being reported as a safety system actuation in accordance with 10 CFR 50.73(a)(2)(iv)(A).
391 | 3912016004 | 2016-06-05 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Watts Bar 2 | P | WE | PO | 13 | On June 5, 2016 at 1227 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant Unit 2 was in MODE 1 at approximately 12.5 percent power when a safety injection (SI) actuation occurred, followed by an automatic reactor protection system (RPS) trip. No primary safety barriers (Reactor Coolant System, containment and fuel clad) were challenged and no primary or secondary safety or relief valves actuated during the event. The Unit 2 plant trip was considered a complicated trip due to SI actuation. Safety equipment operated as expected and SI was promptly terminated. <br /><br /> The reactor trip and SI were caused by a turbine governor valve failing open, causing a steam header pressure rate of decrease SI actuation signal.
391 | 3912016005 | 2016-06-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 2 | P | WE | PO | 32 | On June 20, 2016, the 2B Main Feedwater Pump (MFP) tripped on a loss of vacuum in the 2B MFP turbine condenser, resulting in a loss of normal feed, and the subsequent trip of the main turbine. While operators were reducing power to within the capacity of Auxiliary Feedwater (AFW), the reactor tripped at 1540 Eastern Daylight Time (EDT) on Steam Generator Water Level (SGWL) Lo Lo in Steam Generator No.4. SG water level lowered rapidly due to shrink from the relatively cold AFW following the trip. <br /><br /> All control and shutdown rods fully inserted. All safety systems responded as designed. The trip response was uncomplicated. <br /><br /> The trip was caused by a human performance error during the drain down of the 2A MFP turbine condenser which resulted in a loss of vacuum on the 2B MFP turbine.
391 | 3912016007 | 2016-08-23 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 2 | P | WE | PO | 48 | On August 23, 2016, at 1356 Eastern Daylight Time (EDT), during power ascension testing, Watts Bar Nuclear Plant (WBN) Unit 2 reactor was manually tripped due to a loss of main feedwater. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. All control and shutdown rods fully inserted. All safety systems responded as designed. <br /><br /> The loss of main feedwater was due to a leak on a hydraulic fitting associated with the Main Feedwater Pump Turbine High Pressure Governor valve, resulting in the valve going partially closed with reactor power at 48 percent. With the governor valve partially closed, feedwater flow was reduced such that the unit needed to be manually tripped. Subsequent investigation determined the leak to be caused by the installation of incompatible fittings associated with the governor valve that occurred during plant construction.
391 | 3912016008 | 2016-08-30 | QR5 | Turbine Trip | [45 empty] | Watts Bar 2 | P | WE | PO | 98 | On August 30, 2016, at 2110 Eastern Daylight Time (EDT), the Watts Bar Nuclear Plant (WBN) Unit 2 reactor tripped on turbine trip as a result of an electrical fault. All control rods fully inserted and no safety or relief valves lifted. The Auxiliary Feedwater system actuated as designed. <br /><br /> The electrical fault was caused by an internal fault on the low voltage side of the 2B Main Bank Transformer (MBT) which resulted in a fire. The electrical fault was cleared by the 2B MBT sudden pressure and phase differential relays. Automatic fire suppression operated as expected and a fire fighting team was established by the fire brigade with assistance from local fire departments. The fire was extinguished at 2230 EDT. <br /><br /> The failed 2B MBT was removed from the plant and the spare MBT was connected in its place. The unit was returned to power and replacement transformers are being procured by the Tennessee Valley Authority for long term reliability.
391 | 3912017002 | 2017-03-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 2 | P | WE | PO | 91 | On March 20, 2017 at 0813 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) Unit 2 operations personnel manually tripped the plant from approximately 91 percent power based on lowering steam generator levels. Prior to the plant trip, the 2A Hotwell pump tripped at 0759 EDT and the 2C Condensate Booster Pump subsequently tripped at 0803 EDT. Operations personnel commenced to lower plant power after the 2A Hotwell pump trip in an attempt to maintain steam generator levels, but were unable to recover level and manually tripped the unit. <br /><br /> All control rods fully inserted and all automatically actuated safety related equipment operated as designed. At 0905 EDT, operations personnel exited the emergency operating instructions after the plant was stabilized. <br /><br /> This event resulted when scaffold crews inadvertently depressed the local trip button for the 2A Hotwell pump, which resulted in the secondary system transient. Bump guard covers were subsequently installed on local pushbuttons for selected pumps in the turbine building.
391 | 3912017006 | 2017-12-11 | QR6 | Manual Reactor Trip | [45 empty] | Watts Bar 2 | P | WE | PO | 97 | On December 11, 2017 at 0857 Eastern Standard Time (EST), the Watts Bar Nuclear Plant Unit 2 reactor was manually tripped after Operators observed multiple dropped control rods. All control and shutdown bank rods inserted properly in response to the manual reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant was stabilized with decay heat removal through Auxiliary Feedwater and the Steam Dump System. <br /><br /> An intermittent electrical connection between a rod control power cabinet card and the power cabinet backplane power supply caused a rod control malfunction with control bank A group 2 control rods. The malfunction resulted in four control rods dropping into the reactor core. As a corrective action, all five control rod power cabinets had a 100 percent inspection of backplane connectors on the card cages. Backplane connectors were reformed and aligned as necessary to attain suitable electrical and mechanical connection. Additionally, all associated circuit cards for the power cabinets had their connectors re-formed with a precision tool. <br /><br /> This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as safety system actuations of the Reactor Protection System and Auxiliary Feed Water System.
391 | 3912018001 | 2018-04-12 | QR8 | Spurious Reactor Trip | [45 empty] | Watts Bar 2 | P | WE | PO | 100 | At 0920 Eastern Daylight Time (EDT) on April 12, 2018, the Watts Bar Unit 2 reactor automatically tripped on Reactor Coolant System (RCS) low flow in Loop 1 while operating at 100 percent power. All control and shutdown bank rods inserted properly in response to the automatic reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. <br /><br /> The apparent cause of the plant trip was the failure to recognize the aggregate risk of minor maintenance being performed on the common drain line for the RCS Loop 1 flow transmitters. This maintenance caused a pressure perturbation on the common high side RCS reference leg, resulting in low flow on all three RCS loop 1 flow transmitters. The maintenance on the common drain line was not identified as work involving trip sensitive equipment during the planning process. Corrective actions include briefing affected personnel on this event, labeling the equipment as trip sensitive and revising the procedure on control of sensitive equipment.
391 | 3912018003 | 2018-06-22 | QR5 | Turbine Trip | [45 empty] | Watts Bar 2 | P | WE | PO | 96 | At 0841 Eastern Daylight Time (EDT) on June 22, 2018, the Watts Bar Unit 2 reactor automatically tripped while operating at 96 percent power. All control and shutdown bank rods inserted properly in response to the automatic reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The reactor automatically tripped due to a main turbine trip. The turbine trip was caused by an electrical issue with the main generator differential current trip signal. No actual fault occurred. <br /><br /> The most probable cause of the event was an intermittent equipment failure in the A phase signal loop between the neutral side current transformer of the main generator and the digital protection relays which led to actuation of the A phase main transformer differential current relay. Initial corrective actions implemented a temporary modification to relocate the neutral side differential trip signal to a different neutral side current transformer, thus providing equivalent protection while preventing a trip from the identified likely cause of the June 22, 2018 trip. Additional work will be performed during the next Unit 2 refueling outage to correct and determine the cause of the identified intermittent equipment failure.
391 | 3912018005 | 2018-08-22 | QR5 | Turbine Trip | [45 empty] | Watts Bar 2 | P | WE | PO | 100 | On August 22, 2018, at 0943 Eastern Daylight Time (EDT), the Watts Bar Nuclear Plant (WBN) Unit 2 reactor automatically tripped while operating at 100 percent power when operators changed the turbine control system from Operator Auto to Turbine Manual. All control and shutdown bank rods inserted properly in response to the reactor trip. All safety systems including the Auxiliary Feedwater (AFW) System actuated as expected. The reactor automatically tripped with a follow-on turbine trip in response to throttle valve closure. Throttle valve closure was caused by a turbine control system throttle valve manual up/down (U/D) counter card failure. <br /><br /> The card failure resulted in the closure of throttle valves which caused an initiation of a reactor trip with a follow-on turbine trip. Initial corrective actions included replacing the failed card. The main turbine analog electro-hydraulic (AEH) control system is scheduled to be replaced with a modern fault tolerant digital turbine control system. Installation is scheduled for the Unit 2 Cycle 2 refueling outage in April 2019. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an automatic actuation of the Reactor Protection System (RPS) and the AFW system.
391 | 3912019001 | 2019-05-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Watts Bar 2 | P | WE | PO | 95 | On May 22, 2019, at 0233 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant Unit 2 reactor was manually tripped due to a failure of the Steam Generator (SG) number 2 Main Feedwater Regulating Valve (MFRV) during power ascension following a refueling outage. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. All Control and Shutdown rods fully inserted. All safety systems responded as designed. <br /><br /> This event was caused by a defective actuator diaphragm that led to premature failure and subsequent loss of control of the SG 2 MFRV. Contributing to this event, personnel missed an opportunity to identify the actuator diaphragm was defective during its replacement. Corrective actions include replacement of the defective diaphragm and revising the procedure for diaphragm inspection and installation. <br /><br /> This condition is being reported as a safety system actuation in accordance with 10 CFR 50.73(a)(2)(iv)(A).
391 | 3912021001 | 2021-03-17 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Watts Bar 2 | P | WE | PO | 90 | On March 17, 2021, at 1004 Eastern Daylight Time (EDT), the Watts Bar Nuclear Plant (WBN) Unit 2 experienced an automatic reactor trip on a main turbine trip due to a main feed pump trip on low condenser vacuum. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. All control and shutdown rods inserted properly and all safety systems responded as designed. <br /><br /> The direct cause of the event was failure of a close latch to maintain an Alternate Supply Breaker open after installation in the Unit 2C Board. The Alternate Supply Breaker closed causing the Normal Supply Breaker to open, de-energizing the Unit 2C Board. The 2C Condenser Circulating Water (CCW) Pump lost power causing a reduction of CCW flow and subsequent main feed pump trip on low condenser vacuum. Corrective actions include incorporating vendor enhancements to the breaker maintenance procedures. <br /><br /> This condition is being reported as a safety system actuation in accordance with 10 CFR 50.73(a)(2)(iv)(A).
395 | 3951987015 | 1987-06-16 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Summer | P | WE | PO | 100 | POWER LEVEL - 100%. ON JUNE 16, 1987, AT 2003 HOURS A REACTOR TRIP OCCURRED FROM 100% POWER. THE FAILURE OF A CAPACITOR IN INVERTER XIT 5904 CAUSED AN OUTPUT FUSE TO BLOW WHICH RESULTED IN THE LOSS OF POWER RANGE NUCLEAR INSTRUMENT (NI) 44. THE LOSS OF NI- 44 CAUSED THE STEAM GENERATOR (SG) PROGRAM LEVEL CONTROL SIGNAL TO DECREASE FROM FULL LOAD TO NO LOAD (38%). THE FEEDWATER REGULATING VALVES (FWRVS) REDUCED FLOW TO DECREASE ACTUAL LEVEL TO MEET THE PROGRAMMED LEVEL. WHEN THE OPERATOR PLACED THE FWRV CONTROLS TO MANUAL AND DEMANDED AN OPEN SIGNAL, THE ADDITION OF COOLER FEEDWATER (IN CONJUNCTION WITH THE ALREADY DECREASED LEVEL) CAUSED 'B' STEAM GENERATOR LEVEL TO SHRINK BELOW THE LOW-LOW LEVEL REACTOR TRIP SETPOINT. THE PLANT RESPONDED TO THE REACTOR TRIP WITH NO ABNORMALITIES. MOTOR DRIVEN EMERGENCY FEEDWATER PUMP 'A' AND THE TURBINE DRIVEN EMERGENCY FEEDWATER PUMP STARTED TO SUPPLY FEEDWATER TO THE SGS IN RESPONSE TO THE SG LOW-LOW LEVEL REACTOR TRIP. DUE TO A PREVIOUS STEAM GENERATOR TUBE LEAK, THE STEAM RELEASED FROM THE MAIN STEAM POWER OPERATED RELIEF VALVES AND THE TURBINE DRIVEN EMERGENCY FEEDWATER PUMP EXHAUST TO ATMOSPHERE WAS CONSERVATIVELY CALCULATED TO BE A SMALL FRACTION OF THE ALLOWABLE RELEASE LIMIT.
395 | 3951987021 | 1987-09-02 | QR5 | Turbine Trip | [10 empty] | X | [29 empty] | X |  |  |  |  | Summer | P | WE | PO | 100 | POWER LEVEL - 100%. ON SEPTEMBER 2, 1987, AT 2109 HOURS, WHILE THE PLANT WAS OPERATING AT 100% POWER THE REACTOR TRIPPED DUE TO A TURBINE TRIP CONDITION ABOVE THE 50% POWER P-9 PERMISSIVE. A MAIN GENERATOR STATOR GROUND RESULTED IN AN ELECTRICAL FAULT WHICH CAUSED A MAIN TURBINE TRIP. THE GENERATOR STATOR GROUND CONDITION. THE PLANT RESPONDED TO THE REACTOR TRIP AS EXPECTED WITH NO SAFETY LIMITS EXCEEDED. ALIGNED TO THE CONDENSATE STORAGE TANK, BOTH MOTOR DRIVEN EMERGENCY FEEDWATER PUMPS STARTED TO MAINTAIN STEAM GENERATOR LEVEL WHEN MAIN FEEDWATER WAS ISOLATED ON THE REACTOR TRIP. THE MAIN STEAM POWER OPERATED RELIEF VALVES WERE USED TO MAINTAIN RCS TEMPERATURE BECAUSE THE MAIN CONDENSER VACUUM WAS BROKEN TO ALLOW INSPECTIONS AND REPAIRS TO BE MADE ON THE HEATERS AND HEATER DRAIN VALVES. BECAUSE THE CONDENSATE STORAGE TANK CONTAINED TRACES OF TRITIUM, THE STEAM RELEASED FROM THE MAIN STEAM POWER OPERATED RELIEF VALVES RESULTED IN AN UNMONITORED RELEASE WHICH WAS CALCULATED TO BE 1.008E-04% OF THE TECHNICAL SPECIFICATIONS SECTION 3.11.2 LIMIT. THE FAILED MAIN GENERATOR 'C' PHASE BUSHING WAS REPLACED. THE 'A' AND 'B' PHASE BUSHINGS WERE INSPECTED, AND MEGGAR READINGS WERE TAKEN REVEALING NO ABNORMALITIES.
395 | 3951987024 | 1987-09-24 | QR8 | Spurious Reactor Trip | [45 empty] | Summer | P | WE | PO | 100 | POWER LEVEL - 100%. MODE 1 - REACTOR POWER 100% AT 2210 HOURS, SEPTEMBER 24, 1987, A NEGATIVE RATE REACTOR TRIP OCCURRED WHEN AN INSTRUMENT AND CONTROL (I&C) TECHNICIAN INADVERTENTLY DEENERGIZED TWO ROD CONTROL POWER SUPPLIES WHICH RESULTED IN TWELVE CONTROL RODS INSERTING INTO THE REACTOR CORE. THE CAUSE OF THIS EVENT IS DUE TO PERSONNEL ERROR IN THAT THE I&C TECHNICIAN USED A SCHEMATIC DIAGRAM FROM AN APPROVED TECHNICAL MANUAL IN LIEU OF THE CIRCUIT WIRING DIAGRAM WHILE PERFORMING THIS REPAIR. ALTHOUGH THE TECHNICIAN WAS IN ERROR IN THAT HE WAS WORKING FROM A SCHEMATIC DIAGRAM, CONTRIBUTING TO HIS ERROR WAS THE IDENTIFICATION OF THE POWER SUPPLIES AS 'PRIMARY' AND 'REDUNDANT.' THE SCHEMATIC DIAGRAM OF THE CIRCUITRY AND THE NOMENCLATURE LED THE TECHNICIAN TO BELIEVE THAT THE POWER SUPPLIES WERE IN PARALLEL AND THAT REPLACEMENT OF EITHER POWER SUPPLY COULD BE PERFORMED WITHOUT AFFECTING OPERATION OF THE PLANT. WHEN THE POSITIVE VOLTAGE LEAD WAS LIFTED, BOTH POWER SUPPLIES DEENERGIZED RESULTING IN THE REACTOR TRIP. AS A RESULT OF THIS EVENT, ALL I&C PERSONNEL ARE TO BE TRAINED IN THE PROPER APPLICATION OF LOGIC/SCHEMATIC DIAGRAMS. TRAINING WILL ALSO EMPHASIZE THE DIFFERENCE BETWEEN LOGIC/SCHEMATIC AND WIRING DIAGRAMS. (THIS TRAINING WILL BE COMPLETED BY NOVEMBER 20, 1987.) THERE HAVE BEEN NO SIMILAR EVENTS.
395 | 3951987027 | 1987-10-29 | QC4 | Loss of ac Instrumentation and Control Bus. | [13 empty] | X | [30 empty] | X | Summer | P | WE | PO | 100 | POWER LEVEL - 100%. ON OCTOBER 29, 1987, AT 0313 HOURS WITH THE PLANT AT 100% POWER, BOTH THE PRIMARY AND BACKUP POWER SUPPLIES TO ONE OF THE WESTINGHOUSE 7300 SYSTEM PROCESS RACK PANELS FAILED. THIS RESULTED IN A LOSS OF VARIOUS INSTRUMENTATION AND CONTROL FUNCTIONS INCLUDING FEEDWATER CONTROLS, PRESSURIZER PRESSURE AND LEVEL CONTROLS, AND STEAM DUMP CONTROLS. MANUAL CONTROL OF THE FEEDWATER SYSTEM WAS ATTEMPTED, BUT DUE TO THE NATURE OF THE CONTROL FAILURES, RECOVERY WAS NOT POSSIBLE. THE PLANT TRIPPED ON LOW STEAM GENERATOR 'C' LEVEL COINCIDENT WITH STEAM FLOW/FEED FLOW MISMATCH. A PRESSURIZER POWER OPERATED RELIEF VALVE LIFTED, THE STEAMLINE POWER OPERATED RELIEF VALVES LIFTED, AND THE MOTOR DRIVEN AND TURBINE DRIVEN EMERGENCY FEEDWATER PUMPS STARTED. WITHIN APPROXIMATELY 13 MINUTES I&C PERSONNEL HAD RESTORED POWER TO THE PANEL AND CONTROL SYSTEMS RETURNED TO NORMAL. THE PLANT, UTILIZING THE REESTABLISHED CONTROL FUNCTIONS, RECOVERED NORMALLY FROM THE TRIP. THE CAUSE OF THE EVENT WAS ATTRIBUTED TO A FAILED CAPACITOR ON A STEAM DUMP CONTROL SIGNAL CONVERTER CARD IN ONE OF THE PROCESS RACK PANELS. THIS CAPACITOR SHORTED TO GROUND CAUSING THE BREAKERS TO BOTH THE PRIMARY AND BACKUP POWER SUPPLIES FOR THE PROCESS RACK PANEL TO TRIP. FROM DESIGN CHANGES.
395 | 3951988002 | 1988-02-16 | QR8 | Spurious Reactor Trip | [45 empty] | Summer | P | WE | PO | 100 | On February 16, 1988 at 2331 hours, the reactor tripped from 100% power on a neutron flux negative rate signal. At the time of the trip, Nuclear Instrumentation System (NIS) power range channel N-42 was inoperable with bistables tripped, having failed a surveillance test at 1300 hours earlier that day. A Quadrant Power Tilt Ratio (QPTR) determination was required by Technical Specifications by 0100 hours, February 17, 1988 to maintain 100% power. <br /><br />While inserting the digital volt meter leads into the test point for current readings on N-44, the Shift Engineer moved a loose terminal post adjacent to the test point, momentarily interrupting the current signal and resulting in a negative rate trip signal for N-44. With the bistables for N-42 tripped, the two out of four coincidence was satisfied and the reactor tripped on a power range neutron flux negative rate signal. <br /><br />The primary cause is that the design of the meter test board terminal posts is such that the posts are susceptible to mechanical loosening and did not incorporate the features necessary to lock the connection. The Licensee is currently evaluating various design changes and has incorporated procedure changes to preclude recurrence. <br /><br />Approximately 10 minutes after the trip, a fire occurred in the main genertor ALTERREX cabinet when the exciter field breaker failed to remotely trip from the main control board. Attempts to trip the breaker locally were unsuccessful. The breaker tripped following the extinguishing of the fire.
395 | 3951988006 | 1988-05-12 | QL5 | Partial Closure of MSIVs | [45 empty] | Summer | P | WE | PO | 100 | At 0446 hours, May 12, 1988, a Safety Injection (SI)/Reactor Trip occurred when "A" Main Steam Isolation Valve (MSIV) shut during testing. When the test switch was released following the testing of "A" MSIV, the valve went fully shut decreasing the steam flow from its associated steam generator. This decrease of steam flow on "A" steam header caused a corresponding increase in steam flow and a decrease in steam pressure on B and C steam headers. As part of the "Reactor Protection System," this rapid decrease in steam pressure on two headers caused a Safety Injection (SI)/Reactor Trip. <br /><br />A Notification of an Unusual Event (NUE) was declared at 0510 hours as the result of the SI and was downgraded to normal plant condition at 0515 hours. <br /><br /> On May 16, 1988, during a review of the post trip data by the Independent Safety Engineering Group (ISEG), it was identified that Service Water flow to the Reactor Building Cooling Units (RBCU) decreased below the Technical Specifications limit during the event. <br /><br /> On May 17, 1988, a Management Review Board meeting, chaired by the acting Vice President, Nuclear Operations, was convened to review this event. As a result of this meeting, the following action is to be taken: <br /><br />Engineering is to review the design requirements of the MSIV circuitry, identify what is common in both the normal and test circuit, and what can be monitored during the next test. With respect to the reviewing of post trip data, Computer Services is to evaluate the feasibility of displaying various parameters in graphic form for higher visibility.
395 | 3951988007 | 1988-06-01 | QR8 | Spurious Reactor Trip | [45 empty] | Summer | P | WE | PO | 37 | On June 1, 1988, at 1004 hours, a reactor trip occurred while personnel were testing the "B" train solid state protection system actuation logic and master relay. Personnel in the control room were instructed to close the "B" reactor trip breaker from the main control board. When the control board switch was rotated to the close position, a signal interruption of the 48 volt undervoltage signal to the "A" reactor trip breaker and "B" bypass reactor trip breaker caused the breakers to open, resulting in a reactor trip from he "A" train solid state protection channel. Additional reviews have identified the source of the signal interruption to be a momentary opening of a contact in the undervoltage circuitry which occurs when the reactor trip breaker switch is taken to the lose position from the after-trip position. <br /><br />The cause of the event has been attributed to inadequate procedures. Changes to a surveillance testing procedure made prior to the event did not require the reactor trip breakers to be closed using the main control board switch prior to startup. The following corrective actions were identified to preclude recurrence: <br /><br />1. Procedures were changed to ensure the reactor trip breaker is closed using the main control board switch prior to plant startup. <br /><br />2. Procedures now require individuals to perform closure manipulations of the breaker locally while at power. <br /><br />3. Training was provided to applicable individuals to ensure the operation of the control room switch was understood. <br /><br />4. A new precautionary label was placed at the reactor trip breaker switch on the main control board.
395 | 3951988009 | 1988-07-26 | QR8 | Spurious Reactor Trip | [45 empty] | Summer | P | WE | PO | 100 | On July 26, 1988, at 0928 hours, a reactor trip occurred while personnel were testing the "B" train solid state protection system actuation logic and master relay. Personnel in the control room were instructed to close the "B" reactor trip breaker. When the control board switch was rotated to the close position, "A" reactor trip breaker and "B" bypass reactor trip breaker opened causing a reactor trip from the "A" train solid state protection channel. <br /><br />The event was similar to the reactor trip reported in LER 88-007, dated July 1, 1988, and LER 88-007, Revision 1, dated March 16, 1989. The cause of the event was attributed to he lack of adherence to procedure changes which had been implemented as a result of the previous trip. <br /><br /> The following corrective actions have been identified to preclude recurrence: <br /><br />1. Procedures were changed to ensure the reactor trip breaker is closed using the main control board switch prior to plant startup. <br /><br /> 2. Procedures now require individuals to perform closure manipulations of the breaker locally while at power. <br /><br />3. Training was provided to applicable individuals to ensure the operation of the control room switch was understood. <br /><br />4. A new precautionary label was placed at the reactor trip breaker switch on the main control board. <br /><br />5. I&C personnel have been instructed in the importance of procedure adherence.
395 | 3951989006 | 1989-04-01 | QR5 | Turbine Trip | [45 empty] | Summer | P | WE | PO | 30 | On April 1, 1989 at 0447 hours with the plant operating at approximately 30% power, a turbine-trip occurred as a result of high moisture separator reheater level. Feedwater temperature dropped below the feedwater isolation setpoint on all three steam generators due to the loss of feedwater heating resulting from the turbine trip. Approximately 30 minutes after the turbine trip, with actual feedwater flow as expected for 30% power, indicated flow to "C" steam generator began drifting down. When the transmitter indicated feedwater flow was below the isolation setpoint, the "C" feedwater isolation valve closed on low flow coincident with low temperature signals. Steam generator water level began decreasing and approximately two minutes later the reactor tripped on lo-lo level in steam generator "C." <br /><br /> A similar turbine trip, without a reactor trip, had occurred on March 30, 1989 at 1819 hours. The initial review of system indications, alarms and plant responses for that trip indicated the trip was the result of several erroneous instrumentation signals and not the result of actual moisture separator reheater (MSR) high level conditions. Subsequent to the April 1 reactor trip, several improperly functioning MSR and MSR drain tank level switches, alarms and controllers were discovered and repaired. These malfunctions were responsible for the conflicts seen between actual plant conditions and indicated data during each turbine trip. Also, air was found in the "C" feedwater flow transmitter which caused the indicated low flow condition. <br /><br /> As a result of the events described above, post turbine trip without a reactor trip reviews are being proceduralized to ensure detailed investigations are initiated for secondary plant trips.
395 | 3951989011 | 1989-05-28 | QG10 | Inadvertent Open/Close: 1 Safety/Relief Valve | [45 empty] | Summer | P | WE | PO | 100 | At 0252 hours, May 28, 1989, a manual Reactor Trip was initiated following the failure of a Pressurizer Safety Valve. The valve (XVS-8010-C) became unseated Causing a rapid depressurization of the Reactor Coolant System. The manual Reactor Trip was initiated at approximately 2000 psig and the safety valve reseated prior to reaching the Safety Injection setpoint of 1850 psig. The Reactor Coolant System pressure recovered and was stabilized at approximately 2000 psig. <br /><br /> During the transient, a condenser steam dump valve failed to close and an operator had to fail the air to the valve for closure.<br /><br /> Pressurizer Safety Valves (XVS-8010-B and C) were replaced and the reactor was restarted at 0049 hours, June 11, 1989. Note: Valve 8010 B was replaced due to minor leakage past the seat. <br /><br /> The Licensee has determined that the reason for the misoperation of XVS-8010-C is that the expected margin between normal operating pressure and the pressurizer safety valve relief setpoint pressure was reduced to zero. It was also determined that the most prevalent factor in this margin reduction was a loop seal discharge. This discharge resulted in a reduced valve setpoint because of the steam medium imposed on the valve. As such, the Licensee is focusing the corrective action plan on the elimination of loop seal capability for the pressurizer safety valves. NOTE: A subsequent report (LER 89-015 dated September 20, 1989) documents d similar event involving pressurizer safety valve XVS-8010-A. The Licensee has determined that a loss of loop seal was the cause for the misoperation of XVS-8010-A.
395 | 3951989012 | 1989-07-11 | QR5 | Turbine Trip |  | X | [13 empty] | X | [29 empty] | Summer | P | WE | PO | 100 | On July 11, 1989, a Turbine Trip/Reactor Trip occurred while operating at 100% reactor power. Technicians working inside the "Generator Stator Cooling Water" cabinet inadvertently shorted the power leads on the temperature converter causing the AC power fuse to blow. This gave a false indication of loss of generator stator cooling water which caused a Turbine Trip and a Reactor Trip due to the turbine tripping above 50% reactor power. <br /><br /> In addition to the aforementioned loss, three other generating stations tripped while attempting to compensate for the VARs lost on the grid with the Turbine Trip/Reactor Trip. <br /><br /> As a result of the loss of four generating stations, the offsite voltage to the Engineering Safety Feature (ESF) busses decreased below the minimum acceptable value and a Notification of Unusual Event (NUE) was declared at 1510 hours. The licensee's dispatchers immediately took action to place additional generating units on-line. Both emergency diesel generators came on-line and supplied their respective ESF busses. The offsite voltage to the ESF busses was returned to an acceptable level at approximately 1645 hours and the NUE was terminated at approximately 1710 hours. There were no personnel injuries or releases of radioactive materials as a result of this event.
395 | 3951989015 | 1989-08-25 | QG10 | Inadvertent Open/Close: 1 Safety/Relief Valve | [45 empty] | Summer | P | WE | PO | 100 | At 1000 hours on August 25, 1989, the "A" pressurizer safety valve body inlet temperature increased to greater than 450 degrees F and a plant shutdown was initiated. Shortly after the load reduction was started, the "A" pressurizer safety valve opened at a system pressure of approximately 2260 psig. At 1003 hours, the acoustic leak monitor alarmed, the Reactor Coolant System (RCS) began to rapidly depressurize and at approximately 1004 hours the Shift Supervisor directed a manual reactor trip. The pressurizer safety valve reseated prior to reaching the Safety Injection setpoint of 1850 psig. All plant parameters recovered to their expected post trip values except RCS pressure which was controlled around 2000 psig to avoid lifting the safety valve again. The plant was taken to cold shutdown, the "A" pressurizer safety valve replaced, and the reactor was restarted at 0635 hours on September 1, 1989. Further investigation by the Licensee has shown that a loss of loop seal on the "A" pressurizer safety valve was the cause of the valve's misoperation. <br /><br /> LER 89-011, dated June 27, 1989, documents a similar event involving the "C" pressurizer safety valve. The Licensee has determined that a loss of loop seal was a contributing factor in the event and will submit this finding in a supplemental report. The expected submission date of this report is January 3, 1990.
395 | 3951989020 | 1989-12-02 | QR5 | Turbine Trip | [45 empty] | Summer | P | WE | PO | 100 | On December 2, 1989, at approximately 2202 hours, operations personnel started a load reduction to 90% power for the monthly turbine control valve testing. When the operator pushed the load selector decrease button for the second 2% reduction in power the turbine commenced d rapid power decrease (2209 hours). Operations personnel attempted to counter the loss of load by selecting manual increase; however, the turbine controls failed to respond and the turbine was manually tripped when turbine power decreased below P-9 (Power Permissive < 50% Rated Thermal Power). The exciter field breaker initially failed to open from the Main Control Board (MCB). An operator was immediately dispatched to locally open the breaker. The breaker finally opened after several attempts to cycle the breaker from the MCB. <br /><br /> Main feedwater was manually secured at 2220 hours when the turbine runback transient caused a high level in the deareater (DA). When main feedwater was restored at 2221 hours, the addition of cooler (280 degrees F) water caused a rapid RCS cooldown and steam generator levels to shrink to below the low-low steam generator level reactor trip setpoints. A reactor trip occurred at 2222 hours on "C" Steam Generator low-low level. With the exception of the previously mentioned problems the plant response was normal. A failed turbine control circuit board was replaced and the exciter field breaker PM'd prior to authorizing the plant restart.<br /><br /> Additional actions have been initiated by SCE&G to modify the turbine control circuit and increase the PM frequency on the exciter field breaker.
395 | 3951992003 | 1992-05-20 | QR8 | Spurious Reactor Trip | [45 empty] | Summer | P | WE | SU | 3 | On May 20, 1992, the plant was in mode 2 with reactor power at approximately 3% and secondary system warmup in progress when the reactor tripped on intermediate range high flux. At the time of the trip, operations personnel observed annunciator alarms for intermediate range high flux and instrument inverter trouble. A review of plant performance following the trip determined that equipment response was as expected and that there had been no automatic actuation of Engineered Safety Features systems. <br /><br /> The cause of the event is attributed to personnel error. I&C technicians replacing a defective power supply in the power range nuclear instrument NI-42 drawer shorted the incoming power to ground causing a voltage transient. The power source for NI-42 is common to intermediate range channel NI-36, so it is believed that the short circuit caused a low voltage condition that activated the high flux bistable in NI-36 initiating the reactor trip. <br /><br /> South Carolina Electric & Gas Company has cautioned I&C personnel in the importance of using available technical information and correct safety practices during repair activities. Additional procedural guidance for troubleshooting/repair activities and enhancements to the craft training program are being developed. These actions are expected to be in place by January 1, 1993.
395 | 3951992004 | 1992-05-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Summer | P | WE | PO | 29 | At approximately 0553 hours on May 21, 1992, the reactor tripped from 9% power on low-low steam generator water level in the "C" steam generator. Reactor power was being maintained at approximately 29% power when oscillations in feedwater flow, steam generator level, and steam flow occurred due to the automatic cycling of the steam line power operated relief valves (PORVs). The automatic cycling was caused by a malfunction of Bank 2 of the Steam Dump System, which resulted in an elevated reactor coolant system temperature and consequently elevated main steam line pressure. The cycling of the PORVs resulted in feedwater flow decreasing below the minimum 13% flow setpoint. When feedwater temperature decreased below 225 degrees F, a feedwater isolation to "C" steam generator occurred. An attempt was made to reduce reactor power in order to transfer feedwater back to the emergency feedwater system. "C" steam generator level decreased below the low-low level reactor trip setpoint before this could be accomplished, and a reactor trip occurred.<br /><br /> The reactor protection system responded as designed. A post trip review revealed that six condenser steam dump valves did not fully open on demand. This was caused by replacement of "current to pneumatic" transducers that had higher impedance than the original transducers. The higher impedance prevented the power supply card from developing a full 20 milliamperes current, and the valves could not fully open on a 100% demand signal. The original transducers had been replaced under the "Equal To/Better Than" program. <br /><br /> The installed transducers were replaced with the original lower impedance transducers. The "Equal To/Better Than" procedure (Engineering Services - 419) is being reviewed to determine if it needs any program enhancements.
395 | 3951993001 | 1993-01-12 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Summer | P | WE | PO | 100 | At approximately 0854 on January 12, 1993, the reactor tripped from 100% power on positive flux rate on all four power range channels. With no work being performed on generator protective relays or in the switchyard, a generator backup auxiliary time delay relay spuriously actuated and opened the transformer high side oil circuit breaker (OCB 8902). When it opened, the generator was left supplying only the balance of plant (BOP) busses through the generator breaker. The instantaneous loss of load caused a rapid generator speed increase which resulted in bus frequency increasing to approximately 62.5 hertz. The reactor coolant pumps (RCP), powered from the BOP busses, increased reactor coolant system (RCS) flow. The increased flow caused a reduction core differential temperature, which increased core water density. This, combined with the large negative moderator temperature coefficient at end of life, caused a neutron flux increase and a reactor trip occurred. <br /><br /> The reactor protection system responded as designed. When the generator breaker opened with OCB 8902 already open, there was no backfeed available to the BOP busses and they were deenergized. At 1039 the BOP busses were reenergized. "A" RCP was started at 1113 terminating natural circulation of the RCS. <br /><br /> The cause of the spurious actuation of the generator backup auxiliary time delay relay is unknown; however, the auxiliary time delay relay, along with another relay of the same type, and the generator backup protection relays that feed a signal to the auxiliary time delay relay were replaced.
395 | 3951997001 | 1997-04-22 | QR6 | Manual Reactor Trip | [45 empty] | Summer | P | WE | PO | 100 | On April 22, 1997, plant personnel conservatively initiated a manual reactor trip in response to a leak on the Main Turbine Electro-Hydraulic Control (EHC) system. It was subsequently determined that an ""O"' ring on the shutdown servo t Combined Intercept Valve (CIV) #1 had failed. Although Feedwater Isolation was achieved, one Feedwater Regulating Valve (FRV) was slow to completely close in response to a Feedwater Isolation Signal. All other systems functioned per design. Repairs were accomplished and the plant restarted.
395 | 3951997002 | 1997-04-26 | QP5 | Excessive Feedwater Flow | [13 empty] | X | [30 empty] | X | Summer | P | WE | PO | 6 | On April 26, 1997, at 2043 hours, a main turbine trip from 42% power occurred due to a Hi-Hi Lv1 in "C" steam generator (P-14) signal. This signal also generated a feedwater isolation, causing all main feedwater (FW) pumps to trip, and sent a signal for the feedwater isolation valves (FWIVs), feedwater regulation valves (FRVs), and feedwater regulation bypass valves (FRBVs) to close. Although emergency feedwater pumps auto started upon loss of all main FW pumps, this flow could only meet the steam demand for about 4% power. At 2047 hours, an automatic reactor trip from approximately 6% reactor power occurred due to Lo-Lo Lv1 in "A" steam generator (S/G) during the power reduction. All systems functioned per design in response to this trip. After verification of system integrity and and proper plant response, plant restart was initiated.
395 | 3951999008 | 1999-05-18 | QR6 | Manual Reactor Trip | [45 empty] | Summer | P | WE | PO | 82 | On May 18, 1999, following the completion of RF11 in which the Main Turbine HP Rotor was replaced and during the initial power escalation, plant personnel initiated a manual reactor trip at 82% in response to high vibration on Main Turbine Bearings 1 and 2. As turbine load was being increased, Operations received the Main Turbine Vibration High Annunciator. After verifying actual vibration, Operations initiated a load reduction to attempt to decrease the level of vibration. The levels of vibrations continued to increase as the load was reduced. In accordance with plant procedures, Operations initiated a manual reactor trip when the vibration on Bearing #2 increased above 12 mils. The cause of the high vibration was determined to be light rubbing within the new mono-block high turbine rotor. On May 19, 1999, the plant was restarted successfully.
395 | 3951999009 | 1999-06-04 | QR8 | Spurious Reactor Trip | [45 empty] | Summer | P | WE | PO | 100 | On June 4, 1999 at 1358 hours, while at 100 percent reactor power, the plant experienced a reactor trip upon receipt of 2 out of 4 logic coincidences for power range high flux trip. Prior to the trip, I&C technicians were performing surveillance STP 310.006, "NIS POWER RANGE N42 CALIBRATION." With Nuclear Instrumentation System (NIS) drawer N42 in TEST, a technician was in the process of sliding drawer N42 into its cabinet when a trip signal was generated from the output of drawer N43, completing the 2 out of 4 logic required for a reactor trip. The plant was stabilized in Mode 3. The appropriate Safety Related equipment functioned as designed. All auxiliary and secondary systems functioned as required. All control rods inserted fully into the core. The reactor remained in Mode 3, Hot Standby, until the cause was determined and corrective action was taken. The cause of the plant trip was determined to be the generation of a spurious signal from the in-service N43 channel Power Range Upper Detector Current Meter. The defective meter was replaced and, following a post trip review of the plant response, the plant was returned to service at 0922 hours on June 6, 1999.
395 | 3952002003 | 2002-06-01 | QR8 | Spurious Reactor Trip | [45 empty] | Summer | P | WE | SU | 2 | On June 1, 2002, at 1840, the reactor tripped automatically due to a spike on Nuclear Instrumentation (NI ) Intermediate Range channel N-36. The reactor was being held steady at approximately 2% power and no significant plant evolutions were ongoing at the same time. The indicator for channel N-36 spiked to a value greater than the trip setpoint and the reactor protection system automatically tripped the plant. After the trip, spiking was still occurring on this channel. No other NI channel indicated any power increase during this event. The cause was preliminarily determined to be noise resulting from a failed or degraded circuit card. Multiple circuit cards were replaced and the spiking problem did not reappear. The actual cause of the noise problem has not been determined. The vendor has indicated the power supply vintage has the potential to fail high and cause additional damage to circuit cards, although there is no evidence that a power supply failure occurred. The power supply was not replaced at this time. One circuit card (A-8) has the visual appearance of overheating. The card A8 will be sent off to the vendor for failure analysis. A root cause investigation determined that a high voltage power supply problem was the cause. The power supplies have been replaced. The circuit cards and power supplies are being placed into the preventative maintenance program for routine replacement.
395 | 3952002004 | 2002-06-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Summer | P | WE | PO | 100 | On June 17, 2002, the plant was operating at 100% power when a fuse blew in the digital speed control system for the "C" main feedwater pump. Per procedure, the operating crew began reducing load at the rate of 1% per minute, and the remaining 2 main feedwater pumps began increasing speed and flow to compensate for the loss of the third pump. As the discharge flows for the operating feedwater pumps increased, the flows over-ranged the flow transmitters and the newly installed digital speed control system interpreted the signal as a "bad quality" flow value and the pumps' recirculation valves went full open. With a significant portion of feedwater flow now being diverted to the deaerator instead of the steam generators, steam generator levels began to decrease. Operators were unable to take manual control of the recirculation valves and increased the load reduction rate to 3% per minute, but steam generator levels continued to decrease. "A" steam generator reached its lo-lo level of 30% narrow range first and initiated the reactor trip signal and subsequent reactor trip. The transient response of the plant was appropriate for a reactor trip caused by reduced feedwater flows and resulting decreased steam generator levels. Reactor coolant system average temperature (Tave), pressurizer pressure and level, and steam generator levels returned to normal no-load values within minutes of the initial trip transient. No safety injection set points were challenged, and both the turbine driven and the 2 motor driven emergency feedwater pumps started as designed and supplied sufficient feedwater to effect recovery. The cause of the reactor trip has been determined to be a design deficiency in the implementation of the digital speed control system for the main feedwater pumps.
395 | 3952003002 | 2003-05-12 | QR5 | Turbine Trip | [45 empty] | Summer | P | WE | PO | 100 | A reactor tip on Over Temperature Delta Temperature (OTDT) occurred from 100 percent power on May 12, 2003, at 0102 hours, due to the main generator breaker opening. A root cause team was assembled to investigate the cause of the trip. Troubleshooting identified that the main generator field breaker position sensing circuit had degraded contacts that caused the digital voltage regulator to sense a loss of excitation and open the main generator breaker. Immediate corrective action involved replacing degraded contacts, removing suspect breaker position switch contacts, and adding a redundant circuit for this voltage regulator anticipatory trip function. This was a programmed anticipatory trip function. The main generator never actually lost excitation until the trip and was fully protected. Notification of this event was reported under Event Notification EN# 39838 at 0328 hours on May 12, 2003 in accordance with 10 CFR 50.72(b)(l). Following the plant trip, all major systems functioned as expected. The plant was stabilized in Mode 3.
395 | 3952004001 | 2004-03-30 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Summer | P | WE | PO | 9 | On March 30, 2004, while at power, VCSNS personnel were performing a reactor building inspection to identify the source of reactor coolant system unidentified leakage that was within Technical Specification (TS) limits. At 1129 hours, a pressure boundary leak was identified at the seal injection line nozzle weld to reactor coolant pump "C" (RCP C). Pursuant to TS 3.4.6.2, Action a., VCSNS commenced a controlled reactor shutdown at 1410 on March 30, 2004. During the shutdown, the main turbine experienced higher than normal vibration. At 1517, the turbine was manually tripped at approximately 43% reactor power. Subsequent to the manual turbine trip, feedwater regulating valve IFV-498 failed in the closed position while in automatic with a full open demand signal. The reactor automatically tripped at 1521 due to to-lo level in the "C" steam generator. All control rods fully inserted and all safety systems responded normally. Both motor driven emergency feedwater pumps started as required. The plant stabilized in mode 3. The cause of failure for IFV-498 is attributed to service induced fretting on the positioner pilot valve stem. All positioners on the feedwater regulating valves have been replaced and will be scheduled for future periodic replacement at appropriate intervals. The leakage for RCP C seal injection nozzle has been determined to be a weld failure caused by low-amplitude high cycle fatigue. A modification replaced the line with a new nozzle design with enhanced pipe supports.
395 | 3952005003 | 2005-08-25 | P1 | Total Loss of Feedwater Flow | [7 empty] | X | [5 empty] | X | [19 empty] | X | [10 empty] | X | Summer | P | WE | PO | 100 | On 08/25/2005, at approximately 1126, the B Condensate Pump tripped and the A Condensate Pump was started immediately. The A Condensate pump discharge valve was extremely slow to respond to the open signal, resulting in a decreasing Deaerator (DA) level. At 1129, smoke was reported coming from the B Condensate Pump motor. There was no visible flame at this time. At 1133, all Feedwater Booster Pumps (FWBP) and Main Feedwater Pumps (MFP) tripped due to LO-LO DA level. As a result, the Main Turbine tripped causing a Reactor trip with Reactor power greater than 50%. At 1138, the Fire Brigade was assembled to respond to the fire. At 1141, a Notification of Unusual Event (NUE) was declared due to the fire in the Protected Area greater than 15 minutes in accordance with Emergency Plan Procedure (EPP) 001.1. Telephone notification was made in accordance with 10CFR72(A). At 1317, the fire was declared out in the B Condensate Pump. At 1327, the Site downgraded from the NUE. After repairs were completed the unit was restarted and achieved criticality on 08/27/05 at 0603. The Main Turbine was placed on line on 08/27/05 at 1724. The unit returned to full power operation on 08/28/05 at 1800. The delayed opening of the A discharge valve was determined to be due to wear and galling that led to binding under high dP conditions. All three Condensate Pump discharge valves were replaced or restored to original design in refueling outage (RF16) and will be placed in the plant preventive maintenance program.
395 | 3952007001 | 2007-02-05 | QK4 | Steam or Feed Leakage | [45 empty] | Summer | P | WE | PO | 95 | On February 5, 2007, while returning the "D" feedwater booster pump to service, a steam leak developed in the Turbine Building. Investigation revealed a steam leak had developed in the vicinity of the "D" feedwater booster pump recirculation header. Since the exact location could not be readily identifiable, the shift supervisor conservatively directed a manual reactor trip at 0307. All systems responded as expected on the reactor trip. The emergency feedwater pumps automatically started on Lo-Lo Steam Generator Level. The cause of the steam leak was determined to be a failure of the gasket for the "D" feedwater booster pump recirculation header orifice. The cause of the gasket failure was attributed to normal aging and pipe movement during the startup of the "D" feedwater booster pump. For corrective action, the gaskets and orifice plate were replaced, and the plant was returned to power operation on 2/06/2007. The feedwater system operating operating procedure has been revised to direct operators to ensure certain system conditions are met prior to starting a feedwater booster pump.
395 | 3952008001 | 2008-01-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Summer | P | WE | PO | 100 | On January 24, 2008, the C feedwater flow control valve (IFV00498) exhibited oscillations as indicated by the plant computer and on the Main Control Board (MCB). As the feedwater flow oscillations increased in size, the Shift Supervisor directed the operator to take manual control of the valve. Feedwater flow was greater than steam flow when manual control was implemented. When the operator decreased flow demand on the manual/auto station, IFV00498 indicated closed and feedwater flow decreased to zero. Due to a rapidly decreasing level in C Steam Generator, the Shift Supervisor directed a manual reactor trip at 1604 hours. The operations crew entered the reactor trip procedure. All systems responded as required. The plant was stabilized in Mode 3. The root cause was determined to be the failure of the feedwater flow control valve positioner pilot valve. The failure was due to either fretting as a result of normal operation or foreign material inclusion into the component's air system due to insufficient filtration and vibration induced component wear. On each feedwater flow control valve, the positioners, check valves, and pressure regulators were replaced, and additional filtration was installed. Copper tubing and the brass check valves were replaced with stainless steel to minimize particulate intrusion. In addition, components susceptible to vibration were relocated. To address future problems, an "air-gag" device was installed on each feedwater flow control valve to facilitate on-line maintenance without loss of safety function.
395 | 3952009002 | 2009-10-02 | QR5 | Turbine Trip | [45 empty] | Summer | P | WE | PO | 100 | On October 2, 2009, at approximately 0649 hours, the plant was operating in Mode 1 at 100% power when the reactor automatically tripped due to a main turbine trip. The turbine trip was initiated by a main generator stator ground. All systems responded as required. The emergency feedwater pumps automatically started on low-low steam generator level as expected. The plant stabilized in Mode 3 and remained in Mode 3 until repairs were complete. The cause of the stator ground was determined to be a failure in the 'B' phase of the main generator output breaker. The 'B' phase contact was found to be damaged. Damaged parts were sequestered for investigation and further analysis. After an extensive analysis by the root cause team and the breaker vendor, the root cause of the 'B' phase failure could not be conclusively determined. An independent assessment by external consultants was also inconclusive. Due to obsolescence of the main generator output breaker and difficulties experienced while procuring replacement parts during the breaker repair effort, the main generator breakers are scheduled to be replaced in the next refueling outage.
395 | 3952009004 | 2009-12-16 | QR6 | Manual Reactor Trip | [45 empty] | Summer | P | WE | PO | 46 | On December 16, 2009, VC Summer Nuclear Station (VCSNS) was undergoing a planned downpower to repair main turbine control valve #4. As power was being reduced, the main turbine was manually tripped at approximately 46% reactor power due to elevated turbine vibration. Following the turbine trip, the main steam (MS) dump system failed to operate resulting in actuation of MS power operated relief valves (PORVs) and MS safety valves. Due to increased reactor coolant system (RCS) and main steam pressures, a manual reactor trip was initiated at 1415 hours. The plant was stabilized in Mode 3 and remained in Mode 3 until repairs were completed. The cause of the fault in the MS dump system was determined to be a failed circuit card. Upon replacement of the failed circuit card and repair of the main turbine control valve, the plant returned to power operation on December 17, 2009 at 2002 hours.
395 | 3952014004 | 2014-07-22 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Summer | P | WE | PO | 48 | On 7/22/2014 at 0414, VC Summer Nuclear Station automatically tripped due to low Steam Generator water level in "C" Steam Generator. The trip was the result of the Condensate Bypass Valve, XVB09210-WI, failing to open as required while removing the Condensate Demineralization (WI) System from service during plant startup. With flow removed from the WI system and bypass valve XVB09210-WI closed, condensate flow to the Deaerator Storage Tank (DAST) was isolated. All operating main Feedwater pumps tripped on DAST Low-Low level setpoint. The water level in the Steam Generators decreased and resulted in a reactor trip.<br /><br /> The cause of this event was failure of XVB09210-WI to stroke open due to a failed solenoid actuator and a procedure deficiency in manipulating the WI System. For corrective actions, the solenoid actuator for XVB09210-WI was replaced and the system operating procedure for the WI system has been revised to direct the operator to verify that XVB09210-WI is has actuated open before reducing the flow through the Condensate Polishing Demineralizers.<br /><br /> This report is submitted in accordance with 10CFR50.73(a)(2)(iv)(A).
395 | 3952017002 | 2017-06-29 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Summer | P | WE | PO | 100 | On June 29, 2017 at 0857, VCSNS Unit 1 automatically tripped due to low Feedwater (FW) flow to the 'B' Steam Generator (SG). The trip was the result of a spurious closure of the Main FW to 'B' Steam Generator Flow Control Valve, IFV00488-FW. The Flow Control Valve's closure resulted in low SG level coincident with the low FW flow, which caused an automatic reactor trip. The plant trip response was normal.<br /><br /> The cause of this event was determined to be the inadvertent closure of IFV00488-FW due to solenoid valve failure. The solenoid valve failure appears to be a result of an inadequate solder applied to the solenoid coil during the manufacturing process.
395 | 3952017003 | 2017-08-28 | QR5 | Turbine Trip | [45 empty] | Summer | P | WE | PO | 100 | On August 28, 2017, at 0837, VCSNS Unit 1 automatically tripped due to a turbine trip. The turbine trip was caused by the Main Generator Differential Lockout due to a fault on the center phase, 230 kV lightning arrester, on the Main Transformer (XTF-1). <br /><br /> The plant trip response was normal. All control rods fully inserted. Balance of Plant (BOP) buses automatically transferred to their alternate power source, Emergency Auxiliary Transformers (XTF-31/32). Both Motor Driven (MD) Emergency Feedwater (EF) pumps and the Turbine Driven EF Pump started as designed.<br /><br /> The cause of this event was the failure of the center phase lightning arrester on XTF-1. The failed arrester, along with the other two lightning arresters that were in service on XTF-1 during the reactor trip, was replaced. The lightning arresters were sent to an independent lab, NEETRAC - Georgia Tech, for testing and evaluation. <br /><br /> The examination results indicate that the most probable cause of the arrester failure was an internal flashover of the metal oxide varistor blocks. The cause of the internal flashover is likely moisture ingress from the upper end seal.
395 | 3952017005 | 2017-11-07 | QR5 | Turbine Trip | [45 empty] | Summer | P | WE | PO | 100 | At 1957 on November 07, 2017, VCSNS Unit 1 was operating. in Mode 1 at 100% reactor power when a turbine trip caused an automatic reactor trip. All systems responded as expected, with the exception of 'B' Steam Generator Feedwater Isolation Valve (FWIV) XVG1611B-FW. This valve did not appear to automatically close and was slow to indicate closed from the Main Control Board, however this did not complicate the response. All Control Rods fully inserted and all Emergency Feedwater (EFW) pumps started as required. The Operating crew stabilized the plant, which remained in Mode 3 with decay heat removal via the Steam Dump system to the Main Condenser. <br /><br /> The cause of the turbine trip has been determined to be a loss of Digital Control System (DCS) power to all three Main Feedwater Pumps (FWP), which was caused by the failure of Non-Safety Related Inverter XIT5905.
395 | 3952022001 | 2021-11-15 | QR6 | Manual Reactor Trip | [45 empty] | Summer | P | WE | PO | 47 | On November 15, 2021, at approximately 1728 EST with Unit 1 in Mode 1 at 47 percent power, the reactor was manually tripped due to a fault on the B-phase of the main transformer. The turbine tripped automatically based on the reactor trip signal. Emergency Feedwater (EFW) actuation occurred as expected due to the low-low steam generator water levels which occurred as a result of the trip. The trip was not complex with all systems responding normally post trip. Operations stabilized the plant in Mode 3. Decay heat was removed by the steam generators, utilizing the steam dump system. <br /><br /> Due to the manual Reactor Protection System (RPS) actuation and the automatic actuation of the EFW system, this event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A).
397 | 3971987002 | 1987-03-22 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Columbia | B | GE | PO | 71 | POWER LEVEL - 071%. ON 3-22-87 AT 1940 HRS, THE REACTOR WAS MANUALLY SCRAMMED AS A RESULT OF AN OBSERVED TRIP OF BOTH REACTOR FEEDWATER (RFW) PUMPS AND RAPIDLY DECREASING REACTOR WATER LEVEL. THE RFW PUMPS TRIPPED BECAUSE OF LOW SUCTION PRESSURE CONDITION AS A RESULT OF RAPID ACCELERATION OF THE PUMPS IN RESPONSE TO AN ERRONEOUS FEEDWATER-STEAM FLOW MISMATCH SIGNAL. THE ERRONEOUS SIGNAL WAS CAUSED BY A BLOWN 0.25 AMPERE FUSE IN A SUMMATION CIRCUIT OF THE FEEDWATER LEVEL CONTROL SYSTEM, RESULTING IN A ZERO FEEDWATER FLOW INPUT. THE CAUSE OF THE FUSE FAILURE IS UNKNOWN AND, BASED UPON EXTENSIVE INVESTIGATION, IS NOT DETERMINABLE. FOLLOWING THE LOSS OF FEEDWATER FLOW, WATER LEVEL DECREASED TO LEVEL-2 (-50') AND ALL REQUIRED ESF AND ELECTRICAL ALIGNMENT ACTUATIONS OCCURRED. DURING THE RECOVERY PROCESS, A VALVE ALIGNMENT ERROR OCCURRED WHICH COMPLICATED RECOVERY OPERATIONS AND RESULTED IN THE FLOODING OF THE MAIN STEAM LINES (MSLS). THE AUTOMATIC ACTIONS THAT OCCUR ON A REACTOR LEVEL-2 INITIATION PRESENT A COMPLICATED SCENARIO. REQUIRED CAN BE SIMPLIFIED BY SPECIFIC TRAINING AND DESIGN CHANGES. SUFFICIENT PIPING SYSTEM INSPECTIONS, COMPONENT TESTING AND DATA ANALYSIS OCCURRED TO ENSURE THAT NO DETRIMENTAL AFFECTS WERE CAUSED BY THE FLOODING OF THE MSLS.
397 | 3971987018 | 1987-06-26 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 42 | POWER LEVEL - 042%. ON JUNE 26, 1987 AT 1541 HOURS, THE REACTOR AUTOMATICALLY SCRAMMED BY REACTOR PROTECTION SYSTEM (RPS) ACTUATION DUE TO TURBINE CONTROL VALVE (TCV) FAST CLOSURE. THE TCV FAST CLOSURE WAS IN RESPONSE TO A UNIT LOCKOUT SIGNAL RESULTING FROM THE ACTUATION OF A SUDDEN PRESSURE RELAY ON NORMAL AUXILIARY POWER TRANSFORMER TR-N1. ON JUNE 27, 1987 AT 1813 HOURS, A SIMILAR EVENT OCCURRED INVOLVING THE SUDDEN PRESSURE RELAY ON NORMAL AUXILIARY POWER TRANSFORMER TR-N2. THE CAUSE OF BOTH SUDDEN PRESSURE RELAY ACTUATIONS WAS DETERMINED TO BE THE UNEXPECTED OPENING OF A TEST (POPPET) VALVE ASSOCIATED WITH THE RELAYS (THE VALVES ARE USED TO TEST THE RELAYS). WHEN THE VALVE OPENED, A DIFFERENTIAL PRESSURE DEVELOPED ACROSS THE BELLOWS OF THE SUDDEN PRESSURE RELAYS. THE RELAYS RESPONDED AS DESIGNED BY CAUSING A GENERATOR TRIP, A TURBINE TRIP AND, BECAUSE REACTOR POWER WAS ABOVE 30%, A REACTOR SCRAM. IN BOTH INSTANCES, PLANT POST-TRIP RESPONSE WAS NORMAL IN ALL ASPECTS. THERE IS NO SAFETY SIGNIFICANCE ASSOCIATED WITH EITHER EVENT IN THAT PLANT PROTECTION SYSTEMS AND ELECTRICAL DISTRIBUTION REALIGNMENTS FUNCTIONED AS DESIGNED . THESE EVENTS POSED NO THREAT TO THE HEALTH AND SAFETY OF EITHER THE PUBLIC OR PLANT PERSONNEL.
397 | 3971987018 | 1987-06-27 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 55 | POWER LEVEL - 042%. ON JUNE 26, 1987 AT 1541 HOURS, THE REACTOR AUTOMATICALLY SCRAMMED BY REACTOR PROTECTION SYSTEM (RPS) ACTUATION DUE TO TURBINE CONTROL VALVE (TCV) FAST CLOSURE. THE TCV FAST CLOSURE WAS IN RESPONSE TO A UNIT LOCKOUT SIGNAL RESULTING FROM THE ACTUATION OF A SUDDEN PRESSURE RELAY ON NORMAL AUXILIARY POWER TRANSFORMER TR-N1. ON JUNE 27, 1987 AT 1813 HOURS, A SIMILAR EVENT OCCURRED INVOLVING THE SUDDEN PRESSURE RELAY ON NORMAL AUXILIARY POWER TRANSFORMER TR-N2. THE CAUSE OF BOTH SUDDEN PRESSURE RELAY ACTUATIONS WAS DETERMINED TO BE THE UNEXPECTED OPENING OF A TEST (POPPET) VALVE ASSOCIATED WITH THE RELAYS (THE VALVES ARE USED TO TEST THE RELAYS). WHEN THE VALVE OPENED, A DIFFERENTIAL PRESSURE DEVELOPED ACROSS THE BELLOWS OF THE SUDDEN PRESSURE RELAYS. THE RELAYS RESPONDED AS DESIGNED BY CAUSING A GENERATOR TRIP, A TURBINE TRIP AND, BECAUSE REACTOR POWER WAS ABOVE 30%, A REACTOR SCRAM. IN BOTH INSTANCES, PLANT POST-TRIP RESPONSE WAS NORMAL IN ALL ASPECTS. THERE IS NO SAFETY SIGNIFICANCE ASSOCIATED WITH EITHER EVENT IN THAT PLANT PROTECTION SYSTEMS AND ELECTRICAL DISTRIBUTION REALIGNMENTS FUNCTIONED AS DESIGNED . THESE EVENTS POSED NO THREAT TO THE HEALTH AND SAFETY OF EITHER THE PUBLIC OR PLANT PERSONNEL.
397 | 3971987019 | 1987-06-28 | QR8 | Spurious Reactor Trip | [45 empty] | Columbia | B | GE | PO | 55 | POWER LEVEL - 055%. ON JUNE 28, 1987 AT 1933 HOURS, A REACTOR SCRAM AND PARTIAL CONTAINMENT ISOLATION OCCURRED WHEN THE REACTOR PROTECTION SYSTEM (RPS) EXPERIENCED A FULL TRIP. AT THE TIME OF THE EVENT, RPS CHANNEL B WAS IN A TRIPPED (HALF-SCRAM) CONDITION DUE TO A FAILED PRESSURE SWITCH IN THE TURBINE GOVERNOR VALVE FAST CLOSURE LOGIC. PLANT PERSONNEL WERE IN THE PROCESS OF REPLACING THE SWITCH WHEN A LOSS OF POWER TO RPS CHANNEL A OCCURRED DUE TO THE TRIPPING OF AN RPS ELECTRICAL PROTECTION ASSEMBLY BREAKER. THE LOSS OF POWER TO RPS CHANNEL A PROVIDED THE SECOND HALF-SCRAM CONDITION AND, BY DESIGN, THE REACTOR AUTOMATICALLY SCRAMMED. THE CAUSE OF THE EVENT WAS DETERMINED TO BE CONCURRENT COMPONENT FAILURES IN BOTH RPS CHANNELS. IN RPS CHANNEL B, THE PRESSURE SWITCH WAS LEAKING, PROBABLY DUE TO CYCLIC FATIGUE. IN RPS CHANNEL A, THE CAUSE OF THE BREAKER TRIPPING APPEARED TO BE THE IMPROPER ALIGNMENT OF THE UNDERVOLTAGE RESTRAINT COIL TO LATCH/ARMATURE ASSEMBLY; HOWEVER, THE CAUSE MAY ALSO HAVE BEEN A SPURIOUS TRIP ASSOCIATED WITH THE LOGIC CARD. THERE IS NO SAFETY SIGNIFICANCE ASSOCIATED WITH THIS EVENT IN THAT THE REACTOR PROTECTION SYSTEM OPERATED AS DESIGNED TO CAUSE A FULL PROTECTIVE TRIP. THIS EVENT POSED NO THREAT TO THE HEALTH AND SAFETY OF EITHER THE PUBLIC OR PLANT PERSONNEL.
397 | 3971987020 | 1987-07-02 | QC4 | Loss of ac Instrumentation and Control Bus. | [10 empty] | X | [28 empty] | X | [5 empty] | Columbia | B | GE | PO | 80 | POWER LEVEL - 080%. THE REACTOR SCRAMMED ON JULY 2, 1987, AT 1216 HOURS, WHILE OPERATING AT 80% POWER. ONE MINUTE PRIOR TO THE SCRAM THE MOTOR OF THE REACTOR PROTECTION SYSTEM (RPS) A MOTOR GENERATOR SET FAILED CAUSING THE LOSS OF RPS A POWER. WHEN PLANT OPERATORS ATTEMPTED TO SWITCH RPS A POWER TO ITS ALTERNATE SOURCE, RPS B POWER WAS LOST. THE DEENERGIZATION OF BOTH RPS POWER BUSES CAUSES, BY DESIGN, A REACTOR SCRAM AN INBOARD AND OUTBOARD ISOLATION OF NUCLEAR STEAM SUPPLY SHUTOFF SYSTEM (NS4) GROUPS 1, 2, 5, 6, AND 7, AND A REACTOR BUILDING EXHAUST PLENUM PROCESS RADIATION SYSTEM 'Z' SIGNAL WHICH INITIATES SEVERAL ENGINEERED SAFETY FEATURE (ESF) SYSTEMS INCLUDING STANDBY GAS TREATMENT (SGT), CONTROL ROOM EMERGENCY FILTRATION SYSTEM, AND A REACTOR BUILDING VENTILATION SYSTEM ISOLATION. INITIALLY, DUE TO THE MSIV CLOSURE (NS4 GROUP 1), REACTOR WATER LEVEL WAS CONTROLLED USING THE REACTOR CORE ISOLATION COOLING SYSTEM (RCIC), AND REACTOR PRESSURE WAS CONTROLLED BY MANUALLY OPENING MAIN STEAM LINE SAFETY RELIEF VALVES (MSRVS). WITHIN ONE HOUR ALL SYSTEMS WERE RESTORED TO THEIR NORMAL LINEUP FOR PLANT CONDITIONS AND A NORMAL PLANT SHUTDOWN FOLLOWED. BY 1910 HOURS ON JULY 2, 1987 THE PLANT WAS IN COLD SHUTDOWN. THE CAUSE OF THE MOTOR FAILURE OF THE RPS 'A' MOTOR GENERATOR SET IS BELIEVED TO BE A PHASE TO GROUND SHORT.
397 | 3971987022 | 1987-07-06 | QC5 | Loss of Non-safety-Related Bus | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Columbia | B | GE | PO | 32 | POWER LEVEL - 032%. ON JULY 6, 1987, AT 0546 HOURS A REACTOR SCRAM ON LOW WATER LEVEL OCCURRED DUE TO THE LOSS OF THE SINGLE (ONE OF TWO) OPERATING REACTOR FEEDWATER (TURBINE) PUMP (RFW-P-1B). THE EVENT OCCURRED WHEN PLANT OPERATORS TRANSFERRED POWER ON PLANT BUS SM-2 (4160V) FROM THE STARTUP POWER SUPPLY TO THE NORMAL POWER SUPPLY. IMMEDIATELY AFTER CLOSING THE NORMAL POWER SUPPLY BREAKER N1-2 THE BREAKER TRIPPED OPEN LEAVING BUS SM-2 DE-ENERGIZED. BUS SM-2 THROUGH PLANT BUS SL-21 (480V) POWERS BOTH THE MAIN AND AUXILIARY CONTROL OIL PUMPS OF THE FEEDWATER TURBINE WHICH TRIPPED DUE TO LOW CONTROL OIL PRESSURE. THE HIGH PRESSURE CORE SPRAY DIESEL GENERATOR (HPCS-DG-3) STARTED ON AN SM-2 UNDER VOLTAGE SIGNAL AND ASSUMED THE LOAD ON CRITICAL BUS SM-4 (4160V). IN RESPONSE TO THE LOSS OF REACTOR FEEDWATER, PLANT OPERATORS MANUALLY INITIATED THE REACTOR CORE ISOLATION COOLING (RCIC) SYSTEM. REACTOR WATER LEVEL DECREASED TO -46 INCHES, NEAR THE REACTOR WATER LEVEL-2 SETPOINT, AND AT -46 INCHES A LEVEL-2 NUCLEAR STEAM SUPPLY SHUTOFF SYSTEM (NSSSS) ISOLATION OCCURRED, INCLUDING A MAIN STEAMLINE ISOLATION. THE RCIC SYSTEM RESTORED REACTOR WATER LEVEL TO NORMAL. THE CAUSE OF THE EVENT WAS A BENT FINGER IN THE C PHASE DISCONNECTING CONTACT FINGER CLUSTER WHICH PREVENTED THE N1-2 BREAKER FROM BEING FULLY INSERTED.
397 | 3971988003 | 1988-02-04 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Columbia | B | GE | PO | 100 | On February 4, 1988, while operating at rated power, at 0150 hours, Plant Instrument and Control (I&C) Technicians inadvertently caused the Main Steamline Isolation Valves (MSIVs) to close, which in turn caused the Reactor to scram when the MSIVs reached the 10 percent-closed position. <br /><br />The I&C Technicians initiated the event by simultaneously tripping one Low Condenser Vacuum channel in each MSIV closure trip system (one out of two twice logic) causing a Nuclear Steam Supply Shutoff System (NSSSS) Group 1 MSIV isolation. The immediate Plant response was as expected. All four Reactor Protection System (RPS) MSIV closure channels tripped and initiated a Reactor scram. Four of the 18 Main Steamline Safety Relief Valves (SRVs) automatically opened to attenuate the reactor pressure transient. Plant Reactor Operators manually initiated the Reactor Core Isolation Cooling (RCIC) System to inject water to the reactor, and they manually opened SRVs to control Reactor pressure. The Reactor water level swell associated with opening the SRVs exceeded the Reactor high water level trip setpoint which caused the RCIC System to shutdown. The maximum reactor water level reached during the event was +78 inches well below the bottom of the Main Steamlines. When reactor water level dropped below the Reactor high water level trip setpoint, the RCIC System was restored. The Plant was maintained in Hot Shutdown (Plant Mode 3) until it was restarted on February 5, 1988 at 1300 hours.
397 | 3971988006 | 1988-02-13 | QR6 | Manual Reactor Trip | [13 empty] | X | [30 empty] | X | Columbia | B | GE | PO | 35 | Following a manual scram initiated due to high reactor coolant conductivity problems on February 13, 1988, a series of Reactor Pressure Vessel (RPV) level transients resulted in an actual low RPV Level Reactor Protective System actuation. The low level condition was initiated by loss of the only running Reactor Feedwater (RFW) Pump and was directly caused by opening the Startup Flow Control Valve while RFW System pressure was 250 psig lower than RPV pressure. This resulted in establishing a previously unrecognized diversion flowpath of reactor coolant from the Reactor Water Cleanup System backward through the Startup Flow Control Valve and to the Main Condenser Hotwell via the Long Cycle Cleanup Flow Control Valve. The root cause of the event was determined to be procedural inadequacy. Plant procedures did not give adequate guidance to the operator to ensure that the RFW System would be operated correctly during situations in which RPV pressure is higher than Reactor Feedwater System pressure. <br /><br />Corrective Actions consisted of: <br /><br />Modifying the RFW Speed Control System to eliminate undesirable speed ramp characteristics, modification of operating procedures to add sufficient guidance for RFW System operations, evaluation of the need for Simulator Training, required reading of this LER, evaluation of RPV level management policy, repair of the condensate pump minimum flow control valve and evaluation of the need for feedwater system design changes. During the event all manual and automatic safety system responses occurred as designed. This event posed no threat to the safety of Plant personnel or the public.
397 | 3971989002 | 1989-01-30 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 100 | On January 30, 1989, at 0514 hours, a Reactor Scram occurred due to Turbine Control Valve Fast Closure actuation of the Reactor Protective System logic. This logic was actuated when the main generator 50OKV output breakers tripped as a result of high currents created when a porcelain insulator on the output side of 25/50OKV main transformer TR-Ml shorted to ground. Plant operators responded to maneuver the plant to a safe shutdown condition. The damaged 50OKV insulator stack was replaced. All other 50OKV and 115KV insulators in the transformer yard were cleaned and inspected. Transformer TR-Ml was tested to determine its acceptability for continued use. The immediate cause of the insulator failure was the build up of a chemical residue deposited by the vapor plume from the Circulating Water System cooling towers. This residue was found to be conductive when wet. The residue consisted of river water minerals and sulfate compounds generated by sulfuric acid addition used to control the ph of circulating water.<br /><br /> Two root causes were identified: 1) Equipment Design Deficiency (problem not anticipated ) The insulators used at WNP-2 are not of the type or number recommended for contaminated environments. 2) Equipment Maintenance Deficiency. No formal maintenance/inspection program existed which specifically identified this equipment. The corrective actions consist of performing an evaluation to determine the need for design changes to the insulators and implementation of a preventative maintenance program to cover these insulators. No safety significance was associated with this event.
397 | 3971989028 | 1989-06-29 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 25 | On June 29, 1989, at 0020 hours, during testing of the Main Turbine Overspeed Protection Controller (OPC), a Turbine Throttle Valve Closure Reactor Scram occurred. At the time of the scram, the turbine was operating in throttle valve control coasting down from the OPC actuation setpoint of 1854 RPM. After three unsuccessful attempts to input an 1800 RPM speed demand, the operator decided to wait until actual turbine speed had dropped below 1800 RPM to try again. After turbine speed dropped below 1800 RPM, the operator keyed in another 1800 RPM reference demand at 50 RPM per minute as specified in the procedure. This input was accepted by the turbine control system. The operator, as directed by the procedure, then returned turbine control to the "IN SERVICE" position with the OPC keylock switch. This resulted in rapid opening of the turbine governor and throttle valves and subsequent pressurization of the turbine first stage chamber Since the throttle valves were less than 95% open at this point, this caused actuation of the tubine first stage pressure switches causing the scram logic to be met resulting in a turbine throttle valve closure reactor scram. The root cause of the event was a less than adequate procedure in that the turbine operating procedure did not prevent the OPC test from being done with the turbine in the throttle valve control mode. Corrective actions taken consist of deviation of the operating procedure. The operator training program will be improved in this area. Since all safety systems operated as designed and the plant operators acted promptly to place the plant in a safe shutdown condition this vent posed no threat to the health or safety of plant personnel or the public.
397 | 3971989031 | 1989-08-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Columbia | B | GE | PO | 100 | At 2027 hours on August 6, 1989, a low Reactor Pressure Vessel (RPV) level Reactor Scram was initiated by the Reactor Protective System in response to an actual low water level condition caused by an unplanned trip of Reactor Feedwater Pump 1B (RFW-P-1B). The scram occurred during surveillance testing of the auxiliary and emergency lube oil pumps for Reactor Feedwater Turbine 1B (RFW-DT-1B) with the plant at 100% power. When a solenoid operated drain valve was actuated to depressurize only the auto start pressure switch for the auxiliary lube oil pump, the entire "B" feedwater pump lube oil system was subjected to a low lube oil pressure transient sufficient to cause a low lube oil trip of RFW-P-1B. The remaining feedwater pump was unable to supply enough capacity to maintain RPV level above the reactor scram setpoint. The root cause investigation is still in progress. Two major areas have been identified: 1) Inappropriate RRC FCV Runback setpoint coupled with the change in feedwater pump governor maximum speed capability; 2) Inadvertent trip of RFW-P-1B on low lube pressure during testing of the auxiliary and emergency oil pumps. <br /><br /> Corrective actions consist of: <br /><br /> 1. Revision of the operating procedure for reactor feedwater pumps to incorporate instruction to ensure that the test pushbutton is depressed for a sufficient length of time during feedwater turbine startup to assist adequate venting of the lube oil system.
397 | 3971989035 | 1989-08-17 | QR8 | Spurious Reactor Trip | [45 empty] | Columbia | B | GE | PO | 67 | At 0819 hours, on August 17, 1989, a reactor scram occurred during a surveillance being performed on a reactor level instrument associated with the Automatic Depressurization System (ADS). The scram occurred when an I&C technician prematurely opened the isolation valve from the reference instrument leg of the device being tested. This caused a pressure transient in the reference and variable instrument lines which initiated a reactor scram by the Reactor Protection System (RPS) on reactor water level low - Level 3. The root cause of this event was a personnel error and equipment design deficiency. Immediate corrective action included plant shut down to hot standby and a memo from the Plant Maintenance Manager summarizing immediate corrective actions. Further corrective action includes improved training and increased visibility for "Critical" surveillances. A design study will also be initiated to evaluate the design of the level trip system and its interfacing instrumentation. Since all safety systems operated as designed and plant operators acted promptly to place the plant in a safe shutdown condition, this event posed no threat to the health and safety of the plant personnel or the public.
397 | 3971990021 | 1990-09-25 | QR6 | Manual Reactor Trip | [45 empty] | Columbia | B | GE | PO | 45 | At 0557 hours on September 25, 1990 plant operators manually scrammed the reactor after experiencing main turbine hydraulic control oil pressure problems in the Digital Electro-Hydraulic (DEH) system. The DEH system provides automatic and manual control of the main turbine generator by positioning the turbine steam admission and bypass valves. The positioning of these valves also affects reactor pressure and power.<br /><br /> The cause of this event was traced to a broken pipe nipple in the Auto Stop oil header portion of the Turbine Lube Oil (TO) System. This resulted in a decrease in pressure in the DEH system. The preliminary root cause of the event was traced to the improper installation of a stabilizer strap that may have contributed to the failure. The installation combined with the unanticipated vibration in the area of the pipe nipple led to fatigue failure. <br /><br /> Immediate corrective action was taken to place the plant in a cold shutdown condition. All systems and components performed as designed. Plant maintenance personnel replaced the broken nipple and reinstalled the relief valve and the stabilizer strap. <br /><br /> The event posed no threat to the health and safety of either the public or plant personnel.
397 | 3971990031 | 1990-12-07 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 100 | On December 7, 1990 at 1010 hours, a reactor scram occurred due to actuation of the Reactor Protection System (RPS) logic. The initiating scram signal was "turbine governor valve fast closure" due to a Main Turbine/Generator trip with reactor power greater than 30 percent. The logic was actuated when the Main Generator 500 KV output breakers tripped as a result of high currents created when a procelain insulator in the Transformer Yard shorted to ground. The insulator is on the ouput side of 25/500 KV Main Transformer TR-M2 B" Phase). The electrical fault (flashover) was due to Circulating Water (CW) System Cooling Tower water chemical deposits having built up on the insulator, with wet and icing conditions contributing to provide a conductive path over the surface of the insulator. <br /><br /> At 1019 hours, an "Unusual Event" was declared as directed by the Emergency Classification procedure due to the resulting fault caused explosion within the Protected Area (Transformer Yard). At 1030 hours, the reactor scram was reset and, at 1100 hours, the "Unusual Event" was terminated. <br /><br /> The root causes of this event were: 1) a less than adequate corrective action plan pertaining to the schedule and scope for inspecting and cleaning the 500 KV insulators, and 2) a less than adequate Plant design in that the Transformer Yard is situated in a prevailing, high-speed wind pattern location that results in the insulators being vulnerable to chemical drift deposition.
397 | 3971991032 | 1991-11-19 | QP5 | Excessive Feedwater Flow | [45 empty] | Columbia | B | GE | PO | 100 | On November 19, 1991 at 0741, a reactor scram occurred as a result of Main Turbine Governor Valve Fast Closure initiated by a turbine trip signal from Reactor Pressure Vessel (RPV) high water level signal at Level 8 or +54.5 inches. Later, the High Pressure Core Spray (HPCS) System automatically injected as RPV level approached Level 2 (-50 inches). The high reactor water level was caused by a component failure in the non-safety related Feedwater Level Control (FWLC) System which resulted in the acceleration of the Reactor Feedwater (RFW) pumps in response to an erroneous feed-flow/steam-flow mismatch signal. The erroneous signal was caused by a failed capacitor in a Bailey Type 752 feed flow summation card in the FWLC System, which resulted in opening the 1.0 ampere circuit protection fuse. Low RPV level occurred later as a result of inadequate coolant makeup after the RFW pumps tripped at Level 8. <br /><br /> The immediate corrective action was prompt response by the Plant Operators to maneuver the Plant to a safe shutdown condition and to implement appropriate Plant procedures in a timely manner. <br /><br /> The root cause for failure of the Feed Water Level Control (FWLC) System was a failed capacitor in the feedwater summation circuitry.
397 | 3971991035 | 1991-12-20 | QL6 | Condenser Leakage | [45 empty] | Columbia | B | GE | PO | 20 | On December 20, 1991 at 1250 hours the Plant was manually scrammed to complete a controlled shutdown due to high reactor coolant conductivity. During the event period, Plant personnel were in the process of attempting to identify the source of a suspected Main Condenser tube leak. This troubleshooting effort was being performed as a result of two conductivity excursions that had recently occurred, but where Technical specification limits were not reached. <br /><br /> During troubleshooting efforts, a leak of approximately 65 gpm developed in Section A of the Main Condenser, and conductivity levels increased. Efforts by Plant personnel to control the conductivity excursion by reducing reactor power and securing one of three Circulating Water (CW) System pumps were unsuccessful. Accordingly, Plant Control Room Operators took appropriate and timely action to shutdown the Plant and maneuver to the cold shutdown condition. <br /><br /> The cause of this event was a failed tube in the Main Condenser. An axial rack, approximately 8 to 12 inches in length, was later discovered on an interior tube. Corrective actions consist of 1) plugging the failed tube and performing sonic leak testing of all condenser tubes, 2) performing a Management Evaluation to resolve problems associated with conductivity excursions, and 3) performing Nondestructive Examination (Eddy Current Testing) of tubing during the Spring 1992 Maintenance and Refueling Outage. This event is reportable in accordance with 10CFR50.73 as a completion of any shutdown required by the Plant Technical Specifications.
397 | 3971992033 | 1992-07-06 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Columbia | B | GE | PO | 16 | POWER LEVEL - 016%. This LER reports on events which occurred on July 6 and 11, 1992. On these dates, after being manually opened to support Plant testing, Safety/Relief Valve (SRV) MS-RV-3B failed to reseat at the required pressure. The failure to reseat within two minutes on both occasions resulted in manual scrams of the reactor as required by the Plant's Technical Specifications. <br /><br /> Following the July 6th event, a root cause investigation determined that two adjusting rings within the SRV were found set at the wrong positions. <br /><br /> This misadjustment directly impacts the reseat pressure. A solenoid valve in the valve's pneumatic actuator also was found to not stroke freely. The rings were reset, the solenoid valve was replaced, and following additional testing of MS-RV-3B, the Plant was restarted. On July 11th during startup from the July 6th event MS-RV-3B again failed to reseat at the proper pressure. A detailed investigation revealed that the valve disk ring, replaced during valve refurbishment in early 1992, was improperly sized. The required disk ring size was modified in 1979. The Supply System was not notified by the supplier that the spare disk ring, purchased in 1976 and installed in 1992, was not acceptable for use due to modifications made to the SRV design in 1979. <br /><br /> The root cause of the July 6th event was inadequate vendor support of change management in that the supplier failed to notify the Supply System that without the appropriate modification the spare disk rings were no longer acceptable for use The root cause for the improperly adjusted nozzle and adjustment rings was personnel error in that self-checking was not applied to ensure the proper ring setting were achieved during refurbishment. In addition, the work instructions failed to provide for QC verification of the settings as had previously been Plant practice. The root cause for the failure of the valve to reseat at the proper pressure on July 11, 1992 was Assumed Risk. The preliminary root cause determination completed after the July 6th event concluded that the misadjusted rings in MS-RV-3B, and a sticking solenoid valve in the actuator, were the probable root causes of the failure to reseat at the proper pressure. These probable root causes and associated repairs, in conjunction with the extensive successful testing which had been completed for the valve and actuator, led to the decision to restart. A review has been performed of other SRV spare parts at WNP-2 and the parts have been verified to be acceptable for use in the modified SRV design installed at the Plant. "Self-checking" training will be provided to Maintenance personnel by November 30, 1992.<br /><br /> MS-RV-3B reseated at 940 and 888 psig on July 6 and 11, respectively. These pressures are well within the design limits for WNP-2 but do not meet the valve manufacturers specified reseat range for this model of valve. The temperature transients experienced are not a concern for the Plant. Therefore, these events were not safety significant. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
397 | 3971992033 | 1992-07-11 | G2 | Stuck Open (1 Safety Relief Valve) | [6 empty] | X | [19 empty] | X | [18 empty] | Columbia | B | GE | PO | 14 | POWER LEVEL - 016%. This LER reports on events which occurred on July 6 and 11, 1992. On these dates, after being manually opened to support Plant testing, Safety/Relief Valve (SRV) MS-RV-3B failed to reseat at the required pressure. The failure to reseat within two minutes on both occasions resulted in manual scrams of the reactor as required by the Plant's Technical Specifications. <br /><br /> Following the July 6th event, a root cause investigation determined that two adjusting rings within the SRV were found set at the wrong positions. <br /><br /> This misadjustment directly impacts the reseat pressure. A solenoid valve in the valve's pneumatic actuator also was found to not stroke freely. The rings were reset, the solenoid valve was replaced, and following additional testing of MS-RV-3B, the Plant was restarted. On July 11th during startup from the July 6th event MS-RV-3B again failed to reseat at the proper pressure. A detailed investigation revealed that the valve disk ring, replaced during valve refurbishment in early 1992, was improperly sized. The required disk ring size was modified in 1979. The Supply System was not notified by the supplier that the spare disk ring, purchased in 1976 and installed in 1992, was not acceptable for use due to modifications made to the SRV design in 1979. <br /><br /> The root cause of the July 6th event was inadequate vendor support of change management in that the supplier failed to notify the Supply System that without the appropriate modification the spare disk rings were no longer acceptable for use The root cause for the improperly adjusted nozzle and adjustment rings was personnel error in that self-checking was not applied to ensure the proper ring setting were achieved during refurbishment. In addition, the work instructions failed to provide for QC verification of the settings as had previously been Plant practice. The root cause for the failure of the valve to reseat at the proper pressure on July 11, 1992 was Assumed Risk. The preliminary root cause determination completed after the July 6th event concluded that the misadjusted rings in MS-RV-3B, and a sticking solenoid valve in the actuator, were the probable root causes of the failure to reseat at the proper pressure. These probable root causes and associated repairs, in conjunction with the extensive successful testing which had been completed for the valve and actuator, led to the decision to restart. A review has been performed of other SRV spare parts at WNP-2 and the parts have been verified to be acceptable for use in the modified SRV design installed at the Plant. "Self-checking" training will be provided to Maintenance personnel by November 30, 1992.<br /><br /> MS-RV-3B reseated at 940 and 888 psig on July 6 and 11, respectively. These pressures are well within the design limits for WNP-2 but do not meet the valve manufacturers specified reseat range for this model of valve. The temperature transients experienced are not a concern for the Plant. Therefore, these events were not safety significant. <br /><br /> This event posed no threat to the health and safety of either the public or Plant personnel.
397 | 3971992037 | 1992-08-15 | QR3 | Reactivity Control Imbalance | [45 empty] | Columbia | B | GE | PO | 33 | At 0301 hours on August 15, 1992, the reactor was manually scrammed due to indications of core instability. Plant control room operators noted Average Power Range Monitors (APRMs) swinging between 25 % and 45 % power with numerous Local Power Range Monitor (LPRM) downscale indications. The plant was scrammed within 80 seconds after the oscillations were detected. <br /><br /> The root cause for this oscillation event has been determined to be unanticipated interaction of operating conditions and components. The primary reason for the oscillation was the skewed radial and axial power distribution in the reactor. The Supply System staff and vendor personnel failed to identify the extent of the tendency for this core design to become unstable under certain operating practices. bundles and 74% 8x8s. The 9x9s have a higher pressure drop compared with 8x8 fuel. In addition, the 9x9 fuel assemblies were operated at a higher power relative to the 8x8s. These conditions led the core to be susceptible to power oscillations. <br /><br /> When the first recirculation flow control valve (FCV) was closed, in preparation for the recirculation pump shift to high speed, thermal- hydraulic instability was initiated and self-limiting power oscillations followed. The event was terminated by a manual reactor scram. <br /><br /> Short-term corrective actions were taken to revise operating strategies and related procedures to preclude identified precursor conditions and increase precautions and controls during operation at low power levels. Long-term design process, operating, and management corrective actions are also being pursued.
397 | 3971993002 | 1993-01-21 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Columbia | B | GE | PO | 100 | On January 21, 1993, at 0948 hours, a low Reactor Pressure Vessel (RPV) level reactor scram was initiated by the Reactor Protection System (RPS) in response to an actual low water level condition. The low RPV level was caused by a 'high thrust bearing wear' trip of the Reactor Feedwater (RFW) Pump 1A turbine. The trip signal was generated as a result of wetted vibration sensing circuitry caused by an inadvertent actuation of the RFW Pump Room 'A' fire protection deluge system. The remaining RFW pump was unable to supply enough water to maintain RPV level above the reactor scram setpoint. This was due to the failure of the Reactor Recirculation (RRC) Pump Flow Control Valves to automatically reposition (runback) to reduce reactor power and steam flow to within the capacity of one RFW pump.<br /><br /> The immediate corrective action was prompt response by the Plant Operators to bring the plant to a safe shutdown condition in accordance with approved Plant Operating Procedures. <br /><br /> Three root causes for this event have been identified: <br /><br /> 1. Personnel/work practices error causing the inadvertent actuation of the RFW Pump Room 'A' fire protection deluge. <br /><br /> 2. Management methods/work organization planning effort in that there was no method in the painting prejob planning process to provide the painters with precautionary information relating to sensitive equipment.<br /><br /> 3. Plant equipment/design configuration and analysis error in that the RFW Pump Room fire protection manual discharge stations are not well suited for an industrial machinery environment. <br /><br /> This event posed no threat to the safety of the public or plant personnel.
397 | 3971993006 | 1993-02-06 | QR6 | Manual Reactor Trip | [45 empty] | Columbia | B | GE | PO | 30 | At 0947 hours on February 6, 1993, control room operators at WNP-2 initiated a manual scram after the Reactor Recirculation Pump 1A (RRC-P-1A) tripped during an attempt by the operators to transfer the pump from slow speed to high speed (15 Hz to 60 Hz). During the pump shift, RRC-P-1A tripped, leaving the unit in single recirculation loop operation while operating in the Area of Increased Awareness. A manual reactor scram is the required response to this event, in accordance with PPM 4.12.4.7, 'Unintentional Entry Into the Region of Potential Core Power Instabilities'. <br /><br /> After inserting the manual scram to exit the prohibited area, the immediate corrective action was the prompt response by the operators to bring the plant to a safe shutdown condition in accordance with approved plant procedures. <br /><br /> The root cause is that the risks and consequences associated with a change were not adequately reviewed or assessed. A second root cause for this event has been categorized as a component was not operated within the component design parameters in that the power level and feed flow conditions, at which the transfer to high speed was attempted were not within the acceptable parameters to satisfy to logic circuitry. As a corrective action the RRC system operating procedure was changed. Contributing factors were the operating constraints placed on the plant as a result of the power oscillation event which resulted in the RRC pump shift attempt at the lower power level. Abstract (Cont'd) The event posed no threat to the health and safety of either the public or plant personnel.
397 | 3971993007 | 1993-02-10 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Columbia | B | GE | PO | 94 | On February 10, 1993, at 1727 hours, a low Reactor Pressure Vessel (RPV) level reactor scram was initiated by the Reactor Protection System (RPS) in response to an actual low water level condition. The low RPV level was caused by the loss of Reactor Feedwater (RFW) Pump 1B due to a loss of turbine governor control. <br /><br /> At 1730 hours, steam was observed at the entrance to RFW Pump Room "B", and at 1739 hours, the steam supply to the RFW Pump 1B turbine was isolated. An Unusual Event was declared at 1750 hours to enhance increased awareness of plant personnel. Investigation of the steam in the pump room determined the source to be an RFW Pump 1B suction side relief valve and pump casing drain line. <br /><br /> At approximately 1800 hours, an unplanned Engineering Safety Features (ESF) automatic High Pressure Core Spray (HPCS) suction valve switchover occurred due to an actual high Suppression Pool water level. The high water level resulted from Main Steam Relief Valve (MSRV) discharge to the Suppression Pool during manual actuation for RPV pressure reduction. <br /><br /> The immediate corrective actions were prompt response by Plant Operators to bring the plant to a safe shutdown condition, and to restore HPCS suction to the normal configuration.<br /><br /> The root cause of this event was less than adequate evaluation of corrective actions to prevent recurrence of RFW pump turbine governor actuator connector pin corrosion and failure. Further corrective actions will perform a failure analysis of the connector and implement action(s) to eliminate the connector pin corrosion. <br /><br /> This event posed no threat to the health and safety of either the public or plant personnel.
397 | 3971993027 | 1993-08-03 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Columbia | B | GE | PO | 100 | At 0539 hours on August 3, 1993, during performance of a surveillance procedure to calibrate Main Steam Radiation Indicating Switch MS-RIS-610D, the reactor unexpectedly scrammed from 100% power due to a full isolation of the Main Steam Isolation Valves (MSIVs). The isolation was due to higher than normal steam flow through three of the main steam lines. <br /><br /> Control Room personnel immediately implemented the Emergency Operating Procedures to stabilize the plant in a safe shutdown condition. Additionally, shift management declared an Unusual Event (UE) to promote increased awareness on the part of plant operating staff. <br /><br /> There were three root causes of the MSIV isolation/r actor scram: self-checking not applied, job scoping not thorough, and post-maintenance testing inadequate. Further corrective action consisted of performing a failure analysis on a failed MSIV component and determining the operability of all of the MSIVs. <br /><br /> This event posed no threat to the safety of the public or plant personnel.
397 | 3971994008 | 1994-04-26 | QR6 | Manual Reactor Trip | [45 empty] | Columbia | B | GE | PO | 50 | At 1010 hours on April 26, 1994, with the plant at 50% reactor power and 55% core flow, plant Control Room Operators (CROs) observed slight reactor power fluctuations on the six average power range monitors (APRMs). Based on an indication of potential core instabilities, Control Room personnel manually scrammed the reactor in accordance with Plant Abnormal Operating Procedure PPM 4.12.4.7, 'Unintentional Entry Into Region of Potential Core Power Instabilities.'<br /><br /> Immediate corrective actions were taken by the Control Room staff to bring the plant to a safe shutdown condition in accordance with Emergency Operating Procedure (EOP) 5.1.1, 'RPV Control,' and Recovery Procedure PPM 3.3.1, 'Reactor Scram.' <br /><br /> The root causes for this event were the degraded condition of a Reactor Recirculation (RRC) flow control valve (FCV) position transmitter and the lack of procedural criteria to determine when to 'lock up' the degraded FCV. <br /><br /> Further corrective actions include: (1) replacement of the RRC FCV position transmitters, (2) calibration and testing of the replacement FCV position transmitters, and (3) required reading of this Licensee Event Report (LER) by WNP-2 licensed operators. <br /><br /> This event posed no threat to the health and safety of either the public or plant personnel.
397 | 3971995002 | 1995-02-18 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 78 | An automatic scram of the reactor occurred on February 18, 1995 at 1228 hours due to erroneous positioning of a control during performance of a scheduled periodic functional test of the Main Turbine Generator trip system. Plant systems performed as expected, except for an anomalous opening of one main steam relief valve which promptly reclosed without contributing to the event or hindering recovery. Scram recovery was uneventful. Immediate corrective action was taken to reposition the control, and to initiate scram recovery activities per standard procedures. The reactor scram was reported at 1424 hours via the Emergency Notification System per 10 CFR 50.72(b)(2)(ii) as an automatic actuation of the Reactor Protection System.
397 | 3971995004 | 1995-02-26 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 100 | At 1739 hours on February 26, 1995, with WNP-2 in operational Condition 1 (Power operation) at 100% power, a malfunction in the main turbine digital electro-hydraulic (DEH) control system caused all four high pressure turbine governor valves to rapidly close. The resulting decrease in steam load caused reactor pressure and power to increase until a scram on high neutron flux occurred. All control rods inserted normally. operators completed the scram recovery procedure and placed the reactor in a stable condition. Plant systems and components operated as expected and the recovery was uneventful.<br /><br /> The cause of the DEH system malfunction was a blown fuse on a circuit card that processes the governor valve position limit signal. The cause of the blown fuse is believed to have been a failure on the circuit card. The suspected faulty circuit card was replaced and the DEH system retested satisfactorily.<br /><br /> This event is bounded by the turbine trip transient evaluated in WNP-2's Final Safety Analysis Report and had negligible safety significance.
397 | 3971995006 | 1995-04-05 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 100 | At 0957 hours on April 5, 1995, with WNP-2 at 100% power, a main turbine trip occurred during performance of a surveillance test. When a high reactor water level condition was simulated by opening the equalizing valve on the channel B differential pressure transmitter, the main turbine and one reactor feed pump turbine tripped. This trip occurred because a normally energized Agastat relay in channel A had previously failed in an intermediate position, generating a second trip signal. The reactor scrammed on the turbine governor valve fast closure signal that resulted from the turbine trip. All control rods inserted normally. Operators placed the reactor in a stable condition. <br /><br /> The cause of the relay failure was heating of the coil due to shorted windings. The failed relay was replaced. <br /><br /> This event, which is bounded by analysis in WNP-2's Final Safety Analysis Report, had negligible safety significance.
397 | 3971996004 | 1996-06-24 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Columbia | B | GE | PO | 29 | On June 24, 1996 at 1003, with the plant operating at 29 percent power in Mode 1, the plant was manually scrammed by control room personnel due to a reactor water level transient experienced during testing of the Digital Feedwater (DFW) system. After performing a step of the test procedure which reduced reactor level by 6 inches, reactor level continued to decrease past the intended 6 inches. Control room personnel took manual control of the reactor feedwater system but were unable to recover level control prior to receiving a Reactor Protection System (RPS) 'B' low level half scram. When the half scram was received the reactor was manually scrammed per direction of the control room supervisor. <br /><br /> Event notification was made to the NRC pursuant to the requirements of 10 CFR 50.72(b)(2) as an Engineered Safety Feature (ESF) actuation. <br /><br /> The cause of the event was determined to be a manufacturer's programming error in the DFW system testing software which was later corrected. <br /><br /> The safety significance of this event is minimal.
397 | 3971997004 | 1997-03-27 | QR6 | Manual Reactor Trip | [45 empty] | Columbia | B | GE | PO | 46 | On March 27, 1997 at 0907 hours with the plant in Mode 1 at 46 percent power, plant operators manually scrammed the reactor as required by the Technical Specifications due to indication of entry into Region A of the power-to-flow map during Reactor Recirculation (RRC) and Reactor Feedwater (RFW) System testing. (It was determined by followup, engineering analyses that Region A of the power-to-flow map had not been entered.) The post-modification testing was being performed to demonstrate that the feedwater level control system and recirculation flow runback feature would avoid a scram following the trip of a single reactor feedwater pump during power operation. During the test and after the planned trip of pump RFW-P-1B, an expected reactor recirculation pump speed runback to 27 Hz was observed. Following this planned runback, a second unexpected runback to 15 Hz occurred which, based upon evaluation of plant heat balance data, appeared to have placed the reactor into Region A of the power-to-flow map. The second runback was caused by a reactor recirculation pump differential temperature cavitation interlock condition. Plant operators responded conservatively by immediately scramming the reactor and maneuvering the plant to a safe shutdown condition in accordance with procedures. The root cause of this event was inadequate attention to detail and a lack of a questioning attitude during the design phase of the modifications for the adjustable speed drive and digital feedwater level control systems. Corrective actions included the establishment of internal and external event evaluation teams to investigate the event, and successfully repeating the reactor feedwater pump trip test. There were no indications of power oscillations during the event period. This event posed no threat to the health and safety of the public or plant personnel.
397 | 3971998002 | 1998-03-11 | QL5 | Partial Closure of MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Columbia | B | GE | PO | 100 | At 0516 on March 11, 1998, with the plant operating at 100% power in Mode 1, WNP-2 experienced a plant transient and SCRAM initiated by closure of a single inboard main steam isolation valve (MSIV), MS-V-22D. Immediately after closure of the single MSIV, a reactor SCRAM occurred due to instantaneous high neutron flux, and steam flow was diverted to the remaining three steam lines, causing a high steam line flow condition of 140% flow, and automatic isolation of all MSIVs. Reactor Pressure Vessel (RPV) pressure immediately peaked and was limited to approximately 1090 psig by automatic lifting of two main steam safety relief valves (MSRVs). Due to the pressure peak, sensed vessel level decreased to Level 2 which caused initiation of the Reactor Core Isolation Cooling (RCIC) and High Pressure Core Spray (HPCS) systems. Approximately 60 seconds after the SCRAM, reactor level recovered to above Level 8 causing automatic curtailment of RCIC and HPCS injection. When level subsequently dropped to below the high level trip setpoint, RCIC was manually restarted for RPV level control, and pressure was being controlled by manual MSRV operation. Due to loss of drywell cooling, drywell pressure peaked at about 1.60 psig approximately 11 minutes into the event. The drywell pressure peak caused automatic starting of the emergency diesel generators, and partial makeup of low pressure Emergency Core Cooling System (ECCS) start logic (nominal setpoint at 1.68 psig). At approximately 50 minutes into the event, a second reactor SCRAM occurred due to RPV low level at + 13 inches. This second SCRAM is the subject of LER 98-003. The cause of the closure of MS-V-22D was loss of pneumatic actuating supply pressure due to a cyclic fatigue failure of the supply line tubing. The tubing was reworked to a configuration less susceptible to cyclic fatigue, and other MSIV supply tubing configurations were inspected. The safety consequences of this event were minimal.
397 | 3972000003 | 2000-06-26 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 100 | At 0825 hours PDT on June 26, 2000, with the plant in Mode 1 at 100% power, WNP-2 experienced a Unit Trip. This resulted in the tripping of the 500 kV power circuit breakers and exciter breaker, tripping the station auxiliary breakers, closing of the breakers to supply offsite power from the startup transformer and tripping of the main turbine. The turbine trip in turn initiated a reactor SCRAM. The unit trip was initiated by a signal from the Main Generator and Transformer Overall Differential protection relaying. Immediately after the reactor SCRAM, two main steam relief valves (MSRV) automatically opened on high pressure. Emergency operating procedures were entered on Reactor Pressure Vessel (RPV) low level (+13"), RPV Pressure High (1060 psig), Suppression Pool Level High, and subsequently Suppression Pool Temperature High. Main Steam Bypass Valve #1 (MS-V-160D) temporarily remained open causing the reactor pressure to decrease to approximately 500 psig. The reactor water level increased to level 8 resulting in a trip of the main feedpumps. The pressure decrease was controlled by operator action to close the Main Steam to Auxiliaries Isolation Valve (MS-V-146). The reactor cool down rate limit was not exceeded. Operators restored reactor level to within the normal shutdown limits by a controlled condensate booster pump injection and maintained subsequent reactor vessel level and pressure with the Start-up RPV Level Controller and MSRVs. The cause of the Main Generator and Transformer Overall Differential protection relay trip was a short to ground in an unused tap of one of the 500 kV current transformer's (CT) secondary control circuit wiring. This caused an unbalanced phase current signal to be sent to the relay causing it to actuate.
397 | 3972000007 | 2000-09-18 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Columbia | B | GE | PO | 65 | On September 18, 2000 at 1425 control room operators received an offgas condenser low-level alarm, and noticed a rapid increase in condenser offgas flow while reactor power was at 100%. In response to increasing turbine back pressure, the operators began lowering reactor power. At 1509, with reactor power at 65% and condenser vacuum at 24 inches Hg, control room operators manually scrammed the reactor as directed by plant procedures. A turbine trip occurs automatically at a condenser vacuum of 20 inches Hg. Plant systems responded as expected following the manual reactor scram. Immediate actions included stabilizing the plant in Mode 3 then commencing a plant cooldown to Mode 4 to investigate the cause of the event. The reason for the loss of condenser vacuum was determined to be a broken turbine "slop" drain line. A four-hour event notification phone call was made to NRC headquarters per the requirements of 10 CFR 50.72(b)(2)(ii).
397 | 3972003007 | 2003-06-30 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 79 | On June 30, 2003 while operating at 79% power, Columbia Generating Station automatically scrammed due to a main transformer differential current relay actuation. All equipment operated within design parameters. The cause of the relay actuation was traced to an insulation failure on a current transformer secondary wire that created an impedance unbalance in the sensing circuitry. The root cause of this event is the original construction use of non jacketed cable (single conductor wiring) which is more prone to failure due to fretting action. Corrective actions were to replace main transformer current transformer wiring with jacketed cable. Jacketed cable has heavier insulation which is less susceptible to fretting. The plant's normal transformers were inspected and similar wiring was found in ideal condition.
397 | 3972004004 | 2004-07-30 | QR0 | RCS High Pressure (RPS Trip) | [45 empty] | Columbia | B | GE | PO | 100 | On July 30, 2004, Columbia Generating Station (Columbia) was in Mode 1 with the reactor operating at-100 percent power. At 09:23 PDT, the reactor automatically scrammed when the reactor protection system (RPS) received trip signals from three out of four reactor steam dome pressure - high instrument channels. The high reactor steam dome high-pressure condition was a result of a turbine governor valve (MS-V-GV/1) drifting closed. The turbine governor valve drifted closed due to a failure of a bypass capacitor on a NUCANA Servo Driver (NSD) circuit board associated with the governor valve electro-hydraulic control system. The failed capacitor was a monolithic ceramic capacitor. This capacitor provides high frequency bypass filtering for the onboard power supply at one of the operational amplifiers. The capacitor failed with low resistance which caused a high current load that eventually caused the circuit board protective fuse to clear and the closure of MS-V-GV/1. This event posed no threat to the health and safety of the public. The NSD circuit board was replaced and a detailed failure analysis will be performed on the failed circuit board.
397 | 3972004005 | 2004-08-15 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Columbia | B | GE | PO | 18 | During a reactor startup on August 15, 2004, with reactor power at approximately 18%, plant operators manually initiated the Reactor Protection System in response to decreasing water level in the Reactor Pressure Vessel (RPV) following a reactor feedwater pump (RFW-P-1A) trip. The steam driven RFW-P-1A tripped as designed due to high water level in the pumped drain tank. The Reactor Core Isolation Cooling system was initiated to maintain RPV level until pressure was reduced to within the capacity of the condensate booster pumps to supply water. The subsequent plant transition to mode 4 was normal in all respects and there were no safety consequences related to the event.
397 | 3972004006 | 2004-08-17 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Columbia | B | GE | PO | 20 | On August 17, 2004, with a plant startup in progress and with the plant in Mode 1 at approximately 20% power, a licensed control room operator improperly filled a feedwater heater with condensate following maintenance. This improper filling evolution tripped the only running reactor feedwater pump initiating a loss of feedwater transient. The reactor was scrammed manually prior to level reaching the automatic trip set point and water level stabilized using the Reactor Core Isolation Cooling (RCIC) system and the recovered reactor feedwater pump. Failure of the Reactor Operator to follow written instructions resulted in uncontrolled filling of the feedwater heater and a momentary drop in condensate system pressure. The momentary drop in condensate system pressure directly resulted in a trip of the running feedwater pump on low suction pressure. This event posed no threat to the health and safety of the public or plant personnel. All safety equipment was available during this transient and performed as expected. Following the plant scram, the plant was stabilized in Mode 3 without further event.
397 | 3972005003 | 2005-06-15 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 100 | On June 15, 2005 at 1400 hours, the reactor tripped from 100% power. The trip resulted from a Reactor Protection System (RPS) actuation due to a failure in the Digital Electro-Hydraulic (DEH) system that caused the four turbine throttle valves to spuriously stroke from full open to full close. Although no specific DEH system failure could be identified, the three circuit cards providing the control signals to the four turbine throttle valves were replaced. These cards were identified as the most likely source of the DEH system failure. The root cause of this event is the DEH Control System design has single point vulnerabilities and the cards in this system do not exhibit a predictable failure mechanism which would allow replacement prior to failure. Long-term corrective actions are being pursued as identified in Problem Evaluation Request 205-0424. Energy Northwest is performing a single Failure Vulnerability Assessment to identify and address single failure vulnerabilities. This event did not adversely affect the health and safety of the public. A similar event was reported by Energy Northwest as LER 2004-004-00.
397 | 3972005004 | 2005-06-23 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Columbia | B | GE | PO | 23 | On June 23, 2005, Columbia Generating Station was in Mode 1 with the reactor operating at approximately 23 percent power. At 13:46 PDT, an automatic reactor scram occurred due to a low water level condition in the reactor vessel. The low reactor water level condition was caused by an inadvertent loss of reactor feedwater pump RFW-P-1B due to a false low suction pressure signal caused by human error during planned maintenance activities. Control room operators entered appropriate Emergency Operating Procedures and stabilized the plant following the reactor scram. Plant systems responded as designed with the exception of RCIC as discussed below. As long term corrective action, a time delay will be installed or the low suction pressure trip removed to prevent spurious RFW pump trips. The RCIC system was manually started to restore reactor water level and was later manually tripped. The system had to be reset locally due to tripped mechanical overspeed trip linkage. During two subsequent attempts to restart RCIC the pump tripped on low suction pressure. Operators were then able to successfully start RCIC with the flow controller in manual. A time delay has been added to the RCIC low suction pressure trip logic to resolve this issue.
397 | 3972006001 | 2006-10-31 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Columbia | B | GE | PO | 100 | On October 31, 2006 at 0445 hours, the reactor tripped from 100% power. The trip resulted from a Reactor Protection System (RPS) actuation due to a failure in the Digital Electro-Hydraulic (DEH) system used to position Main Turbine valves. This failure caused four turbine throttle valves (TVs) and four turbine governor valves (GVs) to spuriously stroke to the full close position. When the TVs were closing and reached a position less than 95% open, RPS logic was met and a Reactor Scram occurred. The cause for the valve closure was a failure of an output peripheral driver chip on a DEH Digital Input Card. When the chip failed, the output went to high voltage which is equivalent to a turbine unlatched condition. This false turbine unlatched condition is the initiator for the subsequent turbine valve motion. The card was replaced and the circuit successfully tested. The DEH system has been previously determined to have multiple single point vulnerabilities. Long-term corrective actions have been pursued in which a new DEH system is scheduled to be installed in refueling outage R18 (May/June 2007). This event did not adversely affect the health and safety of the public. Two similar events were reported by Energy Northwest as LERs 2004-004-00 and 2005-003-00.
397 | 3972007004 | 2007-06-28 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Columbia | B | GE | PO | 70 | On June 28, 2007 at 1717 PDT Columbia Generating Station experienced an unexpected trip of Condensate Booster Pump (CBP) 2B (COND-P-2B). The trip occurred while operators were manually transferring the COND-P-2B duplex oil filter to the standby filter. The trip of COND-P-2B resulted in a low suction pressure trip of the reactor feedwater pumps and a reactor scram on low water level. The cause of this event was a latent equipment condition involving the incorrect configuration of the COND-P-2B lube oil filter valves combined with the operational decision to transfer filters with COND-P-2B required to be in service. Corrective actions have been initiated to properly configure the COND-P-2B lube oil transfer valves and enhance plant documentation to ensure the proper configuration is maintained following future maintenance activities. Furthermore, Energy Northwest will enhance the operational directives governing future on-line oil filter transfers. There are no documented previous instances at Columbia involving the inadvertent removal of CBP lube oil filters from service.
397 | 3972008001 | 2008-08-21 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Columbia | B | GE | PO | 65 | On August 21, 2008, an automatic reactor scram occurred at 1606, while the plant was operating at 65% power due to the Digital Electrohydraulic Control (DEH) trip header momentarily depressurizing during post maintenance testing (PMT). All safety systems were available during the event and operated as designed. Plant operators effectively managed the transient. This event did not pose a threat to the health and safety of the public. The direct cause of the reactor scram was instantaneous recompression of an air bubble trapped in the intervalve cavity between the A and B Quadvoter valves during post-maintenance testing (PMT). This allowed backflow of DEH fluid from the emergency trip header into the intervalve cavity during PMT, causing a momentary depressurization of the DEH trip header that resulted in the reactor scram. The root cause of the scram was determined to be a design deficiency in the on-line serviceable Quadvoter assembly which allowed an air bubble to remain in the intervalve cavity following performance of on-line maintenance activities.
397 | 3972009001 | 2009-02-08 | QR5 | Turbine Trip | [45 empty] | Columbia | B | GE | PO | 75 | On February 8, 2009 at 1125 hours, an automatic reactor scram occurred while Columbia was operating in Mode 1 at 75% power. The Digital Electro-Hydraulic (DEH) Control System emergency trip header momentarily depressurized during testing following on-line quadvoter valve assembly replacement. A Turbine Governor Valve Fast Closure trip signal was generated and a reactor scram occurred. The direct cause of the event was the introduction of air into the DEH system during quadvoter valve replacement and subsequent compression of the unvented, entrapped air during post maintenance testing. The compression resulted in backflow and excursion of the trip header pressure below the trip setpoint. The root cause is design deficiencies in the on-line serviceable quadvoter assembly which allowed system conditions that resulted in a reactor trip following performance of on-line maintenance activities. Both quadvoter valve assemblies in the affected channel were replaced. Prior to reactor startup, the DEH system was vented and tested to ensure removal of all air. Corrective actions to address quadvoter design deficiencies and to improve quadvoter performance have been pursued. This event did not adversely affect the health and safety of the public. Since the installation of a new DEH system at Columbia in 2007, one similar event was reported by Energy Northwest in LER 2008-001-00.
397 | 3972009002 | 2009-05-08 | QR6 | Manual Reactor Trip | [45 empty] | Columbia | B | GE | PO | 87 | On May 8, 2009 at 1046 hours, a manual reactor scram was inserted while Columbia was operating in Mode 1 at 87% power. Loss of air side seal oil pressure and consequential loss of hydrogen pressure in the main generator occurred during testing of the seal oil system backup regulator and air side seal oil back up pump. When the backup system was activated, a crud burst of corrosion products from the back up oil supply line and biological growth from the heat exchanger plugged the single in-line filter. This caused a loss of air side seal oil pressure, allowed hydrogen to escape from the generator, and necessitated the manual scram. The process for addressing compensatory measures for the single point vulnerability of the Cuno filter (SO-F-1) was inadequate (Root Cause 1). An ineffective and untimely repair of Seal Steam flange leaks contributed to increased levels of moisture in the air side seal oil system. This resulted in formation of corrosion products and biodegradable material in the seal oil system (Root Cause 2). Interim risk mitigation actions to monitor the in-line filter continuously during backup system operation and seal oil system startup and take actions as necessary are being established in plant operating procedures. The seal oil filter upgrade is scheduled to be implemented during the next refueling outage (R-20). No similar events have been reported by Energy Northwest.
397 | 3972009003 | 2009-06-26 | H1 | Fire | [7 empty] | X | [25 empty] | X | [11 empty] | Columbia | B | GE | PO | 73 | At 1949 on June 26, 2009, with Columbia operating at approximately 75% power, a small fire near the #2 high pressure turbine bearing was reported to the main control room. As directed by procedure, a manual scram was inserted at 1952. The in-service turbine lube oil vapor extractor system did not provide enough differential pressure to prevent lube oil from leaking out of the bearing pedestal. The fire occurred when the leaking lube oil came into contact with a hot pipe causing the oil to flash. The root causes were an out of calibration pressure switch and the integrated system knowledge of the main turbine lube oil exhauster system by Operations and Engineering was weak. The pressure switch has been replaced. Additional corrective actions taken to prevent recurrence include revisions to station procedures to ensure that the turbine lube oil vapor extractor system pressure is monitored via independent instruments during routine operator rounds as well as after any system manipulation. In addition, improvements in training for Operations and Engineering are planned to increase overall system knowledge. No similar events have been reported by Energy Northwest.
397 | 3972009004 | 2009-08-05 | QC5 | Loss of Non-safety-Related Bus | [7 empty] | X |  |  | X | [22 empty] | X | [5 empty] | X | [5 empty] | Columbia | B | GE | PO | 100 | At 0750 on August 5, 2009, while Columbia was operating at 100% power, an electrical fault on a 6.9 kilovolt (kV) non-segregated bus resulted in a turbine trip and automatic reactor scram. During the scram recovery, the turbine bypass valves remained in the full open position and did not automatically modulate to maintain reactor pressure as expected. The most probably cause of the bus failure is a relaxation of bolted connections on the center phase flexible link(s) caused by repeated thermal cycles over time. The root cause identified for this event was the non-performance of preventive maintenance (PM) tasks for torque checks of the non-segregated bus links. The damaged bus has been repaired, and changes to the controls for PMs will be made to ensure proper performance to prevent this type of failure from recurring. The failure of the bypass valves to control pressure resulted from an error introduced during a design change of the Digital Electric Hydraulic (DEH) system implemented in 2007. As a result, the bypass valves transferred to manual pressure control mode when the pressure transient exceeded the main steam throttle inlet pressure input signal limit for all three channels. The DEH system has been modified to correct the erroneous signal limit, and to retain automatic control of the bypass valves during similar high throttle pressure events. No previous similar events have been reported by Columbia.
397 | 3972009005 | 2009-11-07 | QR6 | Manual Reactor Trip | [45 empty] | Columbia | B | GE | PO | 52 | On November 7, 2009, the control room staff had completed a scheduled downpower of Columbia Generating Station to perform maintenance activities. After reaching the targeted power level, a rapid loss of hydraulic fluid from the main turbine digital electro-hydraulic control (DEH) system occurred. This resulted in the initiation of a manual scram of the reactor as directed by plant procedures at 0725. This event meets the reporting requirements of 10 CFR 50.73(a)(2)(iv)(A) for manual actuation of a system described in 10 CFR 50.73(a)(2)(iv)(B)(1). The direct cause for the loss of hydraulic fluid was the failure of an o-ring at the lower mounting block flange of accumulator DEH-TK-1D. This flange was determined to be incorrectly assembled following preventive maintenance performed during the previous refueling outage. The root cause was determined to be that the administrative requirements associated with maintenance on the DEH Accumulators did not impose special verifications, controls, or personal accountability measures to ensure that maintenance is performed appropriately. The affected flange was reassembled with a new o-ring and bolts torqued to recommended values. This event did not adversely affect the health and safety of the public.
397 | 3972016001 | 2016-03-28 | QR6 | Manual Reactor Trip | [45 empty] | Columbia | B | GE | PO | 100 | At 1322 PDT on March 28, 2016, a manual reactor scram was initiated in response to a loss of Reactor Closed Cooling (RCC). The loss of RCC was due to the opening of a Service Water (SW) valve at the inlet side of the Fuel Pool Cooling heat exchanger during performance of a partial surveillance without proper isolation of the RCC system piping from the heat exchanger. The cross-connection of the two systems caused depressurization and loss of flow from the RCC system into the non-pressurized SW piping. The SW valve was closed and the reactor was scrammed. Safety system responses to the scram signal were normal, with all control rods being fully inserted. Reactor decay heat was removed via bypass valves to the Main Condenser. No safety relief valves lifted and no emergency core cooling systems injected following the reactor scram. <br /><br /> The root cause was determined to be that plant Operators did not properly evaluate plant configuration when performing a partial surveillance including the marking as "N/A" (not applicable) of procedural steps, in accordance with plant procedures. Human performance aspects of the event were quickly addressed and additional corrective actions include reinforcing and monitoring procedure standards, and updating work control procedures at the station.
397 | 3972016004 | 2016-12-18 | QR5 | Turbine Trip | [10 empty] | X | [28 empty] | X | [5 empty] | Columbia | B | GE | PO | 100 | On December 18, 2016 at 11:24 hours, an automatic scram occurred due to a fault on an off-site transmission network. A reactor scram was automatically initiated by the plant response to the transient. <br /><br /> All rods fully inserted, Main Steam Isolation Valves [SB,V] automatically closed due to loss of power to both Reactor Protection System [JC] busses. All safety systems operated as designed. Two Safety Relief Valves [SB,V] were initially cycled automatically, then several manually to maintain Reactor Pressure Vessel [AC] pressure. Reactor water level was maintained with Reactor Core Isolation Cooling [BN], Control Rod Drive [AA] flow, and High Pressure Core Spray [BG]. <br /><br /> The entity responsible for the off-site transmission network, Bonneville Power Administration (BPA), performed a cause evaluation for the loss of off-site power. The cause evaluation stated the event was caused by three sequential 500-kV breaker failures. BPA took immediate corrective actions to restore the off-site transmission network. The root cause evaluation addressing the plant response was performed by plant personnel.
397 | 3972017004 | 2017-08-20 | QL7 | Degraded condenser vacuum | [45 empty] | Columbia | B | GE | PO | 100 | On August 20, 2017 at 1605 PDT, Columbia Generating Station was manually scrammed due to a rise in Main Condenser back pressure. The rise in back pressure was due to the spurious closure of the Main Condenser Air Removal Suction Valve (AR-V-1) as a result of the failure of it's associated solenoid pilot valve. Following the reactor scram and depressurization of the reactor a Level 3 actuation occurred. In addition a startup flow control valve failed which necessitated throttling of the Feedwater start-up level control isolation valve to control Reactor Pressure Vessel level. All other safety systems functioned as expected and all control rods were fully inserted. Reactor decay heat was removed via bypass valves to the main condenser.<br /><br /> The apparent cause was the plant modification to address the single point vulnerability of the closure of AR-V-1 was not implemented in time to prevent a plant shutdown. A temporary modification has been installed to maintain AR-V-1 open for the remainder of the operating cycle. <br /><br /> These events are reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A).
397 | 3972018001 | 2018-05-18 | QR5 | Turbine Trip |  |  | X | [13 empty] | X | [28 empty] | Columbia | B | GE | PO | 100 | On May 18, 2018, at 0651 PDT, Columbia Generating Station experienced a Main Transformer lockout relay trip. Coincident with the unplanned trip, an external line to ground fault occurred. A Reactor scram was automatically initiated by the plant in response to the transient. <br /><br /> All rods fully inserted as expected; no Emergency Core Cooling Systems actuated or injected. Plant Operators effectively maintained Reactor power, pressure and level. This event did not pose a threat to the health and safety of the public.<br /><br /> This event was reported via Event Notification #53410 under 10 CFR 50.72(b)(2)(iv)(B) as an event that resulted in actuation of the Reactor Protection System when the Reactor was critical. <br /><br /> The root cause of the Main Transformer lockout and Reactor scram was that the vendor-supplied Buchholz relay did not meet the standard performance requirements to be insensitive to external faults.
400 | 4001987004 | 1987-01-21 | QR8 | Spurious Reactor Trip | [45 empty] | Harris | P | WE | PO | 10 | POWER LEVEL - 010%. ON JANUARY 21, 1987 THE PLANT WAS SEPARATED FROM THE ELECTRICAL GRID AND THE REACTOR POWER LEVEL WAS BEING MANUALLY REDUCED TO UNDER 10 PERCENT IN ORDER TO PERFORM TURBINE MECHANICAL OVERSPEED TRIP TESTING. THE REACTOR POWER WAS BEING REDUCED TO LESS THAN 10 PERCENT TO AVOID A REACTOR TRIP WHICH WOULD OCCUR IF TRIP TESTING ON THE TURBINE WAS PERFORMED ABOVE THIS LEVEL. AT 0016 HOURS ON JANUARY 21, 1987 THE REACTOR TRIPPED WHILE THE POWER LEVEL WAS BEING REDUCED DUE TO ONE INTERMEDIATE RANGE CHANNEL (N-36) WHICH REMAINED IN THE TRIPPED CONDITION AS POWER WAS BEING REDUCED. THE INTERMEDIATE RANGE CHANNEL TRIP RESET VALUE WAS FOUND TO BE SET TOO LOW. ALL RODS FULLY INSERTED INTO THE CORE AND THE PLANT STABILIZED AT NOMINAL OPERATING PRESSURE AND NOMINAL OPERATING TEMPERATURE. THE BISTABLES' SETPOINTS WERE THEN ADJUSTED WITH VALUES BASED ON DATA COLLECTED DURING PLANT OPERATION AT APPROXIMATELY 20 PERCENT POWER AND WESTINGHOUSE RECOMMENDATIONS. THE PLANT WAS RESTARTED AT 2036 HOURS ON JANUARY 21, 1987. THE TURBINE MECHANICAL OVERSPEED TRIP TESTING WAS THEN PERFORMED AND SUCCESSFULLY COMPLETED ON JANUARY 22, 1987 WITHOUT FURTHER INCIDENT.
400 | 4001987005 | 1987-01-22 | QP3 | Loss of Condensate Flow | [45 empty] | Harris | P | WE | PO | 32 | POWER LEVEL - 032%. ON JANUARY 22, 1987, THE SHEARON HARRIS NUCLEAR POWER PLANT UNIT 1 WAS OPERATING AT 32% INDICATED POWER ON POWER RANGE NUCLEAR INSTRUMENTS. THE 'B' CONDENSATE PUMP TRIPPED AT 2216 AND THIS, IN TURN, TRIPPED CONDENSATE BOOSTER PUMP 'B' AND MAIN FEED PUMP 'A' AT 2220, THE REACTOR TRIPPED DUE TO A LOW-LOW LEVEL IN STEAM GENERATOR 'A . ALL CONTROL RODS FULLY INSERTED INTO THE CORE AND A NORMAL PLANT RECOVERY ENSUED.
400 | 4001987008 | 1987-02-27 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 49 | POWER LEVEL - 049%. AT 1902 ON FEBRUARY 27, 1987, SHNPP WAS OPERATING IN MODE 1 AT A 49% THERMAL POWER LEVEL. A TRANSIENT IN TURBINE LOAD OCCURRED AND THE RESULTING FEEDWATER FLOW TRANSIENT CAUSED A LOSS OF ALL MAIN FEEDWATER AND AN AUTOMATIC START OF BOTH MOTOR-DRIVEN AUXILIARY FEEDWATER PUMPS. ATTEMPTS TO RESTORE MAIN FEEDWATER WERE NOT SUCCESSFUL, AND THE REACTOR WAS MANUALLY TRIPPED AT 1903. FOLLOWING THE REACTOR TRIP, AN AUTOMATIC START OF THE TURBINE-DRIVEN AUXILIARY FEEDWATER PUMP OCCURRED DUE TO LOW STEAM GENERATOR WATER LEVELS. THE FULL AUXILIARY FEEDWATER SYSTEM FLOW AND STEAM DEMAND FROM THE TURBINE-DRIVEN PUMP CAUSED A PRIMARY SYSTEM COOLDOWN, AND THE MAIN STEAMLINE ISOLATION VALVES WERE MANUALLY CLOSED. THE SOURCE RANGE NEUTRON DETECTORS FAILED TO AUTOMATICALLY RE-ENERGIZE FOLLOWING THE TRIP DUE TO IMPROPER COMPENSATING VOLTAGE SETTING ON THE INTERMEDIATE RANGE DETECTORS WHICH KEPT THE INTERMEDIATE RANGE CHANNEL LEVEL ABOVE THE SETPOINT FOR AUTOMATIC SOURCE RANGE DETECTOR RE-ENERGIZATION. THE SOURCE RANGE DETECTORS WERE MANUALLY RE-ENERGIZED. THE PLANT WAS STABILIZED IN MODE 3 AT AN RCS TAVG OF 557F (ZERO-LOAD VALUE). THE CAUSE OF THE EVENT WAS IDENTIFIED AND CORRECTED, AND THE PLANT WAS RETURNED TO SERVICE ON MARCH 2, 1987.
400 | 4001987012 | 1987-03-11 | QR5 | Turbine Trip | [45 empty] | Harris | P | WE | PO | 47 | POWER LEVEL - 047%. AT 1700 ON MARCH 11, 1987, WITH THE PLANT OPERATING AT 47% THERMAL POWER LEVEL (370 MWE), A TURBINE TRIP AND REACTOR TRIP OCCURRED DURING TROUBLESHOOTING AT THE MAIN TURBINE SUPERVISORY CONTROL PANEL. SUBSEQUENT TO THE REACTOR/TURBINE TRIP, THE OPERATING MAIN FEEDWATER PUMPS TRIPPED ACTUATING AN AUTOMATIC START OF BOTH MOTOR-DRIVEN AUXILIARY FEEDWATER PUMPS. ALSO THE MAIN STEAM LINE ISOLATION VALVES WERE MANUALLY CLOSED TO LIMIT THE COOLDOWN TRANSIENT ON THE REACTOR COOLANT SYSTEM (RCS). THE PLANT WAS STABILIZED IN MODE 3 AT 557F RCS AVERAGE TEMPERATURE (ZERO-LOAD VALUE). THE TURBINE TRIP WAS DETERMINED TO BE CAUSED DIRECTLY BY DEPRESSING A TEST PUSH BUTTON AT THE TURBINE SUPERVISORY CONTROL PANEL. THE PLANT WAS RETURNED TO SERVICE ON MARCH 12, 1987.
400 | 4001987013 | 1987-03-13 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 49 | MANUAL TRIP OF THE PLANT WAS INITIATED FROM 49% REACTOR POWER DUE TO A LOSS OF MAIN FEEDWATER. THE PLANT HAD RECENTLY COMPLETED FORWARD FLUSHING OF AUXILIARY FEEDWATER CHECK VALVES AND WAS IN THE PROCESS OF OPENING THE PREHEATER BYPASS VALVES. THE PREHEATER BYPASS VALVES ON B AND C STEAM GENERATORS HAD BEEN OPENED, AND A SMALL FEEDWATER FLOW OSCILLATION RESULTED. OPENING THE VALVE FOR A STEAM GENERATOR STARTED A FEEDWATER SYSTEM PRESSURE TRANSIENT WHICH CAUSED THE MAIN FEEDWATER REGULATING VALVES ON ALL THREE STEAM GENERATORS TO OSCILLATE. THIS TRANSIENT CAUSED TRIPS OF THE RUNNING MAIN FEEDWATER PUMP, BOTH CONDENSATE BOOSTER PUMPS, THE RUNNING HEATER DRAIN PUMP, AND BOTH CONDENSATE PUMPS. ATTEMPTS TO RESTART THE PUMPS WERE UNSUCCESSFUL, AND THE REACTOR WAS MANUALLY TRIPPED. THE MOTOR DRIVEN AUXILIARY FEEDWATER PUMPS STARTED AS REQUIRED ON A LOSS OF MAIN FEEDWATER. THE MAIN STEAMLINE ISOLATION VALVES WERE MANUALLY CLOSED SUBSEQUENT TO THE REACTOR TRIP TO LIMIT THE COOLDOWN OF THE RCS. THE REACTOR WAS STABILIZED IN MODE 3 AT 557F (ZERO-LOAD TAVG).
400 | 4001987017 | 1987-03-31 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 56 | At 1129 on March 31, 1987, a reactor trip occurred on steam flow/feedwater flow mismatch coincident with steam generator low level. The initiating event was a feedwater control valve oscillation which caused flow and pressure transients in the main feedwater system; these conditions eventually caused the main feedwater pumps to trip which then resulted in a reactor trip.<br /><br /> At the time of the trip, the plant was operating at 56% reactor power and 385 MWe. The motor-driven auxiliary feedwater pumps actuated as required on loss of both main feedwater pumps, and the turbine-driven auxiliary feedwater pump started subsequent to the reactor trip on low-low steam generator level. The main steamline isolation valves were manually closed to limit the cooldown transient on the Reactor Coolant System (RCS). The plant was stabilized in Mode 3 at a RCS Tavg of 557 degrees Fahrenheit (zero-load value).
400 | 4001987018 | 1987-04-03 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 75 | POWER LEVEL - 075%. AT 1126 ON APRIL 3, 1987, WITH THE PLANT OPERATING AT 75% THERMAL POWER LEVEL AND 560 MWE, A MANUAL TURBINE TRIP AND SUBSEQUENT REACTOR TRIP WAS INITIATED. THE TRIP WAS REQUIRED DUE TO A LOSS OF BOTH MAIN FEEDWATER PUMPS AND THE SUBSEQUENT DECREASE IN STEAM GENERATOR LEVELS. THE MOTOR DRIVEN AUXILIARY FEEDWATER PUMPS STARTED AUTOMATICALLY AS REQUIRED UPON LOSS OF BOTH MAIN FEEDWATER PUMPS. SUBSEQUENT TO THE TRIP THE MAIN STEAMLINE ISOLATION VALVES WERE MANUALLY CLOSED TO LIMIT THE COOLDOWN TRANSIENT ON THE REACTOR COOLANT SYSTEM (RCS). THE PLANT WAS STABILIZED IN MODE 3 AT THE ZERO-LOAD RCS TAVG OF 557F.
400 | 4001987019 | 1987-04-12 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 75 | POWER LEVEL - 075%. THE PLANT WAS OPERATING AT 75 PERCENT REACTOR POWER AND 630 MWE ON APRIL 12, 1987 FOLLOWING COMPLETION OF A 10 PERCENT LOAD SWING TEST. DURING THE TEST, HEATER DRAIN PUMP 'A' TRIPPED AND WAS RESTARTED BUT LEFT IN THE RECIRCULATION MODE. HEATER DRAIN PUMP 'B' TRIPPED DURING THE LOAD INCREASE PORTION OF THE TEST AT 1037 HOURS. HEATER DRAIN PUMP 'A' AGAIN TRIPPED AT 1050 HOURS WHILE BEING ALIGNED BACK TO NORMAL FLOW. THE PLANT CONTINUED OPERATION WITH BOTH HEATER DRAIN PUMPS OFF. AT 1117 HOURS, A HIGH TEMPERATURE DISCHARGE ALARM WAS RECEIVED FOR CONDENSATE PUMP 'B'; AND IN ANTICIPATION OF THE PUMP TRIPPING A MANUAL TURBINE LOAD REDUCTION AND MANUAL CONTROL OF FEEDWATER WAS TAKEN. THE LOAD REDUCTION WAS LARGE AND FAST ENOUGH TO ACTIVATE THE STEAM DUMP SYSTEM. AS ANTICIPATED, AT 1118 HOURS CONDENSATE PUMP 'B' TRIPPED, THUS IMMEDIATELY CAUSING CONDENSATE BOOSTER PUMP 'B' AND MAIN FEEDWATER PUMP 'B' TRIPPING, RESULTING IN TOTAL LOSS OF B TRAIN FEEDWATER. CONSEQUENTLY, WITH THE ACTUATION OF THE STEAM DUMP SYSTEM COMBINED WITH STEAM DEMAND AND FEEDWATER DEMAND REMAINING GREATER THAN THE CAPACITY OF THE REMAINING FEEDWATER TRAIN, CONDENSATE PUMP 'A' AND MAIN FEEDWATER PUMP 'A' TRIPPED WITHIN ONE MINUTE FOLLOWING THE LOSS OF THE 'B' TRAIN FEEDWATER.
400 | 4001987021 | 1987-04-14 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X |  |  | X | [26 empty] | X |  |  |  | X | Harris | P | WE | PO | 87 | POWER LEVEL - 087%. ON APRIL 14, 1987, THE SHEARON HARRIS NUCLEAR POWER PLANT WAS OPERATING IN MODE 1 AT APPROXIMATELY 87% REACTOR POWER. AROUND 1800, DURING THE PROCESS OF CLEANING THE CIRCULATING WATER PUMP SUCTION SCREENS, DEBRIS FROM THE COOLING TOWER BASIN ENTERED THE CIRCULATING WATER SYSTEM AND RESTRICTED FLOW TO THE MAIN CONDENSER. CONDENSATE TEMPERATURES ROSE RAPIDLY AND LED TO A TRIP OF BOTH CONDENSATE PUMPS DUE TO HIGH CONDENSATE TEMPERATURE. THIS RESULTED IN THE LOSS OF BOTH FEEDWATER TRAINS AND, CONSEQUENTLY, A MANUAL TRIP OF THE TURBINE AND REACTOR AT 1830 ON APRIL 14. FOLLOWING PLANT SHUTDOWN, ALL VISIBLE DEBRIS WAS REMOVED FROM ACCESSIBLE AREAS. THE PLANT WAS RETURNED TO SERVICE AT APPROXIMATELY 1500 ON APRIL 15, 1987.
400 | 4001987024 | 1987-04-21 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 100 | POWER LEVEL - 100%. THE PLANT WAS OPERATING AT APPROXIMATELY 100 PERCENT REACTOR POWER AND 882 MWE ON APRIL 21, 1987 IN NORMAL PLANT LINE-UP, WITH THE MAIN FEEDWATER CONTROL VALVES IN MANUAL CONTROL. AT 0450 HOURS, 'B' HEATER DRAIN PUMP TRIPPED DUE TO LOW DIFFERENTIAL PRESSURE. THE PLANT OPERATOR THEN STARTED A MANUAL TURBINE POWER REDUCTION IN ORDER TO STABILIZE PLANT POWER. 'A' HEATER DRAIN PUMP THEN TRIPPED AT 0451 HOURS, ALSO DUE TO LOW DIFFERENTIAL PRESSURE, WHICH INITIATED AN AUTOMATIC TURBINE RUNBACK. DURING THE TURBINE RUNBACK, OPERATORS BEGAN TO MANUALLY CONTROL FEEDWATER FLOW, AND THE PLANT STEAM DUMP SYSTEM ACTIVATED DUE TO THE LARGE LOAD REDUCTION. WHILE TURBINE RUNBACK WAS STILL IN PROGRESS, 'A' MAIN FEEDWATER PUMP TRIPPED AT 0453 HOURS DUE TO LOW SUCTION PRESSURE AND WAS IMMEDIATELY FOLLOWED BY 'B' MAIN FEEDWATER PUMP TRIPPING FOR THE SAME REASON. WITH BOTH MAIN FEEDWATER PUMPS TRIPPED, 'A' AND 'B' CONDENSATE BOOSTER PUMPS TRIPPED DUE TO HIGH DISCHARGE PRESSURE. WITH BOTH FEEDWATER TRAINS TRIPPED AND STEAM GENERATOR WATER LEVELS DECREASING, A MANUAL REACTOR TRIP WAS INITIATED AT 0453 HOURS. THE PLANT WAS THEN STABILIZED IN MODE 3 AT 557F (NORMAL NO LOAD TAVG) AND NORMAL OPERATING PRESSURE WITH STEAM GENERATOR WATER LEVELS RESTORED WITH THE AUXILIARY FEEDWATER SYSTEM.
400 | 4001987025 | 1987-04-22 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 99 | POWER LEVEL - 099%. ON APRIL 22, 1987 AT 2316 HOURS, WHILE THE PLANT WAS OPERATING AT 99 PERCENT REACTOR POWER, 'A' HEATER DRAIN PUMP TRIPPED FROM A LOW FLOW SIGNAL. THIS WAS CAUSED BY A SEPARATED AIR CONNECTION ON THE DISCHARGE VALVE CAUSING THE VALVE TO FAIL SHUT. PLANT OPERATORS INITIATED A MANUAL TURBINE POWER REDUCTION TO COMPENSATE FOR THE LOSS OF THE PUMP. DURING THE MANUAL TURBINE RUNBACK ALARMS FOR LOW FLOW WERE RECEIVED FOR 'B' HEATER DRAIN PUMP, FOLLOWED BY THE PUMP TRIPPING AT 2322 HOURS. THIS INITIATED AN AUTOMATIC TURBINE RUNBACK TO 50 PERCENT TURBINE POWER AND ACTIVATION OF THE PLANT STEAM DUMP SYSTEM DUE TO THE LARGE LOAD REDUCTION. LOW SUCTION PRESSURE THEN TRIPPED BOTH 'A' AND 'B' MAIN FEEDWATER PUMPS AND WAS IMMEDIATELY FOLLOWED BY BOTH 'A' AND 'B' CONDENSATE BOOSTER PUMPS TRIPPING. IN RESPONSE TO THE LOSS OF BOTH MAIN FEEDWATER TRAINS AND DECREASING STEAM GENERATOR WATER LEVELS, A MANUAL PLANT TRIP WAS INITIATED AT 2323 HOURS. THE PLANT WAS THEN STABILIZED IN MODE 3 AT 557F (NORMAL NO LOAD TEMPERATURE) AND NORMAL PRESSURE, AND THE STEAM GENERATORS WATER LEVEL RESTORED WITH THE AUXILIARY FEEDWATER SYSTEM. THE SEPARATED AIR CONNECTION ON THE 'A' HEATER DRAIN PUMP DISCHARGE VALVE WAS REPAIRED FOLLOWING THE EVENT.
400 | 4001987031 | 1987-05-24 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 100 | POWER LEVEL - 100%. ON MAY 24, 1987 THE PLANT WAS OPERATING IN MODE 1 AT 100 PERCENT REACTOR POWER. AT 1002 HOURS 'A' HEATER DRAIN PUMP TRIPPED ON LOW NET POSITIVE SUCTION HEAD DUE TO ITS DISCHARGE LEVEL CONTROL VALVE FAILING TO THE OPEN POSITION. PLANT OPERATORS INITIATED A MANUAL TURBINE POWER REDUCTION TO COMPENSATE FOR THE LOSS OF THE PUMP. DURING THE MANUAL TURBINE RUNBACK, AT 1004 HOURS, 'B' HEATER DRAIN PUMP TRIPPED ON LOW NET POSITIVE SUCTION HEAD. IN APPROXIMATELY 25 SECONDS 'A' MAIN FEEDWATER PUMP TRIPPED ON LOW SUCTION PRESSURE AS A RESULT OF THE LOSS OF THE HEATER DRAIN PUMPS CONTRIBUTION TO FEEDWATER FLOW. THE HIGH STEAM DEMAND AND SUDDENLY REDUCED FEEDWATER FLOW RESULTED IN THE TRIPPING OF BOTH 'A' AND 'B' CONDENSATE BOOSTER PUMPS DUE TO HIGH DISCHARGE PRESSURE. THE LOSS OF THESE PUMPS RESULTED IN 'B' MAIN FEEDWATER PUMP TRIPPING AND THE TOTAL LOSS OF ALL FEEDWATER FLOW. IN RESPONSE TO THE LOSS OF BOTH MAIN FEEDWATER TRAINS AND DECREASING STEAM GENERATOR LEVELS, A MANUAL PLANT TRIP WAS INITIATED AT 1005 HOURS. THE PLANT WAS THEN STABILIZED IN MODE 3 AT 557F (NORMAL NO LOAD TEMPERATURE) AND NORMAL PRESSURE, AND THE STEAM GENERATORS WATER LEVELS RESTORED WITH THE AUXILIARY FEEDWATER SYSTEM. THE DISCHARGE LEVEL CONTROL VALVE FOR 'A' HEATER DRAIN PUMP WAS REPAIRED FOLLOWING THE EVENT.
400 | 4001987035 | 1987-06-17 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Harris | P | WE | PO | 100 | POWER LEVEL - 100%. ON JUNE 17, 1987, THE SHEARON HARRIS NUCLEAR POWER PLANT WAS OPERATING AT 100% REACTOR POWER. AT 0908, REACTOR COOLANT PUMP 'C' TRIPPED WHICH RESULTED IN A REACTOR TRIP DUE TO LOW FLOW IN REACTOR COOLANT LOOP 'C'. LATER INVESTIGATION REVEALED THAT PHYSICAL CONTACT WITH THE BUS ENCLOSURE CAUSED THE TRIP OF AUXILIARY BUS 1C DUE TO THE ACTUATION OF THE PHASE 'A' BUS DIFFERENTIAL RELAY, WHICH ACTUATED THE BUS LOCKOUT RELAY AND DE-ENERGIZED AUXILIARY BUS 1C. PLANT SHUTDOWN RESPONSE WAS NORMAL EXCEPT THAT THE TURBINE-DRIVEN AUXILIARY FEEDWATER (AFW) PUMP STARTED AND THEN TRIPPED ON OVERSPEED. THE MOTOR-DRIVEN AFW PUMPS STARTED NORMALLY.
400 | 4001987037 | 1987-06-21 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 30 | POWER LEVEL - 030%. ON JUNE 21, 1987 AT 2208, A MANUAL REACTOR TRIP WAS INITIATED FROM 30% POWER AFTER THE OPERATING MAIN FEEDWATER TRAIN TRIPPED, RESULTING IN A LOSS OF MAIN FEEDWATER. THE MOTOR-DRIVEN AUXILIARY FEEDWATER PUMPS STARTED AS REQUIRED. PLANT RESPONSE TO THE REACTOR TRIP WAS AS EXPECTED, AND THE PLANT WAS STABILIZED IN MODE 3. THE TRIP OF THE FEEDWATER PUMPS WAS CAUSED BY A FAILED OPEN FEEDWATER PUMP RECIRCULATION VALVE, RESULTING FROM OPEN CIRCUIT IN THE VALVE CONTROL WIRING. THE CIRCUIT WAS REPAIRED, AND THE PLANT WAS RETURNED TO SERVICE ON JUNE 22, 1987.
400 | 4001987038 | 1987-06-22 | QR5 | Turbine Trip | [45 empty] | Harris | P | WE | PO | 6 | POWER LEVEL - 006%. ON JUNE 22, 1987, AT 0307, WITH THE PLANT AT 6% THERMAL POWER LEVEL, THE TURBINE GENERATOR WAS SYNCHRONIZED TO THE POWER GRID DURING A PLANT STARTUP. THE TURBINE CONTROL SYSTEM PICKED UP EXCESSIVE ELECTRICAL LOAD IMMEDIATELY UPON TIE IN TO THE GRID. THE RESULTING TRANSIENT CAUSED A HIGH STEAM GENERATOR WATER LEVEL TURBINE TRIP AND MAIN FEEDWATER ISOLATION, AND THE TURBINE TRIP ACTUATED AN AUTOMATIC REACTOR TRIP ON INTERLOCK. THE PLANT RESPONSE TO THE REACTOR TRIP WAS AS EXPECTED. AUXILIARY FEEDWATER STARTED AUTOMATICALLY WHEN THE MAIN FEEDWATER PUMPS TRIPPED ON THE HIGH STEAM GENERATOR WATER LEVEL. THE PLANT WAS STABILIZED IN MODE 3. THE CAUSE OF THE SUDDEN INCREASE IN ELECTRICAL LOAD COULD NOT BE PRECISELY DETERMINED. REDUCE THE EFFECTS OF ANY FUTURE SIMILAR TRANSIENT, AND THE PLANT WAS RETURNED TO SERVICE WITHOUT REPEAT OF THIS EVENT.
400 | 4001987042 | 1987-07-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Harris | P | WE | PO | 100 | POWER LEVEL - 100%. THE PLANT WAS OPERATING IN MODE 1 AT 100 PERCENT REACTOR POWER ON JULY 9, 1987. OPERATIONS PERSONNEL WERE PREPARING A CLEARANCE TO WORK ON THE SOLENOID OF VALVE 1AF-161, WHICH IS FOR THE AMMONIA SUPPLY TO STEAM GENERATOR 'C'. THE CLEARANCE WAS TO BE IMPLEMENTED BY PULLING 2 FUSES, L5B/1967 AND L6B/1967, WHICH ARE LOCATED IN AUXILIARY RELAY PANEL 1B-SB. DUE TO A MISINTERPRETATION OF PLANT PRINTS AND THE PHYSICAL LOCATION OF THE FUSES, THE WRONG FUSES WERE PULLED. THIS CAUSED THE FEEDWATER REGULATING VALVE FOR STEAM GENERATOR 'C' TO SHUT, STOPPING ALL FEEDWATER FLOW TO STEAM GENERATOR 'C'. THIS RESULTED IN AN AUTOMATIC REACTOR/TURBINE TRIP AT 1007 HOURS DUE TO STEAM GENERATOR LOW-LOW LEVEL COINCIDENT WITH STEAM FLOW-FEED FLOW MISMATCH. PLANT RESPONSE TO THE TRIP WAS NORMAL EXCEPT THREE STEAM GENERATOR BLOWDOWN VALVES DID NOT AUTOMATICALLY SHUT AND WERE MANUALLY ISOLATED. STEAM GENERATOR WATER LEVELS WERE RESTORED WITH THE AUXILIARY FEEDWATER SYSTEM.
400 | 4001987041 | 1987-08-04 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [9 empty] | X | [5 empty] | X | [24 empty] | X | Harris | P | WE | PO | 100 | POWER LEVEL - 100%. THE PLANT WAS OPERATING AT 100 PERCENT REACTOR POWER IN MODE 1, POWER OPERATIONL ON AUG, 1987. INSTRUMENT AIR DRVER 1A WAS OUT OF SERVICE FOR REPAIRS. INSTRUMENT AIR DRYER AS BYPASSED AT APPROXIMATELY 1715 HOURS TO REPLACE THE DESICCANT. WORK WAS COMPLETED THE DRYER 1B AND AT APPROXIMATELY 2150 HOURS THE CLEARANCE ON THE DRYER WAS REMOVED. THE RESTORATION ALIGNMENT ON THE CLEARANCE FOR PLACING DRYER 1B BACK INTO SERVICE WAS INCORRECT. WHEN THE VALVES WERE REPOSITIONED IN ACCORDANCE WITH THE CLEARANCE RESTORATION LINEUP THE INSTRUMENT AIR COMPRESSORS WERE ISOLATED FROM THE AIR SYSTEM. THE AIR ISOLATION CAUSED AIR PRESSURE TO DECAY AND CAUSED AIR OPERATED VALVES TO GO TO 'FAIL SAFE' POSITIONS. IN PARTICULAR, THE MAIN FEEDWATER REGULATING VALVES TO DRIFT SHUT AND THE HEATER DRAIN LEVEL CONTROL VALVES TO DIVERT DRAIN FLOW TO THE CONDENSER. HEATER DRAIN PUMPS 1A AND 1B TRIPPED AND A MANUAL TURBINE RUNBACK WAS INITIATED. THIS WAS FOLLOWED BY A TRIP OF MAIN FEEDWATER PUMP 1A WHICH INITIATED AN AUTOMATIC TURBINE RUNBACK. THE LOSS OF INSTRUMENT AIR RESULTED IN A DECREASE IN STEAM GENERATOR WATER LEVELS. THE TURBINE RUNBACK RESULTED IN SHRINK IN STEAM GENERATOR LEVELS AND RESULTED IN A REACTOR TRIP AT 2154 HOURS DUE TO STEAM GENERATOR FEEDWATER STEAM/FLOW MISMATCH WITH LOW STEAM GENERATOR WATER LEVELS.
400 | 4001987062 | 1987-11-07 | QR7 | Other Reactor Trip (Valid RPS Trip) | [10 empty] | X | [28 empty] | X | [5 empty] | Harris | P | WE | SU | 5 | POWER LEVEL - 005%. ON NOVEMBER 7, 1987, AT 0533, THE PLANT WAS IN MODE 2 AT APPROXIMATELY 4.5% POWER. THE SAFETY INJECTION SYSTEM WAS ACTUATED, THE MAIN STEAM LINE ISOLATION ACTUATED, AND THE REACTOR TRIPPED DUE TO LOW STEAM LINE PRESSURE ON 'A' STEAM GENERATOR. THE LOW PRESSURE WAS DUE TO EXCESSIVE, RAPID, AUTOMATIC CYCLING OF THE STEAM DUMP SYSTEM AFTER THE 'A' MAIN STEAM ISOLATION VALVE OPENED. THE CYCLING OF THE STEAM DUMP VALVES WAS CAUSED BY AN INCORRECT SETTING ON THE STEAM HEADER PRESSURE CONTROLLER. THE SAFETY INJECTION WAS TERMINATED, THE PLANT WAS STABILIZED AND RETURNED TO NORMAL OPERATING TEMPERATURE AND PRESSURE. DURING THE EVENT, THE B EMERGENCY DIESEL GENERATOR FUEL OIL TRANSFER PUMP ROOM EXHAUST FAN (E-85A-SB) TRIPPED AFTER STARTING DUE TO A SPURIOUS LOW FLOW SIGNAL. THE ALTERNATE FAN (E-85B-SB) THEN STARTED AND CONTINUED TO RUN AS REQUIRED. THIS FAILURE DID NOT CONTRIBUTE TO THE EVENT. THE EVENT WAS CAUSED BY PERSONNEL ERROR AND A PROCEDURAL DEFICIENCY. CORRECTIVE ACTION INCLUDED PROCEDURE REVISIONS AND ADDITIONAL OPERATOR TRAINING COVERING THIS EVENT. THE PLANT WAS RESTARTED AND ON LINE IN MODE 1 BY 1505 ON NOVEMBER 8, 1987.
400 | 4001987063 | 1987-11-08 | QP3 | Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 22 | POWER LEVEL - 022%. THE PLANT WAS OPERATING IN MODE 1, POWER OPERATION, AT 22 PERCENT REACTOR POWER ON 11/8/87. THE PLANT WAS IN THE START-UP PROCESS FOLLOWING A SCHEDULED OUTAGE AND WAS PREPARING TO INCREASE POWER FROM 100 MWE TO 150 MWE WITH ONLY THE '1A' FEEDWATER TRAIN IN SERVICE. PRESSURE WHICH CAUSED 1A CONDENSATE BOOSTER PUMP AND 1A MAIN FEEDWATER PUMP TO TRIP, WHICH RESULTED IN A TOTAL LOSS OF MAIN FEEDWATER. THE REACTOR AND TURBINE WERE THEN MANUALLY TRIPPED AT 1625 HOURS. THE MAIN STEAM ISOLATION VALVES WERE SHUT IN ORDER TO LIMIT PLANT COOLDOWN AND THE AUXILIARY FEEDWATER SYSTEM ACTUATED TO RESTORE STEAM GENERATOR WATER LEVELS. ALL PLANT SYSTEMS RESPONDED AS REQUIRED. THE IMMEDIATE CAUSE OF THE EVENT WAS THE CONDENSATE RECIRCULATION VALVE WAS IN THE 'OPEN' POSITION RATHER THAN 'MODULATE' POSITION AS REQUIRED BY NORMAL PLANT OPERATION. THIS CAUSED THE CONDENSATE PUMP AND CONDENSATE BOOSTER PUMP TO BE OPERATING AT NEAR RUN OUT CONDITION AND EVENTUALLY TRIPPED THE CONDENSATE PUMP ON LOW DISCHARGE PRESSURE. THE ROOT CAUSE OF THE EVENT WAS PERSONNEL ERROR AS PLANT OPERATORS WERE NOT FULLY AWARE OF ALL PLANT CONDITIONS.
400 | 4001988007 | 1988-03-09 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Harris | P | WE | PO | 100 | The plant was operating in Mode 1, Power Operation, at 100 percent reactor power on March 9, 1988. At 1654 hours, several alarms were received by operators at the Main Control Board indicating low water level in "B" Steam Generator (SG). <br /><br />Operators observed that the "B" Main Feedwater Regulating Valve (MFRV) had gone shut. The operators then attempted to take manual control of "B" MFRV in an effort to restore water level in "B" SG. However, the operators efforts could not restore the rapidly dropping "B" SG water level as instrument air was lost to "B" MFRV and within 30 seconds the plant tripped due to "B" SG feedwater/steam flow mismatch with low SG water level. <br /><br />There were no safety consequences due to this event and plant response to the trip was normal. The Main Steam Isolation Valves (MSIV) were shut at 1657 hours in order to limit cooldown, SG water levels were restored with the Auxiliary Feedwater System, and the plant was stabilized in Mode 3, Hot Standby. <br /><br />The cause of the event was a failed renewable fuse which fed the solenoid for "B" MFRV. The end cap on the fuse had loosened which resulted in a loss of power to a solenoid which interrupted instrument air to the valve. The valve failed shut cutting off the feedwater supply to "B" SG. <br /><br />Corrective actions include: replacing the renewable fuse with a nonrenewable type, a hold put on renewable fuses in stock, and replacing identified renewable type fuses as plant conditions permit. <br /><br />This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an Engineered Safety System Feature actuation.
400 | 4001988028 | 1988-10-14 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 14 | The plant was operating in Mode 1, Power Operation, at 14 percent reactor power on October 14, 1988. The plant was in the start-up phase following a 77 day refueling outage and was being held at 14 percent power due to Steam Generator (SG) water chemistry conditions. Due to the power level, only the 1B train Feedwater and Condensate System was in service. At 1227 hours, both the 1B Condensate Pump (CP) and the 1B Condensate Booster Pump (CBP) tripped on low discharge pressure. The 1B Main Feedwater Pump (MFW) which should have automatically tripped, had to be manually tripped due to a failed trip relay coil. As a result of this total loss of feedwater, both the reactor and turbine were then manually tripped. The Main Steam Isolation Valves were shut in order to limit plant cool down and the Auxiliary Feedwater System actuated to maintain Steam Generator water levels and the plant was stabilized in Mode 3, Hot Standby. <br /><br />The cause of the event was a low level in the Condenser hot well which caused an automatic trip of the 1B CP on low discharge pressure. The low hot well level was caused by a discrepancy between the Main Control Board (MCB) indicated level and the actual level. The reference leg, for the level transmitters, was partially drained thus indicating a false higher reading at the MCB than actually existed. <br /><br />Corrective actions include: 1) the failed relay coil has been replaced, 2) the Auxiliary Operator round sheets have been revised to include a check of local hot well level and lists acceptable levels, 3) an investigation will be done to resolve the problem of the draining of the reference leg for hot well level indication, and 4) evaluation is being done for the changeout of pneumatic level controllers to electronic level controllers for the condenser hotwell level. <br /><br />There were no safety consequences as a result of this event and is being reported in accordance with 10CFR50.73(a)(2)(iv) as an Engineered Safety System Feature and a Reactor Protection System actuation.
400 | 4001988032 | 1988-10-30 | QP4 | Partial Loss of Condensate Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 98 | On October 30, 1988, the plant was operating in Mode 1 at 98% power. At 18:26:47 hours, the "B" Heater Drain Pump tripped causing an automatic turbine runback. Approximately 25 seconds later, the "A" Heater Drain Pump tripped. Due to the rapid load reduction and sudden decrease in feedwater flow, the "B" Condensate Booster Pump tripped on high discharge pressure at 18:30:36. The control operator tripped the "B" Main Feedwater Pump at 18:31:00, and the "A" Main Feedwater Pump automatically tripped at 18:32:32, resulting in a loss of all feedwater flow. The control operator manually tripped the reactor at 18:32:44 and stabilized the plant in Mode 3. <br /><br />The event was initiated by the trip of the Heater Drain Pump which was attributed to a plywood cover inadvertently left inside Feedwater Heater 3A following maintenance. In addition, the automatic turbine runback did not function as expected by the operators. This hindered their ability to stabilize the plant and avoid a reactor trip. The turbine runbacks were investigated and the response was in accordance with the design. The operators were retrained with the information obtained from the investigation of the runback functions. The plywood cover was removed from the feedwater heater.
400 | 4001989001 | 1989-01-16 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Harris | P | WE | PO | 100 | The plant was operating in Mode 1, Power Operation, at 100 percent reactor power on January 16, 1989. Plant personnel were in the process of removing a clearance on a valve n the Auxiliary Steam Condensate Tank vent line system to the Main Condenser. During the course of the restoration a direct vent path to the atmosphere from the Main Condenser was established due to a mispositioned valve and resulted in a rapid loss of condenser vacuum. A reduction of turbine load ensued and a turbine trip at 1518 hours due to low condenser vacuum. The turbine trip was immediately followed by an automatic reactor trip and a plant shutdown. <br /><br /> The Auxiliary Feedwater System actuated on Steam Generator lo-lo level to maintain water levels and the Main Steam Isolation Valves were closed to limit plant cooldown and the Plant was stabilized in Mode 3, Hot Standby. <br /><br /> The cause of the event was personnel error in not having a shift foreman clearance on a manual valve which was required to be in an abnormal position, and providing insufficient restoration details for the proper valve lineup. <br /><br /> Corrective Actions include: the appropriate personnel been counselled, the event has been discussed stressing the need for good working practices, a shift foreman clearance placed on the manual valve, and repair to the motor operated valve will be completed. <br /><br /> There were no safety consequences as a result of this event at all plant systems functioned as required with the exception of the Turbine Driven Auxiliary Feedwater Pump which tripped after 15 seconds of operation. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an Engineered safety System Feature and Reactor Protection System actuation.
400 | 4001989003 | 1989-02-06 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Harris | P | WE | PO | 100 | February 6, 1989, with the plant operating at 100% power, at 0008 the shaft of the A Main Feedwater Pump (MFP) sheared, causing a sudden reduction in feedwater flow to the steam generators. Within seconds the MFP tripped, causing a turbine runback. The operators took manual control of the feedwater regulating valves and attempted to raise steam generator levels, but the reactor tripped on low steam generator level approximately one minute after the transient began. The plant response to the reactor trip was normal, with all auxiliary feedwater pumps automatically starting to maintain steam generator levels, and the operator manually closing the main steam isolation valves to control the primary plant cooldown. The main generator exciter field breaker did not trip open, and was observed to be smoking. The breaker was locally opened and an extinguisher used on the breaker to prevent ignition. The exciter field breaker was found to have a burned out trip coil which was subsequently repaired. <br /><br /> The MFP shaft was found to be sheared near the coupling between the pump and the coupling. The damaged shaft was sent to a company laboratory, and the preliminary cause was determined to be long term cyclic fatigue. The event caused internal damage to the pump motor, as well as minor missile damage to components in the near vicinity. <br /><br /> Prior to plant restart, the undamaged B MFP shaft keyway was examined and found to be in satisfactory condition. The plant was restarted and brought to approximately 60% power on February 9. Repairs were completed to the A MFP and the nearby components on February 14, and the plant was returned to full power operations. The final results of the examination of the failed shaft will be used to determine any necessary long term corrective actions.
400 | 4001989004 | 1989-02-07 | QL4 | Loss of Non-safety-Related Cooling Water | [10 empty] | X |  |  | X | [26 empty] | X |  |  |  | X | Harris | P | WE | PO | 47 | The plant was operating in Mode 1, Power Operation, with Main Feedwater Train "B" in service at 47% reactor power. At 1055 on February 7, 1989, the sudden loss of all three Circulating Water Pumps (CWPs) resulted in the loss of all flow to the Main Condenser. The plant tripped at 1058 as a result of a sudden loss of vacuum in the Main Condenser. The Low Pressure Turbine Rupture Disks ruptured as designed, a result of the loss of vacuum in the Main Condenser. <br /><br /> The Auxiliary Feedwater System actuated subsequent to the reactor trip as a result of trip of the only operating Main Feedwater Pump. Main Steam isolation valves were closed to limit plant cooldown and the plant stabilized in Hot Standby (Mode 3). <br /><br /> This event was caused by air entering the CWP's Seal Water System and causing the pumps to trip on loss of seal flow. Air entered the Seal Water System due to a failure in the level control system for the Potable Water Hydropneumatic Tank. <br /><br /> Corrective actions included repairing failed components in the Potable Water System, replacing the rupture disks for the turbine, identifying additional modifications for the Seal Water System and the Potable Water System. <br /><br /> There was no impact on plant safety. All systems functioned as expected. This event is reported in accordance with 10CFR50.73(a)(2)(iv) as an Engineered Safety Feature actuation and a reactor protection system actuation.
400 | 4001989005 | 1989-02-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Harris | P | WE | PO | 100 | On February 22, 1989, at 1314, with the plant at 100% power and 878 net MWe, a reactor trip on low steam generator level coincident with steam/feedwater flow mismatch occurred during the performance of a calibration test procedure for steam generator level channel L-474. The section of the procedure being performed caused an isolation of feedwater to A steam generator, causing the steam/feed flow mismatch. A low level signal was already present when the channel was removed from service for the test, so the trip signal occurred almost immediately after the isolation valves closed. The plant was stabilized in hot standby at .557 Degrees F after the trip, with all three auxiliary feedwater pumps automatically starting due to low steam generator levels. <br /><br /> The cause of the trip was performance of a section of the procedure intended to be conducted during shutdown. Cautions in the procedure, intended to alert personnel of the impact on plant operation, were reviewed by the technicians, and by the operators on shift including the shift foreman, but the cautions were not sufficiently explicit to be understood by these individuals.<br /><br /> The plant was returned to service at 2255 of the same day. The procedures which test the feedwater control logic will be revised to ensure explicit instructions are provided as to the effect on performance of the test on the feedwater valve lineup. A review of other calibration procedures which could impact power operations will be conducted to ensure adequate precautions are provided.
400 | 4001989006 | 1989-03-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Harris | P | WE | PO | 100 | The plant was operating at full power producing 890 net MWe on March 14, 1989. Fire Protection Technicians had difficulty in resetting the Fire Protection system deluge valve that supplies the sprinkler system over the Main Feedwater Pumps (MFPs). Their subsequent actions resulted in a small amount of water being sprayed on the "B" MFP. Shortly afterward, an internal short occurred in the motor junction box. The energy from the short blew the door from junction box. The plant controls automatically responded as designed but the reactor tripped on low level in the "A" Steam Generator approximately 71 seconds after the "B" MFP trip. Damage was confined to the motor lead connections and steam plant performance instrument tubing in the trajectory of the junction box door. <br /><br /> The plant trip was caused by plant design considerations. The shorting of "B" MFP motor lead was due to gaps in the electrical enclosure for the "B" MFP motor that allowed water to enter the junction box. Previous exposure of the junction box internals to water spray caused the deterioration of wiring insulation. <br /><br /> The damage to "B" HFP was repaired and the water tightness of the "A" MFP enclosure corrected. The procedures used by Fire Protection personnel will be revised and applicable personnel retrained. The response of the plant will be reviewed to determine if there are any modifications which would allow a successful runback if a loss of a MFP at high power occurs.
400 | 4001989017 | 1989-10-09 | H1 | Fire | [7 empty] | X | [25 empty] | X | X | [10 empty] | Harris | P | WE | PO | 100 | On October 9, 1989, at 2305, a generator and main power transformer phase differential relay tripped the lockout relay of the main generator, tripping the generator and causing a turbine and reactor trip from 100% power. The reactor was stabilized in hot standby at 557 degrees F on auxiliary feedwater and condenser steam dumps. <br /><br /> Actuation of the generator and main power transformer differential relay and subsequent generator trip was caused by multiple ground faults. <br /><br /> The ground faults destroyed the neutral grounding bus and caused three fires: an oil fire at the "B" main power transformer, a hydrogen fire underneath the main generator and a third small oil fire in the generator housing. <br /><br /> An alert was declared, and the site fire brigade responded to the fires, assisted later by off site fire departments. All fires appeared out by 0145, and the emergency condition was terminated at 0245.<br /><br /> The initiator of the ground faults has been identified as aluminum debris in the isolated phase bus duct, which was deposited in the bus duct from previous failures of the duct cooling system dampers. Arcing from the aluminum debris in the bus led to a double phase to ground fault at the "B" main power transformer. Magnetic forces from this fault broke insulators in "A" phase and "B" phase of the isolated phase bus duct. The "A" phase conductor contacted the bus enclosure creating another ground fault. These faults elevated the voltage at the generator neutral and led to another ground fault in the neutral grounding transformer cubicle. <br /><br /> The turbine-driven auxiliary feedwater pump started after the reactor trip, but the pump tripped shortly thereafter. The cause of the trip is believed to be a spurious overspeed trip signal from the tachometer. <br /><br /> Design changes and repairs are being conducted while the plant conducts a refueling outage.
400 | 4001991010 | 1991-06-03 | QR8 | Spurious Reactor Trip | [45 empty] | Harris | P | WE | PO | 100 | The plant received an automatic Reactor Trip on RCS Low Flow during the performance of a maintenance calibration procedure on an RCS flow transmitter. All rods fully inserted on the trip signal. The "A" Reactor Trip Breaker did not open on the automatic reactor trip signal but did open on a subsequent manual trip signal. The failure of the "A" Reactor Trip Breaker to open was due to a failed undervoltage output driver card in the "A" Solid State Protection System. The failure of the undervoltage output driver card was the same as described in IE Notice 85-13 and had apparently occurred during maintenance on May 18, 1991. The failed undervoltage output driver card was replaced with a modified card which prevents this failure mechanism. <br /><br /> This event is being reported as a Technical Specification violation and Engineered Safety Features actuation per 10CFR50.73 (a)(2)(i)(B) and 10CFR50.73 (a)(2)(iv).
400 | 4001992007 | 1992-07-12 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Harris | P | WE | PO | 100 | On July 12, 1992 at 0208 hours an automatic turbine trip and reactor trip occurred due to low condenser vacuum. All safety systems functioned as required, including an automatic Auxiliary Feedwater (AFW) System actuation on steam generator lo-lo level. Main control room personnel stabilized the plant using the appropriate emergency operating procedures. The condenser low vacuum was caused by a failure of the north low pressure turbine exhaust boot seal. This seal is a fabric reinforced rubber expansion joint and appears to have failed due to routine fatigue caused by aging. The failed portion of the seal was repaired on July 13, 1992 and plans were made to replace the entire boot seal in the upcoming refueling outage which begins in September 1992. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an Engineered Safety Feature and Reactor Protection System actuation.
400 | 4001992009 | 1992-07-15 | QC5 | Loss of Non-safety-Related Bus | [45 empty] | Harris | P | WE | PO | 30 | On July 15, 1992 a supply breaker failure occurred while starting Exhaust Fan E-18 which resulted in the fan running with both the inlet and outlet dampers closed. This condition created a potential for fire in the fans charcoal filter unit. Remote and local efforts were made to trip open the breaker and secure the fan, but were unsuccessful, The control room staff determined that the supply bus for the E-18 fan (Bus #1D-2) would have to be deenergized to allow the fan breaker to be racked out and the fan secured. When 1D-2 was deenergized it caused the 'B' Main Feed Pump and 'B' Condensate Booster Pump Recirculation Valves to fail to the full-open position. This caused the running Main Feed Pump to trip on low suction pressure and resulted in rapidly decreasing Steam Generator water levels. A manual reactor trip was initiated by the control operator as required. All safety systems functioned as required including an automatic Auxiliary Feedwater System actuation. The cause of this event was a failure of the E-18 supply breaker. This breaker was replaced and satisfactorily tested on July 15, 1992.
400 | 4001992010 | 1992-07-17 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Harris | P | WE | PO | 100 | On July 17, 1992 at 1218 hours, an automatic turbine trip and reactor trip occurred due to low condenser vacuum. All safety systems functioned as required, including an automatic Auxiliary Feedwater System actuation on steam generator lo-lo level. One Main Steam safety valve (1MS-47) was also observed to open and reseat. Main control room personnel stabilized the plant in mode-3 at normal operating temperature and pressure using the appropriate emergency operating procedures. The cause of the low vacuum condition was a failure of the north low pressure turbine exhaust boot seal. The corrective action for this failure was to replace the entire boot seal on both low pressure turbines instead of the previously performed local repair. Replacement of the boot seals and satisfactory setpoint testing of 1MS-47 were completed on July 21, 1992 and the unit was placed back on line at 2045 on July 22, 1992. <br /><br /> This event is being reported in accordance with 10CFR50.73 (a)(2)(iv) as an unplanned Engineered Safety Feature and Reactor Protection System actuation.
400 | 4001995010 | 1995-10-12 | QR5 | Turbine Trip | [45 empty] | Harris | P | WE | PO | 5 | During performance of the Turbine Mechanical Overspeed Trip Test, the operator incorrectly placed the Overspeed Protection Controller (OPC) switch in the OPC TEST position instead of the OVERSPEED TEST PERMISSIVE position. The OPC functioned as designed, causing the turbine governor and intercept valves to close and turbine speed to reduce. The OPC switch was returned to the IN SERVICE position, which caused the turbine control system to attempt to return the turbine to 1800 rpm causing an increase in steam flow to the turbine. The increase in steam flow caused steam generator levels to swell, generating a Steam Generator High-High Level signal. This resulted in a Turbine Trip, Reactor Trip, and Main Feedwater Isolation. The trip of the Main Feedwater Pump generated an Auxiliary Feedwater start signal to both Motor Driven AFW pumps. The plant was stabilized using Emergency Operating Procedures. <br /><br /> The causes of this event are a lack of operator knowledge on the turbine control panel; and Control Room command and control, teamwork, and communications. This event had minimal safety significance. Reactor power remained less than 10% during this transient and Tave decreased eleven degrees to 548 Degrees F. During the Turbine/Reactor trip systems responded and functioned as required. This event is being reported per 10CFR50.73(a)(2)(iv) as an unplanned ESF Actuation. Corrective actions to be taken include enhancing switch marking and additional training for the Operating crews on the importance of command and control, teamwork, and communications.
400 | 4001995011 | 1995-11-05 | QR9 | Spurious Engineered Safety Feature Actuation | [10 empty] | X | [28 empty] | X | [5 empty] | Harris | P | WE | PO | 100 | On November 5, 1995, A-Train Engineered Safety Feature Actuation System (ESFAS) slave relay surveillance testing was in progress. While performing the test portion that verifies the operability of the Main Steam Line Isolation Signal circuitry, a 'Low Steam Line Pressure Reactor Trip/SI' signal was generated. This occurred when a contact failed to maintain continuity on the K809 relay and eliminated the 'block' function to the 'A' Main Steam Isolation Valve (MSIV), which resulted in the 'A' MSIV closing. As the valve closed and turbine throttle valve position remained constant, increased steam load was carried by 'B' and 'C' Steam Generators (SGs). This resulted in a pressure decrease in the 'B' and 'C' main steam lines due to increased steam flow. The rate compensation feature associated with the low steam line pressure SI initiated a low steam line pressure Reactor Trip/SI Signal for 'C' steam line. Automatic systems responded as required and main control room operators took appropriate actions to stabilize the plant in Mode-3 (Hot Standby). An Unusual Event was declared at 0805 due to the ECCS actuation. The UE was then exited at 0912 based on the termination of SI.<br /><br /> On November 6, 1995, continued ESFAS slave relay testing was being performed following the Reactor Trip/SI event from the previous day. During this testing the Auxiliary Feedwater (AFW) Flow Control Valves fully opened from their original throttled position. While this valve actuation was in accordance with system design, it was not recognized in the procedure. Thus, operators performing the test did not expect the valve operation. The test being performed is normally performed in Mode-1 with the AFW FCV's fully open. throttled to control Steam Generator (SG) level. The operators recognized that the valves were opening and reestablished Steam Generator level control prior to exceeding the normal operating band. During the investigation of this actuation, a similar occurrence was identified where the AFW FCV's partially opened during testing on October 30, 1994. At that time the actuation was not recognized as reportable, but should have been. <br /><br /> This LER revision provides additional information from laboratory failure analysis of the K809 relay contacts which failed to remain closed and caused the unplanned Reactor Trip/Safety Injection event on November 5, 1995.
400 | 4001996008 | 1996-04-25 | QR5 | Turbine Trip | [45 empty] | Harris | P | WE | PO | 100 | On April 25, 1996 at approximately 2107 with the unit operating in Mode 1 at 100% power, a turbine trip/reactor trip occurred due to a main generator lockout. The generator lockout was caused by the failure of a manual disconnect for one of two unit output breakers. At the time of the failure, full generator output was being routed through the breaker whose disconnect failed. During the 1E Bus (B train bus) fast transfer process from the Unit Auxiliary Transformer to the Startup Auxiliary Transformer, a momentary contact closure caused a false under-voltage signal. This under-voltage signal resulted in a loss of power to several electrical busses. Secondary system equipment was secured due to the loss of Normal Service Water. The "A" Emergency Service Water pump started and supplied its header. The "B" bus under-voltage signal caused the Loss of Offsite Power sequencer program to start. Appropriate "B" train safety equipment started as required. The "A" train successfully completed a fast transfer to the Startup Auxiliary Transformer. However, the "A" Emergency Diesel Generator Control Panel status lights indicated that the EDG was in the "Maintenance" mode, rather than the "Operational" mode, which indicated a circuitry problem. Subsequent investigation determined that these status lights were affected by the false under-voltage signal that had been generated. Isolation signals were received for the Containment and Control Room Isolation Systems due to radiation monitor power loss. At approximately 2152, it was noted that the Charging/Safety Injection Pump suction had transferred from the Volume Control Tank (VCT) to the Refueling Water Storage Tank. The swapover occurred due to the loss of electrical power to the boric acid flow transmitter. Operators stabilized the unit in Mode 3. The disconnect failure was caused by improper mating of the contact surfaces and inadequate preventive maintenance. The "A" and "B" phase disconnects for the affected breaker were replaced and the other switchyard disconnect switches were inspected for proper seating. After returning the unit to service, thermography monitoring of the unit output breaker disconnects showed elevated temperatures. The unit was taken off-line and the disconnect contacts on the generator bus sides of the unit output breakers were refurbished. The unit returned to service and subsequent thermography readings indicated expected operating temperatures for the disconnects. This LER revision provides additional information regarding the Normal Service System problems following the April 25, 1996 reactor trip.
400 | 4001996018 | 1996-09-03 | QL4 | Loss of Non-safety-Related Cooling Water | [45 empty] | Harris | P | WE | PO | 100 | On September 3, 1996 at approximately 2338 hours, with the plant operating in mode 1 at 100% power and the "B" Normal Service Water (NSW) pump in service, operators in the main control room received numerous NSW system alarms and observed indication of zero flow and pressure in the NSW header. The Reactor Operator manually started the standby "A" NSW pump to restore flow, but the pump tripped after running for less than two minutes. When re-start attempts on the "A" NSW pump failed, a manual reactor trip was initiated at approximately 2342 hours. Plant systems responded as expected, including an automatic start of the Auxiliary Feedwater System and the unit was stabilized in mode 3 (Hot Standby). <br /><br /> The cause of this event was a mechanical failure of the "B" NSW pump and the failure of the "A" NSW to remain running once manually started. The "B" NSW pump shaft sheared. <br /><br /> Additional investigation was subsequently completed to determine the cause of the "A" NSW pump trip. This investigation revealed that the torque switch on the pump's discharge valve (1SW-289) was actuating and this was preventing the valve from opening to the 10% open position, which is required for pump operation.<br /><br /> Corrective actions included restoring the "A" NSW pump to service, performing a secondary plant walkdown to support plant re-start and evaluating the acceptability of having only one NSW pump available during plant operation while repairs continued on the "B" NSW pump. Subsequent actions included restoring the "B" NSW pump, completing the failure analysis for the "B" NSW pump sheared shaft, and completing the additional investigation into the "A" NSW pump trip that resulted in this LER revision. <br /><br /> This event is reportable per 10CFR50.72 and 10CFR50.73. A 4-hour non-emergency report was made to the NRC at approximately 0207 via the emergency notification system.
400 | 4001997001 | 1997-01-31 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Harris | P | WE | PO | 97 | POWER LEVEL - 097%. On January 31, 1997, with the plant operating in Mode 1 at 97% power, an automatic reactor trip resulted from steam generator low-low level in the 'A' Steam Generator (S/G). This trip occurred while performing quarterly surveillance testing on the Main Feedwater and Main Steam Isolation Valves (Operations Surveillance Test, OST-1018). During this testing, the Main Feedwater Isolation valve to the 'A' S/G (1FW-159) was taken to the TEST position which should have caused the valve to stroke in the closed direction to the 90% open position. However, 1FW-159 stroked fully shut causing a decrease in feed flow and S/G level. The reactor operator performing the surveillance test in the main control room recognized that 1FW-159 had fully shut and attempted to restore feedwater flow the S/G by taking the control switch for 1FW-159 to the SHUT/RESET position and then holding the control switch in the OPEN position. The 'A' feedwater regulating valve was also fully opened to increase feed flow. 1FW-159 would not re-open, thus resulting in a continued decrease in 'A' S/G level. A locally stationed auxiliary operator reported that 1FW-159 opened approximately 2-3 inches then re-shut several times. Based on these conditions, the Unit Senior Control Operator commenced a load reduction to reduce steam demand and made plans to manually trip the reactor if S/G level decreased to 40%. (S/G low low level reactor trip setpoint is 38.5%) At 0438 hours, with lowest main control board indicated S/G level at approximately 44%, an automatic S/G low-low level reactor trip occurred. Feedwater system started as required. All support systems functioned as required except for the pressurizer bank-A backup heater supply breaker, which tripped open after approximately ten minutes of operation. The plant was then stabilized in Mode-3 (Hot Standby). This event was caused by faulty hydraulic relays (solenoid operated shuttle valves) that control the position of 1FW-159. Investigation revealed that the shuttle valve's o-ring seals were leaking by which prevented proper hydraulic oper
400 | 4001997016 | 1997-06-08 | QR8 | Spurious Reactor Trip | [45 empty] | Harris | P | WE | PO | 28 | On June 8, 1997, with the plant at approximately 28% power in Mode 1, a Reactor Trip occurred due to personnel error while attempting to adjust a Power Range (PR) Nuclear Instrumentation (NI) channel following the performance of a calorimetric. The plant was performing a startup following a refueling outage, when PR NI channel N41 was declared inoperable. The PR Neutron Flux High Setpoint, Low Setpoint, High Flux Rate, and Overtemperature differential temperature trips for N41 were placed in the tripped condition per TS 3.3.1 Table 3.3-1 Action 2 a. and 6 a. When the Plant reached approximately 28% Reactor Power the PR NI's were adjusted to match calculated power in accordance with the calorimetric procedure. PR NI channel N41 was adjusted first. PR NI channel N42, was to be adjusted next. As the operator unlocked the coarse adjustment potentiometer, N42 spiked, generating a negative rate trip signal on PR NI channel N42. This signal coupled with the rate trip signal from N41 being inoperable, met the 2/4 coincidence for the PR Flux Rate Trip and a reactor trip occurred. Following the reactor trip, a breaker failure caused a non-safety 6.9 kV bus to deenergize, resulting in the trip of the only running Main Feedwater Pump and initiated an Engineered Safety Features Actuation Signal start of both Motor - Driven Auxiliary Feedwater (MDAFW) Pumps. Harris Nuclear Plant (HNP) has performed the following corrective actions: (1) An Operation's Night Order was issued prohibiting adjustment of a PR NI when a redundant channel is inoperable and on the use of diverse and redundant indications for instrumentation. (2) The Manager - Operations discussed this event with the operating crew. (3) The breaker for auxiliary bus 1A was replaced prior to startup. (4) Procedures were revised to provide operators an aid in identifying, at the PR channel instrument drawer, inoperable PR NI channels. (5) Procedures were revised preventing PR NI adjustment channels with a redundant PR NI channel in a tripped condition. (6) License operators reviewed LER 97-01 6-00 for lessons learned from the causes of this event.
400 | 4001997019 | 1997-07-20 | QR5 | Turbine Trip | [45 empty] | Harris | P | WE | PO | 100 | At approximately 0256 hours on July 20, 1997, with the plant at 100% power in mode 1, a Turbine Trip/Reactor Trip occurred due to a generator lock-out resulting from loss of the main generator excitation field. As a result of the trip, the Auxiliary Feedwater (AFW) System automatically started as required to provide feedwater flow to the Steam Generators (S/G). Operators in the main control room immediately implemented Emergency Operating Procedure (EOP Path-1) and upon verification that a safety injection was not required and had not occurred, entered the Reactor Trip Response procedure (EOP-EPP-004) to stabilize the plant. Approximately 5 minutes after the plant trip, AFW flow to the S/Gs was secured in order to return Reactor Coolant System (RCS) temperature back to 557 degrees (RCS temperature reached approximately 548 degrees during AFW operation). Various plant components not required for plant recovery were observed tripped in the main control room due to the electrical transient involved in the plant trip. Automatic protection and safeguards systems functioned as required and the plant was stabilized in mode 3 (Hot Standby). The cause of the Turbine Trip/Reactor trip was a three phase fault that collapsed the excitation field in the main generator, resulting in a generator lockout. Investigation could not conclusively determine the reason for the electrical fault in the generator exciter. However, the most probable cause appears to be entry of foreign material into the exciter housing that caused multiple shorts on the exciter diode wheel. Corrective actions for this event included replacement of the exciter rotor assembly and inspections to ensure no foreign material was present in the exciter and exciter housing area. Additional actions will include strengthening the plant's Foreign Material Exclusion Program with regards to the Generator Exciter. This will be performed via a revision to Maintenance Procedure, PM-E0045 "Generator Exciter Cleaning, Inspection, and Testing" to specify cleanliness close-out requirements for the Generator Exciter.
400 | 4001998007 | 1998-10-23 | QR6 | Manual Reactor Trip | [45 empty] | Harris | P | WE | PO | 94 | At 19:28 on October 23, 1998, the control room staff commenced a planned shutdown of the unit, from 100% power, for entry into a refueling outage. All four Governor Valves (GVs) on the unit's High Pressure Turbine unexpectedly went full open while the unit was at approximately 85% power. Indicated power increased to approximately 94% prior to the unit being manually tripped by the operators. All turbine control manipulations were performed as required by the operating procedure and in accordance with all written vendor recommendations; however, some unofficial, verbal vendor recommendations regarding transfers from MANUAL control to OPER AUTO control were not performed. It is believed that these recommendations may have resulted in a successful transfer from TURBINE MANUAL to OPER AUTO control of the Digital Electro-Hydraulic (DEH) system. Therefore, the root cause of this event was a failure to incorporate verbal vendor guidance into operating procedures. This additional vendor guidance will be verified and added to applicable procedures, as well as performing diagnostic testing of the DEH system, prior to the next turbine startup. The Harris Nuclear Plant uses a Westinghouse P2000, MOD1 type DEH computer.
400 | 4001999002 | 1999-01-14 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Harris | P | WE | PO | 100 | At approximately 09:18 on January 14, 1999, with the unit at 100% power, personnel performing a relay calibration failed to remove a temporary blocking device prior to reinstalling the relay. This blocking device simulated a continuous trip signal on the output of the undervoltage timing relay; therefore, reinstalling the relay simulated an undervoltage trip signal to the associated bus. Loads powered from this bus included one of the plant's three Reactor Coolant Pumps (RCPs) and the feeder breaker for another bus, which also powered one Reactor Coolant Pump. This loss of power to two of the plant's three RCPs (while above 10% power) satisfied the logic for an automatic reactor trip. Safety systems functioned as required, including the automatic start of the three auxiliary feedwater pumps. Although the procedure for performing the calibration activity directed the technicians to remove the blocking device, the individuals failed to do so. The root cause of this event is human error attributed to the way the technicians were using the procedure (i.e., although one of the technicians had a copy of the procedure in his hand, the technicians were performing some steps from memory). Corrective actions taken have been: 1) Counseled the personnel involved in this event, including their supervision; 2) Conducted a stand-down meeting for site personnel on this and other recent human performance events, and; 3) Created a high-visibility device to be used as a blocking device when calibrating relays. Planned corrective actions include: 1) Revision of the applicable procedure (PIC-E070) to provide more specific guidance on steps applicable to these types of relays.
400 | 4001999004 | 1999-03-12 | QP5 | Excessive Feedwater Flow | [45 empty] | Harris | P | WE | PO | 100 | At 06:39 on March 12, 1999, the unit experienced an automatic reactor trip from 100% power. The unit tripped on a high water level trip signal on one of the three steam generators. The 'hi-hi' steam generator water level signal trip setpoint is 82.4 percent on the narrow range level scale. Just prior to the automatic trip, the 'C' Steam Generator (SG) water level was observed to be increasing in an uncontrolled manner with its Feedwater Regulating Valve (FRV) in automatic control. The control room operators took manual control of the 'C' FRV, in an attempt to restore water level to its normal range. The FRV response, as observed from the controller output signal and the resulting feed flow indications, was slower and not as uniform as expected. After approximately eight minutes of attempting to control the 'C' steam generator water level in manual, the performance of the valve positioner degraded to the point where operator control was highly questionable. The operators had set a limit, at which they would initiate a manual reactor trip; however, an automatic trip occurred prior to their taking the planned action. The most probable failure mechanism for the 'C' FRV is a combination of a loose stroke adjustment screw on the air-operated valve positioner and a sticking pilot valve within that same positioner. This degradation in the material condition of the valve's positioner is attributed to an inadequate preventative maintenance program/schedule for the Feedwater Regulating Valves. Corrective actions that have been taken include: 1) replacing the positioners on all three Feedwater Regulating Valves, including a verification that the stroke adjustment screw on each is not loose, and 2) Determining that similar air operated valve positioners do not have a potential for similar failures which may jeopardize plant safety or reliability. Planned corrective actions include reviewing and revising, as applicable, the preventative maintenance schedules for Bailey air operated valve positioners.
400 | 4001999009 | 1999-12-14 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Harris | P | WE | PO | 100 | On December 14, 1999 at 0353, the Harris Nuclear Plant (HNP) manually tripped the reactor from 60% power. At 0352 on December 14, 1999 the "A" Condensate Pump tripped due to a ground fault on the associated motor. The trip of the "A" Condensate Pump resulted in subsequent trips of the "A" Condensate Booster Pump and the "A" Main Feedwater Pump. The main turbine load control circuitry sensed the trip of the "A" Main Feedwater Pump and automatically reduced turbine power to approximately 60% (turbine runback). The reactor trip coupled with the loss of the "A" Condensate and Feedwater train resulted in a reduction of steam generator water levels. The main control room staff manually started the three auxiliary feedwater pumps in accordance with the applicable abnormal operating procedure. The steam generator levels continued to lower until the main control room staff manually tripped the reactor at approximately 40% steam generator level prior to reaching the steam generator low-low level automatic trip setpoint of 38.4%. Additionally, following the trip an auxiliary feedwater (AFW) actuation signal was generated due to the low-low steam generator level. However, as stated previously, the auxiliary feedwater pumps had been manually started during the transient therefore, the AFW actuation signal did not start any additional components. Cause of this event: A ground fault on the "A" Condensate Pump motor caused a loss of the "A" Condensate and Feedwater train that resulted in low steam generator water levels and a subsequent manual reactor trip and AFW actuation. Corrective actions include: The "A" Condensate Pump motor was replaced on December 16, 1999.
400 | 4002000005 | 2000-06-20 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Harris | P | WE | PO | 100 | On June 20, 2000 at 1631 hours with Harris Nuclear Plant (HNP) at 100% power, control room operators initiated a manual reactor trip in response to lowering level in the "A" Steam Generator (SG). The cause of the lowering level in "A" SG was due to the unexpected closure of the "A" Main Feedwater Isolation Valve (MFIV). The low water level in "A" SG resulted in an automatic actuation of both motor-driven auxiliary feedwater pumps. The control room operators restored "A" SG water level following the reactor trip. There were no other structures, systems, or components that were inoperable at the start of the event and that contributed to the event. Cause of this event: A random manufacturing defect of a diode in a solenoid valve for the "A" MFIV actuator. Corrective actions include: The defective solenoid valve for the "A" MFIV was replaced.
400 | 4002002001 | 2002-01-02 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Harris | P | WE | PO | 7 | On January 2, 2002 at 0305, the Harris Nuclear Plant (HNP) was manually tripped, during a plant startup following RFO-10, due to a failure of a Main Feedwater Regulating Valve Bypass Valve. The plant trip was initiated at approximately 7% reactor power when Steam Generator (SG) divergent level swings were observed on all three SGs. SG level was being controlled in automatic by the Main Feedwater Regulating Valve Bypass Valves (MFRVBV) and the valves were traveling full open to full shut in response to the level swings. Following a full shut swing, "C" MFRVBV (1FW-198) failed to respond to an automatic open demand signal from the associated controller located on the Main Control Board. The Balance of Plant operator attempted to open 1FW-198 by taking the controller to manual with a 100% demand, however, indication of actual valve position showed the valve to be shut. With "C" SG level at 30% narrow range level indication, the Unit Senior Control Operator (USCO) directed a manual reactor trip. The manual reactor trip was successful. Cause: Component Failure: Component degradation. The I/P converter for "C" MFRVBV (1FW 198) experienced a failure attributed to an internal blockage of air. Corrective actions: Replaced the I/P on "C" MFRVBV with a Masoneilan Model 7000 I/P.
400 | 4002002002 | 2002-07-13 | QR6 | Manual Reactor Trip | [45 empty] | Harris | P | WE | PO | 85 | At about 1:10 am on July 13, 2002, with the plant reducing load to perform a turbine valve test, a manual reactor trip was performed due to a Main Turbine Digital Electro-Hydraulic (DEH) control system malfunction. While reducing load to 900 MWe; governor valve 4 indicated shut with demand still indicating 8.4%. The DEH "HOLD" button was pressed but the other three governor valves continued closing. A manual reactor trip was inserted due to the uncontrolled turbine load decrease. An automatic start of the Auxiliary Feedwater Pumps occurred due to low steam generator level during the transient. Cause: A component failure led to conditions requiring the manual reactor trip. Component failure and failure to incorporate industry operating experience into the preventative maintenance program, operating procedures, and training are the root causes identified for this event. Corrective Actions: The failed component was replaced. Ownership of the DEH computer controls system has been transferred from the Nuclear Information Technology Unit to Harris Engineering. Operations procedures are being revised to provide guidance for operator control of turbine DEH system. Training will be provided to operators when MANUAL control of DEH is appropriate.
400 | 4002002003 | 2002-08-15 | QR2 | Loss of Primary Flow (RPS Trip) PWR | [45 empty] | Harris | P | WE | PO | 100 | At 21:26 on 8/15/02 the Harris Plant tripped from Mode 1 and approximately 100% power due to Reactor Coolant Pump (RCP) momentary undervoltage (UV) on two out of three RCPs. The under voltage relays associated with the "B" and "C" RCPs actuated simultaneously making up the required reactor protection logic to initiate a reactor trip as designed. An Auxiliary Feedwater System automatic start also occurred during this event due to low steam generator level resulting from the plant transient. The offsite power supply to Harris Plant and the onsite power distribution systems remained energized throughout the event. Cause: The cause of the reactor trip was the momentary grid undervoltage condition. The cause of the undervoltage condition was a grid transient generated when a faulted transformer was loaded onto a 230 KV transmission line in Raleigh, NC, approximately 20 miles from the Harris Plant. Corrective Actions: The Carolina Power & Light Transmission Department evaluated the event and developed an action plan to decrease the probability of a similar grid event. The Harris Plant will monitor actions by the Transmission Department. No specific actions will be taken for the Harris Plant itself based on equipment and personnel performing in accordance with expectations.
400 | 4002003001 | 2003-05-18 | QR5 | Turbine Trip | [45 empty] | Harris | P | WE | PO | 27 | On May 18, 2003, with the reactor at approximately 27% power following a refueling outage (RFO-11), the reactor was automatically tripped from a turbine trip-reactor trip signal. Plant equipment functioned as required. The operations staff responded to the event in accordance with applicable plant procedures. The plant stabilized at normal operating no-load reactor coolant system (RCS) temperature and pressure following the reactor trip. The most likely failure mode is an electrical failure of the turbine overspeed sensing probe that resulted in generation of a spurious turbine overspeed signal. This spurious signal subsequently resulted in the reactor trip. An installed spare turbine overspeed sensing probe has been placed in service. The sensing probe that was in service at the time of the trip remains installed in the system and is unavailable for forensic analysis until the next refueling outage (RFO-12). The root cause is a design vulnerability in which a single component failure can result in a spurious turbine overspeed signal and subsequently cause a reactor trip. Corrective action includes modifying the electrical turbine overspeed circuit to remove single-point vulnerability for turbine overspeed sensing probe failures.
400 | 4002003002 | 2003-05-20 | P1 | Total Loss of Feedwater Flow | [13 empty] | X | [30 empty] | X | Harris | P | WE | PO | 20 | On May 20, 2003 at 0453 with the reactor at approximately 20 percent power, the reactor was manually tripped in response to an automatic trip of the operating main feedwater pump (MFP). The WA' MFP tripped in response to an unplanned trip of the A" condensate booster pump (CBP). Both motor-driven auxiliary feedwater (AFW) pumps started due to the trip of the MFP. Safety systems functioned as required. The operations crew responded to the event in accordance with applicable plant procedures. The plant was stabilized at normal operating no-load reactor coolant system temperature and pressure following the reactor trip. The cause of the unplanned trip of the "A" CBP was due to low oil pressure after a gear in is variable speed fluid coupling (VSFC) failed following vendor refurbishment. Immediate corrective action was to replace the VSFC. Additional corrective action will be to specify a "run-in" of the gear set following VSFC refurbishment to develop adequate load-carrying capability of the gear teeth.
400 | 4002003003 | 2003-06-14 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Harris | P | WE | PO | 100 | On June 14, 2003 at 1053 EST with the reactor at 100% power, the reactor was manually tripped In response to an automatic trip of one of two operating main feedwater pumps (MFPs). The “B” MFP-tripped following the failure of a Westinghouse (NAL2) bistable comparator card associated with MFP feedwater flow control system. This card failure generated a spurious low-flow alarm and low-flow trip signal to the "B" MFP. Both motor-driven auxiliary feedwater (AFW) pumps and the turbine-driven AFW pump auto-started due to lo-lo steam generator level. Safety systems functioned as required. The operations crew responded to the event in accordance with applicable plant procedures. The cause of the unplanned trip of the “B" MFP was due to a failed T30 transistor on a NAL2 comparator card. Immediate corrective action was to replace the failed card. In addition, HNP will modify the system by the end of the next refueling outage (Fall, 2004) such that failure of an NAL2 bistable comparator card in the MFP control system will not cause an unnecessary MFP trip.
400 | 4002003005 | 2003-08-17 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Harris | P | WE | PO | 100 | On August 17, 2003 at 1551 with the reactor at approximately 100% power, the Harris Nuclear Plant (HNP) manually tripped the reactor in response to an automatic trip of one of two operating condensate pumps (CPS). The "A" CP tripped following an electrical short in its motor due to a severe lightning storm. The trip of the "A" CP resulted in subsequent trips of the "A" condensate booster pump and the "A" main feedwater pump (MFP) as designed. As directed by plant procedures, the operations crew manually tripped the reactor upon the trip of a MFP with initial reactor power greater than 90%. The manual reactor trip coupled with the trip of the "A" condensate and feedwater train resulted in a reduction of steam generator (SG) water levels. The subsequent low-low SG levels resulted in an auto-start of the auxiliary feedwater pumps as designed. Safety systems functioned as required. The cause of the unplanned trip of the "A" CP motor was a lightning voltage surge that overcame the dielectric strength of the motor winding insulation (i.e., an electrical short). In addition, the grounding system was not effective at protecting the "A" CP motor from a lightning strike. Corrective actions included replacing the "A" CP motor and installing surge protection. In addition, HNP will enhance the "A" CP grounding system and install surge protection on the "B" CP motor.
400 | 4002004003 | 2004-05-06 | QR3 | Reactivity Control Imbalance | [45 empty] | Harris | P | WE | PO | 100 | On May 6, 2004 at 12:52 PM EDT, the reactor automatically tripped from 100% power due to a power range flux rate signal. The operations staff responded to the event in accordance with applicable plant procedures. The plant was stabilized at normal operating no-load reactor coolant system (RCS) temperature and pressure following the reactor trip. The trip was caused by the failure of a regulation card in the Rod Control System [AA]. This resulted in the loss of stationary gripper coil current to the Control Rod Drive Mechanisms (CRDMs) for one of the three Shutdown Banks of control rods. Loss of stationary gripper coil current resulted in the insertion of the four associated control rods into the reactor core which led to the high power range negative flux rate trip. Corrective actions included replacing the failed card with a spare and performing visual inspection and testing of additional cards in the Rod Control System Power Cabinets. These actions were completed prior to plant startup.
400 | 4002005002 | 2005-05-01 | QP4 | Partial Loss of Condensate Flow | [45 empty] | Harris | P | WE | PO | 100 | On May 1, 2005 with the reactor at approx . 100% power, operators at the Harris Nuclear Plant (HNP) manually tripped the reactor in response to an automatic trip of an operating condensate pump (CP) . The "B" CP tripped due to a motor shaft shear at the top of the motor coupling hub. By design, the trip of the "B" CP caused subsequent trips of the "B" condensate booster pump and the "B" main feedwater pump (MFP). As directed by plant procedures, the operators manually tripped the reactor upon the trip of a MFP with initial reactor power greater than 90% . The manual reactor trip coupled with the trip of the "B" condensate and feedwater (FW) train resulted in a reduction of steam generator (SG) water levels. The subsequent low-low SG levels resulted in an auto-start of the auxiliary FW pumps as designed. Safety systems functioned as required. The cause of this unplanned trip was the loss of FW to the steam generators initiated by the motor shaft shear for the "B" CP . The root cause of the motor shaft shear is inadequate controls for a vendor weld repair. Completed corrective actions include replacing the failed motor . Planned corrective actions include improving process controls for shaft weld repairs and subsequent non-destructive examination, improving seal installation techniques, establishing coupling inspection criteria, and improving monitoring capability of the CPs.
400 | 4002006003 | 2006-09-19 | QR5 | Turbine Trip | [45 empty] | Harris | P | WE | PO | 100 | At 09:59 EDT on September 19, 2006, with the reactor at 100 percent power, the reactor automatically tripped from a turbine trip due to a generator lockout signal. There was no inoperable equipment at the start of this event that contributed to this event. Safety systems functioned as required and operators responded in accordance with approved procedures. Post trip discovery found that a ground fault protective relay module failure caused by self heating actuated the 86/G1A Main Generator Lockout Relay which initiated a turbine and reactor trip. Further investigation revealed that no module specific inspection requirements exist for the generator, main transformer and auxiliary transformer protective relay modules to detect self heating concerns. Completed corrective actions include replacing the failed relay module for the main generator stator ground detection circuit. Additional corrective actions are to establish specific inspection requirements for the generator, main transformer and auxiliary transformer protective relays and to brief appropriate maintenance personnel.
400 | 4002007003 | 2007-09-28 | QR7 | Other Reactor Trip (Valid RPS Trip) | [45 empty] | Harris | P | WE | PO | 27 | At 22:32 on September 28, 2007, while reducing power for Refueling Outage (RFO) 14, a fault pressure trip on "1A" Startup Transformer (SUT) caused a reactor trip/turbine trip with a loss of all Reactor Coolant Pumps (RCP) and a subsequent Auxiliary Feedwater (AFW) actuation. There was no inoperable equipment at the start of this event that contributed to this event. Safety systems functioned as required and operators responded in accordance with approved procedures. Post trip discovery found that the data to determine the available margin to the "1A" SUT sudden pressure trip setpoint was not available at the time of the design and installation of the Qualitrol 930 series sudden pressure relays. Additionally, it was determined that that the relay was out of calibration in the more sensitive direction. Completed corrective actions include replacing the Qualitrol 930 series relay with the Qualitrol 900 series relay and conducting testing to validate that the "1A" SUT was not damaged. Additional corrective actions are to use a temporary modification to gather data on the "1A" SUT to determine operating margin and implement appropriate design changes to the sudden pressure relays on the SUTs.
400 | 4002008002 | 2008-08-11 | QL6 | Condenser Leakage | [45 empty] | Harris | P | WE | PO | 21 | On August 10, 2008 the Harris Plant experienced an increase in condenser backpressure and changes in the Steam Generator secondary side chemistry. A decision was made to shut the unit down due to rising condenser backpressure. At approximately 21% power, the unit was manually tripped by operators due to reaching predetermined administrative limits. The plant promptly attained normal operation no-load temperature and pressure, and no unusual conditions or additional actuations were observed for plant equipment following the reactor and turbine trip. The increase in condenser backpressure was caused by a failure of the condenser exhaust boot seal due to aging. The root cause of exhaust boot seal failure was that past experience was not applied to the preparation of the preventative maintenance deferral of the condenser exhaust boot. Immediate corrective actions completed include cleaning the boot seal retaining areas and contact surfaces of the trough, and installing new boot seals. Planned corrective actions to prevent reoccurrence include revising the condenser exhaust boot seal replacement frequency based on operating experience and vendor recommendations. This replacement will include requirements to inspect and remove rough edges from mounting hardware and mating surfaces. All preventative maintenance deferrals prepared since June 2005 that deferred Single Point Vulnerability outage maintenance items will be reviewed to ensure technical adequacy. Additionally, plant staff will revise the Nuclear Generation Group procedure governing Preventative Maintenance and Surveillance Testing Administration to provide guidance on Single Point Vulnerability deferrals and identify the appropriate approval levels.
400 | 4002010002 | 2009-11-15 | QR6 | Manual Reactor Trip | [45 empty] | Harris | P | WE | PO | 100 | On November 15, 2009, at 100% power, the Harris plant experienced a significant oil leak from the Hydrogen Seal Oil system. A non-licensed operator notified the Main Control Room (MCR) that the handle rotated each shift by Operations on the Air Side Seal Oil self-cleaning strainer became disconnected during manual rotation after approximately 1/4 turn, resulting in the oil leak. Based on this report and due to receipt of a "Turbine Lube Oil Reservoir Low Level" alarm, a decision was made to initiate a unit shutdown. The unit was manually tripped at 22:42 by the Main Control Room Operators. The plant promptly attained normal operation no-load temperature and pressure. Following the reactor trip, when the decision was made to break condenser vacuum, the "B" steam generator Main Steam Isolation Valve (MSIV) failed to fully close on demand from its control switch, but was closed due to field actions at 23:03 by locally isolating instrument air to the valve. The root cause of the Hydrogen Seal Oil leak was that for past maintenance performed on the Air Side Seal Oil strainer, the Graded Approach to Planning and Scheduling instructions and Decision Tree was too generic. When considering the level of planning detail, the work coordination management procedure, WCM-006 does not provide guidance on considering the vulnerabilities to the plant as a result of the work being performed on the component. As a result, the thrust collars that hold the filter handle in place were not installed during past maintenance which allowed the filter handle to eject. Immediate corrective actions were to stabilize the plant, and secure the Turbine Seal Oil/Lube Oil systems to stop the leak. Aqueous foam was sprayed on the Oil to prevent a fire hazard. The oil was cleaned up and the Air Side Seal Oil strainer replaced. Planned corrective actions to prevent recurrence are to revise and implement WCM-006 such that Level "A" work activities (Quality Critical) are classified based on Equipment Classification that could cause a plant transient or shutdown and define other criteria for Level "A" (Quality Critical).
400 | 4002014001 | 2014-01-18 | QR6 | Manual Reactor Trip | [45 empty] | Harris | P | WE | PO | 75 | On January 18, 2014, while operating at 75 percent power in Mode 1, Harris Nuclear Plant manually actuated the reactor protection system to trip Unit 1 due to indications of a fire in the 480V 1D2 transformer. After the reactor trip, the auxiliary feedwater system automatically initiated and provided feedwater to the steam generators. De-energizing auxiliary bus 1D caused a temporary loss of power to the 6.9kV 1A-SA safety bus, and thus the "A" auxiliary feedwater pump which was recovered when the "A" emergency diesel generator started and re-energized the 1A-SA bus. All safety systems responded as expected during this event.<br /><br /> The root cause was determined to be a combination of age and various electro-magnetic conditions which over time led to failure of the 1D2 transformer. Corrective actions include transformer replacements and additional testing. The impact on safety due to this event is a small risk increase of approximately 3E-6/yr in delta core damage frequency.
400 | 4002016004 | 2016-10-08 | L1 | Inadvertent Closure of All MSIVs | [10 empty] | X | [28 empty] | X | [5 empty] | Harris | P | WE | HD | 0 | On October 8, 2016, the Shearon Harris Nuclear Power Plant was reducing power to enter a planned refueling outage (RFO-20). The plant was at approximately 8 percent power in Mode 1 when the unit experienced an unplanned reactor trip with a safety injection (SI) and main steam line isolation (MSLI). A malfunction of the turbine controller during turbine mechanical overspeed trip testing caused an excessive draw of steam flow from the Steam Generators (SGs). This caused the Engineering Safety Features Actuation System instruments to detect a valid change in SG pressure and initiate a rate compensated Low Steam Line Pressure signal. This signal initiated a SI and MSLI, which in turn initiated reactor trip, turbine trip, feedwater isolation, and closed the main steam isolation valves. <br /><br /> Degraded equipment within the turbine controller resulted in excessive opening of the governor valves; this was caused by an inadequate supply of hydraulic oil to meet the increased system demand during testing. Insufficient hydraulic accumulator capacity was available to support system demand. One accumulator was known to be out-of-service; a second was discovered post-event. Also, a hydraulic oil pressure switch used for turbine control was not functioning properly. The equipment deficiencies have been corrected. Changes have been made to the testing procedure to validate at least four accumulators are in service prior to testing. The Power Operation (Mode 2 to Mode 1) procedure will also be revised to validate at least four accumulators are in service. A new calibration procedure will be implemented for the deficient oil pressure switch to ensure better quality control over verifying switch function.
400 | 4002020001 | 2020-03-23 | QR5 | Turbine Trip | [45 empty] | Harris | P | WE | PO | 100 | On March 23, 2020, at 10:12 Eastern Daylight Time, Shearon Harris Nuclear Power Plant, Unit 1 (HNP), experienced an automatic reactor trip following actuation of the Reactor Protection System (RPS). The trip occurred during restoration from a planned maintenance activity that impacted the auto-stop turbine (AST) trip function of the digital electro-hydraulic system utilized for turbine control. The activity activated pressure switches in the RPS, resulting in a reactor trip. All safety systems functioned as designed. The RPS actuation also resulted in isolation of the main feedwater system and actuation of the auxiliary feedwater system on steam generator low level, an expected condition following a reactor trip. <br /><br /> The trip signal was a result of the restoration activity causing a sufficient depressurization of the AST header to activate pressure switches that feed the RPS. The restoration activity contained an erroneous sequence that reflected the recommended sequence supplied by the manufacturer of the turbine control system (TCS). The TCS was restored to functional and the unit is back online. The restoration sequence will be revised. Due to the actuation of the RPS system and auxiliary feedwater, this event is reportable per 10 CFR 50.73(a)(2)(iv).
400 | 4002020002 | 2020-08-13 | QR3 | Reactivity Control Imbalance | [45 empty] | Harris | P | WE | PO | 100 | On August 13, 2020 at 09:38 Eastern Daylight Time, with Shearon Harris Nuclear Power Plant, Unit 1 (HNP), in Mode 1 at 100 percent power, a control rod dropped during control rod drive (CRD) system surveillance testing. This required a manual reactor trip in accordance with plant procedural guidance. The reactor protection system (RPS) and auxiliary feedwater system (AFWS) actuated as designed. Based upon troubleshooting, it was determined that the control rod drop was due to the accumulation of crud in the dashpot region of the control rod drive mechanism (CRDM) movable gripper latch support assembly, which prevented the stationary gripper from latching onto the CRD shaft when the movable gripper was released. Three full-length exercises for each control rod bank were completed to remove crud from the CRDM surfaces that restored the CRDM to operable for unit startup. The dropped control rod was recovered from the reactor core and restored to the fully withdrawn position. A preventative maintenance activity to exercise the control rod banks 10 steps on a weekly frequency was implemented. Coil current traces will be obtained periodically during rod exercises to monitor for crud presence. After review, the CRD system surveillance test procedure was revised to remove the instruction to trip the reactor if a dropped rod is present with any control rods inserted into the core other than the controlling bank. In the next refueling outage, full length control rod exercises and flushing of applicable CRDMs will be completed. Due to actuation of the RPS and AFWS, this event is reportable per 10 CFR 50.73(a)(2)(iv).
400 | 4002021001 | 2020-12-16 | QR5 | Turbine Trip | [45 empty] | Harris | P | WE | PO | 80 | On December 16, 2020, at 08:51, Shearon Harris Nuclear Power Plant, Unit 1 (HNP) experienced an automatic reactor trip due to lock-out of the main generator. The generator lock-out was triggered by phase-to-phase faults that occurred on the 6.9 kilovolt non-segregated bus from the Unit Auxiliary Transformer 1B to the Auxiliary Bus 1B. <br /><br /> Based on forensics and causal analysis, the event was initiated by electrical faults impacting the non-segregated bus within a wall penetration between the Turbine Building (TB) and the Reactor Auxiliary Building (RAB). Degraded bus insulation (Noryl) combined with a medium to conduct the current (water) resulted in faults on the bus. The bus within the penetration is inaccessible and insulation had not been proactively replaced despite known degradation mechanisms. In addition, the installed configuration of the wall penetration did not match the original design and was not being maintained to ensure weather tight characteristics. Bus insulation will be replaced to ensure ongoing insulation integrity and bus penetrations will be restored to design configuration. Further actions will be taken to emphasize lessons learned from the event, including the need to proactively address known issues.
410 | 4101987031 | 1987-06-12 | QP5 | Excessive Feedwater Flow | [45 empty] | Nine Mile Pt. 2 | B | GE | SU | 3 | POWER LEVEL - 003%. ON JUNE 12, 1987 WITH NINE MILE POINT UNIT 2 IN 'STARTUP' (MODE 2) AND AT LESS THAN THREE PERCENT POWER, OPERATIONS PERSONNEL OBSERVED REACTOR WATER LEVEL RISING AND NEUTRON FLUX LEVELS INCREASING RAPIDLY. FEEDWATER LEVEL CONTROL VALVE 2FWS-LV55A WAS OBSERVED FULL OPEN. OPERATIONS PERSONNEL PLACED THE CONTROLLER IN MANUAL AND ATTEMPTED TO CLOSE THE VALVE. 2FWS-LV55A FAILED TO RESPOND. THE RESULTING COLD WATER INJECTION CAUSED INTERMEDIATE RANGE MONITOR (IRM) CHANNELS B, C, AND D TO EXCEED THEIR HIGH FLUX SCRAM POINTS DUE TO POSITIVE REACTIVITY ADDITION. THE SUBSEQUENT SCRAM OCCURRED ON JUNE 12, 1987 AT 20:56 WITH THE REACTOR AT 842 POUNDS PER SQUARE INCH GAUGE (PSIG) AND 523F. THE CAUSE OF THE EVENT HAS BEEN ATTRIBUTED TO THE FEEDBACK ARM FROM THE VALVE STEM TO THE VALVE POSITIONER UNBOLTING ALLOWING THE VALVE TO RAMP OPEN. FWS-LV55A HAS BEEN REPAIRED AND THE SUBJECT BOLT LOCKWIRED.
410 | 4101987033 | 1987-06-15 | QR8 | Spurious Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | SU | 2 | POWER LEVEL - 002%. WHILE IN THE STARTUP MODE ON JUNE 15, 1987 AT 11:33:10, A DIVISION II ALTERNATE ROD INSERTION (ARI) INITIATION WAS RECEIVED DURING PERFORMANCE OF A REDUNDANT REACTIVITY CONTROL SYSTEM (RRCS) SURVEILLANCE TEST. THE DIVISION II HIGH REACTOR PRESSURE CHANNEL B WAS TRIPPED PER THE APPROVED TEST, WHEN A SPURIOUS LOW LOW WATER LEVEL SIGNAL WAS RECEIVED ON CHANNEL A. THE SUBSEQUENT ARI INITIATION LED TO A REACTOR PROTECTION SYSTEM (RPS) SCRAM ON SCRAM DISCHARGE VOLUME (SDV) HIGH LEVEL 41 SECONDS LATER, AS EXPECTED. AFTER EXTENSIVE TROUBLESHOOTING AND TESTING OF RRCS CIRCUITRY, THE CAUSE OF THE SPURIOUS LOW LOW LEVEL TRIP COULD NOT BE DETERMINED. IMMEDIATE CORRECTIVE ACTIONS WERE TO RESET THE ARI AND RPS SCRAMS, TO ESTABLISH REACTOR COOLDOWN PER THE APPROVED PROCEDURE AND TO BEGIN TROUBLESHOOTING ACTIVITIES. FURTHER CORRECTIVE ACTIONS ARE THE REVISION OF THE RRCS SURVEILLANCE TESTS TO MINIMIZE SPURIOUS ARI INITIATIONS AND THE MONITORING OF VARIOUS RRCS SIGNALS DURING PERFORMANCE OF THE NEXT TEST TO IDENTIFY ORIGIN OF SPURIOUS SIGNALS, IF THEY RECUR.
410 | 4101987043 | 1987-07-11 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | SU | 4 | POWER LEVEL - 004%. WHILE IN THE STARTUP MODE ON JULY 11, 1987 AT APPROXIMATELY 1146 HOURS, A REACTOR SCRAM ON HIGH STEAM DOME PRESSURE OCCURRED DUE TO AN ELECTRO-HYDRAULIC CONTROL (EHC) SYSTEM TUBE RUPTURE. REACTOR PRESSURE WAS 955 PSIG AND COOLANT TEMPERATURE AT 534F. AT 1141 HOURS THE TURBINE TRIPPED ON LOW EHC FLUID PRESSURE, AND THE OPEN BYPASS VALVE BEGAN DRIFTING CLOSED. AS THE BYPASS VALVE CLOSED, REACTOR PRESSURE BEGAN INCREASING. BEFORE THE CONTROL ROOM OPERATOR COULD MANUALLY SCRAM THE REACTOR, THE REACTOR AUTO SCRAMMED ON HIGH STEAM DOME PRESSURE (1027 PSIG RECORDED). THE ROOT CAUSE FOR THE EHC TUBE FAILURE WAS EXCESSIVE VIBRATION DUE TO SPEED SIGNAL NOISE. SPEED SIGNAL NOISE INDUCED HYDRAULIC FLUID VIBRATION IN THE TUBING. CONTRIBUTING FACTORS WERE VALVE CYCLING DURING PREOPERATIONAL TESTING AND AN UNIDENTIFIED CONDITION CAUSING THE TURBINE TO ROLL OFF TURNING GEAR. IMMEDIATE CORRECTIVE ACTIONS WERE TO SECURE THE EHC SYSTEM, RESET THE SCRAM AND BRING THE UNIT TO A SHUTDOWN CONDITION PER THE APPROVED PROCEDURE. FURTHER CORRECTIVE ACTIONS WERE TO REPLACE THE RUPTURED TUBING, REDUCE SPEED SIGNAL NOISE, ADD SUPPORTS TO VERTICAL RUNS OF TUBING AND INSPECT OTHER EHC SUPPLY TUBING FOR POSSIBLE WEAK SPOTS.
410 | 4101987058 | 1987-10-01 | QP5 | Excessive Feedwater Flow | [45 empty] | Nine Mile Pt. 2 | B | GE | SU | 2 | POWER LEVEL - 002%. ON 10/1/87 AT 1213 HOURS, NINE MILE POINT UNIT 2 EXPERIENCED ACTUATION OF AN ENGINEERED SAFETY FEATURE (ESF), SPECIFICALLY, A HIGH NEUTRON FLUX SCRAM ON THE INTERMEDIAT E RANGE MONITORS (IRM). AT THE TIME OF THE EVENT, THE PLANT WAS IN THE STARTUP MODE WITH REACTOR POWER AT APPROXIMATELY 2.5% AND THE REACTOR MODE SWITCH IN THE 'STARTUP/HOT STANDBY' POSITION. REACTOR PRESSURE AND TEMPERATURE WERE APPROXIMATELY 505 PSIG AND 477F, RESPECTIVELY. THE ROOT CAUSE OF THIS EVENT WAS PERSONNEL ERROR. CORRECTIVE ACTIONS FOR THIS EVENT ARE: 1. THE INDIVIDUALS INVOLVED WITH THIS EVENT WERE IMMEDIATELY INSTRUCTED ON THE SYSTEM CHARACTERISTICS AND PARTICIPATED IN THE TRIP INVESTIGATION AND FOLLOW UP REPORT. THE EVENT WAS REVIEWED BY THE OPERATORS DURING SHIFT TURNOVERS. 2. A TRAINING MODIFICATION RECOMMENDATION HAS BEEN INITIATED TO ADDRESS THIS ISSUE. 3. A WORK REQUEST (WR# 125604) HAS BEEN WRITTEN TO INVESTIGATE/REPAIR THE CONDENSATE BOOSTER PUMP MINIMUM FLOW VALVE AND POSITION TRANSMITTER. 4. A TEMPORARY CHANGE NOTICE HAS REVISED THE OPERATING PROCEDURE N2-OP-101A GIVING INSTRUCTIONS TO MAINTAIN STEAM LOADS WITHIN THE CAPABILITY OF THE CONDENSATE LEVEL CONTROL VALVE LV-137. 5. A PROBLEM REPORT (PR# 7387) HAS BEEN SUBMITTED TO ENGINEERING TO EVALUATE LEVEL CONTROL VALVE LV-137. ENGINEERING WILL MAKE A DETERMINATION AS TO WHETHER THE VALVE IS UNDERSIZED. 6. A PROBLEM REPORT HAS BEEN INITIATED.
410 | 4101987064 | 1987-10-23 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Nine Mile Pt. 2 | B | GE | PO | 36 | POWER LEVEL - 036%. ON OCTOBER 23, 1987 AT 1142 HOURS THE TURBINE TRIPPED ON LOW CONDENSER VACUUM, RESULTING IN A REACTOR SCRAM FROM 36% POWER. A FEEDWATER PUMP WAS TAGGED OUT OF SERVICE FOR SEAL REPAIR WORK, BUT TWO MANUAL VALVES IN THE MINIMUM FLOW LINE WERE INADVERTENTLY OMITTED FROM THE MARKUP. DUE TO AN IMPROPER REVIEW OF THIS MARKUP, THE CONTROL ROOM OPERATOR GAVE PERMISSION FOR A RELAY TO BE REMOVED FOR TROUBLESHOOTING IN THE MINIMUM FLOW VALVE CONTROL CIRCUIT. REMOVAL OF THE RELAY CAUSED THE VALVE TO FAIL OPEN, PROVIDING A PATH FOR AIR INLEAKAGE THROUGH THE PUMP BODY TO THE CONDENSER. THE LOW CONDENSER VACUUM INSTRUMENTATION INITIATED A TURBINE TRIP, WHICH SUBSEQUENTLY LED TO A REACTOR SCRAM. THE ROOT CAUSE OF THE EVENT IS COGNITIVE PERSONNEL ERROR. IMMEDIATE CORRECTIVE ACTIONS WERE TO RESET THE SCRAM AT 1206 HOURS, TO FOLLOW THE SCRAM RECOVERY PROCEDURE FOR SAFE SHUTDOWN OF THE PLANT, AND TO INVESTIGATE THE CAUSE FOR THE LOW VACUUM. FURTHER CORRECTIVE ACTIONS TAKEN WERE COUNSELING FOR THE INDIVIDUAL RESPONSIBLE FOR REVIEWING THE MARKUP, ISSUANCE OF A MEMO TO OPERATIONS PERSONNEL FROM THE OPERATIONS SUPERINTENDENT EMPHASIZING ATTENTION TO DETAIL, AND FURTHER TRAINING FOR OPERATORS VIA CONTINUED TRAINING AND THE LESSONS LEARNED PROGRAM.
410 | 4101987081 | 1987-12-26 | L2 | Loss of Condenser Vacuum | [10 empty] | X | [29 empty] | X |  |  |  |  | Nine Mile Pt. 2 | B | GE | PO | 26 | POWER LEVEL - 026%. ON DECEMBER 26, 1987 AT 1218 HOURS, NINE MILE POINT UNIT 2 EXPERIENCED A REACTOR SCRAM FROM APPROXIMATELY 26% OF RATED THERMAL POWER AS A RESULT OF A TURBINE TRIP CAUSED BY LOW CONDENSER VACUUM. AT APPROXIMATELY 0800 HOURS CONTROL ROOM PERSONNEL NOTED THAT CONDENSER VACUUM WAS DECREASING AND THAT OFF GAS SYSTEM FLOW RATES WERE INCREASING. ACTIONS TAKEN BY OPERATORS TO IDENTIFY AND STOP THE SOURCE OF INLEAKAGE TO THE CONDENSER WERE UNSUCCESSFUL AND THE REACTOR SUBSEQUENTLY SCRAMMED AT 1218 HOURS ON THE TURBINE TRIP. THE ROOT CAUSE OF THIS EVENT WAS MALFUNCTION OF THE NORMAL (2HDL-FV5A) AND HIGH (2HDL-FV25A) LEVEL CONTROL VALVES OF THE FIFTH POINT FEEDWATER HEATER (2HDL-E5A). WATER LEVEL IN 2HDL-E5A WAS FLUCTUATING FROM HIGH-HIGH TO LOW LEVEL WHICH RESULTED IN A LARGE VOLUME OF WATER BEING PERIODICALLY DISCHARGED TO THE CONDENSER. THESE HYDRAULIC TRANSIENTS CAUSED THE FAILURE OF CONDENSER NOZZLE WELDS WHICH ALLOWED AIR INLEAKAGE TO THE CONDENSER. IMMEDIATE CORRECTIVE ACTIONS WERE TO RESET THE SCRAM AT 1225 HOURS, TO FOLLOW THE SCRAM RECOVERY PROCEDURE FOR SAFE SHUTDOWN OF THE PLANT, AND TO CONTINUE TO INVESTIGATE FOR THE CAUSE OF THE LOSS OF VACUUM. WORK REQUESTS HAVE BEEN COMPLETED TO REPAIR THE CRACKED WELDS AND THE LEVEL CONTROL VALVES.
410 | 4101988001 | 1988-01-20 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Nine Mile Pt. 2 | B | GE | PO | 41 | On January 20, 1988 at 0944 hours with the reactor operating at approximately 41% power, Nine Mile Point Unit 2 experienced a scram due to an actual low (Level 3) water level condition. The low water level was caused by a loss of feedwater flow to the reactor. An operator while placing a markup (tag out), valved an instrument air system prefilter out of service without ensuring that a redundant prefilter was in service. This isolated the air compressors from the remainder of the system. Instrument air pressure throughout the plant decayed to the point of causing the minimum flow valves for the condensate, condensate booster, and feedwater pumps to fail open. As a result, reduced feedwater flow to the reactor caused reactor water level to rapidly decrease to the Level 3 scram setpoint (159.3 inches). Both the High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) systems actuated on low level instrumentation which restored normal water level in the vessel. The Main Turbine-Generator also tripped due to RCIC injection. <br /><br /> Design and personnel errors were encountered during the event. Corrective actions have been implemented and/or incorporated to minimize the potential of a recurrence.
410 | 4101988014 | 1988-03-13 | P1 | Total Loss of Feedwater Flow | [10 empty] | X |  |  | X | [25 empty] | X |  |  |  |  | X | Nine Mile Pt. 2 | B | GE | PO | 43 | On March 13, 1988 at 17:39 with the reactor mode switch in Run (Operational Condition 1) and at a power level of approximately 43% (see note) rated thermal capacity, Nine Mile Point Unit 2 experienced an automatic reactor scram, an automatic initiation of the Division 3 Emergency Core Cooling System (ECCS) with a subsequent coolant injection, and the automatic actuation of several Engineered Safety Features. These events were the result of low water levels in the reactor vessel caused by a total loss of feedwater flow. An Unusual Event declared at 17:45 was terminated by 18:00 that day. The ECCS injection was manually terminated and a normal reactor shutdown was commenced by the NMP2 operators. (NOTE: Reactor power was at 98% two minutes prior to this event. However, an instrument failure caused the reactor recirculation pumps to downshift to low speed operation, decreasing reactor power to 43%.) <br /><br />The immediate cause for this event is an equipment failure. However, the root cause for this event is a design deficiency. <br /><br /> The corrective actions for this event are; (1) a temporary modification has been performed to bypass the "seal in" logic for the low pressure heater string outlet isolation valves, (2) a permanent modification will be implemented to reroute the piping for the Second Point Feedwater Heaters level switches, and (3) the failed pressure transmitter, which was replaced with an upgraded model, will be sent to the vendor for a failure mode analysis.
410 | 4101988017 | 1988-03-21 | QP5 | Excessive Feedwater Flow | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 98 | On March 21, 1988 at 1027 hours with the reactor mode switch in run (Operational Condition 1) and at a power level of approximately 97.5% rated thermal capacity, Nine Mile Point Unit 2 experienced an automatic reactor scram as a result of the main turbine trip. The turbine trip occurred when a feedwater flow transmitter was valved out of service creating increased feed flow until Level 8 was reached. (Normal turbine trip on high reactor water level.) <br /><br />The root cause of the event is that current work control procedures do not assure proper assessment of plant impact. <br /><br /> Immediate corrective action was to restore reactor water level to normal. Further corrective actions include revision of repair and trouble shooting procedures, plant impact policy issuance, lessons learned transmittals, and system design review.
410 | 4101988019 | 1988-06-02 | QP5 | Excessive Feedwater Flow | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 26 | On June 2, 1988 at 2323 hours, Nine Mile Point Unit 2 (NMP2) experienced a reactor scram at approximately 25.5% of rated thermal power. The scram was caused by turbine control valve fast closure resulting from reactor water level exceeding the high level turbine trip setpoint. The high water level was caused by sudden increase in reactor feedwater flow when a feedwater flow control valve went to the full open position. After the scram, operators brought the plant to a stable water level within 65 seconds. <br /><br />The cause of the event has been determined to be failure of the position feedback linkage of the "A" feedwater level control valve. Failure of the feedback linkage caused the valve to ramp to full open resulting in excess flow to the reactor vessel. The root cause is equipment failure due to inadequate design of the feedwater level control valve position feedback assembly. <br /><br />Immediate corrective action was for operators to complete an orderly plant shutdown. A spherical bearing in the "A" feedwater control valve which failed was replaced and the bearings for the "B" and "C" control valves were checked for wear. A problem report was initiated to modify a retainer ring in the valve feedback linkage so that failure of the spherical bearing will not lead to a complete separation of the feedback control linkage. A modification request has been initiated requesting that the Engineering Department evaluate and make appropriate changes to upgrade the reliability of the linkages. Preventive Maintenance Procedures are being developed to implement activities which will improve the reliability of 2FWS-LV10A-C.
410 | 4101988025 | 1988-06-22 | QP2 | Partial Loss of Feedwater Flow | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 98 | On June 22, 1988 at 0939 with the reactor mode switch in Run (Operational Condition 1) and at a power level of approximately 98% rated thermal capacity, Nine Mile Point Unit 2 (NMP2) experienced an automatic reactor scram and an isolation signal to the Group 4 and 5 Primary Containment Isolation Valves on a low (Level 3) reactor water level. The low reactor water level occurred as a result of a degraded feedwater flow condition caused by a feedwater level control valve (2FWS-LV10C) ramping closed. NMP2 operators subsequently restored feedwater flow to the reactor and brought level up to its normal range. The scram was reset and a normal shutdown was performed in accordance with the plant's shutdown procedure. <br /><br />The cause for this event was determined to be a failure of a solenoid valve in the 2FWS-LV10C hydraulic control unit. However, the most probable root cause for this event is a manufacturing deficiency. <br /><br />The corrective actions for this event are: (1) The solenoid valve for each feedwater level control valve hydraulic operator has been replaced; (2) Additional monitoring instrumentation has been installed on the 2FWS-LV10C control valve; (3) A Problem Report (PR) has been initiated and the component vendor has been contacted concerning the identified manufacturing deficiencies; (4) An enhanced preventative maintenance program is being developed; and (5) A PR has been initiated requesting a design evaluation.
410 | 4101988026 | 1988-06-28 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 9 | On June 28, 1988 at 2012 hours Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature, specifically, a reactor scram. At the time of the event, the plant was in a startup condition with the reactor mode switch in the "Startup/Hot Standby" Position. Reactor pressure and coolant temperature were approximately 850 pounds per square inch gauge (psig) and 527 degrees F, respectively. The reactor was operating at approximately 9% of rated thermal power. <br /><br />The scram occurred due to an Average Power Range Monitor (APRM) upscale trip. The immediate cause of the scram has been attributed to flow "changes" in the reheat system and subsequent changes in reactor steam loads. The root cause of this event has been determined to be operator error. Secondary causes of this event have been determined to be procedural deficiency and training deficiency. <br /><br /> Following the reactor scram, the Technical Specification (TS) maximum allowable cooldown rate of 100 degrees F/hour was exceeded. All applicable action requirements were met. <br /><br />Initial action was to enter into operating procedure N2-OP-101C, "Scram Recovery". Corrective action has been to modify procedure N2-OP-2, "Moisture Separator Reheater System", and to issue a Lessons Learned Transmittal to the Operations Department, and issue a Training Modification Recommendation to the Training Department.
410 | 4101988028 | 1988-07-11 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 45 | On July 11, 1988 at 0305 hours Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature, specifically a manual reactor scram. At the time of the event the reactor mode switch was in the "RUN" position with the reactor at approximately 45% of rated thermal power. <br /><br />At approximately 0037 hours on July 11, 1988 an Electrohydraulic Control (EHC) fluid leak was discovered on a turbine control valve. Attempts to isolate the leak were unsuccessful. Upon reaching the low level point in the EHC reservoir, the decision was made to manually scram the reactor. The scram was initiated at 0305 hours. <br /><br />The immediate cause of the event was a loose fitting causing an EHC fluid leak. The most probable root cause is installation deficiency by contractor personnel. <br /><br />Immediate action was to enter into operating procedure N2-OP-101C, "Scram Recovery". Corrective actions include the issuance of a work request to repair the EHC fitting leak and issuance of a Problem Report to initiate corrective actions, as required, to prevent similar occurrences.
410 | 4101988039 | 1988-08-06 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 53 | On August 6, 1988 at 2101 hours Nine Mile Point Unit 2 (NMP2) experienced an actuation of an engineered safety feature, specifically a reactor scram. At the time of the event the reactor mode switch was in the "RUN" position with the reactor at approximately 53% of rated thermal power. <br /><br /> At approximately 2053 hours Operations personnel observed that turbine Electrohydraulic Control System (EHC) pressure was decreasing rapidly. The EHC pressure decrease was due to an EHC oil leak. The low EHC oil pressure initiated a trip of the turbine resulting in an automatic reactor scram. Reactor pressure control was maintained during the event. <br /><br />The EHC oil leak was due to the failure of an EHC fluid pipe nipple. The immediate cause of the pipe failure has been attributed to excessive vibration. Vibration caused the clamp used to support the failed pipe to its support frame to fail. <br /><br />The pipe then vibrated excessively causing bending at the pump discharge piping. This resulted in fatigue stress and eventual failure. Operator actions were to secure the EHC pumps and issue a work request (WR 136781) to replace the failed pipe and secure the clamp. A work request (WR 135422) was also issued to determine the cause of the vibration.
410 | 4101988051 | 1988-09-22 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 64 | On September 22, 1988 at 1339 hours, with the reactor at approximately 64% of rated thermal power and the mode switch in "RUN", Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature (ESF). Specifically, the ESF consisted of a manual reactor scram. <br /><br />As a result of a post maintenance valve stroke on service water valve 2SWP*MOV18B, the Service Water System (SWP) was cross connected to the Reactor Building Closed Loop Cooling System (CCP). This cross connection caused loss of CCP inventory to the service water discharge header, which eventually resulted in the trip of CCP booster pumps on low suction pressure. Upon loss of CCP, the Station Shift Supervisor ordered a manual scram in accordance with N2-OP-13, "Reactor Building Closed Loop Cooling". <br /><br />The cause of this event was personnel error due to inattention to detail. Operations personnel failed to assess the impact of opening 2SWP*MOV18B with the existing system configuration. <br /><br /> Corrective actions are as follows: 1) CCP was returned to normal and hold out tags were placed on the CCP and SWP valve controls; 2) An operator aid has been added to the control room panels warning of the impact of opening the service water crosstie valves; 3) A lessons learned has been issued stressing the importance of assessing plant impact.
410 | 4101989014 | 1989-04-13 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On April 13, 1989 at 1101 hours with the reactor mode switch in RUN, and the reactor at 100% rated thermal power, Nine Mile Point Unit 2 experienced a reactor scram. This event was a result of a turbine trip due to the actuation of the generator protection circuitry. The generator protection circuitry initiated a fast transfer of house service loads to the station reserve transformers. One of the 13.8kv electrical buses failed to transfer which caused a loss of feedwater. Reactor water level decreased as the turbine control bypass valves modulated to control reactor pressure, which caused the automatic actuation of the High Pressure Core Spray (CSH) and Reactor Core Isolation Cooling (ICS) systems. <br /><br /> The cause for the turbine trip was determined to be a disconnected wire located in the main generator potential transformer cubical. This created a signal to the tripping and alarm relays causing a turbine trip. The cause for the 13.8kv bus fast transfer failure was determined to be the positive interlocking roller for the breaker not fully engaged. <br /><br /> Corrective actions include: (1) Relanded the disconnected wire and tightened other potential transformer connections; (2) Revising the electrical maintenance procedure (N2-EPM-GMS-R693) to check connection integrity in high vibration areas; (3) Issuing a lessons learned transmittal outlining the problems encountered during this event.
410 | 4101989009 | 1989-04-22 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 100 | On April 22, 1989 at 1941 hours, Nine Mile Point Unit 2 (NMP2) experienced a reactor scram as a result of a neutron monitoring system trip.<br /><br /> Specifically, when preparing to perform weekly Turbine Backup Overspeed Trip Testing an operator keyed a radio within the vicinity of the Electro Hydraulic Control (EHC) cabinet. This action caused EHC system disturbances resulting in inadvertent movements of the Turbine Control and Bypass valves. This malfunction created a pressure spike which caused all six Average Power Range Monitors (APRMs) to exceed their upscale trip setpoint.<br /><br /> At the time of the event Reactor Power was at 100% rated thermal power. <br /><br /> The root cause for this event was Human Performance Problems. <br /><br /> Corrective actions taken for this event were: (1) Issuance of a Training Modification Request to ensure appropriate personnel are aware of potential problems with radio use; (2) Installation of permanent Caution signs at each entrance to the Relay Room; and (3) Issuance of a memorandum from the Station Superintendent to all station personnel concerning use of radios/beepers. In addition, other areas of the station which have been identified as radio transmission sensitive have been posted.
410 | 4101989024 | 1989-09-08 | QR6 | Manual Reactor Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 88 | At 18:00:45 hours on September 8, 1989, with the Reactor Mode Switch in "RUN of and the Reactor at 88% rated thermal power (930 MWe), Nine Mile Point #2 experienced a downshift of Reactor Recirculation Pumps to slow speed. This placed the unit above the 100% rod line with core flow <45% (restricted area of operation). The control room annunciators notified the operations personnel of the downshift. Operations personnel immediately performed the required actions per N2-OP-29, Reactor Recirculation System, by placing the reactor mode switch to "SHUTDOWN", initiating a reactor scram. Operations personnel proceeded with scram recovery per N2-OP-101C, Plant Shutdown. 10CFR50.72 notification was made on September 8, 1989, at 2013. <br /><br /> The root cause for recirculation pump trip is a failure of a 24 volt DC power supply (C33A-K613) within the Feedwater Control System. Corrective action was to replace the faulty power supply.
410 | 4101989035 | 1989-10-13 | QL7 | Degraded condenser vacuum | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 54 | On October 13, 1989, at 0949 hours Nine Mile Point Unit 2 (NMP2) experienced an actuation of an Engineered Safety Feature (ESF), specifically an automatic Reactor scram as a result of a main turbine trip. At the time of the event, the reactor was operating at 54% rated power with the mode switch in "RUN" (Operational Condition 1).<br /><br /> The root cause was determined to be personnel error in that an adequate evaluation of plant impact was not performed. A contributing cause was failure of administrative procedures to address a comprehensive plant impact review. <br /><br /> Control Room operators carried out immediate corrective actions. Other corrective actions include revision of plant impact evaluation form and repair of motor generator logic circuit. The responsible Chief Shift Operator (CSO) was directed to write a Special Report concerning this event. Meetings were held to stress the importance of plant impact evaluations. Administrative procedures will be revised. A Lessons Learned transmittal will be issued.
410 | 4101989036 | 1989-10-18 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | SU | 1 | On October 18, 1989, at 06:15:41 hours, Nine Mile Point Unit 2 (NMP2) experienced an Upscale Trip of the Intermediate Range Monitors (IRMs) resulting in an automatic actuation of the Reactor Protection System (RPS) and a full reactor scram. <br /><br /> At the time of the event, the reactor mode switch was in the START/HOT STBY position with reactor power in the Intermediate Range (1%). <br /><br /> The root cause for this event was determined to be inadequate control of activities associated with the Plant Shutdown on the part of Control Room personnel. A contributing factor was a procedural deficiency. Corrective actions include (1) instructing operating shift personnel on this event, (2) revising the Operations training program, and (3) revising Plant Shutdown Procedure N2-OP-101C.
410 | 4101989040 | 1989-12-01 | QR4 | Core Power Excursion (RPS Trip) | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 97 | On December 1, 1989, Nine Mile Point Unit 2 (NMP2) was operating at approximately 97% rated thermal power with the mode switch in the "RUN" position (Operational Condition 1). At 1310 hours, NMP2 experienced an automatic Reactor Scram caused by Average Power Range Monitor (APRM) high neutron flux signals on both divisions of the Reactor Protection System (RPS). At 1313 hours, the turbine was tripped on reverse power by the main generator antimotoring device. <br /><br /> Immediate corrective actions were taken by Operations to carry out all scram recovery actions and to place the plant in a stable "HOT SHUTDOWN" mode (Operational Condition 3). Operations then initiated an investigation of the event. <br /><br /> The immediate cause was a malfunction of the Electrohydraulic Control System (EHC) which resulted in the power transient that caused the scram. <br /><br /> Corrective action was to replace 3 relay boards in the EHC control circuit and correct a ground loop in the turbine speed sensing circuit.
410 | 4101990009 | 1990-05-14 | D1 | Loss of Instrument or Control Air System |  |  |  | X | [15 empty] | X | [25 empty] | Nine Mile Pt. 2 | B | GE | PO | 45 | On May 14, 1990, at approximately 2052 hours, with the reactor mode switch in the "RUN" position and the reactor operating at 100% rated thermal power, Nine Mile Point Unit 2 (NMP2) was experiencing numerous off-normal plant conditions. Operations personnel were responding to several abnormal Offgas System (OFG) indications and alarms, and Main Condenser vacuum was decreasing. At approximately 2058 hours, operators initiated reactor power reduction in response to decreasing condenser vacuum. At 2119 hours with reactor power at approximately 45% rated thermal power, the reactor mode switch was placed in the "SHUTDOWN" position, initiating a reactor scram. <br /><br /> The cause of this event was the partial loss of the Instrument Air System (IAS) due to pipe failure induced by stress-corrosion cracking. Immediate corrective actions included: performing a walkdown of the suspected branch of the IAS to locate source of air loss; generating a Work Request to replace the failed air line; and requesting a failure analysis be performed to identify cause of pipe failure.
410 | 4101990013 | 1990-09-05 | QR5 | Turbine Trip | [45 empty] | Nine Mile Pt. 2 | B | GE | PO | 64 | On September 5, 1990, at 0400 hours, with the Reactor Mode Switch in "RUN" and at approximately 64% rated thermal power (645 MWE), Nine Mile Point Unit 2 experienced an Engineered Safety Feature actuation. Specifically, an automatic reactor scram caused by a Turbine Generator trip which was initiated by a Generator field ground. <br /><br /> The root cause investigation determined that the most probable cause of the generator field ground was leakage current through the insulating teflon tubes in the power rectifier cubicles. <br /><br /> The immediate corrective action was to respond to the reactor scram and turbine trip in accordance with plant procedures. A Work Request was issued to investigate the Turbine Generator field ground. A plant change request to install a meter to monitor ground leakage current is being evaluated. In the interim, the resistance across the rectifier tube banks will be measured during each forced and planned outage.